## Appendix A Status Report
MTEP Approved (Appendix A) Quarterly Status Report through 5/12/2026
Project Level Fields | [6 empty] | Facility Level Fields
Target MTEP Cycle | Current Appendix | Submitting TO | Planning Region | MTEP Project ID | Project | Project Type | Facility ID | Name | Facility Description | Facility Owner(s) | Planning Status | Current Cost | Expected ISD | Facility Type | Facility Sub-Type | From Sub | To Sub | Circuit ID | Max kV | Min kV | Miles New | Miles Upgrade | State 1 | State 2 | Cost Shared Status
MTEP26 | A | HOOSIER ENERGY | Central | 51051 | New Greensburg 138 kV Load Addition | Other | 51899 | New Greensburg Load | Construct a new 138 kV ring bus on the Decatur – Honda 138 kV line to serve a new large load. The new large load has a total estimated load of 50 MW at 95% PF (52.6 MVA, 16.43 MVAR). |  | M2 - Appendix A Approved | 11100000 | 2028-07-01 | Substation | Switching station (breakers only, no transformer) | New Greensburg Load |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | AMERICAN TRANSMISSION COMPANY | West | 51057 | Ozaukee County, DIC, New Substations | Other | 51925 | Ozaukee County DIC Project | Interconnection |  | M3 - Under Construction | 1300000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Decker | Cedar Creek Junction |  | 345 |  |  |  | WI |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51926 | Gilbert Switching Station Equipment Replacement | Gilbert Switching Station has many instances of equipment in the station that need replacement. This includes a breaker, arrestors, batteries, battery charger, switches, motor operated switches, current transformers, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 200000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | GILBERT 115KV SWITCHING STATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51927 | HOLTON 115KV SUBSTATION | Holton station has many instances of equipment in the station that are in need of replacement. This includes arrestors, batteries, current transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 120000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | HOLTON 115KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51928 | Landry 230/115kV Substation | Landry station has many instances of equipment in the station that are in need of replacement. This includes arrestors, switches, and motor operated switches. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 340686 | 2026-12-31 | Substation | Small miscellaneous substation equipment | LANDRY 230/115KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51929 | LANDRY 230/115KV SUBSTATION - REFURBISH TRANSFORMERS | All transformers at Landry are in need of significant refurbishment. This project will provide for a refurbishment of the ancillary and exterior systems of the transformers |  | M2 - Appendix A Approved | 1093513 | 2026-12-31 | Transformer | Transformer Replacement | LANDRY 230/115KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51930 | LOG CABIN 115KV SWITCHING STATION | Log Cabin Bulk Switching Station has many instances of equipment in the station that need replacement. This includes battery charger, switches, motor operated switches, current transformers, potential transformers, carrier equipment, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 100000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | LOG CABIN 115KV SWITCHING STATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51931 | MARION 115KV SWITCHING STATION | Marion station has many instances of equipment in the station that are in need of replacement. This includes arrestors, breakers, current transformers, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 315000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | MARION 115 KV SWITCHING STATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51932 | MOSS BLUFF 230/69KV SUBSTATION | Moss Bluff station has many instances of equipment in the station that are in need of replacement. This includes arrestors, breakers, current transformers, potential transformers, arresters, communication equipment, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 2000000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | MOSS BLUFF 230/69KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51933 | PINE CLIFF 115KV SUBSTATION | Pine Cliff Substation has many instances of equipment in the station that need replacement. This includes breakers, arrestors, battery charger, switches, motor operated switches, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 100000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | PINE CLIFF 115KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51934 | PINE CLIFF 115KV SUBSTATION - REFURBISH TRANSOFRMERS | All transformers at Pine Cliff are in need of significant refurbishment. This project will provide for a refurbishment of the ancillary and exterior systems of the transformers. |  | M2 - Appendix A Approved | 1488080 | 2026-12-31 | Substation | Small miscellaneous substation equipment | PINE CLIFF 115KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51058 | 1803 - 2026 Age and Condition Program | Other | 51935 | TALISHEEK 230/69KV SUBSTATION | Talisheek station has many instances of equipment in the station that are in need of replacement. This includes arrestors, batteries, switches, motor operated switches, current transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 300000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | TALISHEEK 230/69KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51936 | GILBERT 115KV SWITCHING STATION | Gilbert Switching Station has many instances of equipment in the station that need replacement. This includes a breaker, arrestors, batteries, battery charger, switches, motor operated switches, current transformers, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 872000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | GILBERT 115KV SWITCHING STATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51937 | HOLTON 115/69KV SUBSTATION | Holton station has many instances of equipment in the station that are in need of replacement. This includes arrestors, batteries, current transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 980513 | 2027-12-31 | Substation | Small miscellaneous substation equipment | HOLTON 115/69KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51938 | LOG CABIN 115KV SWITCHING STATION | Log Cabin Bulk Switching Station has many instances of equipment in the station that need replacement. This includes battery charger, switches, motor operated switches, current transformers, potential transformers, carrier equipment, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 1008000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | LOG CABIN 115KV SWITCHING STATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51939 | MARION 115KV SWITCHING STATION | Marion station has many instances of equipment in the station that are in need of replacement. This includes arrestors, breakers, current transformers, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 439364 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | Marion 115kV Switching Station |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51940 | MOSS BLUFF 230/69KV SUBSTATION | Moss Bluff station has many instances of equipment in the station that are in need of replacement. This includes arrestors, breakers, current transformers, potential transformers, arresters, communication equipment, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 2052522 | 2027-12-31 | Substation | Small miscellaneous substation equipment | MOSS BLUFF 230/69KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51941 | PINE CLIFF 115/69KV SUBSTATION | Pine Cliff Substation has many instances of equipment in the station that need replacement. This includes breakers, arrestors, battery charger, switches, motor operated switches, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 1583000 | 2027-12-31 | Substation | Small miscellaneous substation equipment | PINE CLIFF 115/69KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51942 | TALISHEEK 230/69KV SUBSTATION | Talisheek station has many instances of equipment in the station that are in need of replacement. This includes arrestors, batteries, switches, motor operated switches, current transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 2808180 | 2027-12-31 | Substation | Small miscellaneous substation equipment | TALISHEEK 230/69KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51059 | 1803 - 2027 Age and Condition Program | Other | 51943 | METROPOLIS 115KV SUBSTATION | The battery charger at Metropolis is in need of replacement. This project will replace the battery charger. |  | M2 - Appendix A Approved | 98072 | 2027-12-31 | Substation | Small miscellaneous substation equipment | METROPOLIS 115KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 50746 | 1803 - 2025 Age and Condition Program | Other | 51944 | LANDRY 230/115KV SUBSTATION - REFURBISH TRANSFORMERS | All transformers at Landry are in need of significant refurbishment. This project will provide for a refurbishment of the ancillary and exterior systems of the transformers |  | M2 - Appendix A Approved | 100000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | LANDRY 230/115KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 50746 | 1803 - 2025 Age and Condition Program | Other | 51945 | PINE CLIFF 115/69KV SUBSTATION - REFURBISH TRANSFORMERS | All transformers at Pine Cliff are in need of significant refurbishment. This project will provide for a refurbishment of the ancillary and exterior systems of the transformers |  | M2 - Appendix A Approved | 300000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | 115 |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51063 | ANGIE 230/69KV SUBSTATION - 230KV LINE BREAKER ADDITIONS | Other | 51954 | ANGIE 230/69KV SUBSTATION | ADD 230KV LINE BREAKERS AND ASSOCIATED EQUIPMENT |  | M2 - Appendix A Approved | 1902000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | ANGIE 230/69KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51064 | HOLTON 115/69KV SUBSTATION - 115KV LINE BREAKER ADDITIONS AND 69KV BUS TIE BREAKER ADDITION | Other | 51955 | HOLTON 115/69KV SUBSTATION | ADD 115KV LINE BREAKERS, A 69KV BUS TIE BREAKER, AND ASSOCIATED EQUIPMENT |  | M2 - Appendix A Approved | 2860000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | HOLTON 115/69KV SUBSTATION |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51065 | TALISHEEK 230KV LINE BREAKER ADDITIONS AND 69KV BUS TIE BREAKER ADDITION | Other | 51956 | TALISHEEK 230/69KV SUBSTATION | ADD 230KVV LINE BREAKERS, A 69KV BUS TIE BREAKER, AND ASSOCIATED EQUIPMENT TO THE EXISTING 1803 TALISHEEK 230/69KV SUBSTATION |  | M2 - Appendix A Approved | 4646000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | TALISHEEK 230/69KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 51070 | EAST MANDEVILLE 230/69KV SUBSTATION | Other | 51961 | EAST MANDEVILLE 230/69KV SUBSTATION | CONSTRUCT A NEW 230/69KV SUBSTATION ON THE EAST SIDE OF MANDEVILLE |  | M2 - Appendix A Approved | 16892500 | 2028-12-01 | Substation | Distribution substation - may include trans high side | MANDEVILLE 230KV SUBSTATION |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 51079 | New Project Raider Load Substation 345 kV | Other | 51997 | New 345kV Substation | New 345kV breaker-and-a-half substation on the 10POSEY345 (253787) – 08GIBSON (249510) transmission line. The new station will be approximately 8 line-miles from the Posey substation. |  | M2 - Appendix A Approved | 29900000 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | 10POSEY345 | 08GIBSON |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 51086 | New Load on Existing HUC Plant 2 69 kV sub | Other | 52001 | New Load on Existing HUC Plant 2 69 kV sub - Distribution Connection | Add new 20 MW data center load to existing sub via distribution connection. |  | M2 - Appendix A Approved | 0 | 2026-11-30 | Substation | Distribution substation - may include trans high side | HUC Plant 2 |  |  | 69 |  | 0 | 0 | MN |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52007 | Indian Creek West 161 kV Substation | Construct new Indian Creek West 161 kV Substation. |  | M2 - Appendix A Approved | 26000000 | 2028-07-01 | Substation | Substation (breakers only, no transformer) | Indian Creek West |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52008 | CBEC-Indian Creek East 161 kV Line Taps | Bisect the CBEC-Indian Creek East 161 kV line and bring two 161 kV lines into the Indian Creek West Substation. |  | M2 - Appendix A Approved | 1500000 | 2028-07-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | CBEC | Indian Creek East |  | 161 |  | 0.3 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52009 | Fox Run 345-161 kV Substation | Construct new Fox Run 345-161 kV Substation. |  | M2 - Appendix A Approved | 45000000 | 2029-07-01 | Transformer | Transformer New | Fox Run |  |  | 345 | 161 |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52010 | CBEC-S3456 345 kV Line Taps | Bisect the CBEC-S3456 345 kV line and bring two 345 kV lines into the Fox Run Substation. |  | M2 - Appendix A Approved | 4000000 | 2029-07-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | CBEC | S3456 |  | 345 |  | 1.4 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52011 | CBEC-S1206 161 kV Line Taps | Bisect the CBEC-S1206 161 kV line and bring two 161 kV lines into the Fox Run Substation. |  | M2 - Appendix A Approved | 3500000 | 2029-07-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | CBEC | S1206 |  | 161 |  | 1.8 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52012 | Indian Creek West-Fox Run 161 kV Line | Construct a new 161 kV line between Indian Creek West and Fox Run Substations. |  | M2 - Appendix A Approved | 8500000 | 2029-07-01 | Line New | New Transmission line, new ROW - may include terminations | Indian Creek West | Fox Run |  | 161 |  | 3 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52013 | Sub 701 and Sub 702 Terminal Upgrades | Replace terminal equipment at Sub 701 and Sub 702. |  | M2 - Appendix A Approved | 300000 | 2029-07-01 | Substation | Small miscellaneous substation equipment | Sub 701 | Sub 702 |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52014 | Sub 701-Sub 702 161 kV Line Uprate | Replace structures on the Sub 701-Sub 702 161 kV line. |  | M2 - Appendix A Approved | 300000 | 2029-07-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sub 701 | Sub 702 |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52015 | Sub 701-S1211 161 kV Line Rebuild | Rebuild the Sub 701-S1211 161 kV line. |  | M2 - Appendix A Approved | 10000000 | 2029-07-01 | Line Upgrade | Line rebuild on existing ROW | Sub 701 | S1211 |  | 161 |  |  | 7 | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51087 | Indian Creek West 161 kV Substation & Associated Upgrades | Other | 52016 | River Bend Substation Add 161 kV Breakers and Associated Work | At River Bend Substation add 161 kV breakers and associated equipment. Additionally, upgrade the ground grid at River Bend Substation. |  | M2 - Appendix A Approved | 4000000 | 2029-07-01 | Substation | Substation (breakers only, no transformer) | River Bend |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51088 | New Morgan County 345/69 kV Transmission Station and 69 kV Line | Other | 52017 | 345 kV Ring Bus Station | Construct a new 345 transmission station as a four position ring bus. |  | M2 - Appendix A Approved | 19900000 | 2030-12-01 | Substation | Switching station (breakers only, no transformer) | Morgan County |  |  | 345 | 69 |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51088 | New Morgan County 345/69 kV Transmission Station and 69 kV Line | Other | 52018 | Morgan Co - Mooresville 69 kV Line | Construct an new 3.65 mile 69 kV line from Morgan County 69 kV station to the HE Mooresville tap line. This will interconnect the new station to the existing 69 kV system. |  | M2 - Appendix A Approved | 6570000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Morgan County | Mooresville |  | 69 |  | 3.65 |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51089 | New Jennings County 161/69 kV Transmission Station and 69 kV Line | Other | 52019 | Jennings County 161 kV Ring Bus | Construct a 161 kV four position ring bus near the existing Selmier Junction. |  | M2 - Appendix A Approved | 12100000 | 2028-12-01 | Substation | Switching station (breakers only, no transformer) | Jennings County |  |  | 161 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51089 | New Jennings County 161/69 kV Transmission Station and 69 kV Line | Other | 52020 | Jennings County - Waynesville 69 kV Line | Construct a new 69 kV line from the new Jennings County 69 kV transmission station to the Waynesville 69 kV transmission station. |  | M2 - Appendix A Approved | 32220000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Jennings County | Waynesville |  | 69 |  | 17.9 |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51090 | New St.Joesph to Northside 138 kV Line and 138/12 kV Station | Other | 52021 | St.Joseph - Northside 138 kV Line | Construct a new 7 mile 138 kV transmission line from St. Joseph to LGEE Northside 138 kV station. Construct a new 138 kV position at each station for the new line terminals. |  | M2 - Appendix A Approved | 14000000 | 2028-03-01 | Line New | New Transmission line, new ROW - may include terminations | Speed | Northside |  | 138 |  | 9 |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51090 | New St.Joesph to Northside 138 kV Line and 138/12 kV Station | Other | 52022 | Payne Koehler 138/12 kV Substation | Construct a new 138/12 kV distribution station near the Hamburg exit on I-65 on the new Speed - Northside 138 kV line. |  | M2 - Appendix A Approved | 3800000 | 2028-03-01 | Substation | Distribution substation - may include trans high side | Payne Koehler |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51088 | New Morgan County 345/69 kV Transmission Station and 69 kV Line | Other | 52023 | 345/69 kV Transformer | One 193 MVA 345/69 kV transformer. |  | M2 - Appendix A Approved | 10000000 | 2030-12-01 | Transformer | Transformer New | Morgan County |  |  | 345 | 69 |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51088 | New Morgan County 345/69 kV Transmission Station and 69 kV Line | Other | 52024 | 69 kV switching station | Construct a three breaker 69 kV ring bus. |  | M2 - Appendix A Approved | 7800000 | 2030-12-01 | Substation | Switching station (breakers only, no transformer) | Morgan County |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51089 | New Jennings County 161/69 kV Transmission Station and 69 kV Line | Other | 52025 | 161/69 kV Transformer | One 81 MVA 161/69 kV transformer |  | M2 - Appendix A Approved | 4739000 | 2028-12-01 | Transformer | Transformer New | Jennings County |  |  | 161 | 69 |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51089 | New Jennings County 161/69 kV Transmission Station and 69 kV Line | Other | 52026 | 69 kV Ring Bus | Construct a three position 69 kV ring bus as part of the transmission station. |  | M2 - Appendix A Approved | 7800000 | 2028-12-01 | Substation | Switching station (breakers only, no transformer) | Jennings County |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51093 | New Gill 345 kV Station and 345 kV Lines | Other | 52027 | Expand Gill into 12-breaker 345kV BAAH Station | Expand Gill into 12-breaker 345kV BAAH Station |  | M2 - Appendix A Approved | 60000000 | 2028-01-01 | Substation | Switching station (breakers only, no transformer) | Gill |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51093 | New Gill 345 kV Station and 345 kV Lines | Other | 52028 | Re-route HE Worthington line into station | Re-route HE Worthington line into Gill station (0.5 mi) |  | M2 - Appendix A Approved | 1800000 | 2028-01-01 | Line New | New Transmission line, new ROW - may include terminations | Gill |  |  | 345 |  | 0.5 |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51093 | New Gill 345 kV Station and 345 kV Lines | Other | 52029 | Re-route Duke Gibson line into station | Re-route Duke Gibson line into Gill station (1.1 mi) |  | M2 - Appendix A Approved | 3900000 | 2028-01-01 | Line New | New Transmission line, new ROW - may include terminations | Gill |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51093 | New Gill 345 kV Station and 345 kV Lines | Other | 52030 | Re-route IPL Sullivan-Petersburg into station | Re-route IPL Sullivan-Petersburg into station (about 1.4 miles) |  | M2 - Appendix A Approved | 4900000 | 2028-01-01 | Line New | New Transmission line, new ROW - may include terminations | Gill |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51093 | New Gill 345 kV Station and 345 kV Lines | Other | 52031 | Upgrade 345kV switches at Merom (12 total) | Upgrade 345kV switches at Merom (12 total) |  | M2 - Appendix A Approved | 1200000 | 2028-01-01 | Substation | Small miscellaneous substation equipment | Merom |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51093 | New Gill 345 kV Station and 345 kV Lines | Other | 52032 | 345kV Line from Merom to Gill | 345kV Line from Merom to Gill (1-mile) |  | M2 - Appendix A Approved | 3500000 | 2028-01-01 | Line New | New Transmission line, new ROW - may include terminations | Merom | Gill |  | 345 |  | 1 |  | IN |  | Not Shared
MTEP26 | A | DUKE ENERGY INDIANA, LLC | Central | 51103 | New Westwood to LEAP 345 kV Lines | BRP | 52044 | AEP Dequine - Westwood - Mechanicsburg - LEAP 345kV Lines | Construct new ~35mi double circuited 345kV line from Westwood to new Mechanicsburg station at 954 ACSS @ 200C or 4000A equivalent conductor for a rating of 2432MVA per line. Construct new ~10mi double circuited 345kV line from new Mechanicsburg substation into LEAP. Upgrade AEP Dequine to Westwood 2.63 miles to 6-wire using existing 345 ckts. combined in parallel and build additional new higher capacity ckt.; Substation expansions/reconfig at Dequine/Westwood |  | M2 - Appendix A Approved | 250300000 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | AEP Dequine | WVPA LEAP |  | 345 |  | 92.6 | 2.63 | IN |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 51113 | Upgrade Montgomery 345 kV terminal equipment | BRP | 52055 | Upgrade Montgomery 345 kV Terminal Equipment | Upgrade Montgomery 345 kV Terminal Equipment |  | M2 - Appendix A Approved | 5000000 | 2029-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Montgomery |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 51114 | Apply Pike – Peno Creek 161 kV E3X | BRP | 52056 | Pike-Peno Creek 161 kV | Pike-Peno creek 161 kV |  | M2 - Appendix A Approved | 800000 | 2029-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Pike | Peno Creek |  | 161 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50738 | New Load Addition at New Yoshi 345 kV substation | Other | 52059 | New Yoshi 345 kV substation | New Yoshi 345 kV substation |  | M2 - Appendix A Approved | 25000000 | 2028-12-01 | Substation | Switching station (breakers only, no transformer) | Yoshi |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50738 | New Load Addition at New Yoshi 345 kV substation | Other | 52060 | Yoshi-Scarlet 345 kV line | Yoshi-Scarlet 345 kV line |  | M2 - Appendix A Approved | 28000000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Yoshi | Scarlet |  | 345 |  | 10 |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50738 | New Load Addition at New Yoshi 345 kV substation | Other | 52061 | Yoshi-Elkhorn 345 kV line | Yoshi-Elkhorn 345 kV line |  | M2 - Appendix A Approved | 28000000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Yoshi | Elkhorn |  | 345 |  | 20 |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50738 | New Load Addition at New Yoshi 345 kV substation | Other | 52062 | Yoshi-Lumberjack 345 kV line | Yoshi-Lumberjack 345 kV line |  | M2 - Appendix A Approved | 28000000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Yoshi | Lumberjack |  | 345 |  | 20 |  | MO |  | Not Shared
MTEP26 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50735 | New RECC Load Addition at Mogul 345 kV substation (Phase 2) | Other | 52063 | New Position at Mogul 345 kV | New Position at Mogul 345 kV |  | M2 - Appendix A Approved | 1200000 | 2028-12-01 | Substation | Substation bus upgrade | Mogul |  |  | 345 |  |  |  | IL |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50737 | New Load Addition at New Elkhorn 345 kV substation (Elkhorn Phase 2) | Other | 52065 | New Nightingale 345 kV substation | New Nightingale 345 kV substation |  | M2 - Appendix A Approved | 25000000 | 2028-12-01 | Substation | Switching station (breakers only, no transformer) | Nightingale |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50737 | New Load Addition at New Elkhorn 345 kV substation (Elkhorn Phase 2) | Other | 52066 | New Lumberjack-Odyssey and Lumberjack-Montgomery 345 kV lines | New Lumberjack-Odyssey and Lumberjack-Montgomery 345 kV lines |  | M2 - Appendix A Approved | 15000000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Lumberjack | Montgomery/Odyssey |  | 345 |  | 3.25 |  | MO |  | Not Shared
MTEP26 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50736 | New Load Addition at Austin 345 kV substation | Other | 52067 | New Positions at Austin 345 kV | New Positions at Austin 345 kV |  | M2 - Appendix A Approved | 12000000 | 2028-12-01 | Substation | Substation bus upgrade | A |  |  | 345 |  |  |  | IL |  | Not Shared
MTEP26 | A | AMEREN ILLINOIS | Central | 50885 | New CADC 138 kV Ring bus | Other | 51692 | Project CADC 138 kV Ring Bus | Project CADC 138 kV Ring Bus |  | M2 - Appendix A Approved | 24100000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | Project CADC |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50743 | New Elkhorn 280 MVAR Cap Bank | BRP | 52057 | 280 MVAR Cap Bank | 280 MVAR Cap Bank |  | M2 - Appendix A Approved | 12000000 | 2028-12-01 | Voltage Device | Capacitor (switched capacitor) | Elkhorn |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50791 | New Project Point 345 kV BAAH substation | Other | 52089 | Reconductor Boyd Branch-Saint Francois 138 kV | Reconductor Boyd Branch-Saint Francois 138 kV |  | M2 - Appendix A Approved | 6825000 | 2029-12-01 | Line Upgrade | Line reconductor | Reconductor Boyd Branch | Saint Francois |  | 138 |  |  | 7 | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50791 | New Project Point 345 kV BAAH substation | Other | 52090 | Reconductor Joachim-Boyd Branch138 kV | Reconductor Joachim-Boyd Branch138 kV |  | M2 - Appendix A Approved | 11700000 | 2029-12-01 | Line Upgrade | Line reconductor | Reconductor Joachim | Boyd Branch |  | 138 |  |  | 12 | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50791 | New Project Point 345 kV BAAH substation | Other | 52091 | Reconductor Joachim-Saint Francois 138 kV | Reconductor Joachim-Saint Francois 138 kV |  | M2 - Appendix A Approved | 18525000 | 2029-12-01 | Line Upgrade | Line reconductor | St Francois | Joachim |  | 138 |  |  | 19 | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50791 | New Project Point 345 kV BAAH substation | Other | 52092 | Reconductor Rush Island-Joachim 345 kV | Reconductor Rush Island-Joachim 345 kV |  | M2 - Appendix A Approved | 30750000 | 2029-12-01 | Line Upgrade | Line reconductor | Rush Island | Joachim |  | 345 |  |  | 5.5 | MO |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52104 | Benton - Install New 345 kV Station #1 | Build a new 345kV 6-row BAAH configuration station. Install 20 345kV, 3000A breakers with at least 63kA interrupting capability and all associated equipment. |  | M2 - Appendix A Approved | 38405000 | 2027-11-30 | Substation | Substation (breakers only, no transformer) | Benton |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52105 | Majestic - Lemoyne OHL Cut-In | Cut in the Lemoyne-Majestic 345kV line into the new station #1. |  | M2 - Appendix A Approved | 3125000 | 2027-11-30 | Line New | New Transmission line, new ROW - may include terminations | Majestic | Lemoyne |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52106 | Majestic-Milan OHL Cut-In | Cut in the Majestic-Milan 345 kV line into the new station #1. |  | M2 - Appendix A Approved | 3125000 | 2027-11-30 | Line New | New Transmission line, new ROW - may include terminations | Majestic | Milan |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52107 | Majestic-Milan OHL Cut-In | Cut in the Majestic-Milan 345kV line into the new station #1. |  | M2 - Appendix A Approved | 3125000 | 2027-11-30 | Line New | New Transmission line, new ROW - may include terminations | Majestic | Milan |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52108 | Benton - Install New 345 kV Station #2 | Build a new 345kV 6-row BAAH configuration station. Install 20 345kV, 3000A breakers with at least 63kA interrupting capability and all associated equipment. |  | M2 - Appendix A Approved | 38405000 | 2027-11-30 | Substation | Substation (breakers only, no transformer) | Benton |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52109 | Majestic-Milan_New Station #2 OHL Cut-In | Cut the existing Majestic-Milan 345kV line into the new Stargate Station #2. |  | M2 - Appendix A Approved | 3125000 | 2027-11-30 | Line New | New Transmission line, new ROW - may include terminations | Majestic | Milan |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 51134 | Project Benton | Other | 52110 | Majestic-Lemoyne_New Station #2 OHL Cut-In | Cut the existing Majestic-Lemoyne 345kV line into the new Stargate Station #2. |  | M2 - Appendix A Approved | 3125000 | 2027-11-30 | Line New | New Transmission line, new ROW - may include terminations | Majestic | Lemoyne |  | 345 |  |  |  | MI |  | Not Shared
MTEP26 | A | ENTERGY MISSISSIPPI, LLC. | South | 51146 | CCS 115 kV Station | Other | 52121 | CCS Substation | New Radial 115 kV substation on the Yazoo City SS to MS Chemical line. |  | M2 - Appendix A Approved | 8200000 | 2027-07-01 | Substation | Switching station (breakers only, no transformer) | Yazoo City | MS Chemical | 1 | 115 |  | 2 |  | MS |  | Not Shared
MTEP26 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 51148 | New Trail Creek 138 kV Load Addition | Other | 52122 | Trail Creek Load Addition | 300MW served at Trail Creek 138kV substation. |  | M2 - Appendix A Approved | 12000000 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Trail Creek |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 51141 | New Hobart 345 kV Load Addition | Other | 52123 | Hobart Load Addition | 1500MW Load Addition that will loop into 345kV circuit Lake George-Schahfer. A new line will be built from Green Acres to the load addition site |  | M2 - Appendix A Approved | 60000000 | 2027-03-01 | Line New | New Transmission line, new ROW - may include terminations | Green Acres |  |  | 345 |  | 5.5 |  | IN |  | Not Shared
MTEP26 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 51142 | New Schahfer 345 kV Load Addition | Other | 52124 | Schahfer Load Addition | 800MW Load addition at Schahfer 345kV substation. |  | M2 - Appendix A Approved | 31000000 | 2027-03-01 | Substation | Substation (breakers only, no transformer) | Schahfer |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 51149 | New Project Raider Cap Banks 69 kV | BRP | 52127 | Culley 69kV Cap Banks | Adding 2 32.2MVAR cap banks to the Culley 69kV substation |  | M2 - Appendix A Approved | 2700000 | 2027-06-01 | Voltage Device | Capacitor (switched capacitor) | Culley |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP26 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 51149 | New Project Raider Cap Banks 69 kV | BRP | 52128 | Northwest 69kV Cap Bank Addition | Adding 2 15.6MVAR cap banks to the Northwest 69kV substation |  | M2 - Appendix A Approved | 1200000 | 2027-06-01 | Voltage Device | Capacitor (switched capacitor) | Northwest |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP26 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 51149 | New Project Raider Cap Banks 69 kV | BRP | 52129 | Leonard Road Cap Bank Addition | Adding 2 15.6MVAR cap banks to the Leonard Road 69kv substation. |  | M2 - Appendix A Approved | 1200000 | 2027-06-01 | Voltage Device | Capacitor (switched capacitor) | Leonard |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51152 | New Merom to Gill 345 kV Line addition | BRP | 52132 | Merom - Gill 345 kV Line | Construct an additional 345 kV line between Merom 345 kV and Gill 345 kV stations. No new terminals will be required. |  | M2 - Appendix A Approved | 2000000 | 2028-01-01 | Line New | New Transmission line, new ROW - may include terminations | Merom | Gill |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | ITC | East | 18208 | Airport - WDHVN Tap 120 kV Sag Remediation | BRP | 25049 | 25049-Airport-WDHVN Tap | Raise the sag on Airport - WDHVN Tap 120 kV section up to the conductor's limit. | ITCT | M2 - Appendix A Approved | 677000 | 2031-01-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Airport | WDHVN Tap | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51498 | New 120 kV Station - Slim | Build a new 120 kV three row breaker and a half station called Slim on the adjacent parcel north of the existing site to connect to existing Cortland. All 120 kV breakers should be standard 3000 A 63 kA breakers. |  | M2 - Appendix A Approved | 17750000 | 2029-02-01 | Substation | Switching station (breakers only, no transformer) | Slim |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51499 | Cortland - Remove ITC Equipment | Remove transmission equipment at Cortland. |  | M2 - Appendix A Approved | 1190000 | 2030-12-31 | Substation | Small miscellaneous substation equipment | Cortland |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51500 | CORTL DTE TRF103 -New Station Line | Build new 120kV station feed line from New Station to new bus at Cortland Station using 1600mm2 cable. |  | M2 - Appendix A Approved | 3400000 | 2028-12-13 | Line New | New underground transmission line | Slim | Cortland |  | 120 |  | 1 |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51501 | CORTL DTE TRF104- New Station Line | Build new 120kV station feed line from New Station to new bus at Cortland Station using 1600mm2 cable. |  | M2 - Appendix A Approved | 2450000 | 2030-06-17 | Line New | New underground transmission line | Slim | Cortland |  | 120 |  | 1 |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51502 | CORTL DTE TRF105- New Station Line | Build new 120kV station feed line from New Station to new bus at Cortland Station using 1600mm2 cable. |  | M2 - Appendix A Approved | 2655000 | 2029-09-17 | Line New | New underground transmission line | Slim | Cortland |  | 120 |  | 1 |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51503 | WAREN-New Station 120 kV Line | Redirect UG line from Cortland-Warren into the new station to become New Station - Warren. |  | M2 - Appendix A Approved | 5068000 | 2030-06-17 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Warren | Slim |  | 120 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51504 | MIDTN- New Station 120 kV Line | Redirect UG line from Cortland-Midtown into the new station to become New Station - Midtown. |  | M2 - Appendix A Approved | 6064000 | 2028-12-13 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Midtown | Slim |  | 120 |  |  |  | MI |  | Not Shared
MTEP26 | A | ITC | East | 50730 | Cortland 120 kV Station Expansion | Other | 51505 | CANIF-New Station 120 kV Line | Redirect UG line from Cortland-Caniff into the new station to become New Station - Caniff. |  | M2 - Appendix A Approved | 4170000 | 2029-09-17 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Caniff | Slim |  | 120 |  |  |  | MI |  | Not Shared
MTEP26 | A | ENTERGY SERVICES, LLC. | South | 50740 | Indian Bayou 230 kV Station | Other | 51509 | Indian Bayou 230 kV Station and cut ins | Breaker and a half 230 kV Station on the Gillis to Goos Ferry 230 kV line and ~16 miles of line to cut in the station. |  | M2 - Appendix A Approved | 68100000 | 2027-09-01 | Substation | Substation (breakers only, no transformer) | Gillis | Goos Ferry | 1 | 230 |  | 16 |  | LA |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50741 | New Montgomery 345 kV Temporary Tap (Elkhorn Phase 1) | Other | 51512 | Project Elkhorn Temporary Tap | Construct temporary taps on Montgomery-Lumberjack 345 kV lines to serve 250 MW of customer load |  | M2 - Appendix A Approved | 250000 | 2027-12-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Montgomery | Lumberjack |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | CITIZENS ELECTRIC CORPORATION 1 | Central | 50732 | New Leemon 69 KV substation for load addition | Other | 51513 | Leemon 69 KV Substation Addition and 69 kV Circuit T21 modification | CEC proposes building a new 10/14 MVA 69-12.47kV distribution substation to address load growth in the Fruitland, MO area. This new substation will connect into the existing TOT-Neely-Fruitland 69 kV T21 transmission line in a network fashion. Minor rerouting of the existing transmission line will be required to accommodate the cut-in. |  | M2 - Appendix A Approved | 2750000 | 2027-06-01 | Substation | Distribution substation - may include trans high side | Fruitland | Neely | 1 | 69 | 12 | 0.08 |  | MO |  | Not Shared
MTEP26 | A | ENTERGY SERVICES, LLC. | South | 50744 | Juban Trails (DEMCO) 230 kV Station | Other | 51515 | Juban Trails 230 kV Station | Entergy wholesale customer DEMCO is proposing to construct a new 230 kV station named Juban Trails to serve a new customer cut into the existing Coly to Vignes 230 kV line in Livingston Parish LA. |  | M2 - Appendix A Approved | 55000000 | 2027-09-01 | Substation | Substation (breakers only, no transformer) | Coly | Vignes |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | SAM HOUSTON ELECTRIC COOPERATIVE, INC. | South | 50747 | New Sub 138kV Sub Fish Lake | Other | 51517 | New Sub-138kV Fish Lake | The current distribution system is energized by a 230 kV/69 kV substation situated at Sour Lake Substation, within the Midcontinent Independent System Operator (MISO) region. The existing distribution system will connect to a new 138kV substation (Fish Lake) by tapping the Cypress (#334319)-Rye (#334194) transmission line, which is located approximately 16.5 miles north of Sour Lake Substation. This is for the EPR- Target MTEP 2025 cycle. I don't see this listed as a date under the Target MTEP Cycle drop down menu. |  | M2 - Appendix A Approved | 10000000 | 2027-10-01 | Substation | Distribution substation - may include trans high side | Fish Lake 138kV Substation |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 50746 | 1803 - 2025 Age and Condition Program | Other | 51520 | Angie 230/69kV Substation | Replace the station battery at the Angie 230/69kV Substation |  | M2 - Appendix A Approved | 75000 | 2026-01-31 | Misc. | Substation battery replacement | Angie Substation |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 50746 | 1803 - 2025 Age and Condition Program | Other | 51521 | Moss Bluff 230/69kV Substation | Moss Bluff station has many instances of equipment in the station that are in need of replacement. This includes arrestors, breakers, current transformers, potential transformers, arresters, communication equipment, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 100000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Moss Bluff 230/69kV Substation |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 50746 | 1803 - 2025 Age and Condition Program | Other | 51522 | Marion 115kV Switching Station | Marion station has many instances of equipment in the station that are in need of replacement. This includes arrestors, breakers, current transformers, potential transformers, and protective relays. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 50000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Marion 115kV Switching Station |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP26 | A | 1803 ELECTRIC COOPERATIVE, INC. | South | 50746 | 1803 - 2025 Age and Condition Program | Other | 51523 | Landry 230/115kV Substation | Landry station has many instances of equipment in the station that are in need of replacement. This includes arrestors, switches, and motor operated switches. This project is to perform the needed replacements. |  | M2 - Appendix A Approved | 100000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Landry 230/115kV Substation |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | ENTERGY SERVICES, LLC. | South | 50779 | Riddle 230 kV Station and Line Upgrade | Other | 51565 | Riddle 230 kV Station | Cut into the Fancy Point to Ventress 230 kV line. |  | M2 - Appendix A Approved | 27700000 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Fancy Point | Ventress |  | 230 |  |  |  | LA |  | Not Shared
MTEP26 | A | GREAT RIVER ENERGY | West | 50780 | West Glencoe | Other | 51566 | West Glencoe | Add new Glencoe Light & Power (GLP) substation to serve a 40 MW load. The new substation will tap the existing McLeod-Armstrong 115kv line. Add 40 MVAr of capacitance to address N-1-1 low voltage concerns. |  | M2 - Appendix A Approved | 6500000 | 2027-10-31 | Substation | Distribution substation - may include trans high side | West Glencoe |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP26 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50789 | Replace Guion South 345/138/13.75 kV Autotransformer | BRP | 51575 | Guion South Autotransformer | 345 kV : 138 kV - 500 MVA Aurotransformer |  | M2 - Appendix A Approved | 11664818 | 2027-12-31 | Transformer | Transformer Replacement | Guion | Guion | S | 345 | 138 |  |  | IN |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50791 | New Project Point 345 kV BAAH substation | Other | 51576 | Project Point Substation | Project Point 8 position BAAH Substation |  | M2 - Appendix A Approved | 31000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Project Point |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50790 | Expand Blue Bluff 138 kV switchyard | BRP | 51577 | Blue Bluff Substation | 138 kV Expansion of substation |  | M2 - Appendix A Approved | 30000000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Blue Bluff |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50795 | Uprate Guion to Whitestown 345 kV-09 | BRP | 51580 | Guion - Whitestown | 345 kV Transmission Line |  | M2 - Appendix A Approved | 15000000 | 2029-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Guion | Whitestown |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | ITC MIDWEST | West | 50775 | Linn County 620 MW Load Addition | Other | 51581 | DAEC 161 kV Bus Expansion | Expand DAEC 161 kV breaker and 1/2 bus to provide 4 new 161 kV line terminals to allow for 4 new CIPCO owned radial 161 kV lines to new load. |  | M2 - Appendix A Approved | 11255407 | 2028-07-01 | Substation | Substation (breakers only, no transformer) | DAEC |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | CITIZENS ELECTRIC CORPORATION 1 | Central | 50797 | Remediate Grand Tower 138 kV Foundation Erosion | Other | 51582 | Grand Tower Foundation Erosion Remediation | CEC proposes civil and structure analysis along with mitigation repairs to address soil erosion issues at an existing lattice tower structure. This structure supports the existing Grand Tower to Wittenberg 138 kV line as the line crosses the Mississippi River near the Grand Tower substation. Due to higher-than-normal river levels recently, CEC noted erosion activities around the foundations of the existing lattice tower. CEC is working with technical experts to determine the most appropriate and cost effect permanent repair. Cost and feasibility of repairs will be the major decision components for selecting the final repair method. |  | M2 - Appendix A Approved | 1500000 | 2027-04-01 | Line Upgrade | Line rebuild on existing ROW | Grand Tower | Wittenberg | 1 | 138 | 138 | 0 | 0 | MO |  | Not Shared
MTEP26 | A | CITIZENS ELECTRIC CORPORATION 1 | Central | 50796 | Repair Wittenberg 138 kV Switching Station Access Road | Other | 51583 | Wittenberg Switching Station Access Road Repair | Due to unforeseen site conditions, the existing access road into the Wittenberg Switching Station has experience a severe slope failure resulting in limited accessibility to the substation. CEC proposes making temporary repairs to keep the existing road in a condition to allow emergency access. CEC also proposes permanent repairs. CEC is working with technical experts to determine the most appropriate and cost effect permanent repair. This will consist of either repairing the existing access road or constructing a new access road in a different location. Cost and feasibility of repairs will be the major decision components for selecting the final repair method. |  | M2 - Appendix A Approved | 1500000 | 2027-04-01 | Substation | Small miscellaneous substation equipment | Grand Tower | Wittenberg | 1 | 138 | 138 | 0 | 0 | MO |  | Not Shared
MTEP26 | A | AMEREN ILLINOIS | Central | 51123 | New 300 MVAR Cap Bank at Truett 345 kV Substation | BRP | 52080 | 300 MVAR Cap Bank | 300 MVAR Cap Bank |  | M2 - Appendix A Approved | 12000000 | 2028-12-01 | Voltage Device | Capacitor (switched capacitor) | Truett |  |  | 345 |  |  |  | IL |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 51128 | Upgrade Sioux-Roxford 138 kV Lines | BRP | 52086 | Sioux-Roxford-6704 138 kV Line | Increase ampacity of the Sioux-Roxford-6704 138 kV line |  | M2 - Appendix A Approved | 4000000 | 2029-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sioux | Roxford |  | 138 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 51128 | Upgrade Sioux-Roxford 138 kV Lines | BRP | 52087 | Sioux-Roxford-6700 138 kV Line | Increase ampacity of Sioux-Roxford-6700 138 kV line |  | M2 - Appendix A Approved | 4000000 | 2029-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sioux | Roxford |  | 138 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50695 | New Hayford 345 kV Substation for load addition | Other | 51439 | Hayford 345 kV Substation | New Hayford 345 kV BAAH Substation |  | M2 - Appendix A Approved | 12000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Hayford |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 50697 | Increment Hayford 345 kV Load Addition | Other | 51441 | Hayford-Graus 345 kV line | Belleau-Hayford-Graus 345 kV line |  | M2 - Appendix A Approved | 8000000 | 2030-12-01 | Substation | Substation bus upgrade | Hayford | Graus |  | 345 |  |  |  | MO |  | Not Shared
MTEP26 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50700 | New Antioch 345 kV Station and Load | Other | 51447 | Antioch 345 kV Station | 345 kV breaker-and-a-half substation on the 16THOMPS (254537) - 16PETE (254529) transmission line approximately 11 line-miles south of the IPL Thompson Substation. |  | M2 - Appendix A Approved | 68800000 | 2027-11-01 | Substation | Substation (breakers only, no transformer) | 16THOMPS | 16PETE |  | 345 |  |  |  | IN |  | Not Shared
MTEP26 | A | ENTERGY SERVICES, LLC. | South | 50713 | Mount Olive to Cargas 500 kV Project and Load Addition | BRP | 51463 | Mt Olive To Cargas 500 kV | • New ~47 mile Mt Olive to Cargas 500 kV line. |  | M2 - Appendix A Approved | 270500000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Mt Olive | Cargas |  | 500 |  | 47 |  | LA |  | Not Shared
MTEP26 | A | HOOSIER ENERGY | Central | 51090 | New St.Joesph to Northside 138 kV Line and 138/12 kV Station | Other | 52133 | 138 kV Switching Station | Construct a new 3 position ring bus that breaks the Duke 13850 and interconnect the new 138 kV line from LG&E Northside 138 kV. |  | M2 - Appendix A Approved | 9400000 | 2028-03-01 | Substation | Switching station (breakers only, no transformer) | St.Joeseph |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | ITC MIDWEST | West | 50775 | Linn County 620 MW Load Addition | Other | 52139 | DAEC - Hazleton 345 kV Sag Limit Mitigation | Mitigate sag limited span on ITCM owned portion of DAEC - Hazleton 345 kV to increase rating to minimum 1120 MVA summer. |  | M2 - Appendix A Approved | 1 | 2028-07-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | DAEC | Hazleton | 1 | 345 | 345 |  |  | IA |  | Not Shared
MTEP26 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 51124 | Sheffield Substation Battery and Trip Coil Monitoring | BRP | 52159 | Sheffield Substation Battery and Trip Coil Monitoring | Project to add monitoring to NIPSCO Sheffield 138kV substation to mitigate NERC TPL-001-5 P5 violation tied to data center load addition. |  | M2 - Appendix A Approved | 25000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Sheffield |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | ITC | East | 51167 | Upgrade Sag on Lark-Washtenaw Jct. 138 kV | BRP | 52166 | Lark-Washtenaw Jct_Upgrade the sag | Raise the sag on Lark-Washtenaw Jct. All upgrades to a minimum SE 196MVA. |  | M2 - Appendix A Approved | 2800000 | 2027-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Lark | Washtenaw Jct |  | 138 |  |  |  | MI |  | Not Shared
MTEP26 | A | AMEREN MISSOURI | Central | 51175 | Rebuild Carbide Tap-Viele 161 kV line (JUA AECI/NE Power) | Other | 52167 | Carbide Tap-Viele 161 kV | Carbide Tap-Viele 161 kV Rebuild by AECI/NE Power |  | M2 - Appendix A Approved | 1 | 2026-11-30 | Line Upgrade | Line rebuild on existing ROW | Carbide Tap | Viele |  | 161 |  |  | 7 | MO |  | Not Shared
MTEP26 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 51092 | Customer A 138 kV | Other | 52187 | Customer A 138kV | 260MW load is being looped into circuit 13803 Wolf Lake to Stateline B (NIPSCO-ComEd). |  | M2 - Appendix A Approved | 25000000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | Wolf Lake |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51216 | Van Meter 161 kV Substation and Associated 161 kV Upgrades | Other | 52246 | Van Meter Substation | Construct new Van Meter 161 kV Substation |  | M2 - Appendix A Approved | 13000000 | 2029-02-01 | Substation | Switching station (breakers only, no transformer) | Van Meter |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51216 | Van Meter 161 kV Substation and Associated 161 kV Upgrades | Other | 52247 | Van Meter-South Waukee Line Tap | 161 kV line tap Van Meter - South Waukee |  | M2 - Appendix A Approved | 2000000 | 2029-02-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Van Meter | South Waukee | 1 | 161 |  | 0.05 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51216 | Van Meter 161 kV Substation and Associated 161 kV Upgrades | Other | 52248 | Van Meter-Booneville Line Tap | 161 kV line tap Van Meter - Booneville |  | M2 - Appendix A Approved | 2000000 | 2029-02-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Van Meter | Booneville |  | 161 |  | 0.05 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51216 | Van Meter 161 kV Substation and Associated 161 kV Upgrades | Other | 52249 | Johnson Creek Line Terminal | Construct Johnson Creek 161 kV line terminal |  | M2 - Appendix A Approved | 4000000 | 2029-02-01 | Substation | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Johnson Creek |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51216 | Van Meter 161 kV Substation and Associated 161 kV Upgrades | Other | 52250 | Van Meter-Johnson Creek 161 kV line | Construct Van Meter - Johnson Creek 161 kV line |  | M2 - Appendix A Approved | 13500000 | 2029-02-01 | Line New | New Transmission line, new ROW - may include terminations | Van Meter | Johnson Creek | 1 | 161 |  | 6 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 51216 | Van Meter 161 kV Substation and Associated 161 kV Upgrades | Other | 52251 | Van Meter-Booneville 161 kV line reconductor | Uprate Van Meter - Booneville 161 kV line by reconductor line |  | M2 - Appendix A Approved | 8000000 | 2029-02-01 | Line Upgrade | Line reconductor | Van Meter | Booneville | 1 | 161 |  |  | 2.5 | IA |  | Not Shared
MTEP26 | A | MONTANA-DAKOTA UTILITIES CO. | West | 51219 | Wishek NW Data Center Load Addition | Other | 52254 | Wishek NW Data Center Bay | New breaker, switches, bus work, jumpers, and dead end at Wishek NW to interconnect the new load. |  | M2 - Appendix A Approved | 2210000 | 2027-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Wishek NW |  |  | 230 |  |  |  | ND |  | Not Shared
MTEP26 | A | AMEREN ILLINOIS | Central | 50633 | Rebuilds on 138 kV from Diamond Core Load Addition (RECC Territory) | BRP | 51386 | Towerline-San Jose Rail-1625 138 kV | Towerline-San Jose Rail-1625 138 kV increase line capacity |  | M2 - Appendix A Approved | 22250000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Towerline | San Jose Rail |  | 138 |  |  | 13 | IL |  | Not Shared
MTEP26 | A | AMEREN ILLINOIS | Central | 50633 | Rebuilds on 138 kV from Diamond Core Load Addition (RECC Territory) | BRP | 51387 | Austin-Yvonne-1545 138 kV | Austin-Yvonne-1545 138 kV line capacity increase |  | M2 - Appendix A Approved | 13500000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Austin | Yvonne |  | 138 |  |  | 7.8 | IL |  | Not Shared
MTEP26 | A | AMEREN ILLINOIS | Central | 50633 | Rebuilds on 138 kV from Diamond Core Load Addition (RECC Territory) | BRP | 51388 | Yvonne-Taylorville South-1601 138 kV | Yvonne-Taylorville South-1601 138 kV line increase capacity |  | M2 - Appendix A Approved | 14500000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Yvonne | Taylorville South |  | 138 |  |  | 9 | IL |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 50721 | East Kanesville 161 kV Substation & 161 kV Lines | Other | 51472 | East Kanesville 161 kV Substation | Construct new East Kanesville 161 kV Substation. |  | M2 - Appendix A Approved | 30000000 | 2028-03-15 | Substation | Substation (breakers only, no transformer) | East Kanesville |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 50721 | East Kanesville 161 kV Substation & 161 kV Lines | Other | 51473 | Quick-Sub 701 161 kV Line Taps | Bisect the Quick-Sub 701 161 kV line and bringing two one span 161 kV lines into the new East Kanesville Substation |  | M2 - Appendix A Approved | 1500000 | 2028-03-15 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Quick | Sub 701 |  | 161 |  | 0.2 |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 50721 | East Kanesville 161 kV Substation & 161 kV Lines | Other | 51474 | Overland Trail 161 kV Terminal Addition | Construct a new 161 kV line terminal at Overland Trail Substation. |  | M2 - Appendix A Approved | 5000000 | 2029-06-01 | Substation | Substation bus upgrade | Overland Trail |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP26 | A | MIDAMERICAN ENERGY CO. | West | 50721 | East Kanesville 161 kV Substation & 161 kV Lines | Other | 51475 | Overland Trail-East Kanesville 161 kV Line | Construct a new 161 kV line from Overland Trail Substation to East Kanesville Substation |  | M2 - Appendix A Approved | 20000000 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | Overland Trail | East Kanesville | 1 | 161 |  | 7 |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50624 | Substation 74: Relocate 161 kV Capacitor Bank from Substation A | BRP | 51329 | Substation 74: Install 161 kV Capacitor Bank | Relocate the existing 161 kV, 50.4 MVAR capacitor bank from Substation A to Substation 74. |  | M3 - Under Construction | 1600000 | 2026-06-01 | Voltage Device | Capacitor (switched capacitor) | Substation 74 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50622 | Substation High Voltage Protection (HVP) Equipment Removal | Other | 51331 | Substation High Voltage Protection (HVP) Equipment Removal | The objective of ATC’s Substation (HVP) Equipment Removal project is to enhance safety within and outside the control house by decommissioning the remaining High Voltage Protection (HVP) telecommunications equipment from (~269) ATC substations. The legacy HVP (copper cable) equipment is no longer in use due to the migration to fiber optic technology upgrades within ATC’s substation environment. |  | M3 - Under Construction | 4800000 | 2027-11-30 | Misc. | Communication equipment | South Beaver Dam |  |  | 0 |  |  |  | WI |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50628 | Upgrade LEAP Transmission Network Phase 2 | Other | 51339 | LEAP Phase 2 | a new 345kV ring bus and approx. 12 miles of 345kV line to the west side of Lebanon where WVPA will construct a 345/138kV substation. Approx. 15 miles of 345kV line will be built to network this 345/138kV station to a planned 345/138kV station on the north side of the LEAP district. WVPA will also connect into the Nucor-Whitestown 345kV line and construct a new 345kV ring and approx. 6 miles of new 345kV line to the new step down substation. |  | M2 - Appendix A Approved | 345000000 | 2029-06-30 | Transformer | Transformer New | Fayette/Wolf Creek | Edwards |  | 345 | 138 | 33 |  | IN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50514 | J1502 Emerson Rd SS Network Upgrades and Interconnection Facilities | GIP | 50812 | J1502 345kV Interconnection Switching Station | The TO’s new 345kV Interconnection Switching Station is arranged as follows: • in an initial three (3) position, • ultimate four (4) position, • three (3) 345kV circuit breaker ring bus with: o a single (1) Generator Lead Line position and o two (2) transmission line positions. |  | M2 - Appendix A Approved | 16094000 | 2028-06-30 | Substation | Switching station (breakers only, no transformer) | Emerson Rd |  |  | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50514 | J1502 Emerson Rd SS Network Upgrades and Interconnection Facilities | GIP | 50813 | W-13 345kV Transmission Line Modifications | The existing W-13 345kV line between Briggs Road and North Madison Substations will be tapped and looped into the new 345kV Interconnection Switching Station to provide transmission access. |  | M2 - Appendix A Approved | 2426000 | 2028-06-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Briggs Road | North Madison | W-13 | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50514 | J1502 Emerson Rd SS Network Upgrades and Interconnection Facilities | GIP | 50814 | 345kV North Madison Substation | The existing Transmission Owner’s 345kV W-13 Line will be rerouted into the Interconnection Station. The existing line relaying at North Madison substation will be upgraded per Transmission Owner system relay protection standards to align with the new Interconnection Station to ensure the line is properly protected. On the Briggs Road line at North Madison substation, there is a phasing designation change between Xcel Energy and ATC. During detailed design it will be determined where location of phase change will occur. |  | M2 - Appendix A Approved | 441000 | 2028-06-30 | Misc. | Relaying, protection, RTU and SCADA equipment | North Madison |  |  | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50514 | J1502 Emerson Rd SS Network Upgrades and Interconnection Facilities | GIP | 50815 | J1502 345kV Interconnection Facilities | The J1502 Transmission Owner Interconnected Facilities consists of substation work associated with the Generator Lead Line entrance at the new Interconnection Switching Station. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. |  | M2 - Appendix A Approved | 886000 | 2028-06-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Emerson Rd |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50515 | J1779 Rockdale SS Interconnection Facilities | GIP | 50816 | ATC System Protection and supporting activities. | The J1214/J1326 Interconnect Station and TOIF facilities are constructed and placed in-service as set forth in the J1214/J1326 GIA. System Protection and supporting activities are required. |  | M2 - Appendix A Approved | 25000 | 2027-10-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Rockdale |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50518 | J1773 J1781 MPFCA Network Upgrades | GIP | 50824 | X-127 138 kV Transmission Line Reconductor | The Hill Valley – Eden 138kV (X-127) reconductor project will replace approximately 1.0 mile of conductor with a bundled TP 477 kcmil ACSR 26/7 Hawk conductor. |  | M2 - Appendix A Approved | 1625089 | 2027-10-10 | Line Upgrade | Line reconductor | Hill Valley | Eden | X-127 | 138 |  |  | 1 | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50518 | J1773 J1781 MPFCA Network Upgrades | GIP | 50825 | X-147 138 kV Transmission Line Reconductor | The Eden – Highland 138 kV (X-147) rebuild project will reconductor approximately 4.5 miles with TP 556.5 kcmil ACSR 26/7 Dove conductor with 26 structures being rebuilt or remediated to support the new conductor. |  | M2 - Appendix A Approved | 5998000 | 2027-10-10 | Line Upgrade | Line reconductor | Eden | Highland | X-147 | 138 |  |  | 4.5 | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50519 | Reactor Relocation from North Madison SS to J1502 POI SS | Other | 50826 | Reactor Relocation | Relocate the 80 Mvar reactor from North Madison SS to J1502 POI SS to regulate voltage when J1502 is unavailable. |  | M2 - Appendix A Approved | 5165000 | 2028-06-30 | Voltage Device | Reactor or Inductor | North Madison | J1502 POI |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50520 | OTP Donaldson - Donaldson South J1575 Network Upgrades | GIP | 50827 | Donaldson - Donaldson South Line | Structure replacements to uprate the line from Donaldson to Donaldson South, the POI for J1575, 115 kV transmission line. |  | M2 - Appendix A Approved | 83341 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Donaldson 115 kV | Donaldson South 115 kV | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50520 | OTP Donaldson - Donaldson South J1575 Network Upgrades | GIP | 50828 | Donaldson Substation | Substation upgrades at Donaldson 115 kV. |  | M2 - Appendix A Approved | 692951 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Donaldson 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50521 | OTP Donaldson South J1575 Interconnection | GIP | 50829 | Donaldson South J1575 POI Substation | New substation designated Donaldson South for the POI of J1575. |  | M2 - Appendix A Approved | 4739048 | 2028-08-03 | Substation | Switching station (breakers only, no transformer) | Donaldson South 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50521 | OTP Donaldson South J1575 Interconnection | GIP | 50830 | Donaldson - Warsaw In/Out | In and out line connections from Donaldson - Warsaw 115 kV line to new Donaldson South J1575 POI 115 kV substation. |  | M2 - Appendix A Approved | 449718 | 2028-08-03 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Donaldson South 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50521 | OTP Donaldson South J1575 Interconnection | GIP | 50831 | Donaldson Relaying | Relaying at Donaldson 115 kV. |  | M2 - Appendix A Approved | 60000 | 2028-08-03 | Misc. | Relaying, protection, RTU and SCADA equipment | Donaldson 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50521 | OTP Donaldson South J1575 Interconnection | GIP | 50832 | Oslo Relaying | Relaying at Oslo 115 kV. |  | M2 - Appendix A Approved | 11000 | 2028-08-03 | Misc. | Relaying, protection, RTU and SCADA equipment | Oslo 115 kV |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50521 | OTP Donaldson South J1575 Interconnection | GIP | 50833 | J1575 Deadend | Deadend at J1575. |  | M2 - Appendix A Approved | 709287 | 2028-08-03 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | J1575 |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50521 | OTP Donaldson South J1575 Interconnection | GIP | 50834 | Donaldson South - J1575 Tie Line | 115 kV tie line from Donaldson South to J1575. Includes commissioning. |  | M2 - Appendix A Approved | 2091244 | 2028-08-03 | Line New | New Transmission line, new ROW - may include terminations | Donaldson South 115 kV | J1575 115 kV | 1 | 115 |  | 2 |  | MN |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50528 | Benoit 230 kV Station | Other | 50852 | Benoit 230 kV Station | Construct a 230 kV Benoit Station on the Mud Lake to Big Lake line. |  | M2 - Appendix A Approved | 61200000 | 2027-07-01 | Substation | Substation (breakers only, no transformer) | Mud Lake | Big Lake |  | 230 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50528 | Benoit 230 kV Station | Other | 50853 | Benoit Capacitor Banks | Two 64.8 MVAR Capacitor Banks |  | M2 - Appendix A Approved | 1 | 2027-07-01 | Voltage Device | Capacitor (switched capacitor) | Benoit |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP25 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 50498 | Byron - Cascade Creek Line Relocation | Other | 50854 | Byron - Cascade Creek Line Relocation | Relocation of 1.2miles of 161kV transmission lines due to MnDOT developing a new interchange on intersection of Hwy 14 & Hwy 44. MnDOT requests the project be completed by Spring 2025. |  | M2 - Appendix A Approved | 3627000 | 2027-12-31 | Misc. | Line relocation (road move) | Byron | Cascade Creek |  | 161 |  |  |  | MN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50529 | Appleton Area Reliability Project | BRP | 50855 | Appleton Area Reliability Project | 1) Construct new 138kV line between City Limits – Northside 2) Rebuild a 138kV line section of 50632 (From STR132131 - City Limits), 3) Rebuild a 138kV line section of 43025 (From STR132131 - Northside), 4) Rebuild two 138kV line sections of 971K11 (Melissa - Meadows Tap and Meadows Tap - Kaukauna Central Tap). |  | M2 - Appendix A Approved | 35700000 | 2031-04-02 | Line New | New Transmission line, new ROW - may include terminations | City Limits | Northside |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50530 | J1750 Grace Lake SS Network Upgrades and Interconnection Facilities | GIP | 50856 | J1750 138kV Interconnection Station | ATC shall construct a 138 kV line interconnection substation to accommodate the generating facility’s collector station to the power system. The new J1750 Substation will be arranged in a three breaker ring bus configuration with one generation position and two line positions, capable of future expansion to an ultimate 4 position ring bus. The new J1750 Substation will segment the Transmission Owner’s overhead X-119 transmission line between existing Empire and Huron Substations into two segments, X-TBD and X-119. All new substation equipment (bus, jumpers, switches, breakers etc) carrying transmission system network current should target a minimum continuous SN rating of 2,000 Amps. New equipment designations will be requested and provided by ATC System Operations. Relay protection and control will consist of two line relay panels with primary and secondary schemes and power line carrier communication (X-TBD and X-119), one line relay panel with dual redundant fiber communications (J1750 Generator lead line), and two panels consisting of breaker failure and auto reclose relay protection for the three J1750 substation breakers. The Transmission Owner will maintain ownership of all X-119 and X-TBD related work and J1750 Substation up to the Point of Change of Ownership (PCO). |  | M2 - Appendix A Approved | 10068000 | 2032-08-04 | Substation | Substation (breakers only, no transformer) | Grace Lake |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50530 | J1750 Grace Lake SS Network Upgrades and Interconnection Facilities | GIP | 50857 | X-119 138kV Transmission Line Modifications | The X-119 138 kV Transmission Line Loop-In project will consist of installing two single-circuit 90deg dead-end steel poles in place of existing tangent H-Frame structure 111 that will segment the line into X-119 towards Huron and X-TBD towards Empire, routing the line through the Transmission Owner’s new switchyard. Insulators on the line dead-end poles and switchyard dead-ends will route the conductors to the bus connections and surge arresters. Shield wire for X-119/X-TBD will terminate at the new two-pole structure and new wires will be strung between the two-pole structure and the switchyard dead-end structures. All equipment and hardware on the switchyard side of the line and shield wire terminations is addressed in the Transmission Owner’s new Interconnection switching station. The Transmission Owner will retain ownership of the line segments, support poles and interconnection facility. |  | M2 - Appendix A Approved | 1581000 | 2032-08-04 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Grace Lake | Empire | X-119 | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50530 | J1750 Grace Lake SS Network Upgrades and Interconnection Facilities | GIP | 50858 | J1750 138kV Interconnection Substation Interconnection Facilities | The J1750 TOIF will consist of jumpers and equipment to connect the Interconnection Customer’s generator lead line equipment with the Transmission Owner rigid bus. The Transmission Owner will furnish, install, own, operate, and maintain the relays and associated communication equipment that are located in the Transmission Owner’s facility for the generator lead line. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. |  | M2 - Appendix A Approved | 461000 | 2032-08-04 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Grace Lake |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50531 | New AECI Load Addition at Ameren Fredericktown 138 kV | Other | 50859 | Line position at Fredericktown 138 kV | Line position at Fredericktown 138 kV for AECI |  | M2 - Appendix A Approved | 1200000 | 2027-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Fredericktown |  |  | 161 | 138 |  |  | MO |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50532 | Stiles - Sherwood 138 kV (L-142), Partial Rebuild | Other | 50860 | Stiles - Sherwood 138 kV (L-142), Partial Rebuild | ~50 structures to replace, initial assumption is to transfer existing wires. |  | M2 - Appendix A Approved | 7000000 | 2030-01-03 | Line Upgrade | Line rebuild on existing ROW | Stiles | Sherwood | L-142 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50533 | S1016 Lone Rock SS Network Upgrades | GIP | 50861 | Lone Rock SS Grounding Mitigation | The S1016 project consists of the installation of 25MW of battery storage and an 8.4 MVAR capacitor bank at the J864 collector station. The J864 lead line and TOIF facilities at Lone Rock Substation will be utilized. Analysis and remediation of the Lone Rock Substation ground grid may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. |  | M3 - Under Construction | 775000 | 2031-06-11 | Substation | Small miscellaneous substation equipment | Lone Rock |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50533 | S1016 Lone Rock SS Network Upgrades | GIP | 50862 | ATC Protection and supporting activities | ATC Protection and supporting activities |  | M3 - Under Construction | 25000 | 2031-06-11 | Misc. | Relaying, protection, RTU and SCADA equipment | Lone Rock |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50534 | J1824 Academy SS Network Upgrades and Interconnection Facilities | GIP | 50863 | J1824 138kV Academy Substation Terminal Addition | The J1824 network upgrades at Academy Substation consist of adding one (1) new line protection panel to the existing control house. New control and fiber will be run from the new line GCB to the control house. |  | M2 - Appendix A Approved | 790000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Academy |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50534 | J1824 Academy SS Network Upgrades and Interconnection Facilities | GIP | 50864 | J1824 138kV Interconnection Facilities | The J1824 TOIF at Academy Substation will consist of adding one (1) 138kV Gas Circuit Breaker, and two (2) disconnect switches, to connect the Customer’s Generator Lead Line to the Transmission Owner’s strain bus 1. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. |  | M2 - Appendix A Approved | 631000 | 2027-12-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Academy |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50534 | J1824 Academy SS Network Upgrades and Interconnection Facilities | GIP | 50865 | Academy Substation - Transformer Replacement | The Academy Substation project will consist of replacing the existing 138/69 kV T31 autotransformer with a new 138/69 kV autotransformer per Transmission Owner standards. A concrete oil containment will be installed around the new transformer and rigid bus will be used to connect from the transformer to the 69 kV box structure. |  | M2 - Appendix A Approved | 8823000 | 2027-12-31 | Transformer | Transformer Replacement | Academy |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | GIP | 50866 | J1732 138 kV Interconnection Substation | TO shall construct a 138 kV interconnection substation to accommodate a generation collection facility addition to the power system. The new J1732 interconnection substation will be located adjacent to the Interconnection Customer yard with a shared fence. |  | M2 - Appendix A Approved | 7988000 | 2028-05-18 | Substation | Substation (breakers only, no transformer) | Wolfram Rd |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | GIP | 50867 | X-68 138kV Transmission Line Modifications | The X-68 138 kV Transmission Line Loop-In consists of two (2) horizontal monopole dead-end structures routing the line through the Transmission Owner’s new substation, segmenting X-68 between the Lewiston and Trienda substations. Also: • Line renaming will be required and determined in detailed design. • Line disconnect switches will isolate the line from the ring bus interconnection substation facility. • Insulators on the line dead-end poles and substation dead-ends will route the conductors to the bus connections and surge arresters. Existing wire for transmission lines will terminate at the new poles and new wire will be strung between the poles and their associated substation dead-end structure. |  | M2 - Appendix A Approved | 902000 | 2028-05-18 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Lewiston | Trienda | X-68 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | GIP | 50868 | Trienda Substation remote end work | The Trienda Substation project will consist of modifications to the protection and communications equipment on the X-68 line terminal to J1732 Substation in support of the J1732 interconnection project. |  | M2 - Appendix A Approved | 357000 | 2028-05-18 | Substation | Small miscellaneous substation equipment | Trienda |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | GIP | 50869 | Kilbourn Substation remote end work | The Kilbourn Substation project will consist of modifications to the protection and communications equipment on the X-68 line terminal to J1732 Substation in support of the J1732 interconnection project. |  | M2 - Appendix A Approved | 301000 | 2028-05-18 | Substation | Small miscellaneous substation equipment | Kilbourn |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | GIP | 50870 | J1732 138 kV Interconnection Substation Interconnection Facilities | The J1732 interconnection will consist of bus and equipment to connect the Interconnection Customer’s Generator Lead Line to the Transmission Owner’s rigid bus. A motor operated line disconnect switch will isolate the Generator Lead Line from the three position ring bus interconnection substation. All aspects of the customer owned yard to be designed and installed by others. Any shielding wire for Interconnection Customer facilities will terminate at the Interconnection substation dead end shield wire vangs. All new substation equipment will target a minimum continuous summer normal rating of 2,000 amps. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. |  | M2 - Appendix A Approved | 346000 | 2028-05-18 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Wolfram Rd |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50538 | J1386 IC Facilities | GIP | 50877 | J1386 | Construct Transmission Owner’s Interconnection Facilities at Transmission Owner’s Green Acres Substation consisting of one monopole, H frame pull off structure, metering equipment, conductor, and fiber optics. |  | M2 - Appendix A Approved | 1726367 | 2028-05-31 | Line New | New Transmission line, new ROW - may include terminations | Green Acres |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50538 | J1386 IC Facilities | GIP | 50878 | J1386 IC Facilities Network Upgrade | Create new position on double breaker double bus Green Acres 138kV bus for generating lead line. |  | M2 - Appendix A Approved | 6397253 | 2028-05-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Green Acres |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50541 | El Dorado 500/345kV Autotransformer Upgrade | BRP | 50879 | El Dorado 500/345kV Autotransformer Upgrade | Upgrade the existing 500/345kV autotransformers and associated equipment to 1200MVA. |  | M2 - Appendix A Approved | 73800000 | 2028-12-01 | Transformer | Transformer Replacement | El Dorado |  |  | 500 | 345 |  |  | AR |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50511 | J1746 Columbia SS Network Upgrades and Interconnection Facilities | GIP | 50807 | J1746 Columbia Substation Terminal Addition | The J1746 network upgrades at Columbia Substation consist of adding: • one (1) 138kV Circuit Breaker, strain span, • three (3) 138kV Bus PTs, • two (2) fiber vaults, • one (1) new line protection panel, and • one (1) new breaker protection & control panel. • New control cable will be run from the new 138kV Circuit Breaker, 138kV PT’s, and • fiber will be run from the existing Northeast A-Frame dead-end to the control house via new buried conduit and existing cable trench. |  | M2 - Appendix A Approved | 1464000 | 2031-08-28 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Columbia |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50511 | J1746 Columbia SS Network Upgrades and Interconnection Facilities | GIP | 50808 | J1746 138kV Interconnection Facilities | The J1746 TOIF at Columbia Substation will consist of adding three (3) surge arresters, two (2) OPGW splice enclosures, one (1) line disconnect switch to support the new Generator Lead Line. Any shielding wire for Interconnection Customer facilities will terminate at the Interconnection substation dead end shield wire vangs. All new substation equipment will target a minimum continuous summer normal rating of 2,000 amps. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. |  | M2 - Appendix A Approved | 381000 | 2031-08-28 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Columbia |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50512 | J1778 Paris SS Network Upgrades | GIP | 50809 | J1778 138kV Paris Substation Upgrades | The scope of work at Paris Substation includes upgrading the protection on Line PARG51 to convert the existing SEL-311C to a DCU scheme over a power line carrier communication channel. A UPLC-II and 85 Cut-Off switch will be installed in the existing PARG51 line relay panel. A wave trap and tuner will be installed on the existing line CCVT on the PARG51 line position to Berryville Substation. Disconnect switches and jumpers will be upgraded for breaker position BS5-6. |  | M2 - Appendix A Approved | 287000 | 2027-11-09 | Misc. | Relaying, protection, RTU and SCADA equipment | Paris |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50512 | J1778 Paris SS Network Upgrades | GIP | 50810 | J1778 138kV Berryville Substation Upgrades | The scope of work at Berryville Substation includes upgrading the protection on Line PARG51 to convert the existing SEL-311C to DCU scheme over a power line carrier communication channel. A UPLC-II and 85 Cut-Off switch will be installed in the existing PARG51 line relay panel. A 138 kV CCVT, wave trap, and tuner will be installed on the PARG51 line position to Paris Substation. The scope of work at Berryville Substation also includes upgrading the protection on Line 3124 to convert the existing SEL-311C to POTT scheme over a fiber communication channel. An 85 Cut-Off Switch to block fiber communication will be installed on the relay panel controlling Line 3124 to Albers Substation. |  | M2 - Appendix A Approved | 315000 | 2027-11-09 | Misc. | Relaying, protection, RTU and SCADA equipment | Berryville |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50512 | J1778 Paris SS Network Upgrades | GIP | 50811 | J1778 Albers Substation Upgrades | The scope of work at Albers Substation includes replacing the line relaying panel protecting Line 3124 with a 421/311C POTT protection scheme. |  | M2 - Appendix A Approved | 209000 | 2027-11-09 | Misc. | Relaying, protection, RTU and SCADA equipment | Albers |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50124 | Portage SS Relay and Breaker Asset Renewal | Other | 50201 | Portage SS Relay and Breaker Asset Renewal | Asset Renewal of the Portage SS control house, all assets within the control house, and 5 oil circuit breakers. |  | M2 - Appendix A Approved | 7100000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Portage |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50125 | Rock River SS and Remote Ends Asset Renewal | Other | 50202 | Rock River SS and Remote Ends Asset Renewal | Asset Renewal of several relay panels, disconnect switches, and two battery banks at Rock River SS. |  | M2 - Appendix A Approved | 3986000 | 2028-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Rock River |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50125 | Rock River SS and Remote Ends Asset Renewal | Other | 50203 | Town Line Road SS Remote Ends Asset Renewal | Asset renewals of several relay panels, RTU panel, disconnect switches, and battery bank at Town Line Road SS. |  | M2 - Appendix A Approved | 1628000 | 2028-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Town Line Road |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50126 | Coyne Street SS Relay, Breaker and House Asset Renewal | Other | 50204 | Coyne Street SS Relay, Breaker and House Asset Renewal | At Coyne Street SS, asset renewal of four 115 kV oil circuit breakers, six 115 kV disconnect switches, and 1 control house with all panels and components. |  | M2 - Appendix A Approved | 7950000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Coyne St |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50127 | Finger Road SS Relays and Remote Ends Asset Renewal | Other | 50205 | Finger Road SS Relays and Remote Ends Asset Renewal | Asset Renewal of the Finger Road SS control house and all assets within the control house. |  | M2 - Appendix A Approved | 5205000 | 2028-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Finger Road |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50127 | Finger Road SS Relays and Remote Ends Asset Renewal | Other | 50206 | Danz Ave SS Relays and Remote Ends Asset Renewal | Project also includes the remote end asset renewal of 3 relay panels and the RTU panel at Danz Avenue. |  | M2 - Appendix A Approved | 596000 | 2028-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Danz Ave |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50128 | Eden SS Relay and House Asset Renewal | Other | 50207 | Eden SS Relay and House Asset Renewal | Asset Renewal of the Eden SS control house and all assets within the control house. |  | M2 - Appendix A Approved | 5081000 | 2027-06-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Eden |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50134 | Huiskamp - Division Street Tap 69 kV (Y-132), Rebuild | Other | 50213 | Huiskamp - Division Street Tap 69 kV (Y-132), Rebuild | Rebuild and install OPGW on approximately 2.7 miles of Y-132 from Huiskamp SS to Division Street Tap switch structure, in addition rebuild 0.2 miles of the Division Street Tap to Division Street SS and install OPGW from Waunakee to Huiskamp SS. |  | M2 - Appendix A Approved | 8500000 | 2030-08-06 | Line Upgrade | Line rebuild on existing ROW | Huiskamp | Division Street Tap | Y-132 | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50542 | S1025 Sheepskin SS Network Upgrades | GIP | 50880 | Sheepskin SS Grounding Mitigation | Analysis and remediation of the Sheepskin Substation ground grid may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. |  | M2 - Appendix A Approved | 200000 | 2032-01-05 | Substation | Small miscellaneous substation equipment | Sheepskin |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50542 | S1025 Sheepskin SS Network Upgrades | GIP | 50881 | ATC Protection and supporting activities | ATC Protection and supporting activities |  | M2 - Appendix A Approved | 25000 | 2032-01-05 | Misc. | Relaying, protection, RTU and SCADA equipment | Sheepskin |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50543 | Racine County, DIC, Cosmos Substation | Other | 50882 | Racine County, DIC, Cosmos Substation | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, 138 kV capacitor banks, and 4 – 345 kV line terminals, and 1 – 138 kV line terminals with a series reactor. |  | M3 - Under Construction | 195000000 | 2028-07-05 | Substation | Distribution substation - may include trans high side | Cosmos |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50544 | MPFCA Rockdale SS Network Upgrade | GIP | 50883 | Rockdale 138 kV Substation | The Rockdale 138 kV Substation project will consist of replacing 8 station post insulators and adding sixteen (16) CCVTs to address overdutied breakers 631-S, 636-S, 646-S, 628-S, 2327-S, and 622-S. 3,000 pF of capacitance is required within 300 feet of the line- or transformer-side bushings on each overdutied breaker. Sixteen (16) pier foundations and sixteen (16) standard low 1Ø CCVT stands will be added to the line terminals and transformer buses. No conduit or control cable will be needed. Jumpers will connect the CCVTs to the bus via compression fittings. Ground tails will be connected to the existing grid via exothermic welds and tees. Eight (8) station post insulators will be replaced with extra-high strength insulators to withstand the 47.6 kA fault current on the 138 kV bus. No conduit, junction boxes, or control cable will be connected to the new CCVTs. Each CCVT will self-power its anti-condensation heater. |  | M2 - Appendix A Approved | 1120000 | 2032-01-27 | Substation | Small miscellaneous substation equipment | Rockdale |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50884 | J1752 138kV Interconnection Switching Station | The proposed 138kV Interconnection Switching Station is arranged in an initial three (3) position, future four (4) position ultimate ring bus configuration with a single (1) Generator Lead Line position and two (2) transmission line positions. The proposed fenced area is approximately 241 feet x 241 feet. The proposed Interconnection Switching Station also includes a ‘hardened’ control building that will house control and protection panels, IT Comm / RTU panels, main termination cabinets (MTC), and AC and DC station service equipment. |  | M2 - Appendix A Approved | 11576000 | 2028-05-15 | Substation | Substation (breakers only, no transformer) | Shady Dr |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50885 | O-119 138kV Transmission Line Modifications | The existing 138 kV line O-119 between Arnott substation and Hartman Creek substation will be looped into the new 138 kV Interconnection Switching Station to provided transmission access. |  | M2 - Appendix A Approved | 2370000 | 2028-05-15 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Arnott | Hartman Creek | O-119 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50886 | 138kV Arnott Substation remote end work | At Arnott Substation, an independent, redundant comm-assisted relay scheme will be required. An additional line CCVT, line tuner, and wave trap will be installed on line O-119 to the new Interconnection Switching Station and the existing line O-119 relay panel 20-02 will be replaced with a new dual UPLC relay panel. |  | M2 - Appendix A Approved | 755000 | 2028-05-15 | Substation | Small miscellaneous substation equipment | Arnott |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50887 | 138kV Golden Sands Substation remote end work | At Golden Sands Substation, the scope of work includes installing an underground fiber to the new J1752 Interconnection Switching Station. |  | M2 - Appendix A Approved | 247000 | 2028-05-15 | Substation | Small miscellaneous substation equipment | Golden Sands |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50888 | 138kV Hartman Creek Substation remote end work | At Hartman Creek Substation an independent, redundant comm-assisted relay scheme will be required. (1) One additional line CCVT, line tuner, and wave trap will be installed on the existing line O-119. New jumpers will be installed to connect the new line trap. The existing line O-119 relay panel N3 will be replaced with new dual UPLC relay panel. |  | M2 - Appendix A Approved | 845000 | 2028-05-15 | Substation | Small miscellaneous substation equipment | Hartman Creek |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50889 | 138kV Harrison North Substation remote end work | At Harrison Substation, line relaying for A-105 line to Hartman Creek will require settings changes. |  | M2 - Appendix A Approved | 46000 | 2028-05-15 | Misc. | Relaying, protection, RTU and SCADA equipment | Harrison North |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | GIP | 50890 | 138kV J1752 Interconnection Facilities | The J1752 Transmission Owner Interconnected Facilities consists of substation work associated with the generator lead line entrance at the new interconnection switching station. The generator lead line will terminate on the attachment vangs of the H-frame dead-end serving as the Point of Change of Ownership (PCO). The TOIF portion will then include all bus and equipment from there down through the motor-operated disconnect (MOD) switch, surge arresters, rigid bus, and all foundations and steel support structures to the POI where it connects to the main bus within the 3-position ring. |  | M2 - Appendix A Approved | 616000 | 2028-05-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Shady Dr |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50546 | Bluepoint 230 kV New Substation and line Cut-ins | Other | 50892 | Bluepoint 230 kV Station | Entergy is proposing to construct a new 230 kV four breaker ring bus station named Bluepoint to serve a new customer cut into the new Commodore to Waterford 230 kV line (~10.4 miles in and out) near Donaldsonville, LA. |  | M2 - Appendix A Approved | 59600000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Commodore | Waterford | 1 | 230 |  | 10.4 |  | LA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50547 | East Beloit SS, DIC, Sub Rebuild | Other | 50893 | East Beloit SS, DIC, Sub Rebuild | In support of a distribution substation relocation/rebuild, ATC will extend COR-BEG 138kV (X-41) line approximately 0.15 mile (double circuit transmission) to the new East Beloit substation and install 2 sets of bus-tie disconnect switches. ATC will retire COR-ESB 69kV (Y-140) line (Approx. 0.5 miles) and the existing East Beloit SS location and install 2 line circuit breakers and 2 line disconnects at Dickinson SS. |  | M2 - Appendix A Approved | 7200000 | 2029-05-24 | Substation | Distribution substation - may include trans high side | East Beloit |  |  | 138 | 12 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50548 | Juneau Industrial SS, DIC, Transformer Addition | Other | 50894 | Juneau Industrial SS, DIC, Transformer Addition | In support of a distribution transformer addition, ATC will rebuild Juneau Industrial and will install 1 bus-side load break disconnect switch, 1 bus side air break 2 bus-tie disconnect switches. |  | M2 - Appendix A Approved | 4800000 | 2028-09-08 | Substation | Distribution substation - may include trans high side | Juneau Industrial |  |  | 69 | 12 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50549 | Waupun Business Park SS, DIC, Transformer Addition | Other | 50895 | Wilson St SS, DIC, Transformer Addition | To support a new distribution substation and associated station retirements, ATC will loop through the existing WAN-WANT 69kV (Y-306) line for new Wilson St SS. ATC will install 2 line disconnect switches and 2 bus-tie disconnect switches. ATC to retire portion of WAN-WANT 69kV (Y-306) line to Waupun Westside (WAW), Waupun Southside (WSS) and Comtech (COMH). |  | M2 - Appendix A Approved | 3200000 | 2028-12-31 | Substation | Distribution substation - may include trans high side | Wilson St |  |  | 69 | 12 |  |  | WI |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | Other | 50896 | Rock Creek 345 kV J1084 TOIF | Relocate TOIF for J1084 to new Rock Creek substation location |  | M2 - Appendix A Approved | 1139666 | 2028-12-31 | Misc. | Line relocation (road move) | Rock Creek | Rock Creek | 1 | 345 | 345 |  |  | IA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50550 | North Monroe Breaker and SCADA Asset Renewal | Other | 50897 | North Monroe Breaker and SCADA Asset Renewal | Asset Renewal of existing substation equipment due to age and condition. Existing and anticipated future poor performance and reliability issues. Replace 138kV Capacitor cans and update bank specifications and equipment as appropriate. ATC Planning to confirm the required MVAR capacity and switching device required. Replace relay panels and Station Manager RTU. Install to current ATC standards including Dual bus differential relays on the 69kV and 138kV busses. Replace 69kV Siemens model SP breaker in Position 719-S. Replace three Turner Electric disconnects and one ITE model HPL disconnect. Replace S&C circuit switcher in Position 207-S. Replace station power transformer connected to 69kV bus. |  | M2 - Appendix A Approved | 3105000 | 2029-07-02 | Substation | Substation (breakers only, no transformer) | North Monroe |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50551 | New Stillwell to Elderberry 345kV Line | Other | 51220 | Stillwell to Elderberry 345kV | Approximately 15 miles of 345kV transmission line |  | M2 - Appendix A Approved | 75000000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Elderberry | Stillwell |  | 345 |  | 15 |  | IN |  | Not Shared
MTEP25 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 50577 | Henderson County Capacitor Bank | Other | 51223 | Henderson County Capacitor Bank | Henderson County Capacitor Bank Addition |  | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Voltage Device | Capacitor (switched capacitor) | Henderson County |  |  | 69 |  |  |  | KY |  | Not Shared
MTEP25 | A | ENTERGY MISSISSIPPI, LLC. | South | 50368 | McAdams 500 kV Bus SPOF | BRP | 51238 | McAdams 500kV | Ensure the McAdams 500 kV station has redundant DC protection. |  | M2 - Appendix A Approved | 4100000 | 2026-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | McAdams 500kV |  |  | 500 |  |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY MISSISSIPPI, LLC. | South | 50367 | 2026 EML Asset Renewal Program | Other | 51239 | Multiple | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements |  | M2 - Appendix A Approved | 68400000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Multiple |  |  | 500 |  |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50352 | Amelia to Poly 69 kV Upgrades | BRP | 51240 | Amelia - Poly 69 kV line | Amelia - Poly 69 kV line upgrade. Upgrade bus and line bay bus at Poly. Upgrade jumpers and line bay riser at Amelia and Poly. Upgrade a couple spans on each end, all to a minimum of 1600A. |  | M2 - Appendix A Approved | 3700000 | 2029-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Amelia | Poly |  | 69 | 69 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50354 | Mid County to Stonegate 138 kV Rebuild | BRP | 51241 | Mid County - Stonegate 138 kV line | Mid County - Stonegate 138 kV line |  | M2 - Appendix A Approved | 6540000 | 2027-05-31 | Line Upgrade | Line rebuild on existing ROW | Mid County | Stonegate |  | 138 | 138 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50539 | Cargas 500 kV and Smalling 500-230 kV stations | Other | 51242 | Cargas 500 kV station | Cargas 500 kV station will be cut into the Perryville to Sterlington 500 kV lines 1 and 2 and Perryville to Baxter Wilson 500 kV line. |  | M2 - Appendix A Approved | 1210000000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Cargas |  |  | 500 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50356 | Port Acres Bulk to Legend 230 kV Rebuild | BRP | 51243 | Port Acres Bulk to Legend 230 kV line Ckt 1 | Cut Port Acres Bulk to Sandling 230 kV line in and out of Legend. Rebuild both Port Acres Bulk to Legend 230 kV lines. |  | M2 - Appendix A Approved | 21900000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Port Acres | Legend | 1 | 230 | 230 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50539 | Cargas 500 kV and Smalling 500-230 kV stations | Other | 51244 | Smalling 500-230 kV station and lines | Smalling 500/230 kV station will be cut into the Cargas to Baxter Wilson 500 kV line. Two additional 27 mile 500 kV lines from Smalling to Cargas. The Smalling 230 kV station will be a breaker and a half substation, including four 1,500 MVA 500/230 kV autotransformers and eight 230 kV lines going to six 230 kV stations which will feed the new load. |  | M2 - Appendix A Approved | 1 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Cargas | Smalling |  | 500 | 230 | 54 |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50356 | Port Acres Bulk to Legend 230 kV Rebuild | BRP | 51245 | Port Acres to Legend 230 kV Ckt 2 | Port Acres Bulk to Legend 230 kV Rebuild ckt 2 |  | M2 - Appendix A Approved | 1 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Port Acres | Legend | 2 | 230 | 230 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50540 | Sarepta to Mount Olive 500 kV Project | BRP | 51246 | Mt Olive to Sarepta 500 kV line | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer |  | M2 - Appendix A Approved | 470100000 | 2028-08-30 | Line New | New Transmission line, new ROW - may include terminations | Sarepta | Mt Olive |  | 500 |  | 60 |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50540 | Sarepta to Mount Olive 500 kV Project | BRP | 51247 | Mt Olive 500-230 kV Auto upgrade | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer |  | M2 - Appendix A Approved | 1 | 2028-08-30 | Transformer | Transformer Replacement | Mt Olive |  |  | 500 | 230 |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50540 | Sarepta to Mount Olive 500 kV Project | BRP | 51248 | Sarepta 500-345 Auto | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer |  | M2 - Appendix A Approved | 1 | 2028-08-30 | Transformer | Transformer New | Sarepta |  |  | 500 | 345 |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50350 | Babel to Webre 500 kV New Line | BRP | 51249 | Babel to Webre 500 kV | Construct a new ~145-mile 500 kV line from Babel to Webre 500 kV line. Construct a new 500 kV open-air Webre station to replace the obsolete GIS bus. |  | M2 - Appendix A Approved | 1066000000 | 2029-08-30 | Line New | New Transmission line, new ROW - may include terminations | Babel | Webre |  | 500 |  | 145 |  | LA | TX | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50357 | Harelson-Jones Creek Tap 69kV Upgrades | BRP | 51250 | Harelson to Jones Creek 69 kV upgrade | Upgrade Harelson to Jone Creek 69 kV line |  | M2 - Appendix A Approved | 14700000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Harelson | Jones Creek |  | 69 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50361 | Willow Glen Protection Improvement SPOF Project | BRP | 51251 | Willow Glen relay upgrades | Install a new battery bank at Willow Glen 138 kV station. The primary 1 relay needs to be on a separate DC panel than primary 2/backup relay. The breakers for the AT must have trip coil #1 and trip coil #2 fed from separate DC panels and the DC panels must be fed from separate battery sets. The DC panels cannot be wired in series or in parallel to one another. |  | M2 - Appendix A Approved | 4000000 | 2026-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Willow Glen |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50362 | Richard 500/138 kV Bus SPOF | BRP | 51252 | Richard 138 kV Bus, 500 kV Line relay upgrades | Relay upgrades for the 138 kV bus, 500 kV bus, including lines |  | M2 - Appendix A Approved | 8700000 | 2027-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Richard |  |  | 500 | 138 |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50363 | Little Prairie – Mud Lake Low Voltage Project | BRP | 51253 | Little Prairie reactive support | Install 223.90 MVAR reactive support (2-SVCs) at Little Prairie 230 kV station |  | M2 - Appendix A Approved | 54300000 | 2031-10-31 | Voltage Device | Static Var Compensator (STATCOM) | Little Prairie |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50364 | Waterford 500/230 kV AT Upgrade | BRP | 51254 | Waterford Auto terminal equipment upgrade | Upgrade Waterford 230 kV jumper (~0.26 miles, located inside 230 kV station) to 1200 MVA min. |  | M2 - Appendix A Approved | 310000 | 2030-06-01 | Substation | Small miscellaneous substation equipment | Waterford |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50360 | War Eagle 138 kV: Construct New Substation and Lines | BRP | 51255 | War Eagle 138 kV substation | Construct a new War Eagle 138 kV substation approximately 0.3 miles north of the Oak Ridge 138 kV substation that cuts into the Oak Ridge – Metro 138 kV. |  | M2 - Appendix A Approved | 110000000 | 2029-06-01 | Substation | Switching station (breakers only, no transformer) | War Eagle |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50360 | War Eagle 138 kV: Construct New Substation and Lines | BRP | 51256 | Porter to War Eagle 138 kV | Construct a new 138 kV line from Porter to the new War Eagle substation. |  | M2 - Appendix A Approved | 1 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | Porter | War Eagle |  | 138 |  | 8 |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50360 | War Eagle 138 kV: Construct New Substation and Lines | BRP | 51257 | War Eagle to Forest 138 kV line | Energize the abandoned 138 kV L-403 by terminating into the War Eagle and Forest 138 kV substations and rebuild. |  | M2 - Appendix A Approved | 1 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | Forest | War Eagle |  | 138 |  | 2.5 |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50359 | Bryan to Runny 138 kV New Line and Substation | BRP | 51258 | Runny Station | Build a new 138 kV switching station between College Station and Grimes 138 kV substations called Runny. |  | M2 - Appendix A Approved | 99400000 | 2030-06-01 | Substation | Switching station (breakers only, no transformer) | Runny |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50359 | Bryan to Runny 138 kV New Line and Substation | BRP | 51259 | Bryan to Runny line | Construct new Bryan to Runny 138 kV line |  | M2 - Appendix A Approved | 1 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Bryan | Runny |  | 138 |  | 13 |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50586 | 2026 ETI Asset Renewal Program | Other | 51260 | 2026 ETI Asset Renewal | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | M2 - Appendix A Approved | 34400000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Multiple |  |  | 500 | 69 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50353 | 2026 ENOL Asset Renewal Program | Other | 51261 | 2026 ENOL Asset Renewal Program | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | M2 - Appendix A Approved | 3200000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Multiple |  |  | 230 | 69 |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50355 | 2026 ELL Asset Renewal Program | Other | 51262 | 2026 ELL asset Renewal | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc |  | M2 - Appendix A Approved | 83300000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Multiple |  |  | 500 | 69 |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50358 | Dupont Beamont to Nitro 69 kV Station Upgrades | BRP | 51263 | Dupont Beaumont 69 kV | Upgrade a switch at Dupont Beaumont 69 kV station |  | M2 - Appendix A Approved | 250000 | 2029-06-01 | Substation | Small miscellaneous substation equipment | Supont Beaumont |  |  | 69 | 69 |  |  | TX |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50587 | Darnen Substation | Other | 51264 | Darnen Substation | Tap the Great River Energy (GRE) owned 'AG-MB' 115 kV line between Morris and Walden to serve a new distribution substation with an 'in-and-out' configuration. |  | M2 - Appendix A Approved | 2362888 | 2026-09-15 | Substation | Distribution substation - may include trans high side | Darnen |  |  | 115 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50329 | Substation 91 Expansion | BRP | 51265 | Sub 91-Quad Cities 345 kV Line Reconfiguration | Relocate the existing Sub 91-Quad Cities 345 kV line to a new line terminal at Sub 91 |  | M2 - Appendix A Approved | 3000000 | 2028-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sub 91 | Quad Cities | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50329 | Substation 91 Expansion | BRP | 51266 | Sub 91-Sub 56 345 kV Line Reconfiguration | Relocate the existing Sub 91-Sub 56 345 kV line to a new line terminal at Sub 91 |  | M2 - Appendix A Approved | 3500000 | 2028-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sub 91 | Sub 56 | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50588 | Forest Junction – Branch River 345 kV (W-15), Line Uprate | BRP | 51267 | Forest Junction – Branch River 345 kV (W-15), Line Uprate | Uprate W-15 Forest Junction – Branch River 345 kV line per ATC T-Line design standards to achieve minimum 1918 Amps (1146 MVA) normal and 2490 Amps (1488 MVA) emergency ratings for all seasons. |  | M2 - Appendix A Approved | 7754000 | 2029-01-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Forest Junction | Branch River |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | ITC | East | 50212 | Avery - New DTE Interconnection | Other | 51268 | Avery-Midtown_Install Underground Fiber | Install underground Fiber from Avery to Midtown station. |  | M2 - Appendix A Approved | 1721000 | 2028-09-29 | Misc. | Communication equipment | Avery | Midtown |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50212 | Avery - New DTE Interconnection | Other | 51269 | Avery-Stonepool_Install Underground Fiber | Install underground Fiber from Avery to Stone Pool station. |  | M2 - Appendix A Approved | 2108000 | 2028-09-29 | Misc. | Communication equipment | Avery | Stonepool |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50590 | Upgrade Sunset 120 kV Switch | BRP | 51273 | Sunset - Upgrade HI Switch | Upgrade "HI" switch at Sunset 120 kV station |  | M2 - Appendix A Approved | 168000 | 2030-06-01 | Substation | Small miscellaneous substation equipment | Sunset |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50591 | Install Phoenix 120 kV Capacitor | BRP | 51274 | Phoenix - Install 50 MVAr Capacitor | Install a 50 MVAr capacitor at Phoenix 120 kV bus 103 and a synchronous breaker with associated disconnects. |  | M2 - Appendix A Approved | 1500000 | 2030-06-01 | Voltage Device | Capacitor (switched capacitor) | Phoenix |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50594 | Helena Harbor Load Addition | Other | 51278 | AECC Helena Harbor to Entergy Ritchie 230kV radial line | A member cooperative's new 230kV Helena Harbor station will be served on a new, approximately 6-mile 230kV radial line off Entergy's Ritchie 230kV station. |  | M2 - Appendix A Approved | 13200000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Helena Harbor 230kV | Ritchie 230kV |  | 230 |  | 6 |  | AR |  | Not Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50594 | Helena Harbor Load Addition | Other | 51279 | Entergy's 230kV Ritchie station position | Entergy will add a new 230kV position to their existing 230kV Ritchie station to accommodate a new radial line. |  | M2 - Appendix A Approved | 5000000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Entergy's 230kV Ritchie |  |  | 230 |  |  |  | AR |  | Not Shared
MTEP25 | A | ITC | East | 50597 | DTE New Hudson Interconnection | Other | 51283 | New Hudson - Install New 120 kV Station | Construct New Hudson as a new 4-breaker ring bus configuration, 120 kV station and allow enough space for future breaker and a half station configuration once DTE’s future positions are needed. All new 120 kV breakers should be standard 3000 A 40 kA breakers. We want to reserve 4 additional rows for future connections. |  | M2 - Appendix A Approved | 10000000 | 2028-03-31 | Substation | Substation (breakers only, no transformer) | New Hudson |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50597 | DTE New Hudson Interconnection | Other | 51284 | Proud - Add CVT and modify relaying at position HB | Add CVT and modify relaying at position HB. |  | M2 - Appendix A Approved | 103000 | 2028-03-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Proud |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50597 | DTE New Hudson Interconnection | Other | 51285 | Cody - Add CVTs to HC and Bus 101 and modify relaying | Add CVTs to HC and Bus 101 and modify relaying. |  | M2 - Appendix A Approved | 267500 | 2028-03-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Cody |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50597 | DTE New Hudson Interconnection | Other | 51286 | Cody-Proud_New Hudson Cut-In | Cut in Cody – Proud 120 kV line about 0.15 mile from Tamarack 120 kV Tap into New Hudson 120 kV station. |  | M2 - Appendix A Approved | 1793000 | 2028-03-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Cody | Proud |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50598 | Progress SS, DIC, Substation Rebuild | Other | 51287 | Progress SS, DIC, Substation Rebuild | ATC will install a 138 kV loop through substation on the Aviation - Ellinwood 138 kV (X-50) line with line switches to support a distribution substation rebuild. |  | M2 - Appendix A Approved | 2500000 | 2028-04-26 | Substation | Distribution substation - may include trans high side | Progress |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50599 | New Merom 345 kV Substation Load Addition | Other | 51288 | New 345kV Line to Customer Site | Extend a new 345kV line from Merom Transmission Station, approximately 1-mile, to a new data center. |  | M2 - Appendix A Approved | 7520000 | 2027-02-01 | Line New | New Transmission line, new ROW - may include terminations | Merom |  |  | 345 |  | 1 |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50599 | New Merom 345 kV Substation Load Addition | Other | 51289 | Install 345kV Breaker and relay/control upgrades | Install 345 kV breaker and make station upgrades at Merom station to accommodate the new 345kV line. |  | M2 - Appendix A Approved | 1626381 | 2027-02-01 | Substation | Circuit Breaker (replacement at existing substation) | Merom |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50599 | New Merom 345 kV Substation Load Addition | Other | 51290 | New Customer Switchyard 345kV | Construct new 345kV straight bus station for customer |  | M2 - Appendix A Approved | 3644303 | 2027-02-01 | Substation | Switching station (breakers only, no transformer) | Merom |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50600 | Oak Bend 230 kV station | Other | 51291 | Oak Bend | New Oak Bend 230 kV station fed from Baxter Wilson 230 kV substation |  | M2 - Appendix A Approved | 150000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Oak Bend |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50600 | Oak Bend 230 kV station | Other | 51292 | Baxter Wilson autotranformers | 2x 500/230 autotransformers at Baxter Wilson 500/230 station |  | M2 - Appendix A Approved | 1 | 2029-12-01 | Transformer | Transformer New | Baxter Wilson |  |  | 500 | 230 |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY MISSISSIPPI, LLC. | South | 50600 | Oak Bend 230 kV station | Other | 51293 | Baxter Wilson 230 station | new Baxter Wilson 230 kV station fed from existing Baxter Wilson 500 kV through 2-500/230 kV auto transformers. |  | M2 - Appendix A Approved | 1 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Baxter Wilson |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50601 | Andes 230 kV Expansion | Other | 51294 | Andes Distribution | Expand existing 230 kV Andes Substation with three breaker bays with (3) 150 MVA 230/34.5 kV transformers. |  | M2 - Appendix A Approved | 40000000 | 2028-04-01 | Substation | Substation bus upgrade | Andes |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50602 | Green Acres 500/230 kV New Substation | Other | 51295 | Green Acres 500/230 kV station | New Green Acres 500/230 kV station will cut in on Lakeover – Ray Braswell 500 kV and Lakeover - McAdams 500 kV lines. |  | M2 - Appendix A Approved | 240000000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | Green Acres |  |  | 500 | 230 |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50602 | Green Acres 500/230 kV New Substation | Other | 51296 | County Line 230kV | New 230 kV substation fed from 3-230 lines from the Green Acres 500/230 substation |  | M2 - Appendix A Approved | 72000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | County Line | Green Acres |  | 230 |  |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50602 | Green Acres 500/230 kV New Substation | Other | 51297 | Green Acres 500/230 | 2-500/230 Autotransformers install at new Green Acres 500/230 station. |  | M2 - Appendix A Approved | 1 | 2029-12-01 | Transformer | Transformer New | Green Acres |  |  | 500 | 230 |  |  | MS |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50602 | Green Acres 500/230 kV New Substation | Other | 51298 | Green Acres - County line | 3-230 kV lines connecting Green Acres - County line |  | M2 - Appendix A Approved | 1 | 2029-12-01 | Line New | New Transmission line, new ROW - may include terminations | Green Acres | County Line |  | 230 |  | 3 |  | MS |  | Not Shared
MTEP25 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 50501 | Byron - Pleasant Valley 161kV Terminal Upgrade | BRP | 51311 | Byron Substation Modernization | Replacing outdated breakers and relays. |  | M2 - Appendix A Approved | 2300000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Byron |  |  | 345 | 161 |  |  | MN |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50608 | Riparian 115 kV Station | Other | 51312 | Riparian 115 kV Station | Entergy is proposing to construct a new 115 kV station named Riparian to serve a new customer cut into the existing Alliance to Happy Jack 115 kV line in Point Celeste, LA. |  | M2 - Appendix A Approved | 38200000 | 2027-12-30 | Substation | Switching station (breakers only, no transformer) | Alliance | Happy Jack |  | 115 |  |  |  | LA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50612 | Blackhawk SS 69kV Pumping Plant Installation | Other | 51315 | Blackhawk SS 69kV Pumping Plant Installation | Relocate Pressurization Source to Blackhawk SS by installing new pumping plant with associated enclosure, tank, pressurization skid & controls, and associated piping connections. Remove the existing pressurization plant at Terrace Riser. |  | M2 - Appendix A Approved | 2900000 | 2028-05-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Blackhawk |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50613 | Central SS, DIC, New Substation | Other | 51316 | Central SS, DIC, New Substation | Construct a new substation with one new 69/12.47 kV, 3.75/5.25 MVA transformer with high-side switch. Install 3-way MOD with supervisory control near Y-71 structure 99. Route approx. 0.5 miles of new 69kV line to new SS location. |  | M2 - Appendix A Approved | 3200000 | 2027-07-08 | Substation | Distribution substation - may include trans high side | Central |  |  | 69 |  | 0.5 |  | WI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50615 | New Central 138 kV Substation Load Addition | Other | 51319 | New position at Central 138 kV Substation | New 138 kV position at Central substation |  | M2 - Appendix A Approved | 1000000 | 2028-06-01 | Substation | Switching station (breakers only, no transformer) | Central |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50617 | New 345 kV Lumberjack substation for Load Connection | Other | 51320 | New 345 kV Lumberjack substation | New 345 kV Lumberjack substation |  | M2 - Appendix A Approved | 20000000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Lumberjack |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50617 | New 345 kV Lumberjack substation for Load Connection | Other | 51321 | New 345 kV position | Add 345 kV position for line to new Lumberjack substation |  | M2 - Appendix A Approved | 4500000 | 2027-12-01 | Substation | Substation bus upgrade | Montgomery |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50617 | New 345 kV Lumberjack substation for Load Connection | Other | 51322 | New Montgomery to Lumberjack 345 kV double circuit line | New 345 kV Line from Montgomery to Lumberjack substation. Double circuit with existing Montgomery-Labadie 345 kV |  | M2 - Appendix A Approved | 14000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Montgomery | Lumberjack |  | 345 |  |  |  | MO |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50104 | Upgrade PJM project b3775.8 St. John to Crete 345 kV | Other | 50154 | St. John to Crete upgrade | Replace existing switch and associated cabling to 4000A. |  | M2 - Appendix A Approved | 1150000 | 2026-06-01 | Substation | Small miscellaneous substation equipment | St. John | Crete | 1 | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50105 | Reconfigure PJM project b3775.9. Green Acres 345kV substation | Other | 50155 | Green Acres 345kV sub reconfigure | At Green Acres, Upgrade the existing 34517 line drop to 4000A (2-1590 AL). Project will also reconfigure the existing St. John and Green Acres 345kV connections, creating a Green Acres to University Park 345kV line and St. Johns to Olive 345kV line. Project includes all associated protection and communication needed to create new tie lines. |  | M2 - Appendix A Approved | 2150000 | 2026-06-01 | Substation | Small miscellaneous substation equipment | Green Acres |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | METC | East | 20020 | Rebuild Gaylord - Mio Dam 138kV line | Other | 52131 | Gaylord-Lewiston Jct_Rebuild with OPGW | Rebuild Gaylord-Lewiston Jct. 138 kV section with 954 ACSR overhead conductor capable of double circuit 230kV. OPGW will be installed on the rebuild. All line switches will be 2000A or greater, if replaced. |  | M2 - Appendix A Approved | 0 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Gaylord | Lewiston Jct. |  | 138 |  |  | 21.23 | MI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 22874 | Upgrade Ashley 161 kV substation | Other | 26907 | 26907-Ashley- | Install high side interrupting devices on XFMRs 1, 2, & 3 Install line breakers on Cahokia and Hall Street | AmerenMO | M2 - Appendix A Approved | 4100000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Ashley |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 22907 | Upgrade Tuscola West 138 kV substation | Other | 26916 | 26916-Tuscola West- | Rebuild to ring bus | AmerenIL | M2 - Appendix A Approved | 5800000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Tuscola West |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 22908 | Rebuild Joppa - Marion South 161kV line | Other | 26922 | 26922-Joppa-Marion South | Rebuild the Joppa-Marion South-1 161 kV line on direct-embed steel H-Frame structures with conductor capable of carry 2000 amps at Summer Emergency conditions. | AmerenIL | M2 - Appendix A Approved | 46500000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Joppa | Marion South |  | 161 |  |  |  | IL |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 28683 | Phase 2: 25.1 MVAR Capacitor Bank at Dobbin 138 kV Substation | 25.1 MVAR Capacitor Bank | Entergy-TX | M2 - Appendix A Approved | 5800000 | 2027-06-01 | Voltage Device | Capacitor (switched capacitor) | Dobbin |  |  | 138 | 138 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 28684 | Phase 1: Grimes Relay Improvement SPOF | Ensure Grimes 138 kV bus and 345/138 kV AT1 have redundant high-speed protection including redundant DC supply such that loss of any component of the auto protection scheme would not result in delayed fault clearing. | Entergy-TX | M2 - Appendix A Approved | 5300000 | 2026-09-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Grimes |  |  | 345 | 138 |  |  | TX |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50166 | Racine County, DIC, Mount Pleasant Substation Expansion | Other | 51417 | Mount Pleasant +/- 350 Mvar STATCOM | Mount Pleasant +/- 350 Mvar STATCOM. WO 605957 |  | M4 - Project in Service | 83000000 | 2025-12-29 | Transformer | Transformer New | Mount Pleasant |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50166 | Racine County, DIC, Mount Pleasant Substation Expansion | Other | 51418 | Mount Pleasant Expansion for Western Feed & 138 kV capacitor banks | Mount Pleasant Expansion for Western Feed & 138 kV capacitor banks. WO 606270 |  | M3 - Under Construction | 20000000 | 2030-07-01 | Transformer | Transformer New | Mount Pleasant |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50149 | Arrowhead 230kV SPF Upgrade | BRP | 50243 | Arrowhead 230kV | Add redundancy or monitoring to the single point of failures to mitigate P5 contingencies associated with the Arrowhead 230kV buses. |  | M2 - Appendix A Approved | 100000 | 2028-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Arrowhead 230kV |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50256 | Overton 345 kV Ring Bus Substation | Overton 345kV switchyard will be converted to four (4) position ring bus and a second 345 / 161 kV transformer rated for 560 MVA will be installed. |  | M2 - Appendix A Approved | 31000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Overton |  |  | 345 |  |  |  | MO |  | Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50257 | California-Overton-1 161 kV Line | Rebuild ~0.04 miles of the California - Overton 161 kV transmission line to be rated for a minimum of 1600 Amps. This is the span of line from the California 161 kV Arbor to first structure (205) outside of the same substation. |  | M2 - Appendix A Approved | 1000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | California | Overton |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50258 | Montgomery-Burns-5481 345 kV Line | Rebuild Montgomery-Burns-5481 345kV line to be 3000 Amps summer emergency rated. This is approximately 30 miles of line from the Montgomery 345 kV substation to the new Burns 345 kV substation |  | M2 - Appendix A Approved | 31000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Montgomery | Burns |  | 345 |  |  |  | MO |  | Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50259 | Montgomery 345 kV Substation | To relieve base case and contingency overload on McCredie to Montgomery 345kV line Ameren will upgrade limiting bus conductor at Montgomery substation to 3000 Amps summer emergency rating. |  | M2 - Appendix A Approved | 350000 | 2027-12-01 | Substation | Substation bus upgrade | Montgomery |  |  | 345 |  |  |  | MO |  | Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50260 | Loy Martin 161 kV Substation | Bus conductor at Loy Martin 161 kV will be upgraded for 1600 Amps minimum. Upgrade Loy Martin H3 Line jumper conductor and H2 bus tie jumper conductor. |  | M2 - Appendix A Approved | 110000 | 2027-12-01 | Substation | Substation bus upgrade | Loy Martin |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50261 | Rebuild Loy Martin-Katy-7429 161 kV Line | Rebuild approximately 8.94 miles of the Loy Martin-Katy-7429 161 kV transmission line for 1600 Amps minimum. This is the length of line from the Loy Martin 161 kV substation to structure 676 outside of the newly constructed Katy 161 kV substation |  | M2 - Appendix A Approved | 5500000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Loy Martin | Katy |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | GIP | 50262 | Relocate Overton-Sedalia East-1 line at Cooper 161 kV Substation. | The former Overton-Sedalia East-1 line will be relocated to the new Cooper 161 kV Substation. |  | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Cooper |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50269 | Big Cedar 345 kV Substation Expansion Phase 1 | Expand Big Cedar 345 kV Switching Station to accommodate two new 345 kV lines to serve a new customer owned substation and a new 2nd 345 kV line between Big Cedar and Morgan Valley. |  | M2 - Appendix A Approved | 14615214 | 2027-09-30 | Substation | Switching station (breakers only, no transformer) | Big Cedar | Big Cedar |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50270 | Big Cedar 345 kV Reactive Compensation Phase 1 | Add reactive compensation at Big Cedar to support Phase 1 load addition |  | M2 - Appendix A Approved | 11996367 | 2027-09-30 | Voltage Device | Capacitor (switched capacitor) | Big Cedar | Big Cedar |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50271 | Big Cedar to Morgan Valley #2 345 kV line | Add 2nd Big Cedar - Morgan Valley 345 kV line on existing structures |  | M2 - Appendix A Approved | 6997500 | 2027-09-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Big Cedar | Morgan Valley |  | 345 | 345 |  | 6 | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50272 | Morgan Valley Substation Expansion | Expand Morgan Valley to add new line terminal for new Big Cedar - Morgan Valley #2 345 kV line |  | M2 - Appendix A Approved | 1847560 | 2027-09-30 | Substation | Switching station (breakers only, no transformer) | Morgan Valley | Morgan Valley |  | 345 | 345 |  | 6 | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50273 | Beverly to Hills 345 kV line | Construct new Beverly - Hills 345 kV line to support Phase 1 load addition at Big Cedar, a portion of the line to be located on new ROW and a portion of the line to overbuild existing 161 kV line between Bertram - Rose Hollow - Johnson |  | M2 - Appendix A Approved | 159575000 | 2029-02-28 | Line Upgrade | Line rebuild on existing ROW | Beverly | Hills |  | 345 | 345 | 5 | 35 | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50277 | Beverly Substation Expansion | Expand Beverly substation to accommodate the new Beverly - Johnson 345 kV line terminal |  | M2 - Appendix A Approved | 4342675 | 2027-09-30 | Substation | Substation (breakers only, no transformer) | Beverly | Beverly |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50278 | Big Cedar to Customer Line #1 | Construct new 345 kV line from Big Cedar to customer owned substation |  | M2 - Appendix A Approved | 1767500 | 2027-09-30 | Line New | New Transmission line, new ROW - may include terminations | Big Cedar | Customer Owned Substation |  | 345 | 345 | 0.25 |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50279 | Big Cedar to Customer Line #2 | Construct new 345 kV line from Big Cedar to customer owned substation |  | M2 - Appendix A Approved | 1767500 | 2027-09-30 | Line New | New Transmission line, new ROW - may include terminations | Big Cedar | Customer Owned Substation |  | 345 | 345 | 0.25 |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50280 | Big Cedar 345 kV Substation Expansion Phase 2 | Expand Big Cedar 345 kV Switching Station to accommodate two new 345 kV lines to serve a new customer owned substation and a new terminal for phase 2 reactive compensation. |  | M2 - Appendix A Approved | 7552222 | 2028-09-30 | Substation | Switching station (breakers only, no transformer) | Big Cedar | Big Cedar |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50281 | Big Cedar Substation Reactive Compensation Phase 2 | Install additional reactive compensation (a new +500 MVAR SCU is being initially proposed) to support the additional load at Big Cedar. |  | M2 - Appendix A Approved | 150000000 | 2028-09-30 | Voltage Device | Dynamic Var | Big Cedar | Big Cedar |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50282 | Big Cedar to Customer Line #3 | Construct new 345 kV line from Big Cedar to customer owned substation |  | M2 - Appendix A Approved | 3433750 | 2028-09-30 | Line New | New Transmission line, new ROW - may include terminations | Big Cedar | Customer Owned Substation |  | 345 | 345 | 0.5 |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50283 | Big Cedar to Customer Line #4 | Construct new 345 kV line from Big Cedar to customer owned substation |  | M2 - Appendix A Approved | 3433750 | 2028-09-30 | Line New | New Transmission line, new ROW - may include terminations | Big Cedar | Customer Owned Substation |  | 345 | 345 | 0.5 |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50284 | Rose Hollow Relay Upgrades | Upgrade relays at Rose Hollow due to addition of Beverly - Johnson 345 kV line |  | M2 - Appendix A Approved | 424412 | 2027-09-30 | Substation | Small miscellaneous substation equipment | Rose Hollow | Rose Hollow |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50285 | Hills - Johnson Line Relocation | Relocate existing Hills - Johnson line to new 345 kV ring bus at Johnson |  | M2 - Appendix A Approved | 2161250 | 2027-09-30 | Line Upgrade | Line rebuild on existing ROW | Johnson | Hills |  | 345 | 345 |  | 0.25 | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50157 | Big Cedar Load Expansion | Other | 50287 | PCI Relay Upgrades | Upgrade relays at PCI due to addition of Beverly - Johnson 345 kV line |  | M2 - Appendix A Approved | 189925 | 2027-09-30 | Substation | Small miscellaneous substation equipment | PCI | PCI |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50161 | Empire Mine – Huron 138 kV (X-119), OPGW Addition | Other | 50289 | Empire Mine – Huron 138 kV (X-119), OPGW Addition | ~10.4 Miles of OPGW Installation - This project will align with the 446 T-Line Reinsulate Project between the National and Presque Isle substations as well as the ~7.5 Miles of OPGW Installation on X-118 (MTEP24) will provide an alternate fiber path establishing two diverse OPGW fiber routes providing high-speed fiber communications connecting into ATC larger OPGW Network Infrastructure. |  | M2 - Appendix A Approved | 13000000 | 2028-04-15 | Misc. | Communication equipment | Empire Mine | Huron | X-119 | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50162 | Substation Technology Package #2 – 2026 | Other | 50290 | Substation Technology Package #2 – 2026 | High level scope is to install Wi-Fi AP’s & Rogue Detection at various substations and remove Inverter equipment at various substations to complete the Wireless connectivity and Cyber Security fortifications. |  | M3 - Under Construction | 11700000 | 2027-06-24 | Misc. | Communication equipment | Various |  |  | 0 |  |  |  | WI |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50163 | New J1358 IC Facilities Interconnection 138 kV | GIP | 50291 | J1358 POI substation | A greenfield 138kV breaker and a half substation that will be cut into the Luchtman Road – Shoreline 138kV line |  | M2 - Appendix A Approved | 19346657 | 2028-05-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Luchtman Rd | Shoreline | 1 | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50163 | New J1358 IC Facilities Interconnection 138 kV | GIP | 50292 | J1358 Line Tap | Tap in / tap out facilities from Luchtman Road – Shoreline 138kV line to new greenfield 138kV station plus fiber runs from greenfield station to Luchtman Road station. |  | M2 - Appendix A Approved | 2385428 | 2028-05-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Luchtman Rd | Shoreline | 1 | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50163 | New J1358 IC Facilities Interconnection 138 kV | GIP | 50293 | J1358 TOIF | 2 monopoles for lead line to Generating Facility plus metering infrastructure. |  | M2 - Appendix A Approved | 1664900 | 2028-05-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Luchtman Rd | Shoreline | 1 | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50165 | Racine County, DIC, Stratus Substation | Other | 50294 | Racine County, DIC, Stratus Substation | A new 138/24.9 kV breaker-and-a-half substation named Stratus, 138 kV capacitor banks, and construct short transmission lines to cut into the Mount Pleasant-Nimbus 138 kV lines (X-171, X-172) and loop in and out of the Stratus Substation. |  | M3 - Under Construction | 68500000 | 2027-06-28 | Substation | Distribution substation - may include trans high side | Stratus |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50166 | Racine County, DIC, Mount Pleasant Substation Expansion | Other | 50295 | Mount Pleasant SS - Install a new 500 MVA, 345/138 kV transformer | Mount Pleasant SS - Install a new 500 MVA, 345/138 kV transformer. WO 605767 |  | M4 - Project in Service | 14000000 | 2025-06-01 | Transformer | Transformer New | Mount Pleasant |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50167 | Racine County, DIC, Jupiter Substation | Other | 50296 | Racine County, DIC, Jupiter Substation | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, +/- 350 Mvar STATCOM, 138 kV capacitor banks, 4 – 345 kV line terminal. |  | M3 - Under Construction | 295000000 | 2027-01-01 | Substation | Distribution substation - may include trans high side | Jupiter |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50168 | Racine County Western Feed Transmission Line Project | Other | 50297 | Racine County Western Feed Transmission Line Project | Construct two new 345 kV double circuit lines from the existing Arcadian – Pleasant Prairie (PLPL81)/Arcadian – Paris (W-30) 345 kV double circuit line to loop in and out of the Jupiter and Mount Pleasant. Construct a new Jupiter – Mount Pleasant 345 kV line. |  | M3 - Under Construction | 124000000 | 2027-01-01 | Line New | New Transmission line, new ROW - may include terminations | Jupiter | Mount Pleasant |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP25 | A | ITC | East | 18192 | Rebuild Hines - Levan 120 kV Line | BRP | 25026 | HINES-LEVAN_ Rebuild | Rebuild the 954 ACSR sections (~0.5 mile) from structure #5680A to Levan and from structure #5686 to Hines with 1431 ACSR using 120kV, double-circuit construction. Install OPGW on the rebuilt sections. | ITCT | M2 - Appendix A Approved | 1645000 | 2028-03-15 | Line Upgrade | Line rebuild on existing ROW | Hines | Levan | 1 | 120 |  |  | 0.5 | MI |  | Not Shared
MTEP25 | A | ITC | East | 18192 | Rebuild Hines - Levan 120 kV Line | BRP | 25028 | Hines - Terminate Fiber into Station | Replace substation fiber runs and patch panels at Hines and install comm cabinet for patch panels at this station. | ITCT | M2 - Appendix A Approved | 141000 | 2028-03-15 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Hines |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 18192 | Rebuild Hines - Levan 120 kV Line | BRP | 25029 | Levan - Replace HD Line Entrance & Terminate Fiber | Upgrade the 954 ACSR bus (line drop) at Levan 120kV position "HD" to at least 375 MVA for summer emergency rating. Replace substation fiber runs and patch panels at Levan and install comm cabinet for patch panels at this station. | ITCT | M2 - Appendix A Approved | 149000 | 2028-03-15 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Levan |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 25328 | Upgrade Charleston NE 138kV line | Other | 28483 | 28483-Charleston NE- | Add line breakers and address aging infrastructure | AmerenIL | M2 - Appendix A Approved | 4019794 | 2027-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Charleston NE |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A |  | Central | 50731 | IPL Adoption of Seasonal Ratings - BRP | Other | 51506 | 345-10 (Whitestown - J993) | Seasonal Rating Adoption |  | M2 - Appendix A Approved | 0 | 2026-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Whitestown | J993 |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A |  | Central | 50731 | IPL Adoption of Seasonal Ratings - BRP | Other | 51507 | 345 - 10 (Whitestown - Wolf Creek) | Seasonal Rating Adoption |  | M2 - Appendix A Approved | 0 | 2029-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Whitestown | Wolf Creek |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50149 | Arrowhead 230kV SPF Upgrade | BRP | 51550 | Arrowhead 230 kV EEE | A new EEE will be required to address the redundancy needed to mitigate single points of failure within the Projection System |  | M2 - Appendix A Approved | 2900000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Arrowhead 230 kV |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25203 | Highland – Hill Valley 138 kV, Construct New Line | Other | 28255 | Highland – Hill Valley 138 kV, Construct New Line | Create a new Highland - Hill Valley 138 kV line by: - Converting 6.25 miles of the existing Highland - Eden 69 kV line Y-207 to 138 kV. Along the 69 kV corridor, new easements will be required. - Construct 0.2 miles of new 138 kV into Highland SS. - Construct 1 mile of new 138 kV into Hill Valley SS. - Add one new ring bus position at Highland SS. - Add one new ring bus position at Hill Valley SS. - Retire and remove 0.2 miles of Y-207 into Eden SS and Highland SS. - Retire and remove two breakers, one at Eden SS and one at Highland SS. | ATC | M2 - Appendix A Approved | 11800000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Highland | Hill Valley |  | 138 |  | 1 | 6.4 | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25185 | Small Capital Project and Asset Renewal Program 2026 | Other | 28264 | Small Capital Project and Asset Renewal Program 2026 | See project description. | ATC | M3 - Under Construction | 45000000 | 2031-03-31 | Substation | Substation (breakers only, no transformer) | Various Subs |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25186 | Communications Reliability Program 2026 | Other | 28265 | Communications Reliability Program 2026 | See project description. | ATC | M3 - Under Construction | 2100000 | 2027-10-05 | Misc. | Communication equipment | Various Subs |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25240 | Line Clearance Mitigation Program 2026 | Other | 28266 | Line Clearance Mitigation Program 2026 | See project description. | ATC | M3 - Under Construction | 9000000 | 2030-06-10 | Line Upgrade | Generic transmission line project (try not to use the generic) | Various Lines |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25187 | Load Interconnection Program 2026 | Other | 28267 | Load Interconnection Program 2026 | See project description. | ATC | M3 - Under Construction | 19000000 | 2031-04-02 | Substation | Distribution substation - may include trans high side | Various Subs |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50696 | New Huster-McClay 138 kV line tap for Hayford load | Other | 51440 | Huster-McClay 138 kV line tap | Huster-McClay 138 kV line tap |  | M2 - Appendix A Approved | 500000 | 2027-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Huster | McClay |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50698 | New Scotland 345/69kV Substation | Other | 51443 | 345kV | 345/69kV Ring-Bus Station |  | M2 - Appendix A Approved | 16000000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | 16PETE | 16W_BLOOMINGTON |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50698 | New Scotland 345/69kV Substation | Other | 51444 | Two 345/69kV Transformers | Two 345/69kV Transformers, 168 MVA each |  | M2 - Appendix A Approved | 14000000 | 2029-12-01 | Transformer | Transformer New | Scotland 345kV |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50698 | New Scotland 345/69kV Substation | Other | 51445 | 69kV Ring-Bus Station | 69kV Ring-Bus Station |  | M2 - Appendix A Approved | 8000000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | Scotland 69kV |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50702 | Elm Road HVB Breaker and Relay Asset Renewal | Other | 51449 | Elm Road HVB Breaker and Relay Asset Renewal | Asset Renewal |  | M2 - Appendix A Approved | 8400000 | 2030-04-26 | Substation | Circuit Breaker (replacement at existing substation) | Elm Road |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50711 | Brookings County - Lyon County 345kV Davit Arm Replacement | MVP | 51458 | Brookings County - Lyon County Davit Arm Replacement | Condition replacement of cracked Davit Arms on Brookings County- Hawks Nest Lake - Lyon County and Brookings County - Steep Bank Lake - Lyon County and Hampton Helena 345kV line structures. |  | M2 - Appendix A Approved | 18100000 | 2030-09-30 | Line Upgrade | Line rebuild on existing ROW | Lyon County | Brookings County | 1 | 345 |  |  | 58 | MN | SD | Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50489 | Split Rock - Chanarambie 345kV line JTIQ | Other | 51460 | Renner 345kV/115kV transformer | Add (1) 345/115kV transformers at Renner |  | M2 - Appendix A Approved | 5000000 | 2033-06-30 | Transformer | Transformer New | Renner |  |  | 345 | 115 |  |  | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50711 | Brookings County - Lyon County 345kV Davit Arm Replacement | MVP | 51461 | Lyon County to Helena Davit Arm Replacement | Age and Condition rebuild of davit arms for Lyon County to Helena (inclusive of line segments extending from Lyon County to MN Valley, and Cedar Mountain to Franklin). |  | M2 - Appendix A Approved | 57100000 | 2030-09-30 | Line Upgrade | Line rebuild on existing ROW | Lyon County | Helena | 1 | 345 |  |  | 177 | MN |  | Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50711 | Brookings County - Lyon County 345kV Davit Arm Replacement | MVP | 51462 | Helena to Hampton 345kV Davit Arm Replacement | Like-for-like age and condition replacement of select davit arms on Hampton - Helena 345kV line |  | M2 - Appendix A Approved | 16700000 | 2030-09-30 | Line Upgrade | Line rebuild on existing ROW | Hampton | Helena | 1 | 345 |  |  | 52 | MN |  | Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50691 | LEAP Phase 2 EPR Mitigations | BRP | 51437 | LEAP Phase 2 & Pittsboro EPR Mitigations | Reactive and thermal project mitigations for LEAP Phase 2 (MTEP 50208) area large load. |  | M2 - Appendix A Approved | 45000000 | 2029-06-29 | Voltage Device | Capacitor (switched capacitor) | Edwards |  |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50077 | New Aster 138 kV interconnection (J1777) | GIP | 50117 | Aster 138 kV (J1777) IF POS | The Great Plains Solar (J1777) Generating Facility will interconnect with the Transmission System via a 138 kV leadline running from the Interconnection Customer's collector substation to the Transmission Owner's Aster Substation in Perry County, IL. |  | M2 - Appendix A Approved | 800000 | 2026-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Aster |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50084 | New Ramsey East 138 kV Connection (J1714) | GIP | 50124 | Ramsey East 138 kV (J1714) IF POS | Install a new 138 kV line position to serve as the Point of Interconnection for Saluki Solar, LLC within the Ramsey East Substation. |  | M2 - Appendix A Approved | 800000 | 2026-12-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Ramsey East |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50100 | Rebuild Baumgartner 138 kV Substation | Other | 50149 | Baumgartner | Baumgartner 138 Aging Infrastructure |  | M2 - Appendix A Approved | 6300000 | 2028-06-01 | Substation | Small miscellaneous substation equipment | Baumgartner |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50185 | Replace Marion South 161/138 kV transformer | Other | 50323 | Marion South XFMR 1 Replacement | Replace XFMR 1 at Marion South with a new 161/138kV 300 MVA unit. |  | M2 - Appendix A Approved | 3600000 | 2026-12-01 | Transformer | Transformer Replacement | Marion South |  |  | 161 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50324 | Montgomery 345kV Substation BAAH Leg | Montgomery 345kV Substation BAAH Leg |  | M2 - Appendix A Approved | 3000000 | 2030-12-01 | Substation | Substation bus upgrade | Montgomery |  |  | 345 | 161 |  |  | MO |  | Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50325 | Montgomery-Burns 345 kV Double Circuit line | New 345 kV line |  | M2 - Appendix A Approved | 84000000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Montgomery | Burns |  | 345 |  |  |  | MO |  | Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50189 | Rebuild Latham-Docket-1409 138 kV line (C1903 MPFCA) | GIP | 50329 | Latham-Docket-1409 138 kV MPFCA (1903) | Rebuild 5 miles of the existing 138 kV Latham-Docket-1409 with OPGW and 1600 A conductor. |  | M2 - Appendix A Approved | 4000000 | 2027-12-01 | Line Upgrade | Line reconductor | Latham | Docket |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50190 | New Peru-Princeton 138 kV line | Other | 50330 | Peru to Princeton 138 kV Line | Rebuild the existing Princeton substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 23-mile 138 kV Transmission line from Ameren's Princeton substation to the new substation near the City of Peru. |  | M2 - Appendix A Approved | 74000000 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | Princeton | Peru (Future) |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50192 | J1529 POI New 69 kV Interconnection Substation and 69 kV Line Taps | GIP | 50331 | Network Upgrades for J1529 Generator (69 kV Interconnection Sub) | Network Upgrades for J1529 Generator (69 kV Interconnection Sub) |  | M2 - Appendix A Approved | 12800000 | 2027-02-01 | Substation | Substation (breakers only, no transformer) | J1529 Sub |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50192 | J1529 POI New 69 kV Interconnection Substation and 69 kV Line Taps | GIP | 50332 | Network Upgrades for J1529 Generator (69 kV line taps) | Network Upgrades for J1529 Generator (69 kV line taps) |  | M2 - Appendix A Approved | 1000000 | 2027-02-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Carroll County | Auburn |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50193 | J1530 POI New 69 kV Interconnection Substation and 69 kV Line Taps | GIP | 50333 | Network Upgrades for J1530 Generator (69 kV Interconnection Sub) | Network Upgrades for J1530 Generator (69 kV Interconnection Sub) |  | M3 - Under Construction | 12800000 | 2026-09-30 | Substation | Substation (breakers only, no transformer) | J1530 Sub |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50193 | J1530 POI New 69 kV Interconnection Substation and 69 kV Line Taps | GIP | 50334 | Network Upgrades for J1530 Generator (69 kV line taps) | Network Upgrades for J1530 Generator (69 kV line taps) |  | M2 - Appendix A Approved | 1000000 | 2026-09-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Hastings | Macedonia |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50194 | J1532 POI New 69 kV Interconnection Substation and 69 kV Line Taps | GIP | 50335 | Network Upgrades for J1532 Generator (69 kV Interconnection Sub) | Network Upgrades for J1532 Generator (69 kV Interconnection Sub) |  | M2 - Appendix A Approved | 12900000 | 2027-09-01 | Substation | Substation (breakers only, no transformer) | J1532 Sub |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50194 | J1532 POI New 69 kV Interconnection Substation and 69 kV Line Taps | GIP | 50336 | Network Upgrades for J1532 Generator (69 kV line taps) | Network Upgrades for J1532 Generator (69 kV line taps) |  | M2 - Appendix A Approved | 1000000 | 2027-09-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Clarinda | Coburg Tap |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50195 | Carroll County-Carroll South 69 kV Line Rebuild for DPP 2020 | GIP | 50337 | Network Upgrades for J1529 Generator (69 kV line rebuild) | Network Upgrades for J1529 Generator (69 kV line rebuild) |  | M2 - Appendix A Approved | 7500000 | 2027-09-01 | Line Upgrade | Line rebuild on existing ROW | Carroll County | Carroll South | 1 | 69 |  |  |  | IA |  | Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50191 | Beebe North 115kV SS - Nelson 115kV SS | BRP | 50338 | Beebe North 115kV Switching Station | Switching Station that will tap EAI's Beebe to Garner line. |  | M2 - Appendix A Approved | 7000000 | 2028-09-01 | Substation | Switching station (breakers only, no transformer) | Beebe North SS |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50191 | Beebe North 115kV SS - Nelson 115kV SS | BRP | 50339 | Sylvania 115kV Substation | Substation that will serve existing Member Coop load. This substation will tap a new 14-mile line from the new Beebe North SS to the new Nelson SS. |  | M2 - Appendix A Approved | 8000000 | 2028-09-01 | Substation | Distribution substation - may include trans high side | Sylvania 115kV Substation |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50191 | Beebe North 115kV SS - Nelson 115kV SS | BRP | 50340 | Nelson 115kV Switching Station | Switching Station that will tie into Member Coop's existing 115kV system. |  | M2 - Appendix A Approved | 7000000 | 2028-09-01 | Substation | Switching station (breakers only, no transformer) | Nelson 115kV SS |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50191 | Beebe North 115kV SS - Nelson 115kV SS | BRP | 50341 | Beebe North SS to Sylvania 115kV Transmission Line | New 115kV transmission line from the new Beebe North SS to the new Sylvania 115kV substation. |  | M2 - Appendix A Approved | 7500000 | 2028-09-01 | Line New | New Transmission line, new ROW - may include terminations | Beebe North SS | Sylvania |  | 115 |  | 7 |  | AR |  | Not Shared
MTEP25 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50191 | Beebe North 115kV SS - Nelson 115kV SS | BRP | 50342 | Nelson SS to Sylvania 115kV Transmission Line | New 115kV transmission line from the new Nelson SS to the new Sylvania substation. |  | M2 - Appendix A Approved | 7500000 | 2028-09-01 | Line New | New Transmission line, new ROW - may include terminations | Nelson 115kV SS | Sylvania |  | 115 |  | 7 |  | AR |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50198 | New Wieland Metals 138 kV Load Addition | Other | 50346 | Wieland Metals Load Addition (Falls) | Construct a new 138 kV substation, four position ultimate in a ring bus arrangement, 3000 Amps minimum continuous capability. The substation will be located approximately 1 mile east from the existing Wood River 138 kV substation. Split the existing Granite City 23rd Street-Wood River-1452 138 kV line and route into the new substation. Provide two positions at the new ring bus for the connection of Wieland Metals. |  | M2 - Appendix A Approved | 10700000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Falls |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50200 | PLPL81 and W-30 345 kV Line, Uprate | Other | 50350 | PLPL81 and W-30 345 kV Line, Uprate | Uprate low rated segments of the Arcadian to Pleasant Prairie 345 kV line (PLPL81) and the Arcadian to Paris 345 kV line (W-30). |  | M2 - Appendix A Approved | 9500000 | 2027-01-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Arcadian | Pleasant Prairie, Paris | PLPL81, W-30 | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50201 | Rebuild Slugger to LGE Trimble 34530 Ckt. 345kV Line | BRP | 50354 | 345kV Line Rebuild - Slugger to LGE Trimble 34530 Ckt. | 34530 Rebuild - Slugger to LGE Trimble to (2)954ACSS@200C (DEI-owned portion only) |  | M2 - Appendix A Approved | 42964000 | 2031-06-01 | Line Upgrade | Line rebuild on existing ROW | Slugger | LGE Trimble Co Jct | 1 | 345 |  |  | 19 | IN |  | Not Shared
MTEP25 | A | METC | East | 50203 | Rebuild and Relocate Alma 138 kV substation | Other | 50355 | New 138 kV Station | Rebuild the 138 kV Alma station to three rows of breaker and a half station capable of three additional rows of BAH expansion. Install eight (8) 138 kV, 3000 A breakers with at least 40 kA interrupting capability. Install new control house and 25 MVAR capacitor. |  | M2 - Appendix A Approved | 13350000 | 2029-12-31 | Substation | Switching station (breakers only, no transformer) | New Station |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50203 | Rebuild and Relocate Alma 138 kV substation | Other | 50356 | Regal-New Station #1 and #2 138 kV Lines | Redirect lines #1 and #2 from Regal into the new station utilizing 954 ACSR Conductor. |  | M2 - Appendix A Approved | 975000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | New Station | Regal |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50203 | Rebuild and Relocate Alma 138 kV substation | Other | 50357 | New Station - Vestaburg 138 kV Line | Redirect line from Vestaburg into the new station utilizing 954 ACSS Conductor. |  | M2 - Appendix A Approved | 325000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | New Station | Vestaburg |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50203 | Rebuild and Relocate Alma 138 kV substation | Other | 50358 | Alma - Remove Equipment | Remove transmission equipment at Alma. |  | M2 - Appendix A Approved | 540000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Alma |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50361 | Big Creek-Warrenton 161 kV reconductor | Big Creek-Warrenton 161 kV reconductor |  | M2 - Appendix A Approved | 4000000 | 2030-12-01 | Line Upgrade | Line reconductor | Big Creek | Warrenton |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50362 | Miller-Meta 138 kV Rebuild | Rebuild 11 miles of the Bland-Miller 138 kV transmission line between Miller and Meta. |  | M2 - Appendix A Approved | 28200000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Miller | Meta |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50363 | Belle-Meta 138 kV Rebuild | Rebuild 20.7 miles of the Bland-Miller 138 kV transmission line between Belle and Meta |  | M2 - Appendix A Approved | 39700000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Belle | Meta |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50364 | Warrenton-Montgomery 161 kV reconductor | Reconductor 17.6 miles of the existing 161 kV Warrenton-Montgomery-3 transmission line |  | M2 - Appendix A Approved | 4000000 | 2030-12-01 | Line Upgrade | Line reconductor | Warrenton | Montgomery |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | GIP | 50365 | Bland-Gasco 138 kV Rebuild | Rebuild 8.3 miles of the Bland-Miller 138 kV transmission line between Bland and Gasco. |  | M2 - Appendix A Approved | 8100000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Bland | Gasco |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50204 | Clinton Railway Substation Interconnection | Other | 50366 | Clinton Railway Substation | ITCM will build the 161 kV 3 row 5 position breaker and a half substation with 2 line positions and 3 transformer positions. |  | M2 - Appendix A Approved | 6659139 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Clinton Rail Air Park Substation |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50204 | Clinton Railway Substation Interconnection | Other | 50367 | Clinton Railway Line Taps | ITCMW will install the line taps to the new 161 kV Clinton Rail and Air Park substation |  | M2 - Appendix A Approved | 2101250 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Clinton Rail Air Park Substation |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50205 | Belmond Diesel to Hancock 69 kV Line Reroute | Other | 50368 | Belmond Diesel to Hancock 69 kV Line Reroute | ITCMW will re-route the Belmond Diesel to Hancock line to a different river crossing |  | M2 - Appendix A Approved | 4097500 | 2028-12-31 | Misc. | Line relocation (road move) | Belmond Diesel | Hancock |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50206 | Rock Creek T2 Replacement | Other | 50369 | Rock Creek T2 Replacement and Breaker Addition | T2 will be replaced with a new 150 MVA 161/69 kV transformer with LTC and the current motor operated switch will be removed and replaced with a new high side breaker and disconnect. |  | M2 - Appendix A Approved | 4044728 | 2027-12-31 | Transformer | Transformer Replacement | Rock Creek |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50207 | Spirit Lake Anchor 69 kV Interconnection | Other | 50370 | Spirit Lake Anchor Substation | ITCMW will build the 69 kV portion of the Spirit Lake Anchor substation |  | M2 - Appendix A Approved | 4451411 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Spirit Lake Anchor |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50207 | Spirit Lake Anchor 69 kV Interconnection | Other | 50371 | Spirit Lake Anchor Line Tap | ITCMW will build the tap to connect the Spirit Lake Anchor substation to its 69 kV transmission system. |  | M2 - Appendix A Approved | 947500 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Spirit Lake Anchor |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50208 | New LEAP 345/138 kV Transmission Network | Other | 50372 | 345kV Transmission LIne | 345kV double circuit to new substation |  | M2 - Appendix A Approved | 76506984 | 2027-12-13 | Line New | New Transmission line, new ROW - may include terminations | Whitestown/Hortonville |  |  | 345 |  | 10 |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50208 | New LEAP 345/138 kV Transmission Network | Other | 50373 | Bartlett 345/138kV Substation | New 345/138kV substation with breaker and half at both voltage levels |  | M2 - Appendix A Approved | 73037306 | 2027-12-13 | Transformer | Transformer New | WItt |  |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50208 | New LEAP 345/138 kV Transmission Network | Other | 50374 | Martin Substation | New 138kV switching station, breaker and a half |  | M2 - Appendix A Approved | 31457701 | 2027-12-13 | Substation | Switching station (breakers only, no transformer) | LEAP North |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50208 | New LEAP 345/138 kV Transmission Network | Other | 50375 | 138kV LInes | 138kV transmission network to serve customer sites |  | M2 - Appendix A Approved | 59671226 | 2027-12-13 | Line New | New Transmission line, new ROW - may include terminations | LEAP North |  |  | 138 |  | 15 |  | IN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50210 | Keokuk West Relay Replacement and 69 kV Tie Breaker Addition | Other | 50377 | Keokuk West Relay Replacement and Tie Breaker Addition | ITC will build a new, separate control enclosure and replace all of its existing relays, and install a new bus tie breaker at the Keokuk West substation. |  | M2 - Appendix A Approved | 2958416 | 2027-12-31 | Misc. | Communication equipment | Keokuk West |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50211 | Hayward - County Line - Ellendale 69 kV Rebuild | BRP | 50378 | County Line to Hayward 69 kV Line Rebuild | Rebuild 13.34 miles of 69kV line to T2-477 ACSR with 69 kV standard between Hayward and County Line |  | M2 - Appendix A Approved | 10671250 | 2028-12-30 | Line Upgrade | Line rebuild on existing ROW | Hayward | County Line |  | 69 |  |  | 13.34 | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50211 | Hayward - County Line - Ellendale 69 kV Rebuild | BRP | 50379 | County Line to Ellendale 69 kV Line Rebuild | Rebuild 5.71 miles of 69kV line to T2-477 ACSR with 69kV standards |  | M2 - Appendix A Approved | 5232500 | 2028-12-30 | Line Upgrade | Line rebuild on existing ROW | County Line | Ellendale |  | 69 |  |  | 5.71 | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50211 | Hayward - County Line - Ellendale 69 kV Rebuild | BRP | 50380 | Hayward 617 69 kV Terminal Upgrades | ITC will replace the jumpers on breaker terminal 617 with a conductor that is capable of 1200 Amps or greater. |  | M2 - Appendix A Approved | 112005 | 2028-12-30 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Hayward |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC | East | 50212 | Avery - New DTE Interconnection | Other | 50381 | NEW STATION - Install a new 120 kV Station | Construct a new 120 kV station as 5-breaker ring bus configuration. All new 120 kV breakers should be 3000 A 50 kA breakers. |  | M2 - Appendix A Approved | 6700000 | 2028-09-29 | Substation | Substation (breakers only, no transformer) | Avery |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50212 | Avery - New DTE Interconnection | Other | 50382 | Frisbie-Waterman_Avery Cut-in | Cut the Frisbie – Waterman 120 kV line at approximately 2 miles to Frisbie to provide transmission service to the new Avery 120 kV station. |  | M2 - Appendix A Approved | 6184000 | 2028-09-29 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Avery |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | Other | 50383 | Rock Creek 345 kV Substation Expansion | ITC will be expanding the Rock Creek 345 kV substation to accommodate two additional 345 kV lines. The substation will be expanded to a Breaker and a Half configuration. All new substation equipment will be capable of 3000 Amps or greater. |  | M2 - Appendix A Approved | 23740163 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Rock Creek |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | Other | 50384 | Rock Creek - Bryant 345 kV line relocation | Move Rock Creek - Bryant 345kV line to terminate from rebuilt Rock Creek |  | M2 - Appendix A Approved | 5138750 | 2028-12-31 | Misc. | Line relocation (road move) | Rock Creek |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | Other | 50385 | Rock Creek 345-161 kV XFMR Terminal Relocation | Relocate Rock Creek transformer terminal upon rebuild of the substation |  | M2 - Appendix A Approved | 1571250 | 2028-12-31 | Substation | Substation bus upgrade | Rock Creek |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50218 | Riverton STATCOM | BRP | 50393 | Riverton STATCOM | Installing a +/- 300 MVAR STATCOM at the Riverton 230 kV Substation |  | M2 - Appendix A Approved | 70000000 | 2028-03-31 | Voltage Device | Static Var Compensator (STATCOM) | Riverton 230 kV |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50220 | Rebuild McCredie-Overton 345 kV Line (MPFCA) | GIP | 50396 | Rebuild 35.5 miles of the 345 kV McCredie-Overton | Rebuild 35.5 miles of the 345 kV McCredie-Overton |  | M2 - Appendix A Approved | 63115000 | 2031-06-01 | Line Upgrade | Line rebuild on existing ROW | McCredie | Overton |  | 345 |  |  |  | MO |  | Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50221 | Rebuild Overton-McBaine Tap 161 kV Line (MPFCA) | GIP | 50397 | McBaine Tap -Overton 161 kV Line Upgrade | McBaine Tap -Overton 161 kV Line Upgrade |  | M2 - Appendix A Approved | 9552000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | McBaine | Overton |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50222 | Rebuild Overton-Sedalia East 161 kV Line (MPFCA) | GIP | 50398 | Rebuild 10 miles of existing Overton – Sedalia East 161 kV | Rebuild 10 miles of existing Overton – Sedalia East 161 kV |  | M2 - Appendix A Approved | 9710000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Overton | Sedalia East |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50223 | Whitewater – Sugar Creek 138 kV (WHIG53), Flow Control Device | Other | 50399 | Whitewater – Sugar Creek 138 kV (WHIG53), Flow Control Device | The Whitewater – Sugar Creek (WHIG53) 138 kV, flow control device is needed to control power flow on WHIG52 and 6541 supporting load additions in south-east Wisconsin. The project will install three single-phase 20-ohm series reactors at the Sugar Creek terminal of WHIG53. |  | M2 - Appendix A Approved | 4000000 | 2027-01-01 | Voltage Device | Reactor or Inductor | Whitewaterq | Sugar Creek |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50225 | North Lake Geneva – Elkhorn 138 kV (X-55), Rebuild | Other | 50401 | North Lake Geneva – Elkhorn 138 kV (X-55), Rebuild | Rebuild X-55 North Lake Geneva - Elkhorn 138 kV line per ATC T-Line design standards to achieve minimum 1342 Amps (321 MVA) normal and 1822 Amps (436 MVA) emergency ratings for all seasons. Missing easements will be acquired. Safety and maintenance improvement expected with distribution removal from double-circuit area. |  | M3 - Under Construction | 23900000 | 2026-08-15 | Line Upgrade | Line rebuild on existing ROW | North Lake Geneva | Elkhorn | X-55 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50226 | New Vulcan 138/34 kV Substation | Other | 50402 | New Vulcan 138/34 kV Substation | Build a new 138-34.5 kV bulk substation on property adjacent to the MSD Lemay Pump |  | M2 - Appendix A Approved | 12000000 | 2030-12-01 | Substation | Distribution substation - may include trans high side | Vulcan |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50227 | Upgrade California 161 kV Terminal | Other | 50403 | California 161 kV Terminal Upgrades | California 161 kV Terminal Upgrades |  | M2 - Appendix A Approved | 17800000 | 2028-06-01 | Substation | Circuit Breaker (replacement at existing substation) | California |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50227 | Upgrade California 161 kV Terminal | Other | 50404 | Double Circuit Rebuild California to Apache Flat Tap 161kV | Double Circuit Rebuild California to Apache Flat Tap 161kV |  | M2 - Appendix A Approved | 4800000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | California | Apache Flat Tap |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | METC | East | 50229 | New Oneida - Tallman 138 kV circuit | Other | 50405 | Oneida - Install BKR 11B7 | Install new 138 kV breaker capable of 40 kA interrupting and complete an existing row at Oneida 138 kV station. |  | M2 - Appendix A Approved | 1080000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Oneida |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50229 | New Oneida - Tallman 138 kV circuit | Other | 50406 | Oneida - Tallman 138 kV New Circuit | Build new Oneida – Tallman 138 kV circuit utilizing 1431 ACSR and double circuit structures capable of OPGW. Use 9.5 miles METC existing easement and obtaining new 0.5 miles ROW to connect this corridor to CE's Tallman. |  | M2 - Appendix A Approved | 20890000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Oneida | Tallman |  | 138 |  | 10 |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50229 | New Oneida - Tallman 138 kV circuit | Other | 50407 | Looking Glass - Rebuild to ring bus station | Install new 138 kV three breaker ring bus station at Looking Glass. Install three 138 kV breakers capable of 40 kA interrupting. |  | M2 - Appendix A Approved | 5920000 | 2029-12-31 | Substation | Switching station (breakers only, no transformer) | Looking Glass |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50229 | New Oneida - Tallman 138 kV circuit | Other | 50408 | Looking Glass - Bingham 138 kV Retermination | METC to reterminate Looking Glass - Bingham and perform any other line work needed due to Looking Glass station rebuild. |  | M2 - Appendix A Approved | 1470000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Looking Glass | Bingham |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50229 | New Oneida - Tallman 138 kV circuit | Other | 50409 | Bingham - Install Fiber Jumpers | Work for fiber jumpers to establish network communications between Bingham and Looking Glass. |  | M2 - Appendix A Approved | 70000 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Bingham |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50229 | New Oneida - Tallman 138 kV circuit | Other | 50410 | LBWL Estimated Station Costs | Work to reterminate LBWL line at Oneida to accommodate new line entrance. |  | M2 - Appendix A Approved | 200000 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Oneida |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50230 | New Harco South-Carrier Mills 161 kV line | Other | 50411 | Harco South-Carrier Mills 161 kV line | Harco South-Carrier Mills 161 kV line |  | M2 - Appendix A Approved | 15000000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Harco South | Carrier Mills |  | 161 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50230 | New Harco South-Carrier Mills 161 kV line | Other | 50412 | Harco South 138 kV Ring Bus and 138/161 kV Transformer | Harco South 138 kV Ring Bus and 138/161 kV Transformer |  | M2 - Appendix A Approved | 15000000 | 2029-12-31 | Substation | Substation bus upgrade | Harco South |  |  | 161 | 138 |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50140 | Upgrade Fargo 138 kV Line Position for Lucky | Other | 50222 | Fargo 138 kV Sub | New 138kV breaker required on Fargo 138kV Bus breaker and a half scheme, and new circuit switcher on the high side of the substation. AIC to construct a new 138kV/13.2kV distribution substation near the Fargo bulk supply substation |  | M2 - Appendix A Approved | 2000000 | 2029-12-01 | Substation | Substation bus upgrade | Fargo |  |  | 345 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50145 | Beloit Area DIC, New Substation | Other | 50236 | Beloit Area DIC, New Substation | - WPL will construct a new substation with two new 138/12.47 kV, 20/33 MVA transformers. - WPL will install a high side circuit breaker for transformer protection and low side bus. - ATC will install two 138kV feeds from the line section between BOC Gas Tap and Tripp Road (X-111) to the new Beloit LNG substation to support the new loop through configuration. - ATC will remove a section of the conductor from X-111. - ATC will install a new loop through configuration at the New Beloit LNG substation with space provision for a future bus tie breaker. - ATC will construct a 138 kV loop through bus at the new Beloit LNG substation and install two 138 kV line circuit breakers with associated line and bus side disconnect switches. - ATC will install two bus-tie disconnect switches and allow space provision for a future bus-tie breaker. |  | M2 - Appendix A Approved | 13500000 | 2029-03-15 | Substation | Distribution substation - may include trans high side | TBD |  |  | 138 | 12 |  |  | WI |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50170 | New J1355 IC Facilities Interconnection 138 kV | GIP | 50299 | Stillwell 138kV bus expansion | Expand existing 138kV bus at Transmission Owner’s Stillwell substation by adding two breakers to accommodate Generating Facility lead line. |  | M2 - Appendix A Approved | 2330778 | 2028-06-01 | Substation | Substation bus upgrade | Stillwell |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50170 | New J1355 IC Facilities Interconnection 138 kV | GIP | 50300 | J1355 POI | Construct Transmission Owner’s Interconnection Facilities at Transmission Owner’s Stillwell Substation consisting of two monopoles, H frame pull off structure, metering equipment, conductor, shield wire, and fiber optics. |  | M2 - Appendix A Approved | 1904848 | 2028-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Stillwell |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50171 | Schahfer 345kV substation Redundancy | GIP | 50301 | Schahfer 345kV Redundnancy | RM Schahfer station’s relay protection requires full redundancy. Both the northwest and northeast 345kV buses at RM Schahfer currently have only one system of protection. To meet the requirements triggered by this interconnection, both buses will require additional bus protection relays. The protection and control schemes require new relaying that will include two bus differential relay panels and the addition of battery monitoring. Major Items  Two (2) bus differential relay panels  Battery monitoring system |  | M2 - Appendix A Approved | 512947 | 2026-07-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Schahfer |  |  | 345 |  |  |  | IN |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50172 | Arpin SS Power Transformer Asset Renewal | Other | 50302 | Arpin SS Power Transformer Asset Renewal | Arpin SS T21 Power Transformer Asset Renewal |  | M2 - Appendix A Approved | 9800000 | 2032-04-14 | Transformer | Transformer Replacement | Arpin |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50173 | Ellinwood SS Power Transformer Asset Renewal | Other | 50303 | Ellinwood SS Power Transformer Asset Renewal | Ellinwood SS T1 Power Transformer Asset Renewal |  | M2 - Appendix A Approved | 3500000 | 2026-12-01 | Transformer | Transformer Replacement | Ellinwood |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50175 | Upgrade Taylorville South 138 kV Substation | Other | 50305 | Taylorville South Aging Infrastructure | This project will reconfigure Taylorville South 138 kV substation in a 4 position ring bus configuration. Replace circuit breakers 1511, 1512 and 1514. Replace associated switches 1511B, 1511L, 1512B, 1512L, 1514B, and 1514L. Install one new 138 kV circuit breaker and two associated breaker disconnect switches. Remove shield wire over substation and install lightning masts and finials. |  | M2 - Appendix A Approved | 5200000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Taylorville South |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50176 | Audubon 230 kV Load Addition and Line upgrades | Other | 50306 | New Load point at Audubon 230 kV | There will be two ~2.8 mile new 230 kV lines from Audubon to the customer station. |  | M2 - Appendix A Approved | 5700000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Audubon | Customer Sub |  | 230 |  | 5.6 |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50176 | Audubon 230 kV Load Addition and Line upgrades | Other | 50307 | Willow Glen to Point Pleasant 230 kV Upgrade | Upgrade Willow Glen to Point Pleasant 230 kV line |  | M2 - Appendix A Approved | 100000 | 2026-06-01 | Line Upgrade | Line reconductor | Willow Glen | Point Pleaasant |  | 230 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50176 | Audubon 230 kV Load Addition and Line upgrades | Other | 50308 | Willow Glen to Wise 230 kV upgrade | Willow Glen to Wise 230 kV upgrade |  | M2 - Appendix A Approved | 100000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Willow Glen | Wise |  | 230 |  |  |  | LA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50231 | J1359 Generator Interconnection - TOIF - PCI 69kV Terminal & Line | GIP | 50413 | J1359 TOIF - PCI Terminal | Equipment dedicated to connecting the J1359 generating facility to a new 69 kV breaker position in the PCI substation. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. |  | M2 - Appendix A Approved | 790014 | 2026-09-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Prairie Creek Industrial |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50231 | J1359 Generator Interconnection - TOIF - PCI 69kV Terminal & Line | GIP | 50414 | J1359 TOIF - PCI to J1359 69 kV Line | A new approximately 0.75 mile 69 kV line from the PCI substation to the J1359 generating facility will need to be constructed. |  | M2 - Appendix A Approved | 1055000 | 2026-06-30 | Line New | New Transmission line, new ROW - may include terminations | Prairie Creek Industrial |  |  | 69 |  | 0.75 |  | IA |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50233 | Birnamwood Area Reliability Project | Other | 50415 | Birnamwood Area Reliability Project | Build a greenfield 69 kV switching station near the location of the Birnamwood tap. The station will be a 6-position straight bus with three breakered line terminals, one for the line segment to Deer Trail, one for the segment to Whitcomb, and one for the radial line to Birnamwood. One position for an 8 MVAR cap bank, provisions for a bus tie breaker and two future positions. |  | M2 - Appendix A Approved | 17500000 | 2028-12-31 | Substation | Switching station (breakers only, no transformer) | Whitcomb | Deer Trail | Y-86 | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50232 | J1359 Generator Interconnection - Network Upgrades - PCI 69kV Bus | GIP | 50416 | J1359 Network Upgrade - PCI Bus Extenstion | The PCI 69 kV bus will be extended to accommodate an additional position for the J1359 TOIF line terminal. |  | M2 - Appendix A Approved | 401708 | 2026-11-30 | Substation | Substation bus upgrade | Prairie Creek Industrial |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MINNESOTA MUNICIPAL POWER AGENCY | West | 50234 | MN River Breaker Install (position 5M518) | Other | 50417 | 24592-MN River- | Penn. Breaker Installation |  | M2 - Appendix A Approved | 625800 | 2027-02-15 | Substation | Substation (breakers only, no transformer) | MN River |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50235 | J1444 Generator Interconnection - TOIF - DAEC 345kV Terminal | GIP | 50418 | J1444 TOIF at DAEC 345 kV | Equipment dedicated to the J1444 generating facility. TOIF cost to include: dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. |  | M2 - Appendix A Approved | 760648 | 2027-07-02 | Substation | Points of Interconnection for generators (User TAP for dist subs) | DAEC |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50236 | J1444 Generator Interconnection - Network Upgrade | GIP | 50419 | J1444 DAEC 345 kV Expansion Network Upgrade | the addition of 3 breaker positions, switches and associated equipment to upgrade to a breaker and half configuration. |  | M2 - Appendix A Approved | 3777724 | 2027-07-01 | Substation | Substation bus upgrade | DAEC |  |  | 345 |  |  |  | IA |  | Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50237 | Butternut Area Projects | Other | 50420 | Butternut - Butternut Tap Rebuild | Rebuild BE-BUT line. SS145 to the Butternut Substation. Line length is approx. 4.5 miles |  | M2 - Appendix A Approved | 4947000 | 2029-12-21 | Line Upgrade | Line rebuild on existing ROW | Butternut | Butternut Tap | 1 | 69 | 69 |  | 4.5 | MN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50238 | MPFCA J1503 & J1504 - TOIF - Huntley 345 kV Terminal | GIP | 50421 | MPFCA J1503 J1504 - TOIF - Huntley 345 kV Terminal | TOIF to include dead-end, PTs, relay panel for gen-tie line, line disconnect switch and other facilities at the switching station dedicated to the gen-tie line at the Huntley substation. |  | M2 - Appendix A Approved | 1083794 | 2027-10-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Huntley |  |  | 345 |  |  |  | MN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50239 | MPFCA J1503 & J1504 - Network Upgrades - Huntley 345 kV Bus | GIP | 50422 | MPFCA J1503 J1504 - Network Upgrades - Huntley 345 kV Bus Expansion | Completing the 2nd row of 345kV breakers by adding two 345kV breakers and adding two 345kV breakers of a 3rd row, and other facilities required to convert the Huntley 345kV ring-bus to breaker and 1/2 station with approx. 3,000A capacity. 90% FSA, 10% Attachment GG. |  | M2 - Appendix A Approved | 5489562 | 2027-10-31 | Substation | Substation bus upgrade | Huntley |  |  | 345 |  |  |  | MN |  | Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50241 | Replace Boonville T1 69 kV | Other | 50423 | Boonville T1 | Replace transformer #1 with new 20MVA. |  | M2 - Appendix A Approved | 2360000 | 2027-10-15 | Transformer | Transformer Replacement | Boonville |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50242 | New Sweden Area Projects | Other | 50424 | New Sweden - New Sweden Tap Rebuild | Rebuild BE-NST line from SS2831 to New Sweden Substation. Line length is approx. 7.4 miles. |  | M2 - Appendix A Approved | 6996498 | 2030-02-28 | Line Upgrade | Line rebuild on existing ROW | New Sweden | New Sweden Tap | 1 | 69 | 69 |  | 7.4 | MN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50240 | J1520 Generator Interconnection - TOIF | GIP | 50425 | J1520 TOIF | Equipment dedicated to the J1520 generating facility. TOIF cost to include: dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. |  | M2 - Appendix A Approved | 1101322 | 2027-10-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Bluebill |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50245 | Replace Culley 138kV CCVT Boxes | Other | 50426 | Culley 138kV CCVT and Relaying | Replace existing line, breaker, and bus relaying panels. Replace existing CCVT junction boxes with new stainless-steel boxes. |  | M2 - Appendix A Approved | 1600000 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Culley 138kV |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50244 | J1520 Generator Interconnection - Network Upgrades | GIP | 50427 | Bluebill 345 kV Expansion Network Upgrade | Add 3rd row and one line position at Bluebill |  | M2 - Appendix A Approved | 4048730 | 2027-10-31 | Substation | Substation (breakers only, no transformer) | Bluebill |  |  | 345 |  |  |  | IA |  | Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50247 | Rebuild Elliott Transformer and Substation 69 kV | Other | 50428 | Elliott Substation | Replace existing ‘Transformer #1’ & ‘Transformer #2’ with new 100MVA transformers. Add new transformer protective relaying. Replace existing 138kV circuit breakers ‘1000’ & ‘3000’ and 69kV circuit breakers ‘100’, ‘200’, ‘300’ & ‘600’. Replace breaker foundations, breaker/line switches, and protective relaying. Replace two (2) existing 69kV capacitor banks. |  | M2 - Appendix A Approved | 15700000 | 2027-12-31 | Transformer | Transformer Replacement | Elliott |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50248 | Replace Newburgh Circuit Switcher 69 kV | Other | 50429 | Newburgh Substation | Remove existing 69kV high-side fuses and associated switch ‘199’ and replace with new 69kV circuit switcher. Install an auto-sectionalizing and RTU panels. Replace existing 7200V voltage regulators. |  | M2 - Appendix A Approved | 1550000 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Newburgh |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50249 | Rebuild Dubois T2 138/69 kV Transformer | Other | 50430 | Dubois Substation | Replace existing 100MVA, 138/69kV ‘Transformer #1’. Replace existing 69kV breakers ‘100’, ‘200’, ‘300’, ‘400’ and ‘500’. Replace existing 138kV and 69kV CCVTs. Install new transformer, 138kV and 69kV breaker and line relaying panels. |  | M2 - Appendix A Approved | 7870000 | 2027-12-31 | Transformer | Transformer Replacement | Dubois |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | METC | East | 50251 | Rebuild Batavia - Dorrance #1 & #2 138 kV lines | Other | 50433 | Batavia-Dorrance_Rebuild with OPGW | Rebuild sections of the Batavia – Dorrance #1 & #2 circuits between Structure 124D100 to Batavia (~4.1mi) with 954 ACSR conductor and OPGW.. |  | M2 - Appendix A Approved | 10305000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Batavia | Byers | 1 | 138 |  |  | 4.1 | MI |  | Not Shared
MTEP25 | A | METC | East | 50251 | Rebuild Batavia - Dorrance #1 & #2 138 kV lines | Other | 50434 | Batavia - Terminate OPGW | Terminate OPGW in Batavia substation |  | M2 - Appendix A Approved | 125000 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Batavia |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50251 | Rebuild Batavia - Dorrance #1 & #2 138 kV lines | Other | 50436 | Dorrance - Install fiber jumpers for Batavia | Install fiber jumpers for Batavia. |  | M2 - Appendix A Approved | 125000 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Dorrance |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 50438 | Phase 3: 25.1 MVAR Capacitor Bank at Dobbin 138 kV Substation | 25.1 MVAR Capacitor Bank |  | M2 - Appendix A Approved | 10000000 | 2029-06-01 | Voltage Device | Capacitor (switched capacitor) | Dobbin |  |  | 138 | 138 |  |  | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 50439 | Phase 4: Rebuild Fish Creek - Deer Lake 138 kV line | Rebuild Fish Creek - Deer Lake 138 kV line |  | M2 - Appendix A Approved | 17000000 | 2035-06-01 | Line Upgrade | Line reconductor | Fish Creek | Deer Lake | 1 | 138 | 138 |  | 4.83 | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 50440 | Phase 5: Rebuild Dobbin - Tubular 138 kV line | Rebuild Dobbin - Tubular 138 kV line |  | M2 - Appendix A Approved | 65000000 | 2031-06-01 | Line Upgrade | Line reconductor | Dobbin | Tubular | 1 | 138 | 138 |  | 18.6 | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 50441 | Phase 6: Rebuild Deer Lake - Spring Branch 138 kV line | Rebuild Deer Lake - Spring Branch 138 kV line |  | M2 - Appendix A Approved | 17000000 | 2035-06-01 | Line Upgrade | Line reconductor | Deer Lake | Spring Branch | 1 | 138 | 138 |  | 4.76 | TX |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 25436 | Bobville Area Menu Phases 1 through 7 | BRP | 50442 | Phase 7: Rebuild Dobbin - Spring Branch 138 kV line | Rebuild Dobbin - Spring Branch 138 kV line |  | M2 - Appendix A Approved | 17000000 | 2035-02-28 | Line Upgrade | Line reconductor | Dobbin | Spring Branch | 1 | 138 | 138 |  | 5.2 | TX |  | Not Shared
MTEP25 | A | ITC | East | 50253 | Oliver - New DTE Interconnection | Other | 50444 | Oliver - Install new 120kV station | Construct Oliver 120kV station as a straight bus station with two new 40kA line breakers and allow enough space for future expansion. DTE to install reverse power relay at Oliver. |  | M2 - Appendix A Approved | 3740000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Oliver |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50253 | Oliver - New DTE Interconnection | Other | 50445 | BADAX-WYATT 1_Cut-In | Remove the Cosmo tap from the Bad Axe – Wyatt #1 120kV line near structure 6267A and bring the Cosmo Tap into a terminate position HN at Bad Axe 120kV through new construction of 0.5 mile using 954 ACSR. Loop in the Bad Axe – Wyatt 1 120kV line near Structures #52027 to provide transmission service to Oliver 120kV. Also Remove 2001 and 2065 PT switches at CosmoTP. |  | M2 - Appendix A Approved | 685000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Bad Axe | Wyatt | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50253 | Oliver - New DTE Interconnection | Other | 50446 | BADAX-OLIVER_OPGW Install | Install OPGW from Bad Axe – Oliver for relay communication. |  | M2 - Appendix A Approved | 167500 | 2028-06-01 | Misc. | Communication equipment | Bad Axe | Oliver | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50253 | Oliver - New DTE Interconnection | Other | 50447 | Bad Axe - Install 120kV Breaker Pos HN | Install a 120kV, 3000 A, 40kA breaker at position HN. Terminate the Bad Axe – Oliver 120kV line at position HN. |  | M2 - Appendix A Approved | 1013000 | 2028-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Bad Axe | Oliver | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50254 | Remsen Township 345 kV Substation Expansion for J1590 | GIP | 50448 | Network Upgrades for J1590 Plymouth Wind Energy | Network Upgrades for J1590 Plymouth Wind Energy |  | M2 - Appendix A Approved | 4000000 | 2027-09-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Remsen Township |  |  | 345 |  |  |  | IA |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50255 | Huiskamp - Ruskin 69 kV (6937), OPGW Addition | Other | 50449 | Huiskamp - Ruskin 69 kV (6937), OPGW Addition | Install ~1.75 miles of ATC standard (DNO-10455) 48 strand OPGW fiber optic cable from structure #232 on T-Line (6937) into the Ruskin substation to complete the connection from Huiskamp. |  | M2 - Appendix A Approved | 2400000 | 2026-12-31 | Misc. | Communication equipment | Huiskamp | Ruskin | 6937 | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50256 | New Tibbe 138/34.5 kV Substation | Other | 50450 | Tibbe 138-34.5 kV Substation | Tibbe 138-34.5 kV Substation |  | M2 - Appendix A Approved | 11000000 | 2029-12-01 | Substation | Distribution substation - may include trans high side | Tibbe |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50256 | New Tibbe 138/34.5 kV Substation | Other | 50451 | Gray Summit-Tibbe 138 kV line | Gray Summit-Tibbe 138 kV line |  | M2 - Appendix A Approved | 11000000 | 2029-12-01 | Line Upgrade | Line conversion to higher voltage | Gray Summit | Tibbe |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50256 | New Tibbe 138/34.5 kV Substation | Other | 50452 | Franklin-Tibbe 138 kV line | Franklin-Tibbe 138 kV line |  | M2 - Appendix A Approved | 11000000 | 2029-12-01 | Line New | New Transmission line, new ROW - may include terminations | Franklin | Tibbe |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50257 | Reconfigure Steeleville 138 kV Substation to Ring Bus | Other | 50453 | Steeleville 138 kV Ring Bus | Rebuild Steeleville 138 kV as a five-position switching station, in a ring bus arrangement, with one additional position for future expansion with continuous capability of 3000 A. Install a new 40 Mvar 138 kV capacitor bank in one of the initial ring bus positions |  | M3 - Under Construction | 6001746 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Steeleville |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50260 | Hettinger-Elgin rebuild to 115 kV | Other | 50455 | Hettinger sub add | Add a 115 kV bay to the Hettinger substation. |  | M2 - Appendix A Approved | 600000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Hettinger |  |  | 230 | 42 |  |  | ND |  | Not Shared
MTEP25 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50260 | Hettinger-Elgin rebuild to 115 kV | Other | 50456 | Hettinger-Elgin rebuild of 69kV line | Build a new 115/69/41.6 kV substation with the rebuild of the Hettinger-Elgin line to 115 kV. |  | M2 - Appendix A Approved | 23000000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Hettinger | Elgin | 1 | 115 |  | 42.2 |  | ND |  | Not Shared
MTEP25 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50260 | Hettinger-Elgin rebuild to 115 kV | Other | 50458 | Elgin Substation | Build new substation at Elgin 115/69/41.6 kV. |  | M2 - Appendix A Approved | 7000000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Elgin |  |  | 115 | 42 |  |  | ND |  | Not Shared
MTEP25 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50260 | Hettinger-Elgin rebuild to 115 kV | Other | 50459 | Elgin transformers | New transformers |  | M2 - Appendix A Approved | 1500000 | 2029-12-31 | Transformer | Transformer New | Elgin |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50243 | Merton Area Projects | Other | 50460 | Merton - SS2755 Rebuild | Rebuild SW-OM line. SS2755 to Merton Substation. Line length is approx. 6.5 miles. Planning has requested line be rebuilt to 161kV. |  | M2 - Appendix A Approved | 9273000 | 2030-09-30 | Line Upgrade | Line rebuild on existing ROW | Merton | SS2755 | 1 | 69 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50262 | Chaffee Creek SS Breaker Asset Renewal | Other | 50461 | Chaffee Creek SS Breaker Asset Renewal | Asset renewal replacement of oil circuit breakers at Chaffee Creek SS. In addition, replace the aging capacitor bank and internal components of the control house. |  | M2 - Appendix A Approved | 5155000 | 2028-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Chaffee Creek |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50263 | Rush City Area Projects | Other | 50462 | Pine City - Rush City Tap Rebuild | Rebuild CP line. CPX Line to the CPT Line. Line length is approx. 11 miles. Rebuild RLT Line. Line length is approx. 0.1 miles Rebuild CPT Line. SS2984 to SS2555. Line length is approx. 1.5 miles |  | M2 - Appendix A Approved | 11751000 | 2029-08-31 | Line Upgrade | Line rebuild on existing ROW | Pine City | Rush City | 1 | 69 | 69 |  | 12.6 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50264 | Soderville Area Projects | Other | 50463 | Blaine - Soderville Rebuild | Rebuild SP line. Soderville Substation to #152. Line length is approx. 10 miles |  | M2 - Appendix A Approved | 21269000 | 2031-03-31 | Line Upgrade | Line rebuild on existing ROW | Blaine | Soderville | 1 | 69 | 69 |  | 10 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50265 | Victor Area Projects | Other | 50464 | Lake Jennie Tap - Victor Rebuild | Rebuild DS line. DSX Line to SS377. Line length is approx. 9.25 miles |  | M2 - Appendix A Approved | 8093000 | 2029-12-12 | Line Upgrade | Line rebuild on existing ROW | Lake Jennie Tap | Victor | 1 | 69 | 69 |  | 9.25 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50266 | Green Lake Area Projects | Other | 50465 | Hawick - Green Lake - Spicer Tap Rebuild | Rebuild SH line. SS306 to Green Lake Sub to Hawick Sub. Line length is approx. 13.7 miles |  | M2 - Appendix A Approved | 12790000 | 2030-04-30 | Line Upgrade | Line rebuild on existing ROW | Hawick | Spicer Tap | 1 | 69 | 69 |  | 13.7 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50267 | Johnsville Double End | Other | 50467 | Johnsville Double End | GRE to convert the existing Johnsville substation to an in-and-out substation. GRE will need to build a short 69 kV transmission line tap and add/alter metering/telecom for the 2nd transformer. 2000-amp motor operated FLB switches should be used. |  | M2 - Appendix A Approved | 2362908 | 2029-12-31 | Substation | Substation bus upgrade | Johnsville |  |  | 69 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | Central Minnesota Municipal Power Agency | West | 50268 | Blue Earth Rice Street Transformer Replacement | Other | 50468 | Rice Street Transformer Upgrade to 12-20 MVA | Rice Street 12/20 MVA Transformer |  | M2 - Appendix A Approved | 2400000 | 2028-05-31 | Transformer | Transformer Replacement | Blue Earth Rice Street |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | DAIRYLAND POWER COOPERATIVE | West | 50270 | J1808 Generation Interconnection Network Upgrades. | GIP | 50469 | Barron Network Upgrades | Barron 161 kV ring bus expansion and POI facilities. |  | M2 - Appendix A Approved | 1438367 | 2027-07-02 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Barron |  |  | 161 |  |  |  | WI |  | Not Shared
MTEP25 | A | DAIRYLAND POWER COOPERATIVE | West | 50271 | Rock Dell-Pleasant Valley N469 Rebuild | Other | 50470 | Rock Dell-Pleasant Valley | Rebuild of 2.0 miles of 69 kV transmission between Rock Dell and Pleasant Valley. |  | M2 - Appendix A Approved | 1227000 | 2027-05-31 | Line Upgrade | Line rebuild on existing ROW | Rock Dell | Pleasant Valley |  | 69 |  |  | 2 | MN |  | Not Shared
MTEP25 | A | DAIRYLAND POWER COOPERATIVE | West | 50272 | Genoa Dist Tap-Ringe Tap N470 Rebuild | Other | 50471 | Genoa Dist-Ringe | Rebuild 7.88 miles of 69 kV transmission between Genoa Dist. Tap and Ringe Tap on DPC's N470 line. |  | M2 - Appendix A Approved | 2959357 | 2026-04-06 | Line Upgrade | Line rebuild on existing ROW | Genoa Dist | Ringe |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50274 | Iona Area Projects | Other | 50472 | Iona Substation | The Iona 115 kV Conversion Project involves building a 0.5-mile 115 kV tap line to interconnect the existing Todd-Wadena Electric Cooperative (TWEC) Iona substation to the 47 Line via a 3-way, 2000-amp, full load break 115 kV switch. Utilize 477 ACSR conductor. |  | M2 - Appendix A Approved | 266271 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Iona | Iona Tap | 1 | 115 | 115 | 3.5 |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50274 | Iona Area Projects | Other | 50473 | Iona Substation Tap Line | The Iona 115 kV Conversion Project involves building a 0.5-mile 115 kV tap line to interconnect the existing Todd-Wadena Electric Cooperative (TWEC) Iona substation to the 47 Line via a 3-way, 2000-amp, full load break 115 kV switch. Utilize 477 ACSR conductor. |  | M2 - Appendix A Approved | 2049476 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Iona | Iona Tap | 1 | 115 | 115 | 3.5 |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50273 | Heartland Lakes Area Projects | Other | 50474 | Heartland Lakes Substation | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. |  | M2 - Appendix A Approved | 203802 | 2029-10-01 | Substation | Distribution substation - may include trans high side | Heartland |  |  | 115 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50273 | Heartland Lakes Area Projects | Other | 50475 | Hubbard Breaker Addition | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. |  | M2 - Appendix A Approved | 1361504 | 2029-10-01 | Substation | Substation (breakers only, no transformer) | Hubbard |  |  | 115 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50273 | Heartland Lakes Area Projects | Other | 50476 | Heartland Lakes - Hubbard Transmission Line | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. |  | M2 - Appendix A Approved | 6920195 | 2029-10-01 | Line New | New Transmission line, new ROW - may include terminations | Heartland | Hubbard | 1 | 115 | 115 | 5 |  | MN |  | Not Shared
MTEP25 | A | Central Minnesota Municipal Power Agency | West | 50269 | Blue Earth Northeast Add 2nd Transformer 20-37.3 MVA | Other | 50477 | Northeast Sub Add 2nd 20-37.3 MVA Transformer | 2nd 20-37.3 MVA Transformer |  | M2 - Appendix A Approved | 4800000 | 2026-05-31 | Transformer | Transformer New | Blue Earth Northeast |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | Central Minnesota Municipal Power Agency | West | 50275 | Blue Earth West Sub Transformer Upgrade | Other | 50478 | Blue Earth West Sub Add 2nd 10/14 MVA Transformer | Add 2nd 10/14 MVA Transformer |  | M2 - Appendix A Approved | 2900000 | 2029-05-31 | Transformer | Transformer New | Blue Earth West Sub |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50279 | Replace Staunton 230/138kV Xfmr Bk1 and 2 | BRP | 50482 | Staunton 230-138kV Xfmr Bk1 and 2 replacement | replace / upgrade the two existing banks 1 and 2 with 250MVA nameplate |  | M2 - Appendix A Approved | 18800000 | 2028-05-26 | Transformer | Transformer Replacement | Staunton |  |  | 230 | 138 |  |  | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50280 | New Neuron - Lafayette 27MW load | Other | 50483 | Project Neuron - 138kV service to new load | Project Neuron (fka Mars) - Lafayette new load @ 27MWs; to be served from the 13806 line very near Tipmont Co Farm - reconfiguration required to loop in existing radial to Tipmont Co Farm and new customer. |  | M2 - Appendix A Approved | 24970000 | 2029-12-31 | Substation | Distribution substation - may include trans high side | Project Mars |  |  | 138 |  | 1.5 | 0.5 | IN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50282 | New Radbourn 345 kV and Leghorn 345 kV Shunt Reactors | Other | 50489 | Radbourn and Leghorn 345 kV Shunt Reactor | Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Radbourn 345 kV substation. Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Leghorn 345 kV substation. |  | M2 - Appendix A Approved | 4800000 | 2026-12-01 | Voltage Device | Reactor or Inductor | Leghorn and Radbourn |  |  | 345 |  |  |  | IL |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50284 | Cormorant to Pelican Rapids Rebuild Projects | Other | 50490 | Cormorant - Tamarac Rebuild | Rebuild all sections of the LR-PC line. |  | M2 - Appendix A Approved | 8501468 | 2030-11-29 | Line Upgrade | Line rebuild on existing ROW | Cormorant | Tamarac | 1 | 115 | 115 |  | 9 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50284 | Cormorant to Pelican Rapids Rebuild Projects | Other | 50491 | Pelican Rapids - Tamarac Rebuild | Rebuild all sections of the LR-PC line. |  | M2 - Appendix A Approved | 6620453 | 2030-05-31 | Line Upgrade | Line rebuild on existing ROW | Pelican Rapids | Tamarac | 1 | 115 | 115 |  | 7 | MN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50285 | New HE Shadow Lake 138/12kV Sub | Other | 50492 | HE Shadow Lake 138/12kV Sub | New HE Shadow Lake 138/12kV distribution substation for Clark Co REMC to be inserted in the 13898 Speed – Jeffersonville 138kV line between River Ridge Central and Stoney Point Jct.; looped through with ATO; loop in/out with 954ACSS/TW20x7@200C conductor |  | M3 - Under Construction | 2974000 | 2026-06-01 | Substation | Distribution substation - may include trans high side | HE Shadow Lake 138/12kV Sub |  |  | 138 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50286 | Lebanon Industrial 2nd 69kV Source | Other | 50493 | Rosston-Lebanon Industrial 69kV | Construct 13 miles of new 69kV |  | M2 - Appendix A Approved | 30311869 | 2027-10-01 | Line New | New Transmission line, new ROW - may include terminations | Rosston | Lebanon Industrial |  | 69 |  | 13 |  | IN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50288 | Replace Marblehead North 161/138 kV transformer | Other | 50496 | Marblehead North Transformer Replacement | Replace existing transformer at Marblehead North with the onsite spare 161/138kV 300 MVA unit. |  | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Transformer | Transformer Replacement | Marblehead North |  |  | 161 |  |  |  | IL |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50289 | New Wabash Industrial 69/12kV Sub | Other | 50497 | Wabash Industrial 69/12kV Sub | Wabash Industrial 69/12kV new sub to serve new 20+MW customer in the 69132 ckt - near Chippewa; includes 14.4MVAR capacitor |  | M3 - Under Construction | 2968000 | 2026-10-16 | Substation | Distribution substation - may include trans high side | Wabash Industrial 69/12kV Sub |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50292 | Fishback Creek 69/12kV Substation | Other | 50502 | Substation | 69/12kV Substation |  | M2 - Appendix A Approved | 6000000 | 2028-12-31 | Transformer | Transformer New | Fishback Creek |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50293 | 6923 69kV Ring Bus | Other | 50503 | 69kV Ring Bus | 3 terminal 69kV ring |  | M2 - Appendix A Approved | 6800000 | 2029-12-31 | Substation | Switching station (breakers only, no transformer) | North Manchester |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50294 | Romine 69kV Switching Station | Other | 50504 | 69kV Ring Bus | 3 terminal 69kV ring |  | M2 - Appendix A Approved | 6800000 | 2028-12-31 | Substation | Switching station (breakers only, no transformer) | Flexel Jct |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50295 | 69154 69kV Ring Bus | Other | 50505 | 69kV Ring Bus | 3 terminal 69kV ring bus |  | M2 - Appendix A Approved | 6800000 | 2030-12-31 | Substation | Switching station (breakers only, no transformer) | Cherry Grove |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50296 | New Dover 69/12 kV Substation | Other | 50506 | 69/12kV Substation | New 69/12kV 22.4MVA substation |  | M2 - Appendix A Approved | 6500000 | 2027-12-31 | Transformer | Transformer New | Dover |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50297 | Milnon 69/12kV Substation | Other | 50507 | 69/12kV Substation | 14MVA 69/12kV Substation |  | M2 - Appendix A Approved | 6649226 | 2027-11-24 | Transformer | Transformer New | Milnon |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50298 | Four Corners 69/12kV Substation | Other | 50508 | 69/12kV Substation | 14MVA 69/12kV Substation |  | M2 - Appendix A Approved | 5764132 | 2027-12-01 | Transformer | Transformer New | Four Corners |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50298 | Four Corners 69/12kV Substation | Other | 50509 | 69kV Line | 2.5 miles of 69kV |  | M2 - Appendix A Approved | 8287998 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Four Corners |  |  | 69 |  | 3.4 |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50300 | Hayworth 69/12kV Substation | Other | 50510 | 69/12kV Substation | 14MVA 69/12kV Station |  | M2 - Appendix A Approved | 5205938 | 2027-12-01 | Transformer | Transformer New | Beaver Creek |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50300 | Hayworth 69/12kV Substation | Other | 50511 | 69kV Line | 2 miles of new 69kV |  | M2 - Appendix A Approved | 5043488 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Beaver Creek |  |  | 69 |  | 2 |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50301 | Maple Leaf 69kV Line | Other | 50512 | 69kV Line | 6 miles of 69kV line |  | M2 - Appendix A Approved | 15000000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Maple Leaf |  |  | 69 |  | 6 |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50302 | New Lacrosse 69/12 kV Substation | Other | 50513 | Substation | New 14MVA 69/12kV Substatoin |  | M2 - Appendix A Approved | 5500000 | 2027-07-28 | Transformer | Transformer New | Lacrosse |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50302 | New Lacrosse 69/12 kV Substation | Other | 50514 | 69kV Line | 2-3 miles of new 69kV |  | M2 - Appendix A Approved | 7000000 | 2027-07-28 | Line New | New Transmission line, new ROW - may include terminations | Lacrosse |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50303 | Jacob Mack 2nd Bank & Source | Other | 50515 | Substation | Add a 2nd bank and expand the 69kV bus for a looped feed |  | M2 - Appendix A Approved | 8594249 | 2027-12-31 | Transformer | Transformer New | Jacob Mack |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50299 | New Wakefield 138 kV switching station | Other | 50516 | Wakefield 138 kV Switching Station | Construct a three (3) position 138 kV substation in a ring bus configuration, with one (1) additional position available for future expansion, all with a 3000 A minimum continuous capability. Route the existing South Bloomington-Tabor-1445 138 kV line in and out of the new Wakefield substation. |  | M2 - Appendix A Approved | 10700000 | 2027-12-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Wakefield |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50305 | Blue Earth Substation Rebuild Projects | Other | 50518 | Blue Earth Substation | BENCO plans to rebuild their 69kV Blue Earth distribution substation on an adjacent property to replace the aged substation as well as increase transformer size to 7.5 MVA bottom 10.5 MVA top end rating . GRE will need to relocate line and install a new building, meter, and telecom equipment. GRE planning has requested the high side be an in-and-out. |  | M2 - Appendix A Approved | 1443735 | 2027-10-29 | Substation | Distribution substation - may include trans high side | Blue Earth |  |  | 69 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50316 | Rebuild Z84 Duff to Petersburgh 138 kV | Other | 50523 | Z84-3 | Complete rebuild of Z84 from Duff to IPL Petersburgh plant. Total rebuild distance is 19.9 miles and involves replacing wood h-frame structures with galvanized steel monopole structures. The existing 765 Drake ACSR conductor to be replaced with new 2-bundled 954 Rail conductor. |  | M2 - Appendix A Approved | 38040000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Duff |  |  | 138 |  |  | 19.9 | IN |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50318 | Adams County-Creston 161 kV Line Uprate for DPP 2020 | GIP | 50524 | Adams County-Creston | Network Upgrades for J1530 and J1532 Generators (161 kV structure replacement) |  | M2 - Appendix A Approved | 700000 | 2026-09-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Adans County | Creston | 1 | 161 |  |  |  | IA |  | Shared
MTEP25 | A | METC | East | 50317 | New Hagensville Junction Interconnection (METC) | Other | 50525 | Hincka - Install Row 6 and breakers | Install Row 6 and 5 138 kV, 40kA breakers to accommodate Wolverine's interconnection. |  | M2 - Appendix A Approved | 5010000 | 2028-12-31 | Substation | Switching station (breakers only, no transformer) | Hincka |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50319 | West Des Moines 69 kV Breaker Replacement | Other | 50526 | West Des Moines - 73rd & Buffalo | Rebuild and reconfigure West Des Moines 69 kV line to 73rd & Buffalo substations. |  | M2 - Appendix A Approved | 1700000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | West Des Moines | 73rd & Buffalo |  | 69 |  |  | 0.75 | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50319 | West Des Moines 69 kV Breaker Replacement | Other | 50527 | West Des Moines - 37th & Rock Island | Rebuild and reconfigure West Des Moines 69 kV line to 37th & Rock Island substations. |  | M2 - Appendix A Approved | 400000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | West Des Moines | 37th & Rock Island |  | 69 |  |  | 0.1 | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50319 | West Des Moines 69 kV Breaker Replacement | Other | 50528 | West Des Moines | Replace 69 kV breaker DAE601 at West Des Moines Substation. |  | M2 - Appendix A Approved | 450000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | West Des Moines |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50320 | E. 17th & Washington 69 kV bus expansion and line breaker installations | Other | 50529 | E. 17th & Washington | Expand E. 17th & Washington Substation steel to accommodate two 69 kV line breakers. |  | M2 - Appendix A Approved | 0 | 2029-12-01 | Substation | Substation bus upgrade | E. 17th & Washington |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50321 | E. 17th & Broadway 69 kV breaker installations | Other | 50530 | E. 17th & Broadway | Install three 69 kV line breakers at E. 17th & Broadway Substation |  | M2 - Appendix A Approved | 0 | 2028-10-01 | Substation | Substation (breakers only, no transformer) | E. 17th & Broadway |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50324 | 88th Street Substation bus expansion and 161-13 kV transformer installation | Other | 50537 | 88th Street | Expand 88th St Substation steel to ring bus and add a third 161-13 kV transformer |  | M2 - Appendix A Approved | 9000000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | 88th Street |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50325 | NE Ankeny - Ames 161 kV relay replacements | Other | 50538 | NE Ankeny | NE Ankeny - new ITC substation line relaying |  | M2 - Appendix A Approved | 400000 | 2026-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | NE Ankeny | New ITC Sub |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50326 | Rebuild Z95 Northwest to AB Brown 138kV | Other | 50539 | Z95 Northwest to AB Brown | Rebuild aging portions of the Z95 Northwest to AB Brown 138kV transmission line. The first section is approximately 1.57 miles long and the second section is approximately 3.47 miles long. Both sections have 795 Drake conductor, which will be replaced with 954 Rail conductor. Aging wood poles will be replaced with tubular steel structures. |  | M2 - Appendix A Approved | 8700000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Northwest |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50327 | Raun: Tekamah 161 kV Line Relay Replacement SPP DISIS-2017 | GIP | 50540 | Raun | Network Upgrades for SPP Generator 105 at Raun Substation |  | M2 - Appendix A Approved | 750000 | 2028-09-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Raun |  |  | 161 |  |  |  | IA |  | Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50328 | Neal North: Replace 161-69 kV Transformer Relaying & 69 kV Breaker Replacement | Other | 50541 | Neal North | Replace 161-69 kV transformer relaying and 69 kV breaker at Neal North Substation |  | M2 - Appendix A Approved | 1500000 | 2029-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Neal North |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50329 | Substation 91 Expansion | BRP | 50542 | Substation 91 Expansion | Expand Substation 91 by converting the 345 kV yard to a ring bus configuration and by installing a second 345-161 kV transformer. |  | M2 - Appendix A Approved | 58000000 | 2028-12-31 | Transformer | Transformer New | Substation 91 |  |  | 345 | 161 |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50330 | Plymouth-Merrill 69 kV Line Uprate | Other | 50543 | Plymouth-Merrill | Replace structures on the Plymouth-Merrill 69 kV line |  | M2 - Appendix A Approved | 2000000 | 2027-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Plymouth | Merrill |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50331 | Substation 39 Replace 345-161 kV Transformer 9T1 | BRP | 50544 | Substation 39 345-161 kV Transformer 9T1 Replacement | At Substation 39, replace the existing 345-161 kV, 500 MVA Transformer 9T1 with a new 560 MVA transformer. |  | M2 - Appendix A Approved | 10500000 | 2029-06-01 | Transformer | Transformer Replacement | Substation 39 |  |  | 345 | 161 |  |  | IL |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50332 | Division-Eastside 69 kV Line Rebuild & Terminal Upgrades | Other | 50545 | Division-Eastside | Rebuild and reconductor Division-Eastside 69 kV line |  | M2 - Appendix A Approved | 2200000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Division | Eastside |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50334 | Eagle Grove-Goldfield 69 kV Interconnection and Clarion-Latimer 69 kV Line Rebuild | Other | 50547 | Eagle Grove - Goldfield | Install two line switches on a steel pole |  | M2 - Appendix A Approved | 500000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Eagle Grove | Goldfield | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50334 | Eagle Grove-Goldfield 69 kV Interconnection and Clarion-Latimer 69 kV Line Rebuild | Other | 50548 | Clarion-Latimer 69 kV Line | Rebuild the Clarion-Latimer 69 kV line sections. |  | M2 - Appendix A Approved | 11500000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Clarion | Latimer | 1 | 69 |  |  | 19.5 | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50335 | Johnson Creek Add 161 kV Breakers | Other | 50549 | Johnson Creek | Install 161 kV breakers and associated equipment. |  | M2 - Appendix A Approved | 2000000 | 2027-08-01 | Substation | Circuit Breaker (replacement at existing substation) | Johnson Creek |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50336 | Substation Equipment Replacement Blanket | Other | 50550 | Kellogg | Replace three 161 kV oil circuit breakers at Kellogg Substation |  | M2 - Appendix A Approved | 1500000 | 2026-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Kellogg |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50336 | Substation Equipment Replacement Blanket | Other | 50551 | Missouri Valley | Replace two 69 kV breakers and associated disconnect switches at Missouri Valley Substation |  | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Missouri Valley |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50336 | Substation Equipment Replacement Blanket | Other | 50552 | Sub T Fort Dodge | Replace four 161 kV oil circuit breakers and two switches at Sub T in Fort Dodge |  | M2 - Appendix A Approved | 3500000 | 2026-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Sub T Fort Dodge |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50336 | Substation Equipment Replacement Blanket | Other | 50553 | Substation Equipment Replacement Blanket | Replace substation equipment because of condition and/or to improve reliability at various substations |  | M2 - Appendix A Approved | 14500000 | 2028-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Various |  |  | 345 | 69 |  |  | IA |  | Not Shared
MTEP25 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50337 | Rebuild Tower - Black Lake 69 kV line to 138 kV capability | Other | 50554 | Tower to Black Lake | Tower to Black Lake transmission line. |  | M2 - Appendix A Approved | 4500000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Tower | Black Lake |  | 69 | 69 | 4.5 |  | MI |  | Not Shared
MTEP25 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50338 | Rebuild Lincoln Junction - Lincoln 69 kV line to 138 kV capability | Other | 50555 | Lincoln Junction to Lincoln | 5 Miles of transmission line between Lincoln and Lincoln Junction |  | M2 - Appendix A Approved | 5000000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Linoln Junction | Lincoln |  | 69 | 69 |  | 5 | MI |  | Not Shared
MTEP25 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50339 | Rebuild Bass Lake - Wolf Lake 69 kV line to 138 kV capability | Other | 50556 | Bass Lake to Wolfe Lake | 11 Miles of transmission line between the Bass Lake and Wolfe Lake substations. |  | M2 - Appendix A Approved | 11000000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Bass Lake | Wolfe Lake |  | 69 | 69 |  | 11 | MI |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50341 | Replace 34507 Gibson-Petersburg 345 kV Line | Other | 50558 | 34507 Gibson-Petersburg Line Improvements | 34507 Gibson-Petersburg Line Improvements - replace 16 aluminum Kaiser A, B, or C towers with 3 pole dead end structures at 2.5 mile intervals |  | M2 - Appendix A Approved | 15207000 | 2027-05-21 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gibson | Petersburg |  | 345 |  |  | 33.53 | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50342 | Rebuild Greencastle Industrial Jct. to WVPA Vandalia 69kV Line | Other | 50559 | Greencastle Industrial Jct. to WVPA Vandalia 69kV Line Rebuild | 6996 Greencastle Industrial Jct. to WVPA Vandalia Rebuild - 0.74 miles with 477ACSR/VR2@120C; Greencastle Industrial Jct. upgrade to ATO / SCADA control |  | M3 - Under Construction | 1984000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Greencastle Industrial Jct. | WVPA Vandalia (new sub) |  | 69 |  |  | 0.74 | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50343 | Terre Haure Water St. 138kV Ring Bus | Other | 50560 | Terre Haure Water St. 138kV Ring Bus | Terre Haure Water St. 138kV sub - construct 3-breaker 138kV ring bus |  | M2 - Appendix A Approved | 16520000 | 2028-12-11 | Substation | Substation (breakers only, no transformer) | Terre Haure Water St. |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50345 | New WVPA Richland 69kV ring bus | Other | 50562 | WVPA Richland 69kV ring bus | WVPA Richland 69kV ring bus: install 3 - CB ring at existing sub; rebuild 0.9 mile WVPA Richland to Rochester Tap 6968 with 954ACSR |  | M2 - Appendix A Approved | 11736000 | 2030-10-18 | Substation | Substation (breakers only, no transformer) | WVPA Richland |  |  | 69 |  |  | 0.9 | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50347 | Replace Frankfort 230/69 Bk1 | Other | 50564 | Frankfort 230/69 Bk1 Replace | Frankfort 230/69 Bk1: Replace 84MVA 230/69kV Transformer with new 150MVA transformer; replace 23069-1 ckt. switcher; replace substation RTU |  | M2 - Appendix A Approved | 6329000 | 2027-01-21 | Transformer | Transformer Replacement | Frankfort 230/69 Bk1 |  |  | 230 | 69 |  |  | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50349 | Crane Naval Base load expansion | Other | 50566 | Crane South Substation | Crane South Substation: expand 138kV bus into (4) CB Ring; Install 100MVA 138/69kV Transformer Bank 2; Add (2) 69kV breakers to the existing ring; construct new 69kV line to Crane Naval Base NW; reconductor 69193 line from Crane South to Crane Naval Base |  | M2 - Appendix A Approved | 28966000 | 2027-12-07 | Transformer | Transformer New | Crane South |  |  | 138 | 69 |  |  | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50351 | Rebuild Arcadia N to Arcadia 69kV Line | Other | 50567 | Arcadia N to Arcadia 69kV Line Rebuild | Arcadia N to Arcadia 69kV Rebuild - 2.5 miles of 69kV line 69180 from Arcadia north sub to Arcadia sub |  | M2 - Appendix A Approved | 5500000 | 2027-11-23 | Line Upgrade | Line rebuild on existing ROW | Arcadia | Arcadia North |  | 69 |  |  | 2.5 | IN |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50365 | Shannon Capacitor Bank Replacement | Other | 50568 | Shannon 230 kV Capacitor Banks | Replace the two existing 230 kV capacitor banks with two 54.3 MVAR capacitor banks |  | M2 - Appendix A Approved | 1200000 | 2026-12-31 | Voltage Device | Capacitor (switched capacitor) | Shannon |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50365 | Shannon Capacitor Bank Replacement | Other | 50569 | Shannon 115 kV Capacitor Banks | Replace the existing 115 kV capacitor bank with a 19.5 MVAR capacitor bank |  | M2 - Appendix A Approved | 550000 | 2026-12-31 | Voltage Device | Capacitor (switched capacitor) | Shannon |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | METC | East | 50366 | Upgrade Mud Lake - Verona #1 138 kV line | BRP | 50570 | Mud Lake-Verona #1_Upgrade 954 ACSR Conductor to 1431 ACSR | Upgrade ~0.67 mile of 954 ACSR to 1431 ACSR on the Mud Lake – Verona #1 138 kV line. |  | M2 - Appendix A Approved | 1410000 | 2030-06-01 | Line Upgrade | Line rebuild on existing ROW | Mud Lake | Verona | 1 | 138 |  |  | 0.67 | MI |  | Not Shared
MTEP25 | A | METC | East | 50366 | Upgrade Mud Lake - Verona #1 138 kV line | BRP | 50571 | Verona - Upgrade 588 Bus and Switch | Upgrade the 2-4/0 Cu stranded bus at position “588” and switch 585 to at least 450 MVA for summer emergency rating. |  | M2 - Appendix A Approved | 180000 | 2030-06-01 | Substation | Small miscellaneous substation equipment | Verona |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50369 | Rebuild Huntington Goblesville Jct to United Jct 69kV Line | Other | 50572 | Huntington Goblesville Jct to United Jct 69kV Line Rebuild | Huntington Goblesville Jct to United Jct 69kV rebuild: 6.45 miles of line 6923 ckt. |  | M2 - Appendix A Approved | 9238000 | 2026-12-11 | Line Upgrade | Line rebuild on existing ROW | Huntington Goblesville Jct | United (Bippus) Jct |  | 69 |  |  | 6.45 | IN |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50371 | Lee Hanna 69/12kV Rebuild | Other | 50574 | 69/12kV Substation | New 33.6MVA substation 69/12kV |  | M2 - Appendix A Approved | 10000000 | 2027-11-01 | Transformer | Transformer New | Lee Hanna |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50374 | Upgrade Dresser 345kV Line | GIP | 50576 | Dresser 345kV Line Upgrades | Dresser 345kV Line Upgrades: 34520 (to Fairbanks) and 34538 (to Sugar Crk) ckts. - replace structures to achieve line ratings of 100°C |  | M2 - Appendix A Approved | 11600000 | 2027-07-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Dresser | 345 lines |  | 345 |  |  | 16.52 | IN |  | Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50579 | Lansing Ave - Construct new 138 kV Station | Rebuild Blackstone 138kV station at a new site approximately 0.20 miles to the north, utilizing new equipment in a six (6) breaker ring bus configuration. All new 138kV breakers should be standard 3000A 50kA breakers. All new equipment at the new station must be rated 450MVA for summer emergency. The tentative name of the new 138kV station is Lansing Ave. |  | M2 - Appendix A Approved | 9450000 | 2030-06-01 | Substation | Switching station (breakers only, no transformer) | New Station |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50580 | Blackstone-Broughwell_Lansing Ave OHL Cut-In | Cut Blackstone-Broughwell 138kV line into the new station utilizing 1431 ACSR Conductor. |  | M2 - Appendix A Approved | 1240000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | New Station | Broughwell |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50581 | Blackstone-Stable_Lansing Ave OHL Cut-In | Cut the Blackstone-Stable 138kV line (Main-Blackstone section) to new station utilizing 1431 ACSR Conductor. |  | M2 - Appendix A Approved | 1170000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | New Station | Maines Road |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50381 | Rebuild Riverside-Hardin Tap 69 kV line | Other | 50582 | Rebuild Riverside-Hardin Tap 69 kV Line | Rebuild Riverside-Hardin Tap 69 kV Line |  | M2 - Appendix A Approved | 5940000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Riverside | Hardin Tap |  | 69 |  |  | 10.8 | IL |  | Not Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50583 | Blackman-Leoni 138kV Line | Tie the existing Blackman-Blackstone #1 and Blackstone-Leoni #1 line utilizing 1431 ACSR Conductor to form the new Blackman-Leoni 138kV line. Also remove all sag limit on Blackman-Leoni 138kV line (on the original Blackman-Blackstone section). |  | M2 - Appendix A Approved | 1440000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Blackman | Leoni |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50584 | Lansing Ave-Blackstone_Construct new 138kV line to CE 46kV TRF #1 | Construct 0.37 miles of 138kV line from Lansing Ave to CE 46kV TRF #1 utilizing 954 ACSR Conductor. |  | M2 - Appendix A Approved | 1255000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | New Station | Blackstone 46kV |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50585 | Blackstone - Decommission 138kV Station | Decommission 138kV Blackstone substation. |  | M2 - Appendix A Approved | 1370000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Blackstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50383 | 2026 EAL Asset Renewal Program | Other | 50587 | EAL Transmission Facilities | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. |  | M3 - Under Construction | 16475000 | 2026-12-30 | Substation | Small miscellaneous substation equipment | Greenbrier |  |  | 161 |  |  |  | AR |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50384 | Hot Springs 500kV SPOF | BRP | 50588 | Hot Springs EHV | All 500kV line panels at Hot Springs need to have primary 1 relays on a separate DC panel than primary 2/backup relays. The breakers for these lines must have trip coil #1 and trip coil #2 fed from separate DC panels. The DC panels must be fed from separate battery sets and the DC panels cannot be wired in series or in parallel to one another. |  | M2 - Appendix A Approved | 2914000 | 2026-11-02 | Substation | Small miscellaneous substation equipment | Hot Springs |  |  | 500 |  |  |  | AR |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50385 | El Dorado Donan - El Dorado Monsanto 115 kV: Rebuild Line | BRP | 50589 | El Dorado Donan - El Dorado Monsanto 115kV | Rebuild the ~3.1 mile line segment along with any other station equipment to achieve a 1300 A flow-through rating. |  | M2 - Appendix A Approved | 7070000 | 2027-06-30 | Line Upgrade | Line rebuild on existing ROW | El Dorado Donan | El Dorado Monsanto |  | 115 |  |  |  | AR |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50386 | Hilltop - Saint Joe 161kV: Rebuild Line | BRP | 50590 | Hilltop - Saint Joe 161kV | Rebuild Hilltop – St Joe along with any other station equipment to achieve a 1300 A through path rating. |  | M2 - Appendix A Approved | 12384021 | 2027-12-07 | Line Upgrade | Line rebuild on existing ROW | Hilltop | Saint Joe |  | 161 |  |  |  | AR |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50387 | Saint Joe - Everton Road 161kV: Rebuild Line | BRP | 50591 | Saint Joe - Everton Road 161kV | Rebuild St Joe – Everton Rd along with any other station equipment to achieve a 1300 A through path rating. |  | M2 - Appendix A Approved | 29720000 | 2028-07-20 | Line Upgrade | Line rebuild on existing ROW | Saint Joe | Everton Road |  | 161 |  |  |  | AR |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50388 | Everton Road - Harrison East 161kV: Rebuild Line | BRP | 50592 | Everton Road - Harrison East 161kV: Rebuild Line | Compliance with NERC Reliability Standard TPL-001, R2.7. Increased reliability by updating aging infrastructure and increased line capacity for improved transmission system performance. |  | M2 - Appendix A Approved | 20140000 | 2029-04-13 | Line Upgrade | Line rebuild on existing ROW | Everton Road | Harrison East |  | 161 |  |  |  | AR |  | Not Shared
MTEP25 | A | METC | East | 50377 | Rebuild Blackstone 138 kV Station | Other | 50593 | Lansing Ave-Blackstone_Construct new 138kV line to CE 46kV TRF #2 | Construct 0.37 miles of 138kV line from Lansing Ave to CE 46kV TRF #2 utilizing 954 ACSR Conductor. |  | M2 - Appendix A Approved | 1075000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | New Station | Blackstone 46kV |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50246 | Replace Caniff #303AB PST Transformer | Other | 50594 | Caniff - Replace 303AB PST Transformer | Replace the Caniff 303(AB) PST Transformer with at least 736 MVA (3543 Amps) summer emergency rated transformer. |  | M2 - Appendix A Approved | 30000000 | 2028-12-31 | Transformer | Transformer Replacement | Caniff |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50389 | New Leesburg 345/138kV Transformer addition | Other | 50601 | Leesburg 345/138kV Transformer | Addition of 2nd Leesburg 345/138kV Transformer |  | M2 - Appendix A Approved | 8000000 | 2027-12-31 | Transformer | Transformer New | Leesburg |  |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50390 | New Dune Acres 138 kV Breaker additions | BRP | 50602 | Dune Acres 138kV breaker additions | Add Breakers to 138kV lines on existing single breaker. |  | M2 - Appendix A Approved | 3000000 | 2029-05-31 | Substation | Substation bus upgrade | Dune Acres |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 50391 | Line 74B Rebuild | Other | 50603 | Colonial Collins – Colonial Kola | A complete rebuild of Line 74B (Colonial Collins – Colonial Kola 0.77 mi.) is recommended at 161kV insulation with more reliable structural designs and OPGW. |  | M2 - Appendix A Approved | 900000 | 2027-01-01 | Line Upgrade | Line rebuild on existing ROW | Colonial Collins | Colonial Kola |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50392 | Elk River Muni West | Other | 50604 | Elk River Muni West | Remove and upgrade 600-amp switches EWSM11 and EWS10 with live parts to 1200 amp. The span of 266 ACSR transmission conductor between the two switch poles should be removed and upgraded to 477 ACSS. Switch EWS14 is 1200-amp and owned by Elk River Municipal and nothing needs to be done to this switch. |  | M2 - Appendix A Approved | 68811 | 2026-10-30 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Elk River Muni West |  |  | 69 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50393 | Iron Range 500kV Reactor Addition | Other | 50605 | Iron Range 500kV Reactor | New 500kV reactor, 150 MVAR. |  | M2 - Appendix A Approved | 4000000 | 2030-12-31 | Voltage Device | Reactor or Inductor | Iron Range |  |  | 500 |  |  |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50394 | Riverton Asset Renewal | Other | 50606 | Riverton Asset Renewal | GRE plans to upgrade equipment and relocated assets ahead of MP Riverton rebuild scheduled for in-service by 2030. The project includes pull all GRE assets out of MP control house that is planned for demo by 2030 into new GRE control house. GRE will also be upgrading physical assets in our yard including the 25WB1 oil breaker, relaying, the Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, GE PT’s, and bus modifications. |  | M2 - Appendix A Approved | 2610398 | 2028-06-30 | Substation | Substation bus upgrade | Riverton |  |  | 115 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 50396 | New BREC Bon Harbor-OMU Sub ‘M’ 69 kV Interconnection | Other | 50608 | BREC-OMU 69 kV Interconnection | This will be a 0.3 mile 69 kV line between BREC's 69 kV system by means of a tap to connect to OMU's Substation M. |  | M2 - Appendix A Approved | 7500000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Bon Harbor |  | 1 | 69 |  | 0.3 |  | KY |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 50399 | Line 35A Rebuild | Other | 50609 | Benndale - Benndale GT | A complete rebuild of Line 35A (Benndale – Benndale GT 69kV) is recommended at 161kV insulation with more reliable structural designs and OPGW. This project will increase reliability of the transmission system and provide an additional OPGW communication link between Benndale and Benndale GT. |  | M2 - Appendix A Approved | 900000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Benndale | Benndale GT |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 50400 | Ovett 69kV Delivery Point | Other | 50610 | Ovett GOAB - Ovett DP | Tap Line 114A (Ellisville - NW Perry 69kV) with a 69kV GOAB and build a new transmission line to the delivery point. |  | M2 - Appendix A Approved | 1975000 | 2026-10-01 | Line New | New Transmission line, new ROW - may include terminations | Ovett GOAB | Ovett DP |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | METC | East | 50372 | Upgrade Dupont-White Lake 138 kV line | BRP | 50611 | Upgrade Dupont-White Lake 138kV Line | Upgrade line from Dupont to White Lake (~5.094 miles) from 336 ACSR to 954 ACSR. |  | M2 - Appendix A Approved | 8050000 | 2030-06-01 | Line Upgrade | Line reconductor | Dupont | White Lake |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 50400 | Ovett 69kV Delivery Point | Other | 50612 | Ovett GOAB | Tap Line 114A (Ellisville - NW Perry 69kV) with a 69kV GOAB. |  | M2 - Appendix A Approved | 125000 | 2026-10-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Ovett GOAB |  |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | METC | East | 50372 | Upgrade Dupont-White Lake 138 kV line | BRP | 50613 | Dupont - Upgrade 199 and 177 Buses | Upgrade buses at Dupont positions “199” and “177” to at least 332 MVA for summer emergency rating. |  | M2 - Appendix A Approved | 248000 | 2030-06-01 | Substation | Substation bus upgrade | Dupont |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50401 | Rebuild East Jordan Junction - Barnard 69 kV line to 138 kV capability | Other | 50614 | East Jordan Junction to East Jordon | 2.25 miles of single circuit steel pole contruction with 795 ACSS. |  | M2 - Appendix A Approved | 2500000 | 2024-12-31 | Line Upgrade | Line rebuild on existing ROW | East Jordon Junction | East Jordon |  | 69 |  |  | 2.25 | MI |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 50402 | Boswell 115/23kV Transformer Addition | Other | 50615 | Boswell 115kV Substation | Bus expansion and breaker addition. |  | M2 - Appendix A Approved | 1550000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Boswell |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50401 | Rebuild East Jordan Junction - Barnard 69 kV line to 138 kV capability | Other | 50616 | East Jordon to Eastport | 11.5 miles of single-circuit steel poles with 795 ACSS. |  | M2 - Appendix A Approved | 13000000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | East Jordon | Eastport |  | 69 |  |  | 11.5 | MI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50403 | Relocate Dardenne 161/138 kV Substation | Other | 50617 | Dardenne Substation Retirement | Dardenne Substation Retirement |  | M2 - Appendix A Approved | 3600000 | 2027-12-01 | Transformer | Transformer Replacement | Dardenne |  |  | 161 | 138 |  |  | MO |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 50404 | Lake Walthall 115kV Delivery Point | Other | 50618 | Lake Walthall SS - Lake Walthall DP | Tap the Entergy owned 115kV line (Tylertown - Dexter) with a 115kV switching station and build a new transmission line to the delivery point. |  | M2 - Appendix A Approved | 1900000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Lake Walthall SS | Lake Walthall DP |  | 115 |  |  |  | MS |  | Not Shared
MTEP25 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50401 | Rebuild East Jordan Junction - Barnard 69 kV line to 138 kV capability | Other | 50619 | Eastport to Barnard | 10 miles of single-circuit steel poles with 795 ACSS |  | M2 - Appendix A Approved | 10500000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Eastport | Barnard |  | 69 |  |  | 10 | MI |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 50404 | Lake Walthall 115kV Delivery Point | Other | 50620 | Lake Walthall SS | Tap the Entergy owned 115kV line (Tylertown - Dexter) with a 115kV switching station. |  | M2 - Appendix A Approved | 930000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Lake Walthall SS |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50405 | Relocate Berlin-Amos 69 kV Line | Other | 50621 | Relocate Berlin-Amos 69 kV Line | Reroute Berlin-Amos 69 kV Line out of creek bottom. |  | M2 - Appendix A Approved | 11175000 | 2029-12-01 | Line New | New Transmission line, new ROW - may include terminations | Berlin | Amos |  | 69 |  | 19 | 1 | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50406 | Rebuild Breiner-Kington 69 kV line | Other | 50622 | Rebuild Breiner-Kington 69 kV Line | Rebuild Breiner-Kington 69 kV Line |  | M2 - Appendix A Approved | 5665000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Breiner | Kington |  | 69 |  |  | 10.3 | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50407 | Rebuild Macomb-Spring Lake Junction 69 kV line | Other | 50623 | Rebuild Macomb Bkr-Woodland 69 kV Line | Rebuild Macomb Bkr-Woodland 69 kV Line |  | M2 - Appendix A Approved | 1010000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Macomb Bkr | Woodland |  | 69 |  |  | 1.75 | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50407 | Rebuild Macomb-Spring Lake Junction 69 kV line | Other | 50624 | Rebuild Woodland-Spring Lake Jct 69 kV Line | Rebuild Woodland-Spring Lake Jct 69 kV Line |  | M2 - Appendix A Approved | 1000000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Woodland | Spring Lake Jct |  | 69 |  |  | 1.7 | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50408 | Rebuild El Dara Junction-Hadley 69 kV line | Other | 50626 | Rebuild El Dara Jct-Hadley 69 kV Line | Rebuild El Dara Jct-Hadley 69 kV Line with 336 ACSR |  | M2 - Appendix A Approved | 2820000 | 2029-12-01 | Line Upgrade | Line rebuild on existing ROW | El Dara Jct | Hadley |  | 69 |  |  | 5.25 | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50409 | New Andrew-Salisbury 69 kV Line | Other | 50628 | New Andrew-Salisbury DC 69 kV Line and Breaker | New Andrew-Salisbury DC 69 kV Line with 336 ACSR and New Andrew 69 kV Breaker for dedicated feed. No new ROW |  | M2 - Appendix A Approved | 1500000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Andrew | Salisbury |  | 69 |  | 0.5 |  | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50412 | New Paragon-Grove City 69 kV line | Other | 50632 | New Paragon-Dunkel 69 kV Line | New Paragon-Dunkel 69 kV Line with 336 ACSR |  | M2 - Appendix A Approved | 4550000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Paragon | Dunkel |  | 69 |  | 3.9 |  | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50412 | New Paragon-Grove City 69 kV line | Other | 50633 | New Dunkel-Owaneco-Velma 69 kV Line | New Dunkel-Owaneco-Velma 69 kV Line with 336 ACSR |  | M2 - Appendix A Approved | 9750000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Dunkel | Velma |  | 69 |  | 13 |  | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50412 | New Paragon-Grove City 69 kV line | Other | 50635 | New Velma-Grove City 69 kV Line | New Velma-Grove City 69 kV Line with 336 ACSR |  | M2 - Appendix A Approved | 5590000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Velma | Grove City |  | 69 |  | 8.6 |  | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50413 | New Edinburg 69 kV Breaker Station | Other | 50636 | New Edinburg 69 kV Breaker Station | New Edinburg 69 kV Breaker Station |  | M2 - Appendix A Approved | 3400000 | 2030-12-01 | Substation | Substation (breakers only, no transformer) | Edinburg |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50414 | New Henton 69 kV Breaker Station | Other | 50637 | New Henton 69 kV Breaker Station | New Henton 69 kV Breaker Station |  | M2 - Appendix A Approved | 3000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Henton |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP25 | A | PRAIRIE POWER, INC. | Central | 50414 | New Henton 69 kV Breaker Station | Other | 50638 | New Henton 69 kV Capacitor Bank | New Henton 69 kV Capacitor Bank 4.8 MVAR |  | M2 - Appendix A Approved | 400000 | 2029-12-01 | Voltage Device | Capacitor (switched capacitor) | Henton |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50416 | Pine City Breaker Replacement | Other | 50640 | Pine City Breaker Replacement | • Replace breaker 4NB2 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace breaker 4NB3 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace 69kV bus PTs, Grasston line PT and Rush City/Rock Lake line CCVT o Remove 69kV PT Fuses • Replace line arresters with new 48kV MCOV Surge Arresters on Grasston and Bear Creek/Hinckley Lines • Replace 69kV bus relaying with SEL-487E pri/sec panel • Replace the #3 311B panel with 2 line 311C panel • Remove NS3 bypass switch • Update Station Service System o Install new 50kVA SSVT (Pri.) o Install new 200A ATS o Install new 200A Safety Switch (Pri.) o Install new 200A Safety Switch (Emer.) o ECE to replace existing 10kVA Aux Xfmr with 50kVA Aux Xfmr • Update line naming/3 letter mnemonics • Review grounding |  | M2 - Appendix A Approved | 1364747 | 2027-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Pine City |  |  | 69 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50315 | New Ralston 138 kV Substation Eagle Valley Reinforcement | Other | 50641 | Ralston Substation | New 4-position ring bus 138 kV Ralston substation looped in on 132-23 Eagle Valley-Sanitation Southport line. |  | M2 - Appendix A Approved | 10000000 | 2031-03-01 | Substation | Distribution substation - may include trans high side | Ralston |  |  | 138 |  | 0 | 0 | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50315 | New Ralston 138 kV Substation Eagle Valley Reinforcement | Other | 50642 | Camby Substation | Add new 138 kV line terminal at Camby substation​ |  | M2 - Appendix A Approved | 4000000 | 2031-03-01 | Substation | Substation bus upgrade | Camby |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50315 | New Ralston 138 kV Substation Eagle Valley Reinforcement | Other | 50643 | Ralston - Camby | Rebuild (as needed) nearby 138 kV idle line and connect into Ralston substation (1.82 rebuild for double circuit; 2.8 refurbish existing line).​ |  | M2 - Appendix A Approved | 10000000 | 2031-03-01 | Line New | New Transmission line, new ROW - may include terminations | Ralston | Camby |  | 138 |  | 1.82 | 2.8 | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50216 | Upgrade Petersburg 138 kV Breakers - 3 Breakers | BRP | 50644 | Petersburg 138 kV breakers #6, #7, & #9 | Replace Petersburg 138 kV breakers #6, #7, & #9 from 40 kA to 63 kA. |  | M2 - Appendix A Approved | 739000 | 2031-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Petersburg |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50217 | Upgrade Stout South Breakers - 12 Breakers 138 kV | BRP | 50645 | 138 kV Stout South Breakers | 80 kA Breakers for #1A, #2A, #2C, #3A, #3B, #3C, #4A, #4C, #5A, #5B, #5C, #5D |  | M2 - Appendix A Approved | 3050000 | 2031-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Stout South |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50398 | Install Inver Hills TRs and Feeders | Other | 50646 | Inver Hills Substation | Add 2x50 MVA Transformers Add breakers Extend feeders |  | M2 - Appendix A Approved | 35100000 | 2028-12-15 | Substation | Distribution substation - may include trans high side | Inver Hills |  |  | 115 | 14 | 0 | 0 | MN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50311 | Rebuild Stout North-Sanitation Belmont-Southwest_132-01_&_132-74_138 kV Lines | BRP | 50647 | Rebuild 138 kV 132-74 | Rebuild existing 2.114 miles 138 kV 132-74 Sanitation Belmont-Southwest line to new Summer rating of 2000A (478 MVA). |  | M2 - Appendix A Approved | 5290000 | 2033-12-01 | Line Upgrade | Line rebuild on existing ROW | Sanitation Belmont | Southwest | 74 | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50312 | Rebuild Southwest-Lilly South 132-10 138 kV Line | BRP | 50648 | Rebuild 138 kV 132-10 | Rebuild existing 2.893 miles 138 kV 132-10 Southwest-Lilly South line to new Summer rating of 2000A (478 MVA). |  | M2 - Appendix A Approved | 7070000 | 2033-12-01 | Line Upgrade | Line rebuild on existing ROW | Southwest | Lilly South |  | 138 |  | 2.89 |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50313 | Rebuild Lilly South-Center 132-61 138 kV Line | BRP | 50649 | Rebuild 138 kV 132-61 | Rebuild existing 1.267 miles 138 kV 132-61 Lilly South-Center line to new Summer rating of 2000A (478 MVA). |  | M2 - Appendix A Approved | 2900000 | 2033-12-01 | Line Upgrade | Line rebuild on existing ROW | Lilly South | Center | 61 | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50314 | Rebuild Georgetown-North 132-86 138 kV Line | BRP | 50650 | Rebuild 138 kV 132-86 | Rebuild existing 7 miles 138 kV 132-86 Georgetown-North line to new Summer rating of 1600A (382 MVA). |  | M2 - Appendix A Approved | 12760000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Georgetown | North | 86 | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50418 | Denham - Kettle River Rebuild | Other | 50651 | Denham - Kettle River Rebuild | The transmission line has had conductor failures over the last few years. A recent failure caused a grass fire. The line was planned to be rebuilt due to age/condition starting in 2027 and due to the current maintenance issues the project should start as soon as possible. |  | M2 - Appendix A Approved | 11442911 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Denham | Kettle River | 1 | 69 | 69 |  | 15.1 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50417 | Rebuild 0735 St Bonifacius to Mound | Other | 50652 | Rebuild 0735 St Bonifacius to Mound | Rebuild 0735 St Bonifacius to Mound and add OPGW |  | M2 - Appendix A Approved | 13157400 | 2027-12-31 | Line Upgrade | Line reconductor | St. Bonifacious | Mound | 1 | 69 |  |  | 8.3 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50419 | Bena Area Projects | Other | 50653 | Bena Area Projects | Rebuild BE line from SS2505 to Bena Substation. Line length is approx. 15 miles. Enbridge plans to remove Line 3 which is located roughly 15ft north of GRE’s BE line between Bena Sub and Str 158 near the Mississippi River crossing (approx 12mi). The corridor where the pipeline and transmission line are located is very crowded, swampy and includes a LCP distribution line which is located about 12ft north of the BE line between the Enbridge Pipeline and BE line. The GRE line and LCP line are tied together with crossarms on many structures and there are side guys which extend under the pipeline in many locations. LCP plans to remove their distribution and relocate. |  | M2 - Appendix A Approved | 17450679 | 2029-11-29 | Line Upgrade | Line rebuild on existing ROW | Bena | Bena Tap | 1 | 69 | 69 |  | 15 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50420 | Lakefield Area Projects | GIP | 50654 | Lakefield Area Projects | Expansion of the 345kV Gen tie bus at the Lakefield substation to accommodate the Three Waters Wind (340MW) Wind Farm. Installation of new 345kV breakers on the existing generator and installation of the GRE controlled EEE, 1500’ of 345kV Transmission to the interconnect 161kV/345kV step up substation |  | M2 - Appendix A Approved | 5217392 | 2027-08-24 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Lakefield |  |  | 345 | 345 |  |  | MN |  | Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50421 | Rebuild 0737 Gleason Lake to Mound | Other | 50655 | Rebuild 0737 Gleason Lake to Mound | Rebuild 0737 Gleason Lake to Mound and install OPGW. |  | M2 - Appendix A Approved | 11500000 | 2028-12-31 | Line Upgrade | Line reconductor | Gleason Lake | Mound | 1 | 69 |  |  | 8.7 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50423 | Essig Substation Rebuild | Other | 50657 | Essig Substation Rebuild | Rebuild end of life Essig substation at neighboring site, converting old 2.4 kV system to standard 12.47kV |  | M2 - Appendix A Approved | 1900000 | 2027-08-31 | Substation | Distribution substation - may include trans high side | Essig |  |  | 69 | 13 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50424 | Maple Street Substation | Other | 50658 | Maple Street Substation | Install new distribution substation to meet load growth in area |  | M2 - Appendix A Approved | 13000000 | 2027-06-01 | Substation | Distribution substation - may include trans high side | Maple Street |  |  | 115 | 13 |  |  | SD |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50425 | Fischer Substation Rebuild | Other | 50659 | Fischer Substation Rebuild | DEA plans to update their 115-kV Fisher in/out distribution substation (both east and west) on the same property to replace the aged substation equipment. GRE will need to move the meter and telecom equipment as part of this work. |  | M3 - Under Construction | 1476377 | 2026-04-13 | Substation | Switching station (breakers only, no transformer) | Fischer |  |  | 115 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50426 | Thunder Substation | Other | 50660 | Thunder Substation | Install new distribution substation to meet load growth in area |  | M2 - Appendix A Approved | 7300000 | 2027-10-15 | Substation | Distribution substation - may include trans high side | Thunder |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50427 | Winthrop to Bell rebuild projects | Other | 50661 | Winthrop to Bell Rebuild Project | Rebuild Winthrop to Bell line, about 12 miles. |  | M2 - Appendix A Approved | 9868407 | 2028-08-31 | Line Upgrade | Line rebuild on existing ROW | Bell | Winthrop | 1 | 69 | 69 |  | 12 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50428 | Replace Cass County TR1 | Other | 50665 | Replace Cass County TR1 | Upgrade Cas County TR1 to support load growth. Rebuild distribution banks and include distribution reactors. |  | M2 - Appendix A Approved | 12200000 | 2028-06-01 | Transformer | Transformer Replacement | Cass County |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50441 | Wrightsville 115kV: Build two 115kV lines | Other | 50668 | Wrightsville 115kV Transmission Line #1 | New 3.5 mile transmission line from Wrightsville 115kV |  | M2 - Appendix A Approved | 8900000 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | Wrightsville |  |  | 115 |  | 3.5 |  | AR |  | Shared
MTEP25 | A | ENTERGY ARKANSAS, LLC | South | 50441 | Wrightsville 115kV: Build two 115kV lines | Other | 50669 | Wrightsville 115kV Transmission Line #2 | A new 3.5 mile 115kV transmission line from Wrightsville 115kV |  | M2 - Appendix A Approved | 8900000 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | Wrightsville |  |  | 115 |  | 3.5 |  | AR |  | Shared
MTEP25 | A | METC | East | 50447 | New [CONS] Baker Interconnection | Other | 50677 | Weeds Lake - Add BM8 Termination | Install two 138 kV, 63kA breakers at Weeds Lake to terminate Baker connection at position “BM8”. |  | M2 - Appendix A Approved | 1910000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Weeds Lake |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50447 | New [CONS] Baker Interconnection | Other | 50678 | Baker-Weeds Lake_Construct New 138 kV Line | Construct ~36.5 miles of new 138 kV line on double-circuit structures (leave vacant side for future use) using 954 ACSR conductor. |  | M2 - Appendix A Approved | 106900000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Weeds Lake | Baker |  | 138 |  | 36.5 |  | MI |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50311 | Rebuild Stout North-Sanitation Belmont-Southwest_132-01_&_132-74_138 kV Lines | BRP | 50681 | Rebuild 138 kV 132-01 | Rebuild existing ~1 mile 138 kV 132-01 Stout North-Sanitation Belmont line to new Summer rating of 2000A (478 MVA). |  | M2 - Appendix A Approved | 4000000 | 2032-12-01 | Line Upgrade | Line rebuild on existing ROW | Stout North | Sanitation Belmont | 01 | 138 |  |  | 1 | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50311 | Rebuild Stout North-Sanitation Belmont-Southwest_132-01_&_132-74_138 kV Lines | BRP | 50682 | Stout North | Optimize Stout North: Move 132-14 south one bay (H16 & New H15), improve bay to double breaker​; Move 132-01 south one bay (H6 & H5) |  | M2 - Appendix A Approved | 5700000 | 2032-12-01 | Substation | Substation bus upgrade | Stout North |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50306 | Rebuild Southwest-Stout CT_132-02_138 kV Line | BRP | 50683 | Rebuild 138 kV 132-02 | Rebuild existing 2.85 mile 138 kV 132-02 Southwest-Stout CT line to new Summer rating of 2000A (478 MVA). |  | M2 - Appendix A Approved | 9300000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Southwest | Stout CT | 02 | 138 |  |  | 2.85 | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50307 | Rebuild Southwest-Northwest 132-04 138 kV Line | BRP | 50684 | Rebuild 138 kV 132-04 | Rebuild existing 4.75 miles 138 kV 132-04 Southwest-Northwest line to new Summer rating of 2000A (478 MVA). |  | M2 - Appendix A Approved | 15200000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Southwest | Northwest | 04 | 138 |  |  | 4.75 | IN |  | Not Shared
MTEP25 | A | METC | East | 50463 | Rebuild [CONS] Blackstone 46 kV Station | Other | 50685 | Blackstone- Install 188 Breaker & Convey CE's 199 to METC | Install a new 138 kV, 40 kA breaker with disconnects at “188” position (connected to Blue Bus). Existing CE “199” breaker with disconnects will be conveyed to METC. Re-name this CE “199” breaker as METC “288” breaker. |  | M2 - Appendix A Approved | 1465000 | 2028-10-01 | Substation | Substation (breakers only, no transformer) | Blackstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50463 | Rebuild [CONS] Blackstone 46 kV Station | Other | 50686 | Blackstone-CE TRF #1 138kV_New Line Construction | METC to build a new radial 138kV single circuit line using 954 ACSR conductor and OPGW from Blackstone to CE TRF #1 terminating at "188" position. |  | M2 - Appendix A Approved | 950000 | 2028-10-01 | Line New | New Transmission line, new ROW - may include terminations | Blackstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50463 | Rebuild [CONS] Blackstone 46 kV Station | Other | 50687 | Blackstone-CE TRF #2 138kV_New Line Construction | METC to build a new radial 138kV single circuit line using 954 ACSR conductor and OPGW from Blackstone to CE TRF #2 terminating at "288" position. |  | M2 - Appendix A Approved | 880000 | 2028-10-01 | Line New | New Transmission line, new ROW - may include terminations | Blackstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50464 | Erie Road Substation Rebuild | Other | 50688 | Erie Road Substation Rebuild | Rebuild the Erie Road substation in Marshall with new 115 kV breakers and other equipment. |  | M2 - Appendix A Approved | 6418700 | 2029-03-31 | Substation | Substation bus upgrade | Erie Rd 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50465 | Pella Underground Conversion | Other | 50689 | Pella Underground Conversion | Rebuild a section of overhead line (~1,135 linear feet of transmission line) to underground line (~800 feet of underground cable). |  | M2 - Appendix A Approved | 268000 | 2026-09-30 | Line Upgrade | Line reconductor | Pella North Plant 69 kV | Pella Clark Street 69 kV | 1 | 69 |  | 0 | 0.2 | IA |  | Not Shared
MTEP25 | A | METC | East | 50466 | METC Customer Interconnections - 2028 | Other | 50690 | METC Customer Interconnections - 2028 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. |  | M2 - Appendix A Approved | 2500000 | 2028-12-31 | Substation | Small miscellaneous substation equipment | METC System |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50468 | ITCT Customer Interconnections - 2028 | Other | 50692 | ITCT Customer Interconnections - 2028 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. |  | M2 - Appendix A Approved | 2500000 | 2028-12-31 | Substation | Small miscellaneous substation equipment | ITCT System |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50470 | OTP Cyrus - Farwell 41.6 kV Rebuild | Other | 50694 | OTP Cyrus - Farwell 41.6 kV Rebuild | Rebuild 41.6 kV line between Cyrus 41.6 kV and Farwell 41.6 kV. |  | M2 - Appendix A Approved | 1130000 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Cyrus 41.6 kV | Farwell 41.6 kV | 1 | 42 |  |  | 14 | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50471 | OTP Ivanhoe 41.6kV Line Recloser | Other | 50695 | OTP Ivanhoe 41.6kV Line Recloser | Install line recloser near Ivanhoe 41.6 kV. |  | M2 - Appendix A Approved | 350000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Ivanhoe 41.6 kV | Farwell 41.6 kV | 1 | 42 |  |  | 14 | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50472 | Hawick Breaker Station | BRP | 50696 | Hawick Breaker Station | Convert the Hawick switching station to a breaker station by installing three breakers at the existing site. |  | M2 - Appendix A Approved | 2000000 | 2026-09-30 | Substation | Substation (breakers only, no transformer) | Hawick |  |  | 69 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50429 | West Byron TR 2 | Other | 50697 | West Byron TR 2 | Install new distribution transformer at West Byron to meet load growth in area |  | M2 - Appendix A Approved | 7535000 | 2026-10-15 | Transformer | Transformer New | West Byron |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | METC | East | 50474 | METC Line Relocation - 2026 | Other | 50698 | METC Line Relocation - 2026 | Relocate portion(s) of METC transmission lines located in public right of way at the government entities’ mandate. |  | M2 - Appendix A Approved | 2500000 | 2026-12-31 | Misc. | Line relocation (road move) | METC Facilities |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50473 | Pennock Area Projects | Other | 50699 | Pennock - St. Johns | Construct a new 69 kV line from the Pennock distribution substation to a new breaker station at the point of interconnection of the GRE owned WS 69 kV line and the WMUC 69 kV line (St. Johns breaker station). Retire BR line west of AG-RK to Granite Falls. |  | M2 - Appendix A Approved | 11000000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Pennock | St. Johns | 1 | 69 | 69 | 7.2 |  | MN |  | Not Shared
MTEP25 | A | METC | East | 50475 | METC Line Relocation - 2027 | Other | 50700 | METC Line Relocation - 2027 | Relocate portion(s) of METC transmission lines located in public right of way at the government entities’ mandate. |  | M2 - Appendix A Approved | 2500000 | 2027-12-31 | Misc. | Line relocation (road move) | METC Facilities |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50476 | ITCT Line Relocation - 2026 | Other | 50701 | ITCT Line Relocation - 2026 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. |  | M2 - Appendix A Approved | 2500000 | 2026-12-31 | Misc. | Line relocation (road move) | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50477 | ITCT Line Relocation - 2027 | Other | 50702 | ITCT Line Relocation - 2027 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. |  | M2 - Appendix A Approved | 2500000 | 2027-12-31 | Misc. | Line relocation (road move) | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 50478 | METC Asset Replacement Program - 2027 | Other | 50703 | METC Asset Replacement Program - 2027 | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  | M2 - Appendix A Approved | 53875000 | 2027-12-31 | Substation | Circuit Breaker (replacement at existing substation) | METC Facilities |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP25 | A | ITC | East | 50479 | ITCT Asset Replacement Program - 2027 | Other | 50704 | ITCT Asset Replacement Program - 2027 | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. |  | M2 - Appendix A Approved | 59750000 | 2027-12-31 | Substation | Circuit Breaker (replacement at existing substation) | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50481 | LG - 2 | Other | 50706 | LG - 2 | Install new facilities to meet load growth in the area. |  | M2 - Appendix A Approved | 120000000 | 2030-12-31 | Substation | Distribution substation - may include trans high side | LG - 2 |  |  | 345 |  |  |  | MN |  | Not Shared
MTEP25 | A | GREAT RIVER ENERGY | West | 50482 | LG - 3 | Other | 50707 | LG - 3 | Install new facilities to meet load growth in the area. |  | M2 - Appendix A Approved | 25000000 | 2026-12-31 | Substation | Distribution substation - may include trans high side | LG - 3 |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50483 | St. John's Lake Breaker Station | Other | 50708 | St. John's Lake Breaker Station | Construct a new 69 kV breaker station near Willmar. |  | M2 - Appendix A Approved | 6000000 | 2029-12-30 | Substation | Switching station (breakers only, no transformer) | WMU-St Johns Lake 69 kV |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50483 | St. John's Lake Breaker Station | Other | 50709 | St. John's Lake to Willmar Tap Rebuild to Double Circuit | Rebuild the 69 kV line from the WMU tap to the new St. John's breaker station to a double circuit line. |  | M2 - Appendix A Approved | 3000000 | 2029-12-30 | Line Upgrade | Line rebuild on existing ROW | WMU-St Johns Lake 69 kV | WMU-Willmar Tap | 1 / 2 | 69 |  | 4 | 4 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50430 | Souris Upgrades | Other | 50710 | Souris Upgrades | Install new bus tie breaker and upgrade limiting equipment at substation |  | M2 - Appendix A Approved | 2000000 | 2028-05-31 | Substation | Substation bus upgrade | Souris |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50484 | Priam Second Transformer | Other | 50711 | Priam Second Transformer | This project adds a second 115/69 kV transformer at the Priam substation near Willmar. |  | M2 - Appendix A Approved | 4000000 | 2029-12-30 | Transformer | Transformer New | WMU-Priam 115 kV | WMU-Priam 69 kV | 2 | 115 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50431 | Line 0846 Relocation | Other | 50712 | Line 0846 Relocation | Relocate structures on High Bridge - Daytons Bluff 115kV line |  | M2 - Appendix A Approved | 200000 | 2026-07-31 | Misc. | Line relocation (road move) | High Bridge | Daytons Bluff | 1 | 115 |  |  | 2 | MN |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50484 | Priam Second Transformer | Other | 50715 | Priam 115 kV Expansion | Expand the 115 kV substation bus for adding a second 115/69 kV transformer at the Priam substation. |  | M2 - Appendix A Approved | 3700000 | 2029-12-30 | Substation | Substation (breakers only, no transformer) | WMU-Priam 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50433 | Install Pine Island Island Area Substation | Other | 50716 | Install Pine Island Island Area Substation | Install new distribution substation in Pine Island Area to meet load growth in area |  | M2 - Appendix A Approved | 8900000 | 2026-12-30 | Substation | Distribution substation - may include trans high side | Pine Island |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 50484 | Priam Second Transformer | Other | 50717 | Priam 69 kV Expansion | Expand the 69 kV substation bus for adding a second 115/69 kV transformer at the Priam substation. |  | M2 - Appendix A Approved | 1300000 | 2029-12-30 | Substation | Substation (breakers only, no transformer) | WMU-Priam 69 kV |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50434 | Replace Meire Grove TR1 | Other | 50718 | Replace Meire Grove TR1 | Upgrade Meire Grove transformer 1 to support load growth |  | M2 - Appendix A Approved | 7700000 | 2027-07-31 | Transformer | Transformer Replacement | Meire Grove |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50435 | Install East Mankato Area Substation | Other | 50719 | Install East Mankato Area Substation | Install new distribution substation in East Mankato area to meet load growth in area |  | M2 - Appendix A Approved | 6700000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | East Mankato |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50436 | rebuild W3449 Marshland to Mississippi River | Other | 50720 | rebuild W3449 Marshland to Mississippi River | rebuild W3449 Marshland to Mississippi River |  | M2 - Appendix A Approved | 7800000 | 2027-12-15 | Line Upgrade | Line reconductor | Marshland | Winona |  | 69 |  |  | 3.9 | WI |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50440 | West Maple Grove Substation | Other | 50724 | West Maple Grove Substation | Build new Substation in Northwest Maple Grove to accommodate load growth |  | M2 - Appendix A Approved | 25000000 | 2028-09-01 | Substation | Distribution substation - may include trans high side | West Maple Grove |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50485 | OTP Eden - Grenville 41.6 kV Rebuild | Other | 50725 | OTP Eden - Grenville 41.6 kV Rebuild | Rebuild 41.6 kV line between Eden 41.6 kV and Grenville 41.6 kV. |  | M2 - Appendix A Approved | 1400000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Eden 41.6 kV | Grenville 41.6 kV | 1 | 42 |  |  | 7 | SD |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50486 | OTP Casselton Town New 115 kV Delivery | Other | 50726 | OTP Casselton Town New 115 kV Delivery | New 115 kV delivery to uprate Casselton town from 41.6 kV to 115 kV. |  | M2 - Appendix A Approved | 1000000 | 2026-12-31 | Substation | Distribution substation - may include trans high side | Casselton Town 115 kV |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50487 | OTP Bemidji Nymore Circuit Breaker | Other | 50727 | OTP Bemidji Nymore Circuit Breaker | New 69 kV breaker at Bemidji Nymore substation. |  | M2 - Appendix A Approved | 350000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Bemidji Nymore 69 kV |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50488 | Upgrade Dumont to Stillwell 138 kV line (PJM Project B3775.11) | Other | 50728 | Stillwell 345kV substation Upgrade | Upgrade Wave Trap and substation conductor on circuit 34501 Dumont to Stillwell |  | M2 - Appendix A Approved | 601914 | 2026-12-01 | Substation | Small miscellaneous substation equipment | Stillwell |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50442 | Rebuild 5400 Richmond to Rich Springs Tap | Other | 50729 | Rebuild 5400 Richmond to Rich Springs Tap | rebuild 2.6 miles of 69kV Line 5400 from Richfield to Rich Springs Tap |  | M2 - Appendix A Approved | 2404191 | 2028-12-29 | Line Upgrade | Line reconductor | Richmond | Rich Springs |  | 69 |  |  | 2.6 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50443 | Monroe County Breaker and Transformer EOL Replacement | Other | 50730 | Monroe County Breaker EOL Replacement | Replace 4 breakers at Monroe county |  | M2 - Appendix A Approved | 400000 | 2028-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Monroe County |  |  | 161 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50443 | Monroe County Breaker and Transformer EOL Replacement | Other | 50731 | Monroe County Transformer EOL Replacement | Replace TR01 and TR02 at Monroe county |  | M2 - Appendix A Approved | 7600000 | 2028-12-01 | Transformer | Transformer Replacement | Monroe County |  |  | 161 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50445 | Sioux Falls 115kV Conversion | Other | 50733 | Sioux Falls 115kV Conversion Rebuild lines 0730 and 0729 Lawrence - South Sioux Falls | Rebuild lines 0730 and 0729 Lawrence - South Sioux Falls |  | M2 - Appendix A Approved | 10000000 | 2029-06-01 | Line Upgrade | Line conversion to higher voltage | Lawrence | South Sioux Falls |  | 115 |  |  | 10 | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50445 | Sioux Falls 115kV Conversion | Other | 50734 | Rebuild lines 0730 and 0729 West Sioux Falls - South Sioux Falls | Sioux Falls 115kV Conversion. Rebuild lines 0730 and 0729 West Sioux Falls - South Sioux Falls |  | M2 - Appendix A Approved | 5000000 | 2029-06-01 | Line Upgrade | Line conversion to higher voltage | West Sioux Falls | South Sioux Falls |  | 115 |  |  | 3 | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50445 | Sioux Falls 115kV Conversion | Other | 50735 | Rebuild lines 0730 and 0729 South Sioux Falls - Lincoln to 115kV | Rebuild lines 0730 and 0729 South Sioux Falls - Lincoln to 115kV |  | M2 - Appendix A Approved | 5000000 | 2029-06-01 | Line Upgrade | Line conversion to higher voltage | South Sioux Falls | Lincoln |  | 115 |  |  | 3 | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50445 | Sioux Falls 115kV Conversion | Other | 50736 | Convert Cliff Avenue 69kV substation to 115kV | Convert Cliff Avenue 69kV substation to 115kV. |  | M2 - Appendix A Approved | 15000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | South Sioux Falls | Lincoln |  | 115 |  |  | 3 | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50445 | Sioux Falls 115kV Conversion | Other | 50737 | Convert West Sioux Falls 69kV substation to 115kV | Convert West Sioux Falls 69kV substation to 115kV |  | M2 - Appendix A Approved | 10000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | West Sioux Falls | Lincoln |  | 115 |  |  | 3 | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50445 | Sioux Falls 115kV Conversion | Other | 50738 | Convert Lincoln 69kV substation to 115kV | Convert Lincoln 69kV substation to 115kV |  | M2 - Appendix A Approved | 15000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | West Sioux Falls | Lincoln |  | 115 |  |  | 3 | SD |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50449 | Roughrider Substation | Other | 50739 | Roughrider Substation | Install new distribution substation to meet load growth in Minot area |  | M2 - Appendix A Approved | 7500000 | 2029-10-15 | Substation | Distribution substation - may include trans high side | Roughrider |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50450 | Upgrade end of life Wilmarth TR7 and TR8 | Other | 50740 | Upgrade end of life Wilmarth TR7 and TR8 | Upgrade end of life Wilmarth TR7 and TR8 |  | M2 - Appendix A Approved | 10500000 | 2028-12-31 | Transformer | Transformer Replacement | Wilmarth |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50451 | Magic City Reactor | BRP | 50741 | Magic City Reactor | Install new reactor at Magic City |  | M2 - Appendix A Approved | 2132841 | 2028-09-01 | Voltage Device | Reactor or Inductor | Magic City |  |  | 230 | 115 |  |  | ND |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50452 | Peace Garden Reactor | BRP | 50742 | Peace Garden Reactor | Install new reactor at Peace Garden |  | M2 - Appendix A Approved | 7811863 | 2029-08-07 | Voltage Device | Reactor or Inductor | Peace Garden |  |  | 230 |  |  |  | ND |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50455 | Prairie Reactor | BRP | 50745 | Prairie Reactor | Install new reactor at Prairie |  | M2 - Appendix A Approved | 500000 | 2026-01-01 | Voltage Device | Reactor or Inductor | Prairie |  |  | 230 | 115 |  |  | ND |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50455 | Prairie Reactor | BRP | 50746 | Prairie Reactor substation upgrades | Substation upgrades to accommodate new reactor at Prairie including retirement of 3 capacitor banks. |  | M2 - Appendix A Approved | 15500000 | 2029-01-01 | Substation | Substation (breakers only, no transformer) | Prairie |  |  | 230 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50456 | Fort Ridgely 69kV Rebuild | Other | 50747 | Fort Ridgely 69kV Rebuild | Upgrade 69 kV lines Fort Ridgley-GRE Schilling Tap, Lafayette-GRE Lafayette, GRE Schilling Tap-GRE Lafayette Tap, and Winthrop-Lafayette |  | M2 - Appendix A Approved | 14000000 | 2029-01-01 | Line Upgrade | Line reconductor | Fort Ridgley | Winthrop | 1 | 69 |  |  | 18 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50457 | Install Montrose TR2 | Other | 50748 | Install Montrose TR2 | Install new distribution transformer to meet load growth in area |  | M2 - Appendix A Approved | 15000000 | 2027-12-31 | Transformer | Transformer New | Montrose |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50458 | Install Avon Area Substation | Other | 50749 | Install Avon Area Substation | Install new distribution substation to meet load growth in the Avon area |  | M2 - Appendix A Approved | 10000000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Avon |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50459 | Install Stewart TR2 | Other | 50750 | Install Stewart TR2 | Install new Stewart distribution transformer 2 to meet load growth in area |  | M2 - Appendix A Approved | 15000000 | 2027-12-31 | Transformer | Transformer New | Stewart |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50460 | Prairie Island TR10 Replacement | Other | 50751 | Prairie Island TR10 Replacement | Replace end of life Prairie Island TR10 |  | M2 - Appendix A Approved | 7990300 | 2031-12-01 | Transformer | Transformer Replacement | Prairie Island |  |  | 345 | 161 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50461 | Line 0868 Le Sauk - Fischer Hills - St Stephens Rebuild | Other | 50752 | Line 0868 Le Sauk - Fischer Hills - St Stephens Rebuild | Rebuild 0868 from Le Sauk to Fisher Hills to St. Stephens |  | M2 - Appendix A Approved | 12231418 | 2029-01-01 | Line Upgrade | Line reconductor | Le Sauk | St. Stephens | 1 | 115 |  |  | 11 | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50489 | Split Rock - Chanarambie 345kV line JTIQ | Other | 50754 | Chanarambie 345kV/115kV transformers | Add (2) 345/115kV transformers at Chanarambie |  | M2 - Appendix A Approved | 10000000 | 2033-06-30 | Transformer | Transformer New | Chanarambie |  |  | 345 | 115 |  |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50489 | Split Rock - Chanarambie 345kV line JTIQ | Other | 50755 | New 345kV line Split Rock-Chanarambie | New 345kV line Split Rock-Chanarambie |  | M2 - Appendix A Approved | 125000000 | 2033-06-30 | Line New | New Transmission line, new ROW - may include terminations | Split Rock | Chanarambie | 1 | 345 |  | 57.5 |  | MN |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50489 | Split Rock - Chanarambie 345kV line JTIQ | Other | 50756 | Upgrade 115kV line Split Rock-Pipestone-Chanarambie. | Upgrade 115kV line Split Rock-Pipestone-Chanarambie. |  | M2 - Appendix A Approved | 25000000 | 2033-06-30 | Line Upgrade | Line reconductor | Pipestone | Chanarambie | 1 | 115 |  |  | 12.2 | MN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50490 | Gill Station 345kV Expansion for New Customer Load | Other | 50758 | Gill 345kV station expansion | Expand Gill 345kV station with additional 345kV bay and line position to customer to serve additional load. |  | M2 - Appendix A Approved | 8000000 | 2028-01-02 | Substation | Substation (breakers only, no transformer) | Merom |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50491 | New Ellettsville 345kV Station | Other | 50759 | Construct 345kV Ring-Bus station | Construct new 345kV transmission station ring-bus along existing Worthington-Bloomington 345kV transmission line. |  | M2 - Appendix A Approved | 20000000 | 2035-01-01 | Substation | Switching station (breakers only, no transformer) | Worthington | Bloomington |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50492 | Expand Wheeler Creek 138 kV Station | Other | 50760 | Expand Wheeler Creek into a Ring-Bus station | Expand Wheeler Creek Transmission Station to a ring-bus station to accept the 138 feeds from SIPC Hamilton and Ameren Kays. |  | M2 - Appendix A Approved | 4700000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | Wheeler Creek |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | HOOSIER ENERGY | Central | 50493 | Rebuild Ashland Tap - Cisne Junction 69 kV Line | Other | 50761 | Ashland Tap - Cisne Junction 69 kV Line | Ashland Tap - Cisne Junction is a 5.74 mile 69 kV line. The current conductor is 1/0, it will be upgraded to 477 ACSR. A new 3 way switch will be installed at Ashland Junction. |  | M2 - Appendix A Approved | 9500000 | 2028-12-01 | Line Upgrade | Line reconductor | Ashland Tap | Cisne Junction |  | 69 |  | 0 | 5.74 | IL |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50494 | Knight Substation | Other | 50762 | Monticello - Oakwood | Install new 115/34.5kV substation in Dayton area to meet area load growth. |  | M2 - Appendix A Approved | 29600 | 2026-12-01 | Substation | Distribution substation - may include trans high side | Monticello | Oakwood |  | 115 | 35 |  |  | MN |  | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50380 | ITC Midwest Asset Management blanket | Other | 50763 | ITC Midwest Asset Management blanket | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. |  | M2 - Appendix A Approved | 53875000 | 2027-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | ITCM Asset Blanket for 2026 | Throughout system |  | 345 | 69 |  |  | IA | MN | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50379 | ITC Midwest Load interconnection blanket | Other | 50764 | Blanket for Customer Interconnections under $1 million for 2027 | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. |  | M2 - Appendix A Approved | 3750000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Blanket for Customer Interconnections | Throughout system |  | 345 | 69 |  |  | IA | MN | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50378 | ITC Midwest SCADA Controlled Motor Operated Switch Addition blanket | Other | 50765 | Blanket for SCADA M.O. Switches for 2026 | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be utilized to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. |  | M2 - Appendix A Approved | 3125000 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Blanket for SCADA M.O. Switches for 2026 | Throughout system |  | 345 | 69 |  |  | IA | MN | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | Other | 50768 | Quad Cities to Rock Creek 345 kV #2 Installation | Add 2nd Quad Cities - Rock Creek 345 kV line on existing spare position on existing structures. New line to be rated 3000 amps nominal. |  | M2 - Appendix A Approved | 6405000 | 2028-12-31 | Line Upgrade | Line reconductor | Quad Cities Station | Rock Creek | 2 | 345 | 345 |  |  | IA | IL | Not Shared
MTEP25 | A | ITC MIDWEST | West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | Other | 50769 | Quad Cities to Rock Creek 345 kV #1 Reconductor | Reconductor existing Quad Cities - Rock Creek 345 kV line to 3000 amp nominal conductor. |  | M2 - Appendix A Approved | 6417500 | 2028-12-31 | Line Upgrade | Line reconductor | Quad Cities Station | Rock Creek | 1 | 345 | 345 |  |  | IA | IL | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50495 | J1745 Fitzgerald SS Network Upgrades and Interconnection Facilities | GIP | 50770 | J1745 138kV Fitzgerald Substation Terminal Addition | J1745 138kV Fitzgerald Substation Terminal Addition |  | M2 - Appendix A Approved | 1017000 | 2031-11-18 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Fitzgerald |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50495 | J1745 Fitzgerald SS Network Upgrades and Interconnection Facilities | GIP | 50771 | J1745 138kV Fitzgerald Interconnection Substation Interconnection Facilities | J1745 138kV Fitzgerald Interconnection Substation Interconnection Facilities |  | M2 - Appendix A Approved | 1004000 | 2031-11-18 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Fitzgerald |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 50728 | Add 3rd 345/138kV Bank at Edwards Sub | BRP | 51496 | Edwards Third 345/138kV Bank | Adding a third bank to Edwards substation. It will be a 606MVA 345/138kV bank. |  | M2 - Appendix A Approved | 15000000 | 2029-06-30 | Transformer | Transformer New | Edwards |  |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 9740 | Reconductor Grand Tower-Campbell Hill 138 kV line | Other | 21127 | 21127-Grand Tower-Campbell Hill | Reconductor to 1200 A summer emergency capability. | AmerenIL | M2 - Appendix A Approved | 34900000 | 2029-12-01 | Line Upgrade | Line reconductor | Grand Tower | Campbell Hill | 1 | 138 | 138 |  | 7.94 | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 24919 | Mill Road – Granville Project | BRP | 28140 | Mill Road – Granville Project | - Construct new 345/138 kV Mill Road SS, with one 500 MVA 345/138 kV transformer, - Loop in Granville – Arcadian 345 kV line and Cypress – Arcadian 345 kV line to new Mill Road 345 SS, Rebuild Mill Road SS – Granville SS section as 345 kV double circuit, - Loop in Germantown – Bark River 138 kV line and west portion of the Tamarack – Sussex 138 kV line into new Mill Road 138 kV SS, install series reactor in line to Sussex. - Construct new Mill Road SS – Tamarack SS – Butler SS 138 kV line, - Butler SS 138 kV reconfiguration, and install series reactor between Butler bus 1 and bus 2, - Granville SS 345 kV ring bus expansion, Replace 345/138 kV transformer T3. | ATC | M3 - Under Construction | 423705000 | 2027-10-01 | Line Upgrade | Line rebuild on existing ROW | Mill Road | Granville |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 25018 | New Moonshine Solar Bootleg 138 kV switching station (J1382) | GIP | 28149 | 28149-Bootleg- | The J1382 150MW Solar Interconnection Switching Station will split the existing Hutsonville-Neoga South-1 138 kV. | AmerenIL | M2 - Appendix A Approved | 8000000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Bootleg |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 24924 | Straits SS Power Transformer Asset Renewal | Other | 28170 | Straits SS Power Transformer Asset Renewal | Straits SS Power Transformer Asset Renewal | ATC | M2 - Appendix A Approved | 10100000 | 2028-08-15 | Substation | Substation (breakers only, no transformer) | Straits |  |  | 138 | 69 |  |  | MI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 24982 | Range Line Dist (WE) - Range Line Switchyard 138 kV (61441), Replace Underground Cable | Other | 28172 | Range Line Dist (WE) – Range Line Switchyard 138 kV (61441), Replace Underground Cable | Replace underground cable between Range Line Distribution SS and Range Line Switchyard. | ATC | M2 - Appendix A Approved | 4000000 | 2029-06-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Range Line Dist | Range Line Switchyard | 61441 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 24925 | Range Line Dist (WE) - Range Line Switchyard 138 kV (61452), Replace Underground Cable | Other | 28173 | Range Line Dist (WE) – Range Line Switchyard 138 kV (61452), Replace Underground Cable | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | ATC | M2 - Appendix A Approved | 6000000 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Range Line Dist | Range Line Switchyard | 61452 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 25040 | Replace Tyson 345/138 kV transformer 3 | Other | 28191 | 28191-Tyson- | Replace Tyson XFMR 3 with a new 345/138kV 700 MVA unit. | AmerenMO | M2 - Appendix A Approved | 8500000 | 2030-12-01 | Transformer | Transformer New | Tyson |  |  | 345 | 138 |  |  | MO |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25161 | Sun Prairie Area Reliability Project | BRP | 28224 | Sun Prairie Area Reliability Project | The Sun Prairie Area Reliability Project provides additional sources in the Sun Prairie Area to prevent thermal overloads due to multiple contingencies. Sun Prairie Area Reliability Project scope is as it follows: • Loop through Sun Prairie – Kegonsa (Y-81) 69-kV line in Reiner Road SS, constructing a 2-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Reiner Road SS. Finally, install new equipment due to asset renewal needs. • Loop through DeForest – Sun Prairie (Y-137) 69-kV line in Yahara River SS, constructing a 1.1-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Yahara River SS. Finally, install new equipment due to asset renewal needs. • Jumper replacements in Sun Prairie SS and additional modifications due to asset renewal needs. | ATC | M2 - Appendix A Approved | 61450000 | 2029-06-30 | Substation | Substation (breakers only, no transformer) | Sun Prairie Area |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 21922 | Sigel - Vesper 69 kV (Y-108/Y-107), Partial Rebuild | Other | 26530 | Sigel - Vesper 69 kV (Y-108/Y-107), Partial Rebuild | Sigel - Vesper 69 kV (Y-108/Y-107), Partial Rebuild | ATC | M2 - Appendix A Approved | 5500000 | 2032-05-25 | Line Upgrade | Line rebuild on existing ROW | Sigel | Vesper | Y-108/Y-107 | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 24474 | Winnebago County, New DIC | Other | 27901 | Winnebago County, New DIC | WPS is proposing to construct a new T-D substation with two new 69/12.47 kV transformers with circuit breakers. ATC will construct a 69 kV loop-through straight bus with two line switches with load breaks. ATC will also install two manual bus-tie switches and make provisions for a future bus-tie breaker. ATC will loop through the new substation from the Sunset Point – Oshkosh 69 kV (E-5) line on the line section between Sunset Point and Bowen St. | ATC | M2 - Appendix A Approved | 2900000 | 2028-11-01 | Substation | Distribution substation - may include trans high side | Winnebago County DIC |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 25264 | Ridgeview Transformer Addition | Other | 28388 | 28388-Ridgeview- | Add two 115kV circuit breakers to existing Ring Bus to allow for a new 115/34.5 kV Transformer addition. | MP | M2 - Appendix A Approved | 2000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Ridgeview |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | MINNESOTA POWER INC. | West | 25267 | 180 Line Rebuild | BRP | 28391 | 28391-Hibbing-Maturi | Rebuild 115kV 180 Line (Hibbing -Maturi) with 636 ACSR. | MP | M2 - Appendix A Approved | 9750000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Hibbing | Maturi |  | 115 |  |  | 13 | MN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 25269 | Replace West Frankfort East 345/138 kV transformer 1 | Other | 28399 | 28399-West Frankfort East- | At West Frankfort East substation replace the existing 560 MVA 345/138 kV Transformer 1 with a new 345/138 kV 700 MVA transformer | AmerenIL | M2 - Appendix A Approved | 10600000 | 2026-12-01 | Transformer | Transformer New | West Frankfort East |  |  | 345 | 138 |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 25314 | Pittsville Area Reliability Project | Other | 28400 | 28400-Sigel-Port Edwards | • ATC will construct ~9.6 miles of single circuit 138 kV transmission line to interconnect the proposed distribution substation. • ATC will construct a 138 kV loop-through straight bus with three line breakers to accommodate tapping X-42 and terminating the new line. | ATC | M2 - Appendix A Approved | 35900000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Pittsville Area |  | X-42 | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 25496 | New Blanchette 138 kV Ring Bus | Other | 28758 | 28758-Blanchette- | Install a 4 position ring bus at Blanchette 138kV Substation. In addition, fiber will be installed to Kisker with some line re-routing. | AmerenMO | M2 - Appendix A Approved | 7000000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | Blanchette |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN MISSOURI | Central | 25497 | Reconfigure Overton 161kV Substation | Other | 28763 | 28763-Overton- | Rebuild the existing Overton 161kV straight bus as a breaker-and-a-half (BAAH) station. | AmerenMO | M2 - Appendix A Approved | 46000000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Overton |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 25502 | Line 4B Rebuild | Other | 28767 | 28767-Lake-Decatur | A complete rebuild of Line 4B and line extension to the existing Decatur Substation (Lake – Decatur 69kV) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Lake and Decatur. | SMEPA | M2 - Appendix A Approved | 10430000 | 2027-03-01 | Line Upgrade | Line rebuild on existing ROW | Lake | Decatur |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 25541 | Line 5 Rebuild | Other | 28768 | 28768-Newton-Decatur | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 9.7 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | SMEPA | M2 - Appendix A Approved | 5975000 | 2027-04-01 | Line Upgrade | Line rebuild on existing ROW | Newton | Decatur |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | COOPERATIVE ENERGY | South | 25541 | Line 5 Rebuild | Other | 28769 | 28769-Decatur- | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 9.7 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | SMEPA | M2 - Appendix A Approved | 125000 | 2027-04-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Decatur |  |  | 69 |  |  |  | MS |  | Not Shared
MTEP25 | A | METC | East | 20020 | Rebuild Gaylord - Mio Dam 138kV line | Other | 25705 | Lewiston Jct-Mio_Rebuild with OPGW | Lewiston Jct. - Mio 138 kV section with 954 ACSR overhead conductor capable of double circuit 230kV. OPGW will be installed on the rebuild. All line switches will be 2000A or greater, if replaced. | METC | M2 - Appendix A Approved | 86900000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Lewiston Jct | Mio | 1 | 138 |  |  | 19.19 | MI |  | Not Shared
MTEP25 | A | METC | East | 20020 | Rebuild Gaylord - Mio Dam 138kV line | Other | 25706 | Gaylord Pos 377 Terminal Upgrade & OPGW termination | Upgrade the Gaylord Position 377 Relay equipment and OPGW termination. | METC | M2 - Appendix A Approved | 189000 | 2029-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Gaylord |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | METC | East | 20020 | Rebuild Gaylord - Mio Dam 138kV line | Other | 25707 | Mio Dam OPGW termination | OPGW termination at Mio Dam. | METC | M2 - Appendix A Approved | 165000 | 2029-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Mio Dam |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50119 | New Moro-Cottage Hills 138 kV Line (C1908 MPFCA) | GIP | 50189 | New Moro-Cottage Hills 138 kV Line (C1908 MPFCA) | These Common Use Upgrades consist of equipment for all the substation and transmission line upgrades to support New Moro-Cottage Hills MPFCA. Add 138 kV position at Moro, expand Cottage Hills to a 4 pos., 6 ult. ring bus. Add second circuit between Moro and Cottage Hills on existing ROW utilizing DC structures. Rebuild Moro to Laclede N Tap, Cottage Hills to Laclede S tap and Laclede S tap to Mississippi tap. |  | M2 - Appendix A Approved | 38550000 | 2029-06-01 | Substation | Substation bus upgrade | Moro | Cottage Hills |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | Other | 51342 | Loose Creek-Barnett 345 kV line | 40 mile single circuit line from Loose Creek-Barnett |  | M2 - Appendix A Approved | 1 | 2029-12-01 | Line New | New Transmission line, new ROW - may include terminations | Loose Creek | Barnett |  | 345 |  | 40 |  | MO |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | Other | 51343 | Barnett Substation | New 345/161 kV substation at Barnett |  | M2 - Appendix A Approved | 16000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Barnett |  |  | 345 | 161 |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | Other | 51344 | Overton-Barnett 345 and 161 kV double circuit | Convert existing 38 mile 345 and 161 kV double circuit line from Overton to Barnett. |  | M2 - Appendix A Approved | 107000000 | 2030-12-01 | Line Upgrade | Line conversion to higher voltage | Overton | Barnett |  | 345 | 161 | 38 |  | MO |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | Other | 51345 | Clinton 345 kV Substation | New Clinton 345 kV Substation |  | M2 - Appendix A Approved | 16000000 | 2030-12-01 | Substation | Substation (breakers only, no transformer) | Clinton |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | Other | 51346 | Clinton to Stilwell double circuit 345 kV line | New 50 mile double circuit 345 kV line from Clinton to Stilwell. |  | M2 - Appendix A Approved | 1 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Clinton | Lacygne |  | 345 | 345 | 50 |  | MO |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | Other | 51352 | Barnett to Clinton 345 kV double circuit line | New 65 mile double circuit 345 kV line from Barnett to Clinton |  | M2 - Appendix A Approved | 260000000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Barnett | Clinton |  | 345 |  | 65 |  | MO |  | Not Shared
MTEP25 | A | Southern Illinois Power Cooperative | Central | 50637 | Big Muddy Solar - J1303 Generator Interconnection | GIP | 51356 | Vergennes 161 kV Switchyard | 161 kV Switchyard |  | M2 - Appendix A Approved | 9389000 | 2026-10-01 | Substation | Switching station (breakers only, no transformer) | SIPC Jackson Substation |  |  | 161 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50642 | Substation Technology Package #3 - 2026 | Other | 51362 | Substation Technology Package #3 - 2026 | Installation of Edge computing hardware at multiple substation locations. Scope includes edge compute interoperability with physical security cameras, rogue detection sensors and asset monitor devices. |  | M2 - Appendix A Approved | 3000000 | 2026-12-31 | Misc. | Communication equipment | Various |  |  | 0 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50655 | R1049/R5061 Edgewater SS, Network Upgrades and Interconnection Facilities | GIP | 51380 | 345 kV CT Contributions | 345 kV CT contributions, bus 3 differential relay panel, wiring updates in the bus 3 differential relay panel to support Edgewater Unit 5 GSU high side circuit breaker installation |  | M2 - Appendix A Approved | 225000 | 2026-11-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Edgewater |  |  | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50655 | R1049/R5061 Edgewater SS, Network Upgrades and Interconnection Facilities | GIP | 51381 | 345 kV Transmission Owner System Protection Facilities | 345 kV Transmission Owner System Protection Facilities - System Protection Setting Modifications and Supporting Activities |  | M2 - Appendix A Approved | 35000 | 2026-11-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Edgewater |  |  | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMEREN MISSOURI | Central | 50616 | New Rootbeer 345 kV Substation Load Addition | Other | 51382 | New 345 kV position at Rootbeer substation | Add 345 kV position at Rootbeer substation |  | M2 - Appendix A Approved | 2000000 | 2026-12-01 | Substation | Substation bus upgrade | Rootbeer |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50636 | New Diamond Core Load Addition (RECC Territory) at Mogul 345 kV substation | Other | 51383 | Towerline-San Jose Rail 138 kV | Towerline-San Jose Rail-increase line capacity |  | M2 - Appendix A Approved | 0 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Towerline | San Jose Rail |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50636 | New Diamond Core Load Addition (RECC Territory) at Mogul 345 kV substation | Other | 51384 | Austin-Yvonne 138 kV | Austin-Yvonne 138 kV increase line capacity |  | M2 - Appendix A Approved | 0 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Austin | Yvonne |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50636 | New Diamond Core Load Addition (RECC Territory) at Mogul 345 kV substation | Other | 51385 | Yvonne-Taylorville 138kV | Yvonne-Taylorville 138kV increase line capacity |  | M2 - Appendix A Approved | 0 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Yvonne | Taylorville S |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50670 | Werner SS Relay and Remote Asset Renewal | Other | 51402 | Werner SS Relay and Remote Asset Renewal | Asset renewal of Werner control house and 138kV relay asset renewal at Werner, Werner West and White Lake SS. Install an additional breaker and eliminate two S&C Mark VI circuit switchers when replacing cap bank relaying at Werner. |  | M3 - Under Construction | 8600000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Werner |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50673 | Portage - Columbia 138 kV (X-13/X-20), Reconductor | BRP | 51411 | Portage - Columbia 138kV (X-13/X-20), Reconductor | This project resolves thermal overloads under single contingency conditions on either the X-13 or X-20 lines between Portage and Columbia. |  | M2 - Appendix A Approved | 39500000 | 2026-12-30 | Line Upgrade | Line rebuild on existing ROW | Portage | Columbia |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50675 | Cove Ridge 138 kV Station | Other | 51413 | Cove Ridge Substation | Substation including breakers and Capacitor bank |  | M2 - Appendix A Approved | 24100000 | 2027-03-30 | Substation | Substation (breakers only, no transformer) | Hollywood | Orange |  | 138 |  |  |  | LA |  | Not Shared
MTEP25 | A | ENTERGY SERVICES, LLC. | South | 50671 | RiverPlex 500-230 kV Station | Other | 51414 | RiverPlex 500-230 kV | 500 kV ring bus and 6 bay breaker and a half 230 kV station |  | M2 - Appendix A Approved | 284000000 | 2028-08-30 | Substation | Substation (breakers only, no transformer) | RiverPlex |  |  | 500 | 230 |  |  | LA |  | Not Shared
MTEP25 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 50153 | Owatonna 161kV Cap Bank Addition | BRP | 50773 | West Owatonna - Capacitor | 47MVAr Cap Bank located on 161kV bus to mitigate low voltage scenarios from P6 contingencies in the area. |  | M2 - Appendix A Approved | 3500000 | 2027-01-01 | Voltage Device | Capacitor (switched capacitor) | West Owatonna |  |  | 161 |  |  |  | MN |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | BRP | 50774 | Hills: Add 345 kV Line Terminal | Add new 345 kV line terminal at Hills to accommodate the new ITCM Hills-Beverly 345 kV line |  | M2 - Appendix A Approved | 12000000 | 2027-09-30 | Substation | Substation (breakers only, no transformer) | Hills |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | BRP | 50775 | Morgan Valley-Tiffin 345 kV Uprate | Replace transmission structures to increase the rating of the Morgan Valley-Tiffin 345 kV line |  | M2 - Appendix A Approved | 1500000 | 2027-09-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Morgan Valley | Tiffin | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | BRP | 50776 | Hills-Tiffin 345 kV Uprate | Replace transmission structures to increase the rating of the Hills-Tiffin 345 kV line |  | M2 - Appendix A Approved | 2500000 | 2027-09-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hills | Tiffin | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | BRP | 50777 | Sub 91-Utica Ridge 161 kV Uprate | Replace transmission structures to increase the rating of the Sub 91-Utica Ridge 161 kV line |  | M2 - Appendix A Approved | 200000 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sub 91 | Utica Ridge | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | BRP | 50778 | Sub 91: 161 kV Line Terminal Uprates | Replace limiting equipment on the Sub 91-Utica Ridge and Sub 91-QC Enron 161 kV line terminals to increase the rating of each line |  | M2 - Appendix A Approved | 500000 | 2028-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Sub 91 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50500 | Byron - Pleasant Valley 161kV Line Upgrade | Other | 50779 | Byron - Pleasant Valley 161kV Line Upgrade | Upgrade Byron - Pleasant Valley 161kV Line |  | M2 - Appendix A Approved | 20000000 | 2029-06-01 | Line Upgrade | Line reconductor | Byron | Pleasant Valley | 1 | 161 |  |  | 16.6 | MN |  | Not Shared
MTEP25 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 50501 | Byron - Pleasant Valley 161kV Terminal Upgrade | BRP | 50780 | Byron - Pleasant Valley 161kV Terminal Upgrade | Upgrading Terminal equipment of line to 3000A. |  | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Byron |  |  | 161 |  |  |  | MN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50502 | New Brownsburg East 138 kV Substation | Other | 50781 | Brownsburg East | New WVPA 138kV, 4 position ring bus substation to serve load |  | M2 - Appendix A Approved | 8600000 | 2029-09-30 | Substation | Substation (breakers only, no transformer) | Brownsburg East |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50503 | New Pleasant Acres Substation Feed 2 138 kV line | Other | 50782 | Pleasant Acres - Winding Ridge | Second 138 kV feed from Winding Ridge to Pleasant Acres. Cost accounted for in MTEP 24293. |  | M2 - Appendix A Approved | 2000000 | 2026-05-15 | Line New | New Transmission line, new ROW - may include terminations | Winding Ridge | Pleasant Acres |  | 138 |  | 0.1 |  | IN |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50504 | Upgrade Dupo Ferry 138 kV breakers | GIP | 50783 | Dupo Ferry 138 kV Breaker Upgrades | Dupo Ferry 138kV Breakers Upgrade - Replace 4 overstressed 138kV circuit breakers, existing interrupting capability 40kA, with 50kA new breakers 3000A minimum continuous |  | M2 - Appendix A Approved | 2500000 | 2026-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Dupo Ferry Road |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50505 | J1793 Holland SS Network Upgrades | GIP | 50784 | J1793 138kV Holland Substation | Protective relays will require new programming to protect line GT104 as a three-terminal line. Minor fiber jumper connection changes within the Transmission Owner’s existing fiber patch panel may need to be made for Transmission Owner’s relays to communicate with both the Customer’s relays along with the relays located in the existing Onion River Collector Substation (J1153). |  | M2 - Appendix A Approved | 142000 | 2032-02-18 | Substation | Small miscellaneous substation equipment | Holland |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | GIP | 50785 | J1706 138kV North Monroe Substation Terminal Addition | The 138 kV yard at North Monroe Substation will be expanded to accommodate a generation collection facility addition to the power system. A new 138 kV line terminal will be built to the south requiring the yard to be expanded to the south 25 feet. Relay protection and control will be added for the new breaker and line position. |  | M2 - Appendix A Approved | 1523000 | 2031-06-28 | Substation | Small miscellaneous substation equipment | North Monroe |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | GIP | 50786 | J1706 138kV Interconnection Facilities | The J1706 interconnection will consist of jumpers and equipment to connect the Interconnection Customer’s Transmission Line equipment with the Transmission Owner’s rigid bus. A line disconnect switch, breaker, and bus side disconnect switch will isolate the line from the 138 kV bus. Any shielding wire for interconnection Customer facilities will terminate at the dead-end vangs. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility |  | M2 - Appendix A Approved | 686000 | 2031-06-28 | Substation | Points of Interconnection for generators (User TAP for dist subs) | North Monrow |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | GIP | 50787 | Elkhorn Substation | The existing Elkhorn substation work will consist of upgrading the 138 kV X-55 line and bus jumpers entering the substation. |  | M2 - Appendix A Approved | 216000 | 2031-06-28 | Substation | Substation bus upgrade | Elkhorn |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | GIP | 50788 | North Lake Geneva Substation Grounding Upgrades | The existing North Lake Geneva substation work will consist of upgrading the 138 kV X-55 line and bus jumpers entering the substation and 138 kV Bus 8B1 strain span. |  | M2 - Appendix A Approved | 381000 | 2031-06-28 | Substation | Small miscellaneous substation equipment | North Lake Geneva |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | GIP | 50789 | X-55 138 kV Transmission Line Partial Rebuild | The X-55 138 kV Transmission Line Partial Rebuild project will consist of installing approximately 8 miles of T2-477 26/7 ACSR Hawk conductor per ATC design standards to achieve a minimum 1229 Amps (294 MVA) normal and 1682 Amps (402 MVA) emergency ratings for all seasons. The Transmission Owner will retain ownership of the line segment, support poles and Interconnection Facility. |  | M2 - Appendix A Approved | 15460000 | 2031-06-28 | Line Upgrade | Line rebuild on existing ROW | Elkhorn | North Lake Geneva | X-55 | 138 |  |  | 8 | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50790 | 115kV J1508 Interconnection Switching Station | New 115 kV Interconnection Switching Station that is to be arranged with 3 positions, 3 138 kV circuit breakers ring bus, with 1 generator lead line position, and 2 transmission line positions. The new station will also include a control house. |  | M2 - Appendix A Approved | 8976000 | 2032-04-29 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Galvin Ave |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50791 | 115kV Line B-54 Transmission Line Modifications | The existing B-54 115kV line between McMillan and Stratford South Substations will be tapped and looped into the new 115kV Interconnection Switching Station to provide transmission access. Existing structure 118 will be removed, and two (2) 138kV single circuit vertical monopole dead-end steel structures will be installed on the existing alignment between existing structures 119 and 117. New conductor, shield wire, and OPGW will be utilized to tap and loop the B-54 line into the new switching station. The Transmission Owner will retain ownership of the line segments, support poles and Interconnection Facility. |  | M2 - Appendix A Approved | 998000 | 2032-04-29 | Line New | Install tap (typically a pole a switch or in-and-out loop) | McMillan | Stratford South | B-54 | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50792 | 115kV Arpin Substation remote end work | At Arpin substation, the existing U-14 relay panel will be removed from service and saved as system spare for future use. A new line protection relay panel will be installed for line U-14. A new module will be installed in existing ATC communication cabinet. |  | M2 - Appendix A Approved | 266000 | 2032-04-29 | Misc. | Relaying, protection, RTU and SCADA equipment | Arpin |  | U-14 | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50793 | 115kV Hume Substation remote end work | At Hume substation, CCVT/ wave trap/ line tuner will be installed at line A-157 and P-120. Secondary line protection packages of existing A-157 will be modified to utilize power line carrier. Existing P-120 line panel N4 will be removed and new line relay panel will be installed for line P-120. |  | M2 - Appendix A Approved | 754000 | 2032-04-29 | Misc. | Relaying, protection, RTU and SCADA equipment | Hume |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50794 | 115kV McMillan Substation remote end work | At McMillan substation, CCVT/ wave trap/ line tuner will be installed at line B-54 and N-144. A module will be installed and secondary line protection packages of existing B-54 and N-114 on both relay panels and will be modified to utilize power line carrier. In addition, existing relay will be removed and replaced on B-54 line panel. |  | M2 - Appendix A Approved | 684000 | 2032-04-29 | Misc. | Relaying, protection, RTU and SCADA equipment | McMillan |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50795 | 115kV Mill Creek Substation remote end work | At Mill Creek substation, one new CCVT/ wave trap/ line tuner will be installed at line P-120. Existing line P-120 relay panel W-6 and U-14 panel W-7 will be removed. A new line relay panel will be installed for line P-120. A new line relay panel will be installed for line U-14. The existing wall mount ATC communications cabinet will be removed, and a new ATC communication cabinet will be installed in open position with the existing router relocated. |  | M2 - Appendix A Approved | 767000 | 2032-04-29 | Misc. | Relaying, protection, RTU and SCADA equipment | Mill Creek |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50796 | 115kV Wien Substation remote end work | At Wein substation, one new CCVT/ wave trap/ line tuner will be installed at line B-54. Existing line B-54 relay panel S3 will be removed. A new line relay panel will be installed for line B-54. New module will be installed in existing ATC communication cabinet to establish communication ring. SEL-ICON at Wein substation will establish connection to SEL-ICON at Interconnection substation using existing fiber being cut-in at Interconnection Switching Station. |  | M2 - Appendix A Approved | 592000 | 2032-04-29 | Misc. | Relaying, protection, RTU and SCADA equipment | Wien |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50797 | 115kV Wildwood Substation remote end work | Existing A-157 and N-144 line CCVT will be removed. New CCVT/ wave trap/ line tuner will be installed at line A-157 and N-144. Line protection packages at existing A-157 and N-144 line panel will be modified to utilize power line carrier communication. |  | M2 - Appendix A Approved | 605000 | 2032-04-29 | Misc. | Relaying, protection, RTU and SCADA equipment | Wildwood |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | GIP | 50798 | 115kV J1508 Interconnection Facilities | The J1508 Transmission Owner Interconnected Facilities consists of substation work associated with the Generator Lead Line entrance at the new interconnection Switching Station. |  | M2 - Appendix A Approved | 452000 | 2032-04-29 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Galvin Ave |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50190 | New Peru-Princeton 138 kV line | Other | 50799 | Lima 4-position138 kV substation | Construct the new Lima substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. near Peru, IL. |  | M2 - Appendix A Approved | 8000000 | 2027-10-01 | Substation | Switching station (breakers only, no transformer) | Lima |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMEREN ILLINOIS | Central | 50190 | New Peru-Princeton 138 kV line | Other | 50800 | Backbone 4-position138 kV substation | Rebuild the existing Princeton substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. |  | M2 - Appendix A Approved | 8000000 | 2029-06-01 | Substation | Switching station (breakers only, no transformer) | Backbone |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50508 | J1629 Welsh Prairie SS Network Upgrades and Interconnection Facilities | GIP | 50801 | J1629 345 kV Interconnection Switching Station | The new J1629 Interconnection Switching Station will be arranged in a three-breaker ring bus configuration with one generation position and two-line positions. The station will be capable of future expansion to an ultimate 6 position ring bus if future generation positions are added. The new J1629 interconnection switching station will bisect the Transmission Owner’s overhead W-5 345 kV transmission line between existing Columbia and South Fond du Lac substations in two segments, W-TBD and W-5. |  | M2 - Appendix A Approved | 16826000 | 2028-06-30 | Substation | Substation (breakers only, no transformer) | Welsh Prairie |  |  | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50508 | J1629 Welsh Prairie SS Network Upgrades and Interconnection Facilities | GIP | 50802 | Underground Fiber | The existing relay protection for the 345kV line W-5 is presently using fiber through a ICON network as a relay communication path. Sectionalizing the line requires the ICON fiber network to be brought into the new substation to maintain this configuration. The existing ICON fiber network does not run along W-5. The ICON fiber network is on the Y-64 line which is north of the proposed J1629 Switching Station. The fiber ICON ring segment between South Fond du Lac Substation and Columbia Substation includes OPGW over Y-64 from structure 100076 at Y-64 ACEC Cambria Tap to the Rio Pumping Station. The existing fiber network will be tapped at splice box on structure 100075. From there the fiber will be routed to J1629 Switching Station by underground fiber buried along road ROW. Total fiber route is approximately 3 miles. |  | M2 - Appendix A Approved | 1661000 | 2028-06-30 | Misc. | Communication equipment | Welsh Prairie |  | W-56 | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50508 | J1629 Welsh Prairie SS Network Upgrades and Interconnection Facilities | GIP | 50803 | W-5 345 kV Transmission Line Modifications | The W-5 345 kV Transmission Line Loop-In project will consist of installing two new single-circuit 90deg dead-end poles between structures 111 and 112, that will allow existing line W-5 to run through the Transmission Owner’s new switchyard, segmenting the line into W-5 towards South Fond Du Lac (SFL) and W-TBD towards Columbia (COL). The Transmission Owner will retain ownership of the line segments, support poles and Interconnection Facility. |  | M2 - Appendix A Approved | 1994000 | 2028-06-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | South Fond Du Lac | Columbia | W-5 | 345 |  |  |  | WI |  | Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50508 | J1629 Welsh Prairie SS Network Upgrades and Interconnection Facilities | GIP | 50804 | J1629 345 kV Interconnection Switching Station Interconnection Facilities | The J1629 TOIF will consist of jumpers and equipment to connect the Interconnection Customer’s Generator Lead Line equipment with the Transmission Owner’s rigid bus. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. |  | M2 - Appendix A Approved | 980000 | 2028-06-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Welsh Prairie |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | OTTER TAIL POWER COMPANY | West | 50510 | OTP Bellingham 115 kV Delivery | Other | 50806 | OTP Bellingham 115 kV Delivery | New 115 kV delivery for town of Bellingham by tapping the Big Stone to Marietta 115 kV line. |  | M2 - Appendix A Approved | 650000 | 2030-12-31 | Substation | Distribution substation - may include trans high side | Bellingham 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP25 | A | MIDAMERICAN ENERGY CO. | West | 50329 | Substation 91 Expansion | BRP | 51468 | Sub 91-Utica Ridge 161 kV Line Reconfiguration | Reterminate the Sub 91-Utica Ridge 161 kV line on a new 161 kV line terminal at Sub 91. |  | M2 - Appendix A Approved | 1500000 | 2028-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Substation 91 | Utica Ridge | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50718 | Rebuild Cayuga to Nucor 345 kV line | BRP | 51469 | Cayuga-Nucor Rebuild | Line rebuild (~32.3mi) to bundled 954ACSS conductor or 4000A equivalent. |  | M2 - Appendix A Approved | 95529061 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Cayuga | Nucor |  | 345 |  |  | 32.3 | IN |  | Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50719 | Rebuild Nucor to Wolf Creek 345 kV line | BRP | 51470 | Nucor-Wolf Creek Rebuild | Line rebuild (~14mi) to bundled 954ACSS conductor or 4000A equivalent. |  | M2 - Appendix A Approved | 49000000 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Nucor | Wolf Creek |  | 345 |  |  | 14 | IN |  | Shared
MTEP25 | A | NORTHERN STATES POWER COMPANY | West | 50720 | Fargo-St. Cloud-Monticello 345kV Davit Arm Replacement | Other | 51471 | 0973 – Quarry to Monticello Davit Arm Replacement | Like-for-like age and condition replacement of select steel davit arms on line 0973 - Quarry to Monticello. |  | M2 - Appendix A Approved | 12500000 | 2030-09-30 | Line Upgrade | Line rebuild on existing ROW | Quarry | Monticello | 1 | 345 |  | 0 | 28.8 | MN |  | Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50722 | New Pond Creek 345 : 138 kV Substation | BRP | 51476 | Pond Creek Substation - 345 kV | 345 kV portion of Substation |  | M2 - Appendix A Approved | 20000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Pond Creek |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50722 | New Pond Creek 345 : 138 kV Substation | BRP | 51477 | Pond Creek Substation - 138 kV | 138 kV Portion of Pond Creek Substation |  | M2 - Appendix A Approved | 10000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Pond Creek |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50722 | New Pond Creek 345 : 138 kV Substation | BRP | 51478 | Pond Creek Transformation 345 : 138 | Transformation at Pond Creek |  | M2 - Appendix A Approved | 10000000 | 2029-06-01 | Transformer | Transformer New | Pond Creek |  |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP25 | A | AMERICAN TRANSMISSION COMPANY | West | 50724 | North Appleton - Werner West (NAPL31) 345 kV, Rerate | Other | 51479 | North Appleton - Werner West (NAPL31) 345 kV, Rerate | Line Clearance |  | M2 - Appendix A Approved | 5300000 | 2030-06-10 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | North Appleton | Werner West | NAPL31 | 345 |  |  |  | WI |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50725 | Rebuild Kokomo HP to Tipton West to Cammack Rd Jct 230kV | BRP | 51482 | Tipton West to Cammack Rd Jct | ~11.8mi of 23008 line from Tipton West to Cammack Rd Jct to bundled 954ACSS conductor or 4000A equivalent |  | M2 - Appendix A Approved | 29500000 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Tipton West | Cammack Rd Jct |  | 230 |  |  | 11.8 | IN |  | Not Shared
MTEP25 | A | DUKE ENERGY INDIANA, LLC | Central | 50725 | Rebuild Kokomo HP to Tipton West to Cammack Rd Jct 230kV | BRP | 51483 | Kokomo Highland Park to Tipton West | ~14.4mi of 23032 line from Kokomo Highland Park to Tipton West to bundled 954ACSS conductor or 4000A equivalent |  | M2 - Appendix A Approved | 36000000 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Kokomo Highland Park | Tipton West |  | 230 |  |  | 14.4 | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50723 | Uprate IPL Petersburg to Cato 138 kV Equipment | BRP | 51494 | Petersburg 138 kV Terminal to Cato/Duff | Replace wave trap and jumpers at Petersburg |  | M2 - Appendix A Approved | 4000000 | 2028-12-31 | Substation | Small miscellaneous substation equipment | Petersburg |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP25 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50727 | Replace Thompson 345/138/13.75 MVA Autotransformer at Thompson Substation | BRP | 51495 | Thompson Autotransformer | 500 MVA, 345 : 138n kV Autotransformer |  | M2 - Appendix A Approved | 15000000 | 2029-12-31 | Transformer | Transformer Replacement | Thompson | Thompson |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP24 | A | CITIZENS ELECTRIC CORPORATION 1 | Central | 51107 | Rebuild Salem Bulk to Seminary 69kV Line T10 | Other | 52048 | Rebuild Salem Bulk to Seminary 69kV Line T10 | Rebuild 29.54 miles of 69kV between Salem Bulk and Seminary. Voltage issue fix from Long Range Study. |  | M2 - Appendix A Approved | 60000000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Salem Bulk | Seminary | T10 | 69 |  |  | 29.54 | MO |  | Not Shared
MTEP24 | A | CITIZENS ELECTRIC CORPORATION 1 | Central | 51109 | New Sprott 69/12kV Substation | Other | 52050 | Sprott 69/12kV Substation | New 5/7MVA 69-12kV Substation |  | M2 - Appendix A Approved | 1200000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Sprott 69kV |  |  | 69 | 12 |  |  | MO |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50184 | Elm Road Generation POI Relocation Project | GIP | 51324 | Elm Road TOIF - Short conductor spans between POI and PCO | Short conductor spans between POI and PCO |  | M3 - Under Construction | 3750000 | 2026-08-29 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Elm Road |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50536 | Raun - S3452 345kV Line and New Terminal | GIP | 50871 | Raun - IA/NE State Line | New 345 kV Line from S3452 to Raun; reflects Iowa section only |  | M2 - Appendix A Approved | 9500000 | 2031-12-31 | Line New | New Transmission line, new ROW - may include terminations | Raun | S3452 | 1 | 345 | 161 | 2 |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50536 | Raun - S3452 345kV Line and New Terminal | GIP | 50872 | Raun - Sioux City (WAPA) Line | Relocate Raun - Sioux City (WAPA) 345 kV line |  | M2 - Appendix A Approved | 2150000 | 2031-12-31 | Misc. | Line relocation (road move) | Raun | Sioux City | 1 | 345 |  |  | 0.5 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50536 | Raun - S3452 345kV Line and New Terminal | GIP | 50873 | Raun - Remsen Line | Relocate Raun - Remsen 345 kV line |  | M2 - Appendix A Approved | 1675000 | 2031-12-31 | Misc. | Line relocation (road move) | Raun | Remsen | 1 | 345 |  |  | 0.5 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50536 | Raun - S3452 345kV Line and New Terminal | GIP | 50874 | Raun - Ida County West Line | Relocate Raun - Ida County West 345 kV line |  | M2 - Appendix A Approved | 1675000 | 2031-12-31 | Misc. | Line relocation (road move) | Raun | Ida County West | 1 | 345 |  |  | 0.5 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50536 | Raun - S3452 345kV Line and New Terminal | GIP | 50875 | Raun | New 345 kV Line Terminal at Raun Substation |  | M2 - Appendix A Approved | 5000000 | 2031-12-31 | Substation | Substation (breakers only, no transformer) | Raun |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50008 | Bluff Creek TR2 | Replace Overstressed Bluff Creek TR2 with new breaker with larger interrupting capacity. |  | M2 - Appendix A Approved | 80000 | 2024-05-01 | Substation | Circuit Breaker (replacement at existing substation) | Bluff Creek |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50009 | Crossroads TR3 | Replace Overstressed Crossroads TR3 with new breaker with larger interrupting capacity. |  | M2 - Appendix A Approved | 80000 | 2026-05-01 | Substation | Circuit Breaker (replacement at existing substation) | Crossroads |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50010 | Eden Prairie Breakers | Replace overstressed breakers Eden Prairie TR1 and TR3 that are end of life with breakers of larger interrupting capacity. |  | M2 - Appendix A Approved | 160000 | 2026-05-01 | Substation | Circuit Breaker (replacement at existing substation) | Eden Prairie |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50011 | Fifth Street 89T4H | Replace overstressed breaker Fifth Street 89T4H that is at end of life with breaker of larger interrupting capacity. |  | M2 - Appendix A Approved | 80000 | 2024-05-01 | Substation | Circuit Breaker (replacement at existing substation) | Fifth Street |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50012 | Red Rock Breakers | Replace overstressed breakers Red Rock 5P96, Cap1 and Cap 3 that are at end of life with breakers of larger interrupting capacity. |  | M2 - Appendix A Approved | 240000 | 2025-11-21 | Substation | Circuit Breaker (replacement at existing substation) | Red Rock |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50013 | Rich Valley Breaker 5TR1 | Replace overstressed breaker Rich Valley 5TR1 that is at end of life with breaker of larger interrupting capacity. |  | M2 - Appendix A Approved | 80000 | 2023-05-01 | Substation | Circuit Breaker (replacement at existing substation) | Rich Valley |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50002 | Overstress Breaker Replacement | Other | 50014 | T Corners Breaker 4E16 | Replace overstressed breaker T Corners 4E16 that is at end of life with breaker of larger interrupting capacity. |  | M2 - Appendix A Approved | 80000 | 2024-05-01 | Substation | Circuit Breaker (replacement at existing substation) | T Corners |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | ENTERGY ARKANSAS, LLC | South | 50004 | J1670 Crooked Lake 2 GIA upgrades | GIP | 50015 | J1670 GIA Crooked Lake Solar II Upgrades | Upgrades consist of power quality metering panel, CT removal, revenue metering install, new telcom equipment, and installation of digital disturbance recorder panel. |  | M2 - Appendix A Approved | 1296000 | 2028-06-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Crooked Lake 161kV |  |  | 161 |  |  |  | AR |  | Not Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50005 | OTP Donaldson 41.6 kV CB 215 Reconductor | Other | 50016 | OTP Donaldson 41.6 kV CB 215 Reconductor | Reconductor 10.5 miles of 41.6 kV line between Donaldson 41.6 kV and Drayton 41.6 kV. |  | M2 - Appendix A Approved | 692495 | 2026-12-31 | Line Upgrade | Line reconductor | Donaldson 41.6 kV | Drayton 41.6 kV | 1 | 42 |  |  | 10.5 | MN |  | Not Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50006 | OTP Marvin - Corona Area 41.6 kV Rebuild | Other | 50017 | OTP Marvin - Corona Area 41.6 kV Rebuild | Rebuild 6 miles of 41.6 kV line between Wilmot 41.6 kV and Summit 41.6 kV surrounding Marvin/Corona 41.6 kV. |  | M2 - Appendix A Approved | 1500000 | 2027-06-30 | Line Upgrade | Line rebuild on existing ROW | Wilmot 41.6 kV | Summit 41.6 kV | 1 | 42 |  |  | 6 | SD |  | Not Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50007 | OTP Omemee Rebuild 41.6 kV Line | Other | 50018 | OTP Omemee Rebuild 41.6 kV Line | Rebuild and relocate 2.5 miles of 41.6 kV line between Rugby 41.6 kV and Bottineau 41.6 kV near Omemee. |  | M2 - Appendix A Approved | 800000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Rugby 41.6 kV | Bottineau 41.6 kV | 1 | 42 |  |  | 2.5 | ND |  | Not Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50012 | OTP Buffalo Area 41.6 kV Rebuild | Other | 50025 | OTP Buffalo Area 41.6 kV Rebuild | Rebuild 41.6 kV line from Buffalo 41.6 kV to Colgate 41.6 kV. |  | M2 - Appendix A Approved | 3770000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Buffalo 41.6 kV | Colgate 41.6 kV | 1 | 42 |  |  | 15.2 | ND |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50020 | 0711 Redwing - Str 11 Rebuild | Other | 50034 | 0711 Red Wing - GRE Spring Creek | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. |  | M2 - Appendix A Approved | 3600000 | 2027-03-31 | Line Upgrade | Line rebuild on existing ROW | Red Wing | GRE Spring Creek | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50026 | Kaukauna Central Tap - Melissa 138 kV (971K11), Rerate | Other | 50045 | Kaukauna Central Tap - Melissa 138 kV (971K11), Rerate | Rerate line 971K11. |  | M3 - Under Construction | 2700000 | 2026-04-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Kaukauna Central Tap | Melissa | 971K11 | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50029 | SE Soteria Add 161 kV Breakers | Other | 50050 | SE Soteria Add 161 kV Breakers for Transformer 4 | Install 161 kV breakers and associated equpiment. |  | M4 - Project in Service | 2000000 | 2025-05-01 | Substation | Circuit Breaker (replacement at existing substation) | SE Soteria |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50029 | SE Soteria Add 161 kV Breakers | Other | 50051 | SE Soteria Add 161 kV Breakers for Transformer 5 | Install 161 kV breakers and associated equipment. |  | M4 - Project in Service | 2000000 | 2025-08-01 | Substation | Circuit Breaker (replacement at existing substation) | SE Soteria |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50029 | SE Soteria Add 161 kV Breakers | Other | 50052 | SE Soteria Add 161 kV Breakers for Transformer 6 | Install 161 kV breakers and associated equipment. |  | M3 - Under Construction | 2000000 | 2026-06-01 | Substation | Circuit Breaker (replacement at existing substation) | SE Soteria |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50030 | Johnson Creek Add 161 kV Breakers | Other | 50053 | Johnson Creek Add 161 kV Breakers for Transformer 4 | Install 161 kV breakers and associated equipment. |  | M4 - Project in Service | 2000000 | 2025-05-01 | Substation | Circuit Breaker (replacement at existing substation) | Johnson Creek |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50030 | Johnson Creek Add 161 kV Breakers | Other | 50054 | Johnson Creek Add 161 kV Breakers for Transformer 5 | Install 161 kV breakers and associated equipment. |  | M4 - Project in Service | 2000000 | 2025-08-01 | Substation | Circuit Breaker (replacement at existing substation) | Johnson Creek |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50030 | Johnson Creek Add 161 kV Breakers | Other | 50055 | Johnson Creek Add 161 kV Breakers for Transformer 6 | Install 161 kV breakers and associated equipment. |  | M3 - Under Construction | 2000000 | 2026-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Johnson Creek |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50031 | Maffitt Lake Add 161 kV Breakers | Other | 50056 | Maffitt Lake Add 161 kV Breakers for 8T6 | Install 161 kV breakers and associated equipment. |  | M4 - Project in Service | 2000000 | 2024-08-01 | Substation | Circuit Breaker (replacement at existing substation) | Maffitt Lake |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50031 | Maffitt Lake Add 161 kV Breakers | Other | 50057 | Maffitt Lake Add 161 kV Breakers for 8T8 | Install 161 kV breakers and associated equipment. |  | M3 - Under Construction | 2000000 | 2026-04-01 | Substation | Circuit Breaker (replacement at existing substation) | Maffitt Lake |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50037 | Ellendale load 2 addition | Other | 50067 | Ellendale sub add | Breakers, and line work. |  | M3 - Under Construction | 16776939 | 2027-06-30 | Substation | Substation (breakers only, no transformer) | Ellendale |  |  | 230 | 35 |  |  | ND |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 50039 | J1561 Generator Interconnection at Richard138 kV | GIP | 50069 | J1561 | Facilities required for the interconnection of J1561 at the Richard 138 kV station. |  | M2 - Appendix A Approved | 1880000 | 2029-04-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Richard |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 50039 | J1561 Generator Interconnection at Richard138 kV | GIP | 50070 | Richard 138 Network upgrades | Network Upgrades to tie J1561. |  | M2 - Appendix A Approved | 6383000 | 2029-04-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Richard |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP24 | A | ENTERGY ARKANSAS, LLC | South | 50040 | Morrilton East 161kV: POI for J1559 | GIP | 50071 | Morrilton East 161kV POI | A new point of interconnection at the existing Morrilton East 161kV substation that includes an extension of the operating bus, new breaker, CCVT, and support structures and foundations. |  | M2 - Appendix A Approved | 3175000 | 2027-03-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Morrilton East |  |  | 161 |  |  |  | AR |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50041 | West Junction SS 138 kV Sectionalizing | Other | 50072 | West Junction SS 138 kV Sectionalizing | • Add a 138 kV bus with two-line breakers and a bus tie breaker and associated facilities at West Junction substation to provide for the required sectionalizing facilities, • Retirement of the West Junction Tap to Bluemound portion of 138 kV line 5066 and associated facilities in coordination with the Milwaukee Area 230 kV conversion to 345 kV Project, • Modification of the protection scheme and implement required networking protection. |  | M2 - Appendix A Approved | 29500000 | 2028-03-23 | Substation | Substation (breakers only, no transformer) | West Junction |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50044 | Hull-Marion-7324 Rebuild | Other | 50083 | Hull-Marion-7324 Rebuild | Rebuild the 7 mile Hull-Marion-1690 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. |  | M2 - Appendix A Approved | 9400000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Hull | Marion |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50045 | Austin Transformer 3 Replacement | Other | 50084 | Austin Transformer 3 Replacement | Replace transformer 3 at Austin Substation which is AIC owned. |  | M2 - Appendix A Approved | 6800000 | 2027-12-01 | Transformer | Transformer Replacement | Austin |  |  | 345 | 138 |  |  | IL |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50057 | Vessel Bulk Sub - Add 2nd 138/34 kV Transformer | Other | 50096 | Vessel Bulk Sub - Add 2nd 138/34 kV Transformer | At Vessel Bulk Sub install the second 84 MVA transformer. |  | M2 - Appendix A Approved | 4000000 | 2030-01-01 | Transformer | Transformer New | Vessel |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP24 | A | ENTERGY ARKANSAS, LLC | South | 50059 | Kinder 161kV: New POI J1558 | GIP | 50097 | Kinder 161kV: New POI J1558 | A new 161kV switching station will be constructed on the Moreland - St. Vincent 161kV line section to interconnect the J1558 200 MW solar project. Line relaying panels will be upgraded at ANO and Pleasant Hill 161kV stations. |  | M2 - Appendix A Approved | 14012000 | 2028-05-29 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Kinder |  |  | 161 |  |  |  | AR |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50120 | J1615 Morgan SS Network Upgrades and Interconnection Facilities | GIP | 50191 | J1615 138 kV Interconnection Station | Existing Morgan Substation will add one (1) new 138kV breaker and two (2) disconnect switches to expand the ring bus configuration to allow the J1615 line to enter the Morgan Substation. Existing G8 bus VTs will be relocated at end of existing bus. One (1) new protective relay panel will be added to the existing control house for the new line and new breaker protection. The new breaker control/protection relaying will be installed in an existing breaker control panel to provide protection for the new breaker. The existing substation yard will be expanded by 175’ x 70’ to the Southwest to square out that corner. |  | M2 - Appendix A Approved | 2909000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Morgan |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50120 | J1615 Morgan SS Network Upgrades and Interconnection Facilities | GIP | 50192 | J1615 138kV Interconnection Facilities | J1615 138kV Interconnection Facilities |  | M2 - Appendix A Approved | 433000 | 2028-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Morgan |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | METC | East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Other | 50193 | ETAWS-QUARY_Relocate w OPGW | Relocate approximately ~5.78 miles from structure #504804 to structure Quarry onto the vacant side of the recently-rebuilt Twining – Whittemore utilizing existing double- circuit structures, using 954 ACSR conductor and install OPGW. De-energize old section after relocating to new location. |  | M2 - Appendix A Approved | 4700000 | 2028-09-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | East Tawas | Quary | 1 | 138 |  |  | 5.78 | MI |  | Not Shared
MTEP24 | A | METC | East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Other | 50194 | COTGR-QUARY_Relocate w OPGW | Relocate approximately ~39.04 miles from Quarry to Cottage Grove onto the vacant side of the recently-rebuilt Twining – Whittemore & Shale – Twining utilizing existing double- circuit structures, using 954 ACSR conductor and install OPGW. Construct ~1.5 mile from Cottage Grove to new location on a new ROW. Relocate existing PT switches at Santiago tap, at Saganing tap, and at Seven Mile tap De-energize old section after relocating to new location. |  | M2 - Appendix A Approved | 26750000 | 2028-09-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Quary | Cottage Grove | 1 | 138 |  |  | 34.04 | MI |  | Not Shared
MTEP24 | A | METC | East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Other | 50195 | COTGR-KARN_Relocate w OPGW | Relocate approximately ~ 7.5 miles from Cottage Grove to Karn onto the vacant side of the recently-rebuilt Shale – Twining utilizing existing double- circuit structures, using 954 ACSR conductor and install OPGW. De-energize old section after relocating to new location. |  | M2 - Appendix A Approved | 6650000 | 2028-09-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Cottage Grove | Karn | 1 | 138 |  |  | 7.5 | MI |  | Not Shared
MTEP24 | A | METC | East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Other | 50197 | Cottage Grove - Remove Switches and Bus Work | Remove switches 388, 500, 502, 504, and associated bus work. Convey switch 377 and remainder of Cottage Grove station to Consumers Energy. |  | M2 - Appendix A Approved | 230000 | 2028-04-28 | Substation | Small miscellaneous substation equipment | Cottage Grove |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Other | 50198 | QUARY-Terminate OPGW | Terminate OPGW at Quary station |  | M2 - Appendix A Approved | 280000 | 2028-04-28 | Substation | Small miscellaneous substation equipment | Quary |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50136 | Baraboo SS, DIC, Substation Relocation | Other | 50216 | Baraboo SS, DIC, Sub Relocation | The LDC is planning to relocate the Baraboo substation from its current location to a nearby site. To accommodate this ATC will install 2x new T-Line structures and replace one T-Line structure to reroute the Kirkwood-Dam Heights 69kV (Y-75) line. This will require roughly 0.04 miles of new conductor. Additionally, a new 3 way tap structure to the new substation will be required. A new ATC control house will be required to retain supervisory control of the tap switches. Lastly, ATC to retire 9x T-Line poles and the substation equipment at the current Baraboo location. |  | M2 - Appendix A Approved | 5000000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Baraboo |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50138 | Dodge County, DIC, New Substation | Other | 50218 | Dodge County, DIC, New Substation | Construct one new 138 kV interconnection substation named Manhattan near the city of Beaver Dam. Also, expand and upgrade the exiting North Randolph 138 kV bus to support additional circuits to Manhattan. Rebuild the existing N Randolph – N Beaver Dam 138 kV line (X-47) forming a new North Randolph - Manhattan 138 kV line and construct a new double circuit 138 kV transmission line between North Randolph and Manhattan substations. |  | M3 - Under Construction | 192000000 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Manhattan |  | X-47 | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50098 | Hagensville Junction Interconnection | BRP | 50152 | Hagensville Junction Station | Build a 3 terminal station with 138/69kV stepdown transformer. One terminal will connect to new Hagensville Junction to Hagensville 138kV line. One terminal will connect to the 69kV line to the the Airport station. One terminal will connect to the 69 kV line to the Tower station. |  | M2 - Appendix A Approved | 9000000 | 2028-12-31 | Substation | Switching station (breakers only, no transformer) | Hagensville Junction |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 50106 | Big Cedar Interconnection | Other | 50156 | Big Cedar Switching Station | New Big Cedar 345 kV Switching Station |  | M2 - Appendix A Approved | 33106789 | 2026-06-01 | Substation | Switching station (breakers only, no transformer) | Big Cedar |  |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 50106 | Big Cedar Interconnection | Other | 50157 | Line Taps for Big Cedar Switching Station | Line taps from existing Beverly - Morgan Valley line to new Big Cedar Switching Station |  | M4 - Project in Service | 5736250 | 2026-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Big Cedar | Morgan Valley |  | 345 | 345 | 0.5 |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 50106 | Big Cedar Interconnection | Other | 50158 | Beverly - Big Cedar #2 345 kV Line | Add 2nd Beverly - Big Cedar 345 kV line on existing double circuit capable structures. |  | M4 - Project in Service | 2652500 | 2026-03-31 | Line New | New Transmission line, new ROW - may include terminations | Beverly | Big Cedar | 2 | 345 | 345 | 2 |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 50106 | Big Cedar Interconnection | Other | 50159 | Beverly Substation Upgrades for Big Cedar Interconnection | Add line terminal for Big Cedar #2 line at Beverly substation, converting substation from ring bus to breaker and 1/2 configuration. |  | M4 - Project in Service | 5667950 | 2026-03-31 | Substation | Substation (breakers only, no transformer) | Beverly |  |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 50106 | Big Cedar Interconnection | Other | 50160 | Morgan Valley Relay Upgrades | Upgrade relays at Morgan Valley on terminal for line to Big Cedar Switching Station. |  | M2 - Appendix A Approved | 97328 | 2026-10-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Morgan Valley |  |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 50106 | Big Cedar Interconnection | Other | 50161 | Lines from Big Cedar to Customer substations | New 345 kV feeds from Big Cedar Switching Station to customer owned substations |  | M4 - Project in Service | 16482500 | 2026-03-31 | Line New | New Transmission line, new ROW - may include terminations | Big Cedar |  |  | 345 |  | 4 |  | IA |  | Not Shared
MTEP24 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50099 | Lewisville West Capacity Increase | Other | 50162 | Lewisville West XFMR Addition | Add 2nd autotransformer at Lewisville West substation. New transformer to be rated for 115/69 kV, 100 MVA. |  | M2 - Appendix A Approved | 4500000 | 2026-06-01 | Transformer | Transformer New | Lewisville West |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50898 | Line: MN/ND State Line - Bison - 345 kV | Install second 345kV circuit on existing spare position. | GRE, MP, MRES, OTP, XEL | M2 - Appendix A Approved | 19600000 | 2032-06-01 | Line Upgrade | 2nd circuit on existing spare position | MN/ND State Line | Bison |  | 345 |  |  | 34 | ND |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 8219 | 8219-St Louis County-VSC HVDC Converter | New, Relocated VSC HVDC Converter Station, Symmetric Monopole Configuration, +/-250kV | MP | M2 - Appendix A Approved | 352500000 | 2028-12-31 | Misc. | High Voltage DC line or terminal | St Louis County | VSC HVDC Converter |  | 250 |  | 0.1 |  | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 8220 | 8220-East Oliver-VSC HVDC Converter | New, Relocated VSC HVDC Converter Station, Symmetric Monopole Configuration, +/-250kV | MP | M2 - Appendix A Approved | 352500000 | 2028-12-31 | Misc. | High Voltage DC line or terminal | East Oliver | VSC HVDC Converter |  | 250 |  | 1 | 0 | ND |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 21767 | 13 Line Rebuild | Other | 26360 | 26360-Riverton-GRE-Portage Lake | Rebuild GRE-Portage Lake - Aitkin Tap 115 kV Line | MP | M2 - Appendix A Approved | 12000000 | 2030-03-31 | Line Upgrade | Line rebuild on existing ROW | Riverton | GRE-Portage Lake |  | 115 |  | 0 | 27.5 | MN |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21786 | Vestaburg 69kV Relocation | Other | 26362 | 26362-Vestaburg 69kV Station- | Rebuild and relocate station | WPSC | M2 - Appendix A Approved | 8500000 | 2025-12-31 | Substation | Switching station (breakers only, no transformer) | Vestaburg 69kV Station |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 21968 | Delaney 138 kV Station Rebuild | Other | 26596 | 26596-New Station-Delaney | Construct ~1.1 miles of line through new right-of-way, using 1431 ACSR conductor, to connect Delaney distribution substation to the new 138 kV station. | METC | M2 - Appendix A Approved | 0 | 2029-05-01 | Line New | New Transmission line, new ROW - may include terminations | New Station | Delaney | 1 | 138 |  | 1.1 |  | MI |  | Not Shared
MTEP24 | A | METC | East | 21968 | Delaney 138 kV Station Rebuild | Other | 26597 | 26597-Delaney- | Remove METC equipment from Delaney substation. | METC | M2 - Appendix A Approved | 0 | 2029-05-01 | Substation | Substation (breakers only, no transformer) | Delaney |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 22015 | Blackstone – Leoni #1 138 kV Rebuild | BRP | 26664 | 26664-Blackstone-Leoni #1 | Rebuild approximately 4.2 miles of the Blackstone – Leoni #1 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double-circuit structures with OPGW. | METC | M2 - Appendix A Approved | 9232000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Blackstone | Leoni | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 22018 | Blackstone – Leoni #3 and #2 138 kV Rebuild | BRP | 26666 | Blackstone_Leoni #3 & #2 138kV Rebuild | Rebuild approximately 2.65 miles of the Blackstone – Leoni #3 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double- circuit structures to structure #10C2012 with OPGW. Rebuild approximately 2.72 miles of the Blackstone – Leoni #2 circuit entirely onto the double circuit structures carrying the Blackstone – Leoni #3 circuit utilizing 1431 ACSR conductor to structure #10C229 with OPGW. | METC | M2 - Appendix A Approved | 7972000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Blackstone | Leoni |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 22015 | Blackstone – Leoni #1 138 kV Rebuild | BRP | 26679 | 26679-Blackstone - Upgrade pos 677 and Line Drop | Upgrade Terminal Equipment at Blackstone. | METC | M2 - Appendix A Approved | 481000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Blackstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 22015 | Blackstone – Leoni #1 138 kV Rebuild | BRP | 26680 | 26680-Leoni-Upgrade station equipment's and connect OPGW | Upgrade terminal equipment at Leoni and connect OPGW. | METC | M2 - Appendix A Approved | 127000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Leoni |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 22018 | Blackstone – Leoni #3 and #2 138 kV Rebuild | BRP | 26681 | Blackstone_Upgrade pos 888 and 777 Buses and Line Drops | Upgrade 636 ACSR line drop and 2-4/0 CU bus at Blackstone 138 kV position 888 and 777. Connect OPGW. | METC | M2 - Appendix A Approved | 297000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Blackstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 22018 | Blackstone – Leoni #3 and #2 138 kV Rebuild | BRP | 26682 | Leoni_Upgrade station equipment's and Connect OPGW | Upgrade Leoni BM12 795 ACSS METC to a minimum of 450MVA. Connect OPGW at Leoni 138 kV position BM12 and BM8. | METC | M2 - Appendix A Approved | 136000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Leoni |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 23706 | 158 Line Rebuild | Other | 27486 | 27486-Cromwell-Portage Lake | Rebuild Cromwell to Portage Lake ("158 Line") 115 kV Transmission Line. | MP | M2 - Appendix A Approved | 25000000 | 2029-03-31 | Line Upgrade | Line rebuild on existing ROW | Cromwell | Portage Lake |  | 115 |  | 0 | 27.5 | MN |  | Not Shared
MTEP24 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 24694 | Coop Office Breaker Addition | Other | 28064 | 28064-Coop Office-Colt | Sectionalizing breaker to be added on the Coop Office to Colt 69kV line | AECC | M2 - Appendix A Approved | 2500000 | 2028-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Coop Office | Colt |  | 69 |  |  |  | AR |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 24738 | Rebuild Hull-Herleman-1682 138 kV Transmission Line | Other | 28070 | 28070-Hull-Herleman | Rebuild the Hull-Herleman-1682 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | AmerenIL | M2 - Appendix A Approved | 24000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Hull | Herleman |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 24778 | Grant County, DIC, New Substation | Other | 28084 | Grant County, DIC, New Substation | New load interconnection request in SW Wisconsin. Project scope includes construction of a new 69-kV transmission line to network Hillman – Miners (Y-130) 69-kV line with a new 69-kV substation near the customer site. | ATC | M3 - Under Construction | 38300000 | 2027-06-30 | Substation | Distribution substation - may include trans high side | Grant County |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | METC | East | 14344 | Airport - Hillman Tap 138 kV Sag Remediation | BRP | 23317 | 23317-Airport-Hillman Tap | Remediate the sag limit on ~17.0 miles of 266.8 ACSR conductor of the ~21.3 mile-long Airport - Hillman Tap 138 kV section of the Airport - Mio 138 kV line to at least the planned target summer emergency rating of 133 MVA/556 Amps. | METC | M2 - Appendix A Approved | 1061250 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Airport | Hillman Tap | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 22798 | Small Capital Project and Asset Renewal Program 2025 | Other | 26866 | Small Capital Project and Asset Renewal Program 2025 | See project description. | ATC | M3 - Under Construction | 45000000 | 2031-09-16 | Substation | Substation (breakers only, no transformer) | Various Subs |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 22911 | Load Interconnection Program 2025 | Other | 26868 | Load Interconnection Program 2025 | See project description. | ATC | M3 - Under Construction | 19000000 | 2030-11-19 | Substation | Distribution substation - may include trans high side | Various Subs |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 22872 | Upgrade Macomb NE 138 kV substation | Other | 26900 | 26900-Macomb NE- | Add line breaker on the Macomb West line Relay: Replace relays: MCBW-MCNE-1, SEL-221-16 MCBW-MCNE-1, SEL-221F MCBW-MCNE-1, REL-302 | AmerenIL | M2 - Appendix A Approved | 1800000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Macomb NE |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 22949 | Rebuild Stoddard 161 kV substation | Other | 26911 | 26911-Stoddard- | Rebuild Stoddard substation into a ring bus configuration, including replacement of aging/overstressed/broken equipment. | AmerenMO | M2 - Appendix A Approved | 15900000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Stoddard |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 22950 | Upgrade Watson 138 kV substation | Other | 26914 | 26914-Watson- | Add line breakers to Pos. V & W Remove HSGS' and Add CS/PCB on the XFMRs 1,2,3 | AmerenMO | M2 - Appendix A Approved | 6200000 | 2032-12-01 | Substation | Substation (breakers only, no transformer) | Watson |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 22878 | Upgrade Cat Mapleton 138 kV substation | Other | 26917 | 26917-Cat Mapleton- | New ring bus across road with two lead lines back to Cat Mapleton. | AmerenIL | M2 - Appendix A Approved | 8700000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Cat Mapleton |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 22880 | Zion 161 kV Substation Add High Side Interrupter | Other | 26919 | 26919-Zion- | Add high side interrupting Device on 161/69kV Transformer | AmerenIL | M2 - Appendix A Approved | 2000000 | 2027-06-01 | Substation | Small miscellaneous substation equipment | Zion |  |  | 161 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 22951 | Upgrade Rantoul 138 kV substation | Other | 26921 | 26921-Rantoul- | Reconfigure 138kV into ring bus | AmerenIL | M2 - Appendix A Approved | 7100000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Rantoul |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 22886 | Reconfigure Berkeley 138 kV substation | Other | 26954 | 26954-Berkeley- | Remove HSGS' on XFMRs 1,2,3,4. Add high side interrupting devices. Add line BRKs to Pos. D & J. Would require add'l bus diff panels for Buses 3 & 4 Relay: If no new Control Enclosure, upgrade two of the tie breakers and the 138 kV buses. | AmerenMO | M3 - Under Construction | 39200000 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | Berkeley |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25449 | Norwoodville Substation and 69 kV lines | Other | 28619 | 28619-Norwoodville-E. 17th & Broadway | Norwoodville-E. 17th & Broadway 69kV line | MEC | M2 - Appendix A Approved | 1000000 | 2028-10-01 | Line New | New Transmission line, new ROW - may include terminations | Norwoodville | E. 17th & Broadway | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25449 | Norwoodville Substation and 69 kV lines | Other | 28620 | 28620-Norwoodville-John Deere West | Norwoodville-John Deer West 69 kV line | MEC | M2 - Appendix A Approved | 1000000 | 2028-10-01 | Line New | New Transmission line, new ROW - may include terminations | Norwoodville | John Deere West | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25424 | NE 6th St Substation and 161 kV line taps | Other | 28621 | 28621-NE 6th Street- | Construct new 161-13 kV substation | MEC | M2 - Appendix A Approved | 4000000 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | NE 6th Street |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25424 | NE 6th St Substation and 161 kV line taps | Other | 28622 | 28622-NE 6th Street-NE Ankeny | Tap NE Ankeny - Big Creek 161 kV | MEC | M2 - Appendix A Approved | 1250000 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | NE 6th Street | NE Ankeny | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25424 | NE 6th St Substation and 161 kV line taps | Other | 28623 | 28623-NE 6th Street-Big Creek | Tap NE Ankeny - Big Creek 161 kV | MEC | M2 - Appendix A Approved | 1250000 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | NE 6th Street | Big Creek | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25425 | Metro East Substation 161 kV line breakers | Other | 28624 | 28624-Metro East- | Install 161 kV line breakers and relaying | MEC | M2 - Appendix A Approved | 3000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Metro East |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25460 | Southridge Substation and 161 kV line taps | Other | 28625 | 28625-Southridge- | Construct new 161-13 kV substation | MEC | M2 - Appendix A Approved | 4000000 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Southridge |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25460 | Southridge Substation and 161 kV line taps | Other | 28626 | 28626-Southridge-Greenfield Plaza | Tap SE Polk - Greenfield Plaza 161 kV | MEC | M2 - Appendix A Approved | 1250000 | 2027-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Southridge | Greenfield Plaza | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25460 | Southridge Substation and 161 kV line taps | Other | 28627 | 28627-Southridge-SE Polk | Tap SE Polk - Greenfield Plaza 161 kV | MEC | M2 - Appendix A Approved | 1250000 | 2027-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Southridge | SE Polk | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25461 | Johnson Creek - Maffitt Lake 161 kV line | Other | 28628 | 28628-Johnson Creek- | Install Johnson Creek 161 kV line terminal | MEC | M2 - Appendix A Approved | 3400000 | 2027-08-01 | Substation | Substation (breakers only, no transformer) | Johnson Creek |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25461 | Johnson Creek - Maffitt Lake 161 kV line | Other | 28629 | 28629-Maffitt Lake- | Install Maffitt Lake 161 kV line terminal | MEC | M2 - Appendix A Approved | 3400000 | 2027-08-01 | Substation | Substation (breakers only, no transformer) | Maffitt Lake |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25461 | Johnson Creek - Maffitt Lake 161 kV line | Other | 28630 | 28630-Johnson Creek-Maffitt Lake | Johnson Creek - Maffitt Lake 161 kV line | MEC | M2 - Appendix A Approved | 8500000 | 2027-08-01 | Line New | New Transmission line, new ROW - may include terminations | Johnson Creek | Maffitt Lake | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25450 | Rebuild Breiner-Spring Lake Jct. 69 kV Line | Other | 28631 | Rebuild Breiner-Spring Lake Jct. 69 kV Line | Rebuild Breiner-Spring Lake Jct. 336 ACSR 69 kV Line | PPI | M2 - Appendix A Approved | 5500000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Breiner | Spring Lake Jct. |  | 69 | 69 |  | 10.36 | IL |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28632 | 28632-Cleveland- | Upgrade Cleveland C515 switch to 1200 A. | GRE | M2 - Appendix A Approved | 655705 | 2025-09-26 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Cleveland |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28633 | 28633-Jamestown Tap GRE- | Upgrade Jamestown Tap switches (SS2824) to 1200 A. | GRE | M2 - Appendix A Approved | 600000 | 2025-09-26 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Jamestown Tap GRE |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28634 | 28634-St. Thomas Tap- | Upgrade St. Thomas Tap (SS265) switch to 1200 A. | GRE | M2 - Appendix A Approved | 691822 | 2025-10-23 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | St. Thomas Tap |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28635 | 28635-Pratt Tap- | Upgrade Pratt Tap (SS2765) switches to 2000 A. | GRE | M2 - Appendix A Approved | 300000 | 2024-12-03 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Pratt Tap |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28636 | 28636-Johnson Junction- | Upgrade Johnson Junction (SS380) switches to 2000 A. | GRE | M2 - Appendix A Approved | 479508 | 2025-03-07 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Johnson Junction |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28637 | 28637-Benton County- | Upgrade Benton County wave trap and jumpers. | GRE | M2 - Appendix A Approved | 300000 | 2025-03-07 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Benton County |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28638 | 28638-Inman-Miltona | Replace structures in the Inman - Elmo - Parkers Prairie - Miltona line to increase rating. | GRE | M2 - Appendix A Approved | 1190849 | 2024-10-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Inman | Miltona | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25428 | New Shenandoah Substation and 69 kV lines | Other | 28654 | 28654-New Shenandoah- | Construct new substation with two 69 kV line terminals and a 69 kV capacitor bank | MEC | M2 - Appendix A Approved | 10000000 | 2029-06-30 | Substation | Substation (breakers only, no transformer) | New Shenandoah |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25428 | New Shenandoah Substation and 69 kV lines | Other | 28655 | 28655-Shenandoah-New Shenandoah | Construct new Shenandoah-Shenandoah 69 kV line | MEC | M2 - Appendix A Approved | 2000000 | 2029-06-30 | Line New | New Transmission line, new ROW - may include terminations | Shenandoah | New Shenandoah | 1 | 69 |  | 2 |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25428 | New Shenandoah Substation and 69 kV lines | Other | 28656 | 28656-New Shenandoah-Clarinda | Construct new Shenandoah-Clarinda 69 kV line | MEC | M2 - Appendix A Approved | 7000000 | 2029-06-30 | Line New | New Transmission line, new ROW - may include terminations | New Shenandoah | Clarinda | 1 | 69 |  | 6.5 |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25428 | New Shenandoah Substation and 69 kV lines | Other | 28657 | 28657-Clarinda-Shenandoah | Retire section of the Clarinda-Shenandoah 69 kV line (approximately 2.5 miles) | MEC | M2 - Appendix A Approved | 300000 | 2029-06-30 | Misc. | Remove existing branch from model | Clarinda | Shenandoah | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25464 | CBEC Upgrade Sync Check Relaying | Other | 28658 | 28658-CBEC- | Relay replacement at CBEC substation | MEC | M3 - Under Construction | 1700000 | 2026-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | CBEC |  |  | 345 | 161 |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25429 | Liberty Substation 161-69 kV Expansion and Associated Lines | Other | 28659 | 28659-Liberty- | Expand Liberty Substation to install a 161-69 kV, 125 MVA transformer, a new 161 kV terminal and new 69 kV bus. | MEC | M2 - Appendix A Approved | 13300000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Liberty |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25429 | Liberty Substation 161-69 kV Expansion and Associated Lines | Other | 28660 | 28660-Liberty-Terra | Construct new 69 kV line from Liberty Substation to new Terra Substation | MEC | M2 - Appendix A Approved | 2500000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Liberty | Terra | 1 | 69 |  | 0.6 |  | IA |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25410 | Winshire 69 kV Capacitor Banks | BRP | 28661 | 28661-Winshire- | Install 2 - 11 MVAR cap banks | Entergy-TX | M2 - Appendix A Approved | 7000000 | 2027-12-01 | Voltage Device | Capacitor (switched capacitor) | Winshire |  |  | 69 |  |  |  | TX |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25429 | Liberty Substation 161-69 kV Expansion and Associated Lines | Other | 28662 | 28662-Neal North-Terra | Rebuild Neal North-Terra 69 kV line | MEC | M2 - Appendix A Approved | 1000000 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Neal North | Terra | 1 | 69 |  |  | 0.5 | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25411 | Second 69 kV Line into Rock Valley Town Substation | Other | 28663 | 28663-Rock Valley Town-NIPCO K218 | Construct a second 69 kV line into Rock Valley Town Substation and retire a section of the Rock Valley Town Tap-NIPCO K218 69 kV line | MEC | M2 - Appendix A Approved | 1500000 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | Rock Valley Town | NIPCO K218 | 1 | 69 |  | 0.6 |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25411 | Second 69 kV Line into Rock Valley Town Substation | Other | 28664 | 28664-Rock Valley Town Tap-NIPCO K218 | Retire a section of the Rock Valley Town Tap-NIPCO K218 69 kV line (~0.25 miles) | MEC | M2 - Appendix A Approved | 100000 | 2029-06-01 | Misc. | Remove existing branch from model | Rock Valley Town Tap | NIPCO K218 | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25430 | Fairview to Madisonville 230 kV Upgrades | BRP | 28665 | 28665-Fairview-Madiosnville | Upgrade short 230 kV line | Entergy-LA | M2 - Appendix A Approved | 700000 | 2027-12-01 | Line Upgrade | Line reconductor | Fairview | Madiosnville |  | 230 |  |  |  | LA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25431 | Dakota Dunes: Install 69 kV Capacitor Bank | Other | 28666 | 28666-Dakota Dunes- | Expand Dakota Dunes Substation to install a 14.7 MVAR 69 kV capacitor bank | MEC | M3 - Under Construction | 4000000 | 2026-09-01 | Voltage Device | Capacitor (switched capacitor) | Dakota Dunes |  | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 25446 | Willmar System Upgrades | Other | 28667 | 28667-Willmar System- | Willmar is upgrading SCADA, relays, RTUs, and replacing 69 kV poles due to age. | MRES | M2 - Appendix A Approved | 1600000 | 2028-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Willmar System |  |  | 230 | 69 |  |  | MN |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25433 | J1270 POI New 345 kV Interconnection Substation and 345 kV Line Taps | GIP | 28668 | 28668-J1270 Sub- | Network Upgrades for J1270 Generator (Graettinger Marsh Sub) | MEC | M2 - Appendix A Approved | 18500000 | 2027-09-01 | Substation | Substation (breakers only, no transformer) | J1270 Sub |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25433 | J1270 POI New 345 kV Interconnection Substation and 345 kV Line Taps | GIP | 28669 | 28669-Graettinger Marsh-Palo Alto | Network Upgrades for J1270 Generator (345 kV line taps) | MEC | M2 - Appendix A Approved | 2500000 | 2027-09-15 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Graettinger Marsh | Palo Alto | 1 | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 25446 | Willmar System Upgrades | Other | 28670 | 28670-69 kV system- | Replace 69 kV poles due to condition | MRES | M4 - Project in Service | 400000 | 2025-12-31 | Line Upgrade | Line rebuild on existing ROW | 69 kV system |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25433 | J1270 POI New 345 kV Interconnection Substation and 345 kV Line Taps | GIP | 28671 | 28671-Graettinger Marsh-Trumbull Lake | Network Upgrades for J1270 Generator (345 kV line taps) | MEC | M2 - Appendix A Approved | 2500000 | 2027-09-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Graettinger Marsh | Trumbull Lake | 1 | 345 |  |  |  | IA |  | Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25432 | Cypress to Legend 500 kV line | BRP | 28672 | 28672-Cypress-Legend | New ~35 mile 500 kV line | Entergy-TX | M2 - Appendix A Approved | 420000000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Cypress | Legend |  | 500 |  |  |  | TX |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25432 | Cypress to Legend 500 kV line | BRP | 28673 | 28673-Legend- | Install 500-230 kV Auto at Legend | Entergy-TX | M2 - Appendix A Approved | 1 | 2028-12-01 | Transformer | Transformer New | Legend |  |  | 500 | 230 |  |  | TX |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25434 | J1218/J1229 Network Upgrades at Sub 92 | GIP | 28674 | 28674-Substation 92- | Network Upgrades for J1218/J1229 Generator | MEC | M2 - Appendix A Approved | 6200000 | 2028-06-30 | Substation | Substation (breakers only, no transformer) | Substation 92 |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25435 | Serpent to Tupper 69 kV Upgrade | BRP | 28675 | 28675-Tupper- | Upgrade Tupper 69 kV Bus | Entergy-LA | M2 - Appendix A Approved | 1200000 | 2028-12-01 | Substation | Substation bus upgrade | Tupper |  |  | 69 |  |  |  | LA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25412 | Line Rebuilds Blanket 2025 - 2027 | Other | 28676 | 28676-CBEC-Sub 706 | Rebuild section of CBEC-Sub 706 69 kV line | MEC | M2 - Appendix A Approved | 3000000 | 2029-12-01 | Line Upgrade | Line rebuild on existing ROW | CBEC | Sub 706 | 1 | 69 |  |  | 1.2 | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25412 | Line Rebuilds Blanket 2025 - 2027 | Other | 28677 | 28677-Percival-Hamburg | Rebuild Percival-Hamburg 69 kV line | MEC | M2 - Appendix A Approved | 7500000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Percival | Hamburg | 1 | 69 |  |  | 7.5 | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25437 | Substation 85: Convert to Ring Bus | Other | 28679 | 28679-Substation 85-161 kV Ring Bus | Install 161 kV circuit breakers and bus work to convert Substation 85 to a ring bus configuration | MEC | M2 - Appendix A Approved | 7000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Substation 85 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25439 | Sub G 69 kV Line Taps | Other | 28681 | 28681-Sub G-Sub Q | Install two 69 kV line taps terminating at Sub G 69 kV line breakers. | MEC | M2 - Appendix A Approved | 300000 | 2030-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sub G | Sub Q | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25439 | Sub G 69 kV Line Taps | Other | 28682 | 28682-Sub G-Sub K | Install two 69 kV line taps terminating at Sub G 69 kV line breakers. | MEC | M2 - Appendix A Approved | 300000 | 2030-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sub G | Sub K | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25466 | Maynard Substation: Replace Three 69 kV Breakers and Relaying | Other | 28688 | 28688-Maynard- | Replace oil breakers, bus differential relaying, and breaker failure relaying. | MEC | M2 - Appendix A Approved | 1600000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Maynard |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25467 | Substation P Iowa City Transformer Breakers | Other | 28690 | 28690-Sub P IC- | Add two 161 kV breakers at Substation P to separate the distribution transformers from the substation's line terminals | MEC | M3 - Under Construction | 5200000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Sub P IC |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25468 | Southline to Jacinto 138 kV New Line | BRP | 28691 | 28691-Jacinto-Southline | New ~6 mile 138 kV line | Entergy-TX | M2 - Appendix A Approved | 40700000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Jacinto | Southline |  | 138 |  |  |  | TX |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25470 | Sunrise 230 kV New Station | BRP | 28692 | 28692-Sunrise- | New 230 kV station on the Wells to Labbe 230 kV line. | Entergy-LA | M2 - Appendix A Approved | 39600000 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Sunrise |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25455 | Amite South/DSG Reactive Support Project | Other | 28693 | 28693-Multiple- | Install cap banks at Little Gypsy, Peters Road, and Munster | Entergy-LA | M2 - Appendix A Approved | 21100000 | 2027-07-01 | Voltage Device | Capacitor (switched capacitor) | Multiple |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25412 | Line Rebuilds Blanket 2025 - 2027 | Other | 28694 | 28694-Various- | Blanket project to rebuild 69 kV, 161 kV and 345 kV lines due to condition and to improve reliability and operational flexibility. | MEC | M2 - Appendix A Approved | 32000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Various |  |  | 345 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25457 | PCI 69 kV Breaker Upgrades | Other | 28695 | 28695-PCI- | Replace 3 69 kV breakers | Entergy-LA | M2 - Appendix A Approved | 2730000 | 2027-06-01 | Substation | Circuit Breaker (replacement at existing substation) | PCI |  |  | 69 |  |  |  | LA |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25458 | Gibson 345kV Ckt Brkr Upgrades | BRP | 28696 | 28696-Gibson Gen Station- | Gibson 345 CB upgrades - TPL-001 short ckt overduty - replace (14) 345kV-63kA interrupting rated CBs with new standard CBs that have a "higher DC component"; replace breaker disconnect switches and upgrade bus conductor as needed; install new control building | DEI | M2 - Appendix A Approved | 23170000 | 2028-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Gibson Gen Station |  |  | 345 |  |  |  | IN |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25475 | Merricourt Reactor | BRP | 28712 | 28712-Merricourt- | Add 50 Mvar reactor to the Merricourt Substation | MDU | M2 - Appendix A Approved | 5000000 | 2026-12-31 | Voltage Device | Reactor or Inductor | Merricourt |  |  | 230 |  |  |  | ND |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25456 | Spring Creek Upgrade Projects | Other | 28718 | 28718-Spring Creek- | Replace the two 161/69 kV 70 MVA transformers with 140 MVA units and complete the 161 kV topology to a ring bus. | GRE | M2 - Appendix A Approved | 19992124 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Spring Creek |  |  | 161 | 69 |  |  | MN |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 23951 | Line Clearance Mitigation Program 2025 | Other | 27683 | Line Clearance Mitigation Program 2025 | See project description. | ATC | M3 - Under Construction | 5400000 | 2026-05-22 | Line Upgrade | Generic transmission line project (try not to use the generic) | Various Lines |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 24034 | Coffeen N. XFMR 2 Replacement | Other | 27728 | 27728-Coffeen N- | Replace Existing XFMR 2 at Coffeen North Substation with a new 345/138kV 700 MVA unit. | AmerenIL | M2 - Appendix A Approved | 12000000 | 2026-12-01 | Transformer | Transformer New | Coffeen N |  |  | 345 | 138 |  |  | IL |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24413 | Richer-Littlefork 230 kV Line Rebuild | Other | 27840 | 27840-Richer-Roseau | Roseau-Richer 230 kV | MPC | M2 - Appendix A Approved | 630000 | 2025-02-28 | Line Upgrade | Line rebuild on existing ROW | Richer | Roseau | 1 | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24413 | Richer-Littlefork 230 kV Line Rebuild | Other | 27841 | 27841-Roseau-Moranville | Moranville-Roseau 230 kV | MPC | M2 - Appendix A Approved | 60000 | 2025-02-28 | Line Upgrade | Line rebuild on existing ROW | Roseau | Moranville |  | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24413 | Richer-Littlefork 230 kV Line Rebuild | Other | 27842 | 27842-Moranville-Lund | Moranville - Lund 230 KV | MPC | M2 - Appendix A Approved | 360000 | 2025-02-28 | Line Upgrade | Line rebuild on existing ROW | Moranville | Lund |  | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24413 | Richer-Littlefork 230 kV Line Rebuild | Other | 27843 | 27843-Lund-Littlefork | Lund - Littlefork 230 KV | MPC | M2 - Appendix A Approved | 540000 | 2026-02-28 | Line Upgrade | Line rebuild on existing ROW | Lund | Littlefork |  | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24375 | Center-Maple River 345 kV Foundation Restoration | Other | 27844 | 27844-Center-Jamestown | Center - Jamestown 345 KV | MPC | M2 - Appendix A Approved | 4400000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Center | Jamestown |  | 345 |  |  |  | ND |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24375 | Center-Maple River 345 kV Foundation Restoration | Other | 27845 | 27845-Jamestown-Buffalo | Buffalo - Jamestown 345 KV Line | MPC | M2 - Appendix A Approved | 2000000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Jamestown | Buffalo |  | 345 |  |  |  | ND |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24375 | Center-Maple River 345 kV Foundation Restoration | Other | 27846 | 27846-Buffalo-Bison | Bison - Buffalo 345 KV Line | MPC | M2 - Appendix A Approved | 750000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Buffalo | Bison |  | 345 |  |  |  | ND |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50900 | Substation - Cass County | Replace 115kV substation bus and equipment to achieve 3000A rating for the outgoing Red River 115kV transmission line. | XEL | M2 - Appendix A Approved | 7700000 | 2032-06-01 | Substation | Substation bus upgrade | Cass County |  |  | 115 |  |  |  | ND |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50901 | Substation - Bison | Add one 345kV position and convert the existing four-position ring bus into a five-position breaker-and-a-half bus arrangement. | XEL | M2 - Appendix A Approved | 10600000 | 2032-06-01 | Substation | Substation bus upgrade | Bison |  |  | 345 |  |  |  | ND |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50902 | Substation - Red River | Replace existing 115kV substation bus and equipment to achieve 3000A rating for the outgoing Cass County 115kV transmission line. | XEL | M2 - Appendix A Approved | 4800000 | 2032-06-01 | Substation | Substation bus upgrade | Red River |  |  | 115 |  |  |  | ND |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50903 | Substation - Sheyenne | Replace existing 230kV substation bus and equipment to achieve 3000A rating for the outgoing Fargo (WAPA) and Maple River 230kV transmission lines. | XEL | M2 - Appendix A Approved | 8500000 | 2032-06-01 | Substation | Substation bus upgrade | Sheyenne |  |  | 230 |  |  |  | ND |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50904 | Line: Sheyenne - Fargo (WAPA) - 230 kV | Replace existing Sheyenne - Fargo (WAPA) 230kV single-circuit transmission line with 230kV single-circuit structures to achieve 3000A rating. | XEL | M2 - Appendix A Approved | 9300000 | 2030-02-27 | Line Upgrade | Line rebuild on existing ROW | Sheyenne | Fargo (WAPA) |  | 230 |  | 0 | 5 | ND |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50905 | Substation - Fargo (WAPA) | Replace existing 230kV substation bus and equipment to achieve 3000A rating for the outgoing Sheyenne 230kV transmission line. | WAPA | M2 - Appendix A Approved |  | 2032-06-01 | Substation | Substation bus upgrade | Fargo (WAPA) |  |  | 230 |  |  |  | ND |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50906 | Line: Sheyenne - Maple River - 230 kV | Replace existing Sheyenne - Maple River 230kV single-circuit transmission line with 230kV single-circuit structures to achieve 3000A rating. | XEL | M2 - Appendix A Approved | 13400000 | 2030-02-27 | Line Upgrade | Line rebuild on existing ROW | Sheyenne | Maple River |  | 230 |  | 0 | 7 | ND |  | Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50907 | Line: Forman - Hankinson - 230 kV | Replace existing Forman - Hankinson 230kV single-circuit transmission line with 230kV single-circuit structures to achieve 2000A rating. | OTP | M2 - Appendix A Approved | 66500000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Forman | Hankinson |  | 230 |  | 0 | 37 | ND |  | Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50908 | Substation - Hankinson | Replace existing 230kV substation bus and equipment to achieve 2000A rating for the outgoing Forman 230kV transmission line. | OTP | M2 - Appendix A Approved | 1100000 | 2032-06-01 | Substation | Substation bus upgrade | Hankinson |  |  | 230 |  |  |  | ND |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50909 | Substation - Alexandria | Add 1-345kV line position (breaker-and-a-half bus). Add 1-345kV 50MVAr reactor connected to one of the 345kV busses. The reactor will have a dedicated breaker for switching. | MRES | M2 - Appendix A Approved | 8300000 | 2032-06-01 | Substation | Substation bus upgrade | Alexandria |  |  | 345 |  |  |  | MN |  | Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50553 | LRTP-20: Maple River - Cuyuna | MVP | 50910 | Substation - Maple River | Add one ring bus position to the existing four-position 345kV ring bus: 1) 345kV line to Cuyuna. Add 1-345kV 50MVAr line reactor with dedicated circuit breaker (for outgoing line to Cuyuna). Replace existing 230kV substation bus and equipment to achieve 3000A rating for the outgoing Sheyenne 230kV transmission line. | OTP | M2 - Appendix A Approved | 12400000 | 2033-06-01 | Substation | Substation bus upgrade | Maple River |  |  | 345 |  |  |  | ND |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50553 | LRTP-20: Maple River - Cuyuna | MVP | 50911 | Line: Maple River - ND/MN State Line - 345 kV | Construct new 345kV single-circuit transmission line on double-circuit-capable structures. Note: The structure design should allow for a Surge Impedance Loading (SIL) on the 345kV circuit of 550 MW or greater. | GRE, MP, OTP | M2 - Appendix A Approved | 29700000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | Maple River | ND/MN State Line |  | 345 |  | 6 | 0 | ND |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50553 | LRTP-20: Maple River - Cuyuna | MVP | 50912 | Line: ND/MN State Line - Cuyuna - 345 kV | Construct new 345kV single-circuit transmission line on double-circuit-capable structures. Note: The structure design should allow for a Surge Impedance Loading (SIL) on the 345kV circuit of 550MW or greater. | GRE, MP, OTP | M2 - Appendix A Approved | 1038900000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | ND/MN State Line | Cuyuna |  | 345 |  | 160 | 0 | MN |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50553 | LRTP-20: Maple River - Cuyuna | MVP | 50913 | Substation - Cuyuna | Add 1-345kV line position (breaker-and-a-half bus). Add 1-345kV 50MVAr reactor connected to one of the 345kV busses. The reactor will have a dedicated breaker for switching. | MP | M2 - Appendix A Approved | 12800000 | 2033-06-01 | Substation | Substation bus upgrade | Cuyuna |  |  | 345 |  |  |  | MN |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50914 | Substation - Iron Range | Add 1-345kV line position to the existing 345kV breaker-and-a-half bus: 1) New 345kV line to St. Louis County substation. | MP | M2 - Appendix A Approved | 7200000 | 2032-06-01 | Substation | Substation bus upgrade | Iron Range |  |  | 345 |  |  |  | MN |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50915 | Line: Iron Range - St. Louis County - 345 kV | Construct new 345kV single-circuit transmission line on double-circuit-capable structures. | MP | M2 - Appendix A Approved | 377200000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Iron Range | St. Louis County |  | 345 |  | 62 | 0 | MN |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50916 | Substation - St. Louis County | Replace the existing two-position straight bus with 5-345kV breaker-and-a-half positions: 1) Existing HVDC Pole 1, 2) Existing 345kV line to the 230kV substation, 3) New 345kV line to Iron Range, 4) New 345kV line to Arrowhead #1, 5) New 345kV line to Arrowhead #2. | MP | M2 - Appendix A Approved | 31400000 | 2032-06-01 | Substation | Substation bus upgrade | St. Louis County |  |  | 345 |  |  |  | MN |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50917 | Line: St. Louis County - Arrowhead - 345 kV | Construct new 345kV double-circuit transmission line. | ATC, MP | M2 - Appendix A Approved | 12000000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | St. Louis County | Arrowhead |  | 345 |  | 1 | 0 | MN |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50918 | Substation - Arrowhead | Add 2-345kV line positions and convert the existing 345kV ring bus to a five-position breaker-and-a-half arrangement: 1) Existing 345kV line to the 230kV substation, 2) Existing 345kV line to Stone Lake, 3) Existing 345kV capacitor banks, 4) New 345kV line to St. Louis County #1, 5) New 345kV line to St. Louis County #2. Decommission the 230kV phase shifter and bypass around it to maintain the 230kV connection to the existing 345/230kV transformer. | ATC | M2 - Appendix A Approved | 12600000 | 2032-06-01 | Substation | Substation bus upgrade | Arrowhead |  |  | 345 |  |  |  | MN |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50919 | Substation - Stinson | Add four-position 115kV ring bus with the following positions: 1) 115kV line termination for the series connected 115kV Modular Static Synchronous Series Compensator (MSSSC) on the Stinson line, 2) 115kV line termination for the 187MVA 161/115kV transformer on the Gordon 161kV line termination, 3) 115kV Bayfront line termination, 4) 115kV line termination for the MSSSC bypass line to Stinson. Replace existing 161/115kV transformer with a 187 MVA unit (234 MVA emergency rating). Upgrade 115kV connection between Stinson and expanded Stinson bus. Rebuild two existing breaker positions to 1200A for connections to expanded Stinson 115kV bus. Decommission and remove existing Stinson 115kV phase shifting transformer. The anticipated MSSSC minimum emergency rating is 232MVA. | MP | M2 - Appendix A Approved | 54700000 | 2032-06-01 | Misc. | Phase angle regulating transformer (phase shifter) | Stinson |  |  | 115 |  |  |  | WI |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50920 | Line: Stinson - 161 kV | Modify the existing Stone Lake 161kV line by constructing structures to relocate the line termination into the expanded Stinson bus. Minimum emergency rating to match the 161/115kV transformer rating. | MP | M2 - Appendix A Approved | 1800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Stinson |  |  | 161 |  |  |  | WI |  | Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 50554 | LRTP-21: Iron Range - Arrowhead | MVP | 50921 | Line: Stinson - 115 kV | Modify the existing Stinson - Bayfront 115kV line by constructing structures to relocate the line termination into the expanded Stinson bus. | MP | M2 - Appendix A Approved | 1700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Stinson |  |  | 115 |  |  |  | WI |  | Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 50555 | LRTP-22: Big Stone South - Brookings County - Lakefield Junction | MVP | 50922 | Transformer - Big Stone South | Add a single 765kV breaker between two bus positions. The two positions are: 1) New 765kV transmission line to Brookings County, 2) 765/345kV 2250MVA transformer #1. Note: All of these positions have a minimum 4000A rating. Add 1-765/345kV 2250MVA transformer. Add 1-765kV 300MVAr line reactor with dedicated circuit breaker (for outgoing line to Brookings County). Add 1-345kV double-breaker, double-bus line position: 1) 765/345kV 2250MVA transformer #1. Note: This position has a minimum 4000A rating. Include one single-phase spare 765/345kV transformer, and one single-phase spare 765kV reactor. | OTP | M2 - Appendix A Approved | 165700000 | 2034-06-01 | Transformer | Transformer New | Big Stone South |  |  | 765 | 345 |  |  | SD |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50555 | LRTP-22: Big Stone South - Brookings County - Lakefield Junction | MVP | 50923 | Line: Big Stone South - Brookings County - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | OTP, XEL | M2 - Appendix A Approved | 310100000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Big Stone South | Brookings County |  | 765 |  | 65 | 0 | SD |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50555 | LRTP-22: Big Stone South - Brookings County - Lakefield Junction | MVP | 50924 | Transformer - Brookings County | Add 3-765kV double-breaker, double-bus line positions: 1) New 765kV transmission line to Big Stone South, 2) New 765kV transmission line to Lakefield Junction, 3) 765/345kV 2250MVA transformer. Note: All of these positions have a minimum 4000A rating. Add 1-765/345kV 2250MVA transformer. Add 2-765kV 300MVAr line reactor with dedicated circuit breaker (for each outgoing line to Big Stone South and Lakefield Junction). Add 1-345kV double-breaker, double-bus line position: 1) 765/345kV 2250MVA transformer connection. Note: This position has a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). Replace the existing 345/115kV 448MVA transformer 9 & 345/115kV 448MVA transformer 10 with 2-345/115kV 672MVA transformers. Replace existing 115kV substation ring bus and equipment to achieve 3000A rating and breaker-and-a-half bus arrangement. | XEL | M2 - Appendix A Approved | 196500000 | 2034-06-01 | Transformer | Transformer New | Brookings County |  |  | 765 | 115 |  |  | SD |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50555 | LRTP-22: Big Stone South - Brookings County - Lakefield Junction | MVP | 50925 | Line: Brookings County - SD/MN State Line - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | ITCM, XEL | M2 - Appendix A Approved | 51200000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Brookings County | SD/MN State Line |  | 765 |  | 11 | 0 | SD |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50555 | LRTP-22: Big Stone South - Brookings County - Lakefield Junction | MVP | 50926 | Line: SD/MN State Line - Lakefield Junction - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | ITCM, XEL | M2 - Appendix A Approved | 582000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | SD/MN State Line | Lakefield Junction |  | 765 |  | 92 | 0 | MN |  | Shared
MTEP24 | A | ITC MIDWEST | West | 50555 | LRTP-22: Big Stone South - Brookings County - Lakefield Junction | MVP | 50927 | Transformer - Lakefield Junction | Add 5-765kV double-breaker, double-bus line positions: 1) New 765kV transmission line to Brookings, 2) New 765kV transmission line to Pleasant Valley, 3) New 765kV transmission line to the MN/IA State Border (East Adair), 4) 765/345kV 2250MVA transformer #1, 5) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Add 2-765/345kV 2250MVA transformers. Add 3-765kV 300MVAr line reactor with dedicated circuit breaker (for each outgoing line to Brookings, Pleasant Valley, and MN/IA State Border (East Adair)). Add 2-345kV double-breaker, double-bus line positions: 1) 765/345kV 2250MVA transformer #1, 2) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include three single-phase spare 765kV reactors (one for each outgoing line). | ITCM | M2 - Appendix A Approved | 433984746 | 2034-06-01 | Transformer | Transformer New | Lakefield Junction |  |  | 765 | 345 |  |  | MN |  | Shared
MTEP24 | A | ITC MIDWEST | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50928 | Line: Lakefield Junction - MN/IA State Line - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | ITCM | M2 - Appendix A Approved | 115256769 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Lakefield Junction | MN/IA State Line |  | 765 |  | 18 | 0 | MN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50929 | Line: MN/IA State Line - East Adair - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 874100000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | MN/IA State Line | East Adair |  | 765 |  | 173 | 0 | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50930 | Transformer - East Adair | Construct new four-position 765kV double-breaker, double-bus and seven-position 345kV breaker-and-a-half bus substation. 765kV bus positions: 1) New 765kV transmission line to MN/IA State Border (Lakefield Junction), 2) New 765kV transmission line to Marshalltown (Twinkle), 3) 765/345kV 2250MVA transformer #1, 4) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. 345kV breaker-and-a-half bus positions: 1) New 345kV transmission line to Arbor Hill, 2) Cut-in to existing 345kV Booneville - Southern Hills transmission line #1, 3) Cut-in to existing 345kV Booneville - Southern Hills transmission line #2, 4) Cut-in to existing 345kV Orient - Madison County transmission line #1, 5) Cut-in to existing 345kV Orient - Madison County transmission line #2. Note: All of these positions have a minimum 3000A rating. 345kV double-breaker, double-bus positions: 6) 765/345kV 2250MVA transformer #1, 7) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Install 2-765/345kV 2250MVA transformers. Install 2-765kV 300MVAr line reactor with dedicated circuit breaker (for each outgoing line to MN/IA State Border (Lakefield Junction) and Marshalltown (Twinkle)). Install 1-345kV 50MVAr shunt reactor with dedicated breaker connected to one of the 345kV busses. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 241500000 | 2034-06-01 | Transformer | Transformer New | East Adair |  |  | 765 | 345 |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50931 | Line: East Adair - 345 kV | Modify the existing Booneville - Southern Hills 345kV single-circuit line by constructing transmission structures to cut-in the Booneville - Southern 345kV line into the East Adair substation. | MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | East Adair |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50932 | Line: Orient - Deadend East of York Avenue - 345 kV | Replace existing single-circuit 345kV structures and conductors with single-circuit 345kV structures that are capable of 1792 MVA from Orient to within approximately 0.2 miles of the intersection of York Avenue and the existing Orient - Madison County 345kV line. The structures being replaced are part of the existing Orient - Madison County 345kV line. | MEC | M2 - Appendix A Approved | 22200000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Orient | Deadend East of York Avenue |  | 345 |  | 0 | 8 | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50933 | Line: Deadend East of York Avenue - East Adair - 345 kV | Construct new 345kV double-circuit transmission line from within approximately 0.2 miles of the intersection of York Avenue and the existing Orient - Madison County 345kV line. One circuit is to cut-in the existing Orient - Madison County 345kV line into the East Adair substation. The other circuit is part of the Orient - East Adair 345kV line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved |  | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Deadend East of York Avenue | East Adair |  | 345 |  | 7 | 0 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50934 | Line: Southern Hills - East Adair - 345 kV | Replace existing single-circuit 345kV structures and conductors with single-circuit 345kV structures that are capable of 1792 MVA. The structures being replaced are part of the existing Southern Hills - Booneville 345kV line. | MEC | M2 - Appendix A Approved | 28300000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Southern Hills | East Adair |  | 345 |  | 0 | 10 | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50935 | Line: East Adair - Arbor Hill - 345 kV | Construct new 345kV single-circuit transmission line on double-circuit-capable structures. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 73800000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | East Adair | Arbor Hill |  | 345 |  | 14 | 0 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50556 | LRTP-23: Lakefield Junction - East Adair | MVP | 50936 | Substation - Arbor Hill | Add 1-345kV line position (ring bus). | MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Substation | Substation bus upgrade | Arbor Hill |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 50557 | LRTP-24: Lakefield Junction - Pleasant Valley - North Rochester | MVP | 50937 | Line: Lakefield Junction - Pleasant Valley - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | GRE, ITCM | M2 - Appendix A Approved | 813000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Lakefield Junction | Pleasant Valley |  | 765 |  | 130 | 0 | MN |  | Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 50557 | LRTP-24: Lakefield Junction - Pleasant Valley - North Rochester | MVP | 50938 | Transformer - Pleasant Valley | Add 3-765kV double-breaker, double-bus line positions: 1) New 765kV transmission line to Lakefield Junction, 2) New 765kV transmission line to North Rochester, 3) 765/345kV 2250MVA transformer. Note: All of these positions have a minimum 4000A rating. Add 1-765/345kV 2250MVA transformer. Add 2-765kV 300MVAr line reactor with dedicated circuit breaker (for each outgoing line to Lakefield Junction and North Rochester). Replace the existing four-position ring bus with a six-position breaker-and-a-half bus arrangement: 1) Existing 345/161kV transformer #1, 2) Existing 345/161kV transformer #2, 3) Existing 345kV transmission line to Adams, 4) Existing 345kV transmission line to Byron, 5) New 345kV transmission line to North Rochester, Note: These positions have a minimum 3000A rating. Add 1-345kV double-breaker, double-bus line position: 6) 765/345kV 2250MVA transformer. Note: This position has a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). Re-terminate the existing Byron 345kV line and the existing Adams 345kV line. | GRE | M2 - Appendix A Approved | 393000000 | 2034-06-01 | Transformer | Transformer New | Pleasant Valley |  |  | 765 | 345 |  |  | MN |  | Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 50557 | LRTP-24: Lakefield Junction - Pleasant Valley - North Rochester | MVP | 50939 | Line: Pleasant Valley - North Rochester - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | GRE, XEL | M2 - Appendix A Approved | 196000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Pleasant Valley | North Rochester |  | 765 |  | 31 | 0 | MN |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50557 | LRTP-24: Lakefield Junction - Pleasant Valley - North Rochester | MVP | 50940 | Transformer - North Rochester | Add 3-765kV double-breaker, double-bus line positions: 1) New 765kV transmission line to Pleasant Valley, 2) New 765kV transmission line to MN/WI State Border (Columbia), 3) 765/345kV 2250MVA transformer. Note: All of these positions have a minimum 4000A rating. Add 1-765/345kV 2250MVA transformer. Add 2-765kV 300MVAr line reactor with dedicated circuit breaker (for each outgoing line to Pleasant Valley and MN/WI State Border (Columbia). Add 1-345kV double-breaker, double-bus line position: 1) 765/345kV 2250MVA transformer. Note: This position has a minimum 4000A rating. Add 2-345kV breaker-and-a-half bus line positions: 1) New 345kV transmission to Hampton, 2) New 345kV transmission line to Pleasant Valley. Note: All of these positions have a minimum 3000A rating. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). | XEL | M2 - Appendix A Approved | 553000000 | 2034-06-01 | Transformer | Transformer New | North Rochester |  |  | 765 | 345 |  |  | MN |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50558 | LRTP-25: Pleasant Valley - North Rochester - Hampton Corner | MVP | 50941 | Line: Pleasant Valley - North Rochester - 345 kV | Replace existing single-circuit 345kV structures with double-circuit structures with two circuits operating at 345kV**. | XEL | M2 - Appendix A Approved | 160000000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Pleasant Valley | North Rochester |  | 345 |  | 0 | 31 | MN |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50558 | LRTP-25: Pleasant Valley - North Rochester - Hampton Corner | MVP | 50942 | Substation - Hampton Corner | Add 1-345kV line position (breaker-and-a-half bus). | XEL | M2 - Appendix A Approved | 7000000 | 2032-06-01 | Substation | Substation bus upgrade | Hampton Corner |  |  | 345 |  |  |  | MN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50943 | Line: North Rochester - Existing 161kV Line Near Marion - 765 kV | Construct new 765kV single-circuit transmission line from North Rochester to the existing Rochester - Adams 161kV line within approximately two miles of Marion. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | DPC, XEL | M2 - Appendix A Approved | 175000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | North Rochester | Existing 161kV Line Near Marion |  | 765 |  | 34 | 0 | MN |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50944 | Line: Existing 161kV Line Near Marion - Existing 161kV Line Near Adams - 765 kV | Replace existing single-circuit 161kV structures from within approximately two miles of Marion to Adams with double-circuit structures that have one underbuilt circuit operating at 161kV and one circuit operating at 765kV**. The structures being replaced are part of the existing Rochester - Adams 161kV line. Note: Structure design should allow a minimum Surge Impedance Loading (SIL) of 2400 MW. | DPC | M2 - Appendix A Approved | 195100000 | 2034-06-01 | Line Upgrade | Line rebuild on existing ROW | Existing 161kV Line Near Marion | Existing 161kV Line Near Adams |  | 765 | 161 | 0 | 32 | MN |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50945 | Line: Existing 161kV Line Near Adams - MN/WI State Line (Existing Genoa River Crossing) - 765 kV | Replace existing single-circuit 161kV structures from Adams to the existing Mississippi River crossing at Genoa with double-circuit structures that have one underbuilt circuit operating at 161kV and one circuit operating at 765kV**. The structures being replaced are part of the existing Adams - Genoa 161kV line. Note: Structure design should allow a minimum Surge Impedance Loading (SIL) of 2400 MW. | DPC | M2 - Appendix A Approved | 444900000 | 2034-06-01 | Line Upgrade | Line rebuild on existing ROW | Existing 161kV Line Near Adams | MN/WI State Line (Existing Genoa River Crossing) |  | 765 | 161 | 0 | 73 | MN |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50946 | Line: Beaver Creek - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | DPC | M2 - Appendix A Approved | 1800000 | 2034-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Beaver Creek |  |  | 161 |  |  |  | MN |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50947 | Line: Harmony - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | DPC | M2 - Appendix A Approved | 4100000 | 2034-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Harmony |  |  | 161 |  |  |  | MN |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50948 | Line: MN/WI State Line (Existing Genoa River Crossing) - Existing 161kV Line Near Bell Center - 765 kV | Replace existing single-circuit 161kV structures from Genoa to Bell Center to Hillsboro with double-circuit structures that have one underbuilt circuit operating at 161kV and one circuit operating at 765kV**. The structures being replaced are part of the existing Genoa - Bell Center and Bell Center - Hillsboro 161kV lines. Note: Structure design should allow a minimum Surge Impedance Loading (SIL) of 2400 MW. | DPC | M2 - Appendix A Approved | 238700000 | 2034-06-01 | Line Upgrade | Line rebuild on existing ROW | MN/WI State Line (Existing Genoa River Crossing) | Existing 161kV Line Near Bell Center |  | 765 | 161 | 0 | 34 | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50949 | Line: Existing 161kV Line Near Bell Center - Columbia - 765 kV | Construct new 765kV single-circuit transmission line from Bell Center to Columbia substation. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 520176758 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Existing 161kV Line Near Bell Center | Columbia |  | 765 |  | 100 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50950 | Transformer - Columbia | Add 4-765kV double-breaker, double-bus line positions: 1) New 765kV transmission line to MN/WI State Border (North Rochester), 2) New 765kV transmission line to Sugar Creek, 3) 765/345kV 2250MVA transformer #1, 4) 765/345kV 2250 MVA #2. Note: All of these positions have a minimum 4000A rating. Add 2-765/345kV 2250MVA transformers. Add 2-765kV 300MVAr line reactors with dedicated circuit breaker on the outgoing line to MN/WI State Border (North Rochester). Add 1-765kV 300MVAr line reactor with dedicated circuit breaker on the outgoing line to Sugar Creek. Add 1-765kV 300MVAr line reactor with dedicated circuit breaker on the bus. Add 2-345kV double-breaker, double-bus line positions: 1) 765/345kV 2250MVA transformer connection, 2) 765/345kV 2250MVA transformer connection. Note: All of these positions have a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include three single-phase spare 765kV reactors (one for each reactor bank). | ATC | M2 - Appendix A Approved | 280200000 | 2034-06-01 | Transformer | Transformer New | Columbia |  |  | 765 | 345 |  |  | WI |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50951 | Line: Genoa - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | DPC | M2 - Appendix A Approved | 4400000 | 2034-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Genoa |  |  | 161 |  |  |  | WI |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50952 | Line: Seneca - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | DPC | M2 - Appendix A Approved | 4400000 | 2034-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Seneca |  |  | 161 |  |  |  | WI |  | Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 50559 | LRTP-26: North Rochester - Columbia | MVP | 50953 | Line: Bell Center - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | DPC | M2 - Appendix A Approved | 4400000 | 2034-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Bell Center |  |  | 161 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50560 | LRTP-27: Rocky Run - Werner - North Appleton | MVP | 50954 | Substation - Rocky Run | Replace existing 345kV substation bus and equipment to achieve 3000A rating for the outgoing Werner West 345kV transmission line. | ATC | M2 - Appendix A Approved | 3100000 | 2032-06-01 | Substation | Substation bus upgrade | Rocky Run |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50560 | LRTP-27: Rocky Run - Werner - North Appleton | MVP | 50955 | Line: Rocky Run - East of US 45 - 345 kV | Replace existing Rocky Run - Werner West 345kV single-circuit transmission line with new 345kV single-circuit structures to achieve 3000A rating. | ATC | M2 - Appendix A Approved | 135400000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Rocky Run | East of US 45 |  | 345 |  | 0 | 46 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50560 | LRTP-27: Rocky Run - Werner - North Appleton | MVP | 50956 | Line: East of US 45 - Werner West - 345 kV | Replace existing double-circuit 345/138kV structures that are part of the Rocky Run - Werner West transmission line with 345/138kV double-circuit structures to achieve 3000A rating for the 345kV circuit. | ATC | M2 - Appendix A Approved | 12000000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | East of US 45 | Werner West |  | 345 |  | 0 | 2 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50560 | LRTP-27: Rocky Run - Werner - North Appleton | MVP | 50957 | Substation - Werner West | Replace existing 345kV substation bus and equipment to achieve 3000A rating for the 345kV ring bus, the Rocky Run 345kV line termination, and the North Appleton 345kV line termination. | ATC | M2 - Appendix A Approved | 2000000 | 2032-06-01 | Substation | Substation bus upgrade | Werner West |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50560 | LRTP-27: Rocky Run - Werner - North Appleton | MVP | 50958 | Line: Werner West - North Appleton - 345 kV | Replace existing Werner West - North Appleton 345kV single-circuit transmission line with 345kV single-circuit structures to achieve 3000A rating. | ATC | M2 - Appendix A Approved | 58600000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Werner West | North Appleton |  | 345 |  | 0 | 20 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50560 | LRTP-27: Rocky Run - Werner - North Appleton | MVP | 50959 | Substation - North Appleton | Replace existing 345kV substation bus and equipment to achieve 3000A rating. | ATC | M2 - Appendix A Approved |  | 2032-06-01 | Substation | Substation bus upgrade | North Appleton |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50960 | Substation - South Fond du Lac | Add one line position to the existing 345kV ring bus: 1) 345kV line to Jefferson. | ATC | M2 - Appendix A Approved | 2500000 | 2033-06-01 | Substation | Substation bus upgrade | South Fond du Lac |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50961 | Line: South Fond du Lac - Jefferson - 345 kV | Construct new 345kV single-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 230500000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | South Fond du Lac | Jefferson |  | 345 |  | 66 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50962 | Substation - Jefferson | Add 4-345kV ring bus positions: 1) New 345kV line to Rockdale, 2) New 345kV line to South Fond du Lac, 3) New 345kV line to Sugar Creek, 4) 80MVar 345kV shunt reactor with a dedicated breaker for switching. | ATC | M2 - Appendix A Approved | 16700000 | 2033-06-01 | Substation | Substation bus upgrade | Jefferson |  |  | 345 | 138 |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50963 | Line: Jefferson - Rockdale - 345 kV | Replace the existing single-circuit 138kV structures with double-circuit structures with one circuit operating at 138kV and one circuit operating at 345kV**. | ATC | M2 - Appendix A Approved | 67200000 | 2033-06-01 | Line Upgrade | Line rebuild on existing ROW | Jefferson | Rockdale |  | 345 | 138 | 0 | 12 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50964 | Substation - Rockdale | Add 1-345kV line position (breaker-and-a-half bus). | ATC | M2 - Appendix A Approved | 4200000 | 2033-06-01 | Substation | Substation bus upgrade | Rockdale |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50965 | Line: Jefferson - Fort Atkinson - 345 kV | Replace existing single-circuit 138kV structures with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. The structures being replaced are part of the existing Jefferson – Fort Atkinson 138kV Line 6631. | ATC | M2 - Appendix A Approved | 24900000 | 2033-06-01 | Line Upgrade | Line rebuild on existing ROW | Jefferson | Fort Atkinson |  | 345 | 138 | 0 | 5 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50966 | Line: Fort Atkinson - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Fort Atkinson |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50967 | Line: Whitewater - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Whitewater |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50968 | Line: Fort Atkinson - Whitewater - 345 kV | Construct new 345kV single-circuit transmission line (constructed with 345/138kV double-circuit capable structures) from Fort Atkinson substation to approximately one mile west of Whitewater substation. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 74000000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | Fort Atkinson | Whitewater |  | 345 |  | 14 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50969 | Line: Whitewater - Sugar Creek - 345 kV | Replace existing single-circuit 138kV structures from approximately one mile west of Whitewater substation to Sugar Creek substation with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. The structures being replaced are part of the existing Sunrise – Whitewater 138kV Line 4434 and Whitewater – Sugar Creek 138kV Line WHIG53. | ATC | M2 - Appendix A Approved | 65500000 | 2033-06-01 | Line Upgrade | Line rebuild on existing ROW | Whitewater | Sugar Creek |  | 345 | 138 | 0 | 13 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50970 | Line: Whitewater - Guardian Tap - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Whitewater | Guardian Tap |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50971 | Line: Whitewater - Bluff Creek Tap - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Whitewater | Bluff Creek Tap |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50972 | Substation - Big Bend | Construct new six-position breaker-and-a-half bus substation: 1) New 345kV transmission line #1 to Sugar Creek, 2) New 345kV transmission line #2 to Sugar Creek, 3) Cut-in to existing Arcadian - Paris 345kV transmission line #1, 4) Cut-in to existing Arcadian - Paris 345kV transmission line #2, 5) Cut-in to existing Arcadian - Pleasant Prairie 345kV transmission line #1, 6) Cut-in to existing Arcadian - Pleasant Prairie 345kV transmission line #2. The location of the substation is within approximately one mile of the existing Mukonago - Edgewood 138kV and Arcadian - Paris and Arcadian Pleasant Prairie double-circuit 345kV crossing. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 26800000 | 2033-06-01 | Substation | Substation (breakers only, no transformer) | Big Bend |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50973 | Line: Big Bend - 345 kV | Modify the existing Arcadian - Paris and Arcadian - Pleasant Prairie double-circuit 345kV transmission lines to construct transmission structures to cut-in the existing Arcadian - Paris and Arcadian - Pleasant Prairie 345kV lines into the Big Bend substation. | ATC | M2 - Appendix A Approved | 13300000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Big Bend |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50974 | Line: Big Bend - Sugar Creek - 345 kV | Construct new 345kV double-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 140100000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | Big Bend | Sugar Creek |  | 345 |  | 24 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50975 | Line: Sugar Creek - Paris - 345 kV | Replace existing 138kV single-circuit structures on the Sugar Creek - North Lake Geneva Tap, North Lake Geneva Tap - Burlington, Burlington - Air Liquide Tap, and Air Liquide Tap - Paris 138kV lines with double-circuit structures with one circuit operated at 138kV and one circuit operating at 345kV**. | ATC | M2 - Appendix A Approved | 160700000 | 2033-06-01 | Line Upgrade | Line rebuild on existing ROW | Sugar Creek | Paris |  | 345 | 138 | 0 | 29 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50976 | Line: North Lake Geneva Tap - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1800000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | North Lake Geneva Tap |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50977 | Line: Burlington - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 4100000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Burlington |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50978 | Line: Air Liquide Tap - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1800000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Air Liquide Tap |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50979 | Substation - Paris | Add 3-345kV breaker-and-a-half positions: 1) New 345kV transmission line to Sugar Creek, 2) Cut-in #1 to Arcadian - Pleasant Prairie 345kV transmission line, 3) Cut-in #2 to Arcadian - Pleasant Prairie 345kV transmission line. | ATC | M2 - Appendix A Approved | 11900000 | 2033-06-01 | Substation | Substation bus upgrade | Paris |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50980 | Line: Paris - 345 kV | Modify existing Arcadian - Pleasant Prairie single-circuit 345kV transmission line to construct transmission structures to cut-in existing Arcadian - Pleasant Prairie 345kV transmission line into Paris Substation. | ATC | M2 - Appendix A Approved | 7200000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Paris |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50981 | Line: Sugar Creek - REC Bradford - 345 kV | Construct new 345kV single-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 55700000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | Sugar Creek | REC Bradford |  | 345 | 138 | 16 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50982 | Line: REC Bradford - Kitty Hawk - 345 kV | Replace existing single-circuit 138kV structures with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. The structures being replaced are part of the existing Rock River – Colley Road 138kV Line X-23 and Rock River – North Creek 138kV Line X-79. | ATC | M2 - Appendix A Approved | 84400000 | 2033-06-01 | Line Upgrade | Line rebuild on existing ROW | REC Bradford | Kitty Hawk |  | 345 |  | 0 | 16 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50983 | Line: Rock River - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Rock River |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50984 | Line: REC La Prairie - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | REC La Prairie |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50985 | Line: REC Bradford - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | ATC | M2 - Appendix A Approved | 1900000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | REC Bradford |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50986 | Substation - Kitty Hawk | Add 1-345kV breaker-and-a-half bus position: 1) 345kV line to Sugar Creek. | ATC | M2 - Appendix A Approved | 4200000 | 2033-06-01 | Substation | Substation bus upgrade | Kitty Hawk |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50987 | Substation - Sheboygan River | Construct a new 345kV four-position ring bus within approximately one mile of the existing Cypress - Arcadian and South Fond du Lac - Edgewater 345kV crossing. Expand the four-position ring bus to a five-position breaker-and-a-half bus by adding one position to support the Expedited Project Request (MTEP Project ID 51057) | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 13900000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Sheboygan River |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50988 | Line: Sheboygan River - 345 kV | Modify the existing South Fond du Lac - Edgewater single-circuit 345kV transmission line by constructing transmission structures to cut-in the existing South Fond du Lac - Edgewater 345kV line into the Sheboygan River substation. | ATC | M2 - Appendix A Approved | 7200000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sheboygan River |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50989 | Line: Sheboygan River - 345 kV | Modify the existing Cypress - Arcadian single-circuit 345kV transmission line by constructing transmission structures to cut-in the existing Cypress - Arcadian 345kV line into the Sheboygan River substation. | ATC | M2 - Appendix A Approved | 7200000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sheboygan River |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50990 | Substation - Mullet River Junction | Construct a new 345kV four-position ring bus within approximately one mile of the existing South Fond du Lac - Edgewater and Granville - Sheboygan Falls Energy Center 345kV crossing. Expand the four-position ring bus to a seven-position breaker-and-a-half bus by adding three positions to support the Expedited Project Request (MTEP Project ID 51057). | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 13400000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Mullet River Junction |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50991 | Line: Mullet River Junction - 345 kV | Modify the existing South Fond du Lac - Edgewater single-circuit 345kV transmission line by constructing transmission structures to cut-in the existing South Fond du Lac - Edgewater 345kV line into the Mullet River Junction substation. | ATC | M2 - Appendix A Approved | 7200000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mullet River Junction |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50992 | Line: Mullet River Junction - 345 kV | Modify the existing Sheboygan Falls - Granville single-circuit 345kV transmission line by constructing transmission structures to cut-in the existing Sheboygan Falls - Granville 345kV line into the Mullet River Junction substation. | ATC | M2 - Appendix A Approved | 7200000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mullet River Junction |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50993 | Substation - Cedar Creek Junction | Construct a new 345kV four-position ring bus within approximately one mile of where the existing Granville - Sheboygan Falls Energy Center 345kV line and Arcadian - Cypress 345kV line attach to a common structure. Expand the four-position ring bus to a five-position breaker-and-a-half bus by adding one position to support the Expedited Project Request (MTEP Project ID 51057). | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 13900000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Cedar Creek Junction |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50994 | Line: Cedar Creek Junction - 345 kV | Modify the existing Cypress - Arcadian single-circuit 345kV transmission line by constructing transmission structures to cut-in the existing Cypress - Arcadian 345kV line into the Cedar Creek Junction substation. | ATC | M2 - Appendix A Approved | 10500000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Cedar Creek Junction |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50561 | LRTP-28: South Fond du Lac - Rockdale - Big Bend - Sugar Creek - Kitty Hawk | MVP | 50995 | Line: Cedar Creek Junction - 345 kV | Modify the existing Sheboygan Falls - Granville single-circuit 345kV transmission line by constructing transmission structures to cut-in the existing Sheboygan Falls - Granville 345kV line into the Cedar Creek Junction substation. | ATC | M2 - Appendix A Approved | 10500000 | 2033-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Cedar Creek Junction |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 50996 | Substation - Granville | Replace existing six-position 345kV ring bus with a seven-position 345kV breaker-and-a-half bus arrangement: 1) New 345kV transmission line to Bluemound, 2) Existing 345kV transmission line to Saukville, 3) Existing 345kV line to Mill Road, 4) Existing planned 345kV line to Mill Road, 5) Existing 345kV line to Sheboygan Falls Energy Center, 6) Existing 345/138kV transformer, 7) Existing 345/138kV transformer. Upgrade the existing 138kV Butler line termination to 2000A. Remove the existing 138kV Tosa line termination. | ATC | M2 - Appendix A Approved | 13300000 | 2032-06-01 | Substation | Substation bus upgrade | Granville |  |  | 345 | 138 |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 50997 | Line: Granville - Deadend for Butler/Tosa/Tamarack Tap - 345 kV | Replace existing double-circuit 138kV structures with double-circuit 345/138kV structures. This section is approximately the first three miles out of Granville. There is an approximately one-mile section along this route where the 138kV line will be underground and the 345kV line will be on single-circuit compact towers. | ATC | M2 - Appendix A Approved | 42500000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Granville | Deadend for Butler/Tosa/Tamarack Tap |  | 345 | 138 | 0 | 3 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 50998 | Substation - Butler | Upgrade two 138kV line terminations and breakers to achieve an emergency rating of 2000A or greater. Remove three 138kV line terminations. | ATC | M2 - Appendix A Approved | 4900000 | 2032-06-01 | Substation | Substation bus upgrade | Butler |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 50999 | Substation - Tosa | Replace two existing 138kV line terminations, substation bus, and substation equipment to achieve 2000A rating. Reconfigure substation so that both 138kV line terminations leave to the north. | ATC | M2 - Appendix A Approved | 7000000 | 2032-06-01 | Substation | Substation bus upgrade | Tosa |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51000 | Line: Deadend for Butler/Tosa/Tamarack Tap - Butler - 345 kV | Replace existing 138kV double-circuit structures from south of deadend to Butler with 345/138kV double-circuit high-capacity structures with one circuit operating at 138kV and one circuit operating at 345kV**. The 138kV circuit should have an emergency rating of 2000A or greater. | ATC | M2 - Appendix A Approved | 9800000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Deadend for Butler/Tosa/Tamarack Tap | Butler |  | 345 | 138 | 0 | 2 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51001 | Line: Butler - Structure 4271 - 345 kV | Replace existing triple-circuit 138kV structures from Butler south to Structure 4271 with 345/138kV double-circuit high-capacity structures with one circuit operating at 138kV and one circuit operating at 345kV**. The 138kV circuit should have an emergency rating of 2000A or greater. | ATC | M2 - Appendix A Approved | 4000000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Butler | Structure 4271 |  | 345 | 138 | 0 | 1 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51002 | Line: Structure 4271 - Line 5401 - 345 kV | Construct new 345/138kV double-circuit transmission line from Structure 4271 south to 138kV Line 5401. | ATC | M2 - Appendix A Approved | 21500000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Structure 4271 | Line 5401 |  | 345 | 138 | 4 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51003 | Line: Line 5401 - Bluemound - 345 kV | Replace existing 138kV Line 5041 from Bluemound to the intersection with new 345/138kV line with double-circuit 345/138kV structures. | ATC | M2 - Appendix A Approved | 10900000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Line 5401 | Bluemound |  | 345 | 138 | 0 | 2 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51004 | Substation - Bluemound | Decommission the 230kV bus and add 345kV five-position ring bus. Positions will be occupied by three 345kV lines and two transformers including: 1) New 345kV transmission line to Granville, 2) New 345kV transmission line to Elm Road, 3) New 345kV transmission line to Arcadian, 4) 345/138kV, 560MVA transformer #1, 5) 345/138kV, 560 MVA transformer #2. Replace three 230/138kV transformers with two 345/138kV 560 MVA transformers. Upgrade one 138kV termination to 2000A. Remove all 230kV equipment (two lines and three transformers) and remove two 138kV line terminations. | ATC | M2 - Appendix A Approved | 44600000 | 2032-06-01 | Substation | Substation bus upgrade | Bluemound |  |  | 345 | 138 |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51005 | Line: Bluemound - Deadend for Triple-Circuit South of Bluemound - 345 kV | Decommission existing 230/230/138kV triple-circuit structures and construct a new line of double-circuit 345kV structures. | ATC | M2 - Appendix A Approved | 13000000 | 2030-04-30 | Line New | New Transmission line, new ROW - may include terminations | Bluemound | Deadend for Triple-Circuit South of Bluemound |  | 345 |  | 2 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51006 | Line: Deadend for Triple-Circuit South of Bluemound - Elm Road - 345 kV | Replace existing 230/138kV structures with double-circuit structures with one circuit operating at 138kV and one circuit operating at 345kV to achieve 3000A rating**. | ATC | M2 - Appendix A Approved | 137900000 | 2030-04-30 | Line Upgrade | Line rebuild on existing ROW | Deadend for Triple-Circuit South of Bluemound | Elm Road |  | 345 |  | 0 | 27 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51007 | Line: Deadend for Triple-Circuit South of Bluemound - Arcadian - 345 kV | Replace existing 230/138kV double-circuit structures with double-circuit structures with the existing 2156 ACSR 138kV conductor transferred and retained and one circuit operating at 345kV**. | ATC | M2 - Appendix A Approved | 34400000 | 2030-04-30 | Line Upgrade | Line rebuild on existing ROW | Deadend for Triple-Circuit South of Bluemound | Arcadian |  | 345 | 138 | 0 | 6 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51008 | Line: Arcadian - 345 kV | Modify the existing Elm Road - Bluemound 230kV line on double-circuit structures by constructing structures to cut-in the Elm Road - Bluemound 230kV line into the Arcadian substation and re-energize to 345kV. | ATC | M2 - Appendix A Approved | 3100000 | 2030-04-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Arcadian |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51009 | Substation - Arcadian | Add 2-345kV breaker-and-a-half positions: 1) 345kV line to Bluemound, 2) 345kV line #2 to Muskego Dam Road. Re-terminate 4-345kV lines to new positions. Replace existing 138kV substation bus and equipment to achieve 2000A rating for both outgoing 138kV Waukesha transmission lines. | ATC | M2 - Appendix A Approved |  | 2030-04-30 | Substation | Substation bus upgrade | Arcadian |  |  | 345 | 138 |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51010 | Line: Arcadian - Waukesha - 138 kV | Replace existing double-circuit 138kV structures with 138kV double-circuit structures to achieve 2000A rating. | ATC | M2 - Appendix A Approved | 10400000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Arcadian | Waukesha |  | 138 |  | 0 | 4 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51011 | Substation - Waukesha | Replace existing 138kV substation bus and equipment to achieve 2000A rating for the outgoing Arcadian 138kV transmission line. | ATC | M2 - Appendix A Approved | 3600000 | 2032-06-01 | Substation | Substation bus upgrade | Waukesha |  |  | 138 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51012 | Line: Arcadian - Muskego Dam Road - 345 kV | Replace existing double-circuit 345/230kV structures with double-circuit structures with two circuits operating at 345kV**. | ATC | M2 - Appendix A Approved | 81200000 | 2030-04-30 | Line Upgrade | Line rebuild on existing ROW | Arcadian | Muskego Dam Road |  | 345 |  | 0 | 14 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51013 | Substation - Muskego Dam Road | Construct new 8-345kV breaker-and-a-half bus substation: 1) Cut-in to existing Arcadian - Elm Road transmission line #1, 2) Cut-in to existing Arcadian - Elm Road transmission line #2, 3) Cut-in to existing Arcadian - Paris 345kV transmission line #1, 4) Cut-in to existing Arcadian - Paris 345kV transmission line #2, 5) Cut-in to existing Arcadian - Pleasant Prairie 345kV transmission line #1, 6) Cut-in to existing Arcadian - Pleasant Prairie 345kV transmission line #2, 7) New 2nd 345kV line to Arcadian (230kV conversion), 8) New 2nd 345kV line to Elm Road (230kV conversion). Construct a new 345kV 80MVAr shunt reactor and connect it to one of the main 345kV busses. The reactor will have a dedicated breaker. The location of the substation is within approximately one mile of where the existing Arcadian - Paris 345kV circuit, existing Arcadian - Pleasant Prairie 345kV circuit, existing Arcadian - Elm Road 345kV circuit, and the existing Bluemound - Elm Road 230kV circuit share common right-of-way. | ATC | M2 - Appendix A Approved | 39100000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Muskego Dam Road |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51014 | Line: Muskego Dam Road - 345 kV | Modify the existing Arcadian - Paris and Arcadian - Pleasant Prairie double-circuit 345kV transmission lines by constructing transmission structures to cut-in the existing Arcadian - Paris and Arcadian - Pleasant Prairie 345kV lines into the Muskego Dam Road substation. | ATC | M2 - Appendix A Approved | 16600000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Muskego Dam Road |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51015 | Line: Muskego Dam Road - 345 kV | Modify the existing Arcadian - Elm Road (345kV) and Elm Road - Bluemound (230kV) double-circuit 345/230kV transmission lines by constructing transmission structures to cut-in the existing Arcadian - Pleasant Prairie and Elm Road - Bluemound double-circuit 345/230kV lines into the Muskego Dam Road substation. Re-energize Elm Road - Arcadian - Bluemound to 345kV. | ATC | M2 - Appendix A Approved | 16600000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Muskego Dam Road |  |  | 345 | 230 |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51016 | Line: Muskego Dam Road - 3.3 Miles West of Elm Road - 345 kV | Replace existing 345/230kV structures with double-circuit structures with the existing 2156 ACSR 345kV conductor transferred and retained and one circuit operating at 345kV to achieve 3000A rating**. | ATC | M2 - Appendix A Approved | 81200000 | 2030-04-30 | Line Upgrade | Line rebuild on existing ROW | Muskego Dam Road | 3.3 Miles West of Elm Road |  | 345 |  | 0 | 14 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51017 | Line: 3.3 Miles West of Elm Road - Elm Road - 345 kV | Decommission existing 230kV double-circuit structures and construct a new line of double-circuit 345kV structures. | ATC | M2 - Appendix A Approved | 23000000 | 2030-04-30 | Line New | New Transmission line, new ROW - may include terminations | 3.3 Miles West of Elm Road | Elm Road |  | 345 |  | 4 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51018 | Substation - Elm Road | Add 3-345kV breaker-and-a-half positions: 1) New 345kV transmission line to Bluemound, 2) New 345kV transmission line to Muskego Dam Road, 3) New 345kV transmission line to Racine. Remove two 230kV line terminations from the 345kV sub. Remove two 138kV line terminations from the 138kV yard. Decommission and remove the 230kV facilities at Elm Road / Oak Creek. | ATC | M2 - Appendix A Approved | 18600000 | 2030-04-30 | Substation | Substation bus upgrade | Elm Road |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51019 | Line: Elm Road - Deadend North of Existing 345/138kV - 345 kV | Construct new 345kV single-circuit transmission line. | ATC | M2 - Appendix A Approved | 14000000 | 2029-02-01 | Line New | New Transmission line, new ROW - may include terminations | Elm Road | Deadend North of Existing 345/138kV |  | 345 | 138 | 4 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51020 | Line: Deadend North of Existing 345/138kV - Structure 4923 - 345 kV | Convert the existing 345kV/138kV double-circuit line to a 345kV double-circuit line by re-energizing existing (currently operated at 138kV) conductors to 345kV. | ATC | M2 - Appendix A Approved | 7600000 | 2029-02-01 | Line Upgrade | Line conversion to higher voltage | Deadend North of Existing 345/138kV | Structure 4923 |  | 345 |  | 0 | 9 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51021 | Line: Structure 4923 - Racine - 345 kV | Replace existing 138kV conductor with 345kV conductor, insulators, and hardware on existing double circuit structures. | ATC | M2 - Appendix A Approved | 600000 | 2029-02-01 | Line Upgrade | Line reconductor | Structure 4923 | Racine |  | 345 |  | 0 | 1 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51022 | Substation - Racine | Replace existing five-position 345kV ring bus with six-position breaker-and-a-half bus: 1) Existing 345/138kV transformer #1, 2) Existing 345/138kV transformer #2, 3) Existing 345kV Mount Pleasant line #1, 4) Existing 345kV Mount Pleasant line #2, 5) Existing 345kV Elm Road line #1, 6) New 345kV Elm Road line #2. | ATC | M2 - Appendix A Approved | 7900000 | 2029-02-01 | Substation | Substation bus upgrade | Racine |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51023 | Substation - Lakeview | Add 6-345kV line positions (breaker-and-a-half bus): 1) Cut-in to existing Paris - Zion 345kV transmission line #1, 2) Cut-in to existing Paris - Zion 345kV transmission line #2, 3) Cut-in to existing Pleasant Prairie - Zion 345kV transmission line #1, 4) Cut-in to existing Pleasant Prairie - Zion 345kV transmission line #2, 5) Cut-in to existing Arcadian - Pleasant Prairie 345kV transmission line #1, 6) Cut-in to existing Arcadian - Pleasant Prairie 345kV transmission line #2. | ATC | M2 - Appendix A Approved | 25000000 | 2032-06-01 | Substation | Substation bus upgrade | Lakeview |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51024 | Line: Lakeview - 345 kV | Modify the existing Paris - Zion and Pleasant Prairie - Zion double-circuit 345kV lines by constructing structures to cut-in the existing Paris - Zion and Pleasant Prairie - Zion 345kV lines into the Lakeview substation. | ATC | M2 - Appendix A Approved | 14400000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Lakeview |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50562 | LRTP-29: Bluemound - Arcadian - Waukesha - Muskego - Elm Road - Racine | MVP | 51025 | Line: Lakeview - 345 kV | Modify the existing Arcadian - Pleasant Prairie and Zion - Pleasant Prairie double-circuit 345kV lines by constructing structures to cut-in the existing Arcadian - Pleasant Prairie 345kV line into the Lakeview substation. | ATC | M2 - Appendix A Approved | 7200000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Lakeview |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50563 | LRTP-30: Columbia - Sugar Creek | MVP | 51026 | Line: Columbia - Sugar Creek - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 443948511 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Columbia | Sugar Creek |  | 765 |  | 91 | 0 | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50563 | LRTP-30: Columbia - Sugar Creek | MVP | 51027 | Transformer - Sugar Creek | Add 4-765kV double-breaker, double-bus positions: 1) New 765kV transmission line to Columbia, 2) New 765kV transmission line to IL/WI State Line, 3) New 765/345kV 2250MVA transformer, 4) New 765/345kV 2250MVA transformer. Note: All of these positions have a minimum 4000A rating. Add 2-765/345kV 2250 MVA transformers. Add 5-345kV breaker-and-a-half bus positions: 1) New 345kV line to Jefferson, 2) New 345kV line to Big Bend, 3) New 345kV line to Big Bend, 4) New 345kV line to Paris, 5) New 345kV line to Kitty Hawk. Note: All of these positions have a minimum 3000A rating. Add 2-345kV double-breaker, double-bus line positions: 1) 765/345kV 2250MVA transformer, 2) 765/345kV 2250MVA transformer. Note: All of these positions have a minimum 4000A rating. Add a 300MVAr shunt reactor bank (single-phase units) on each 765kV line. Reactor banks will each have a dedicated breaker. Add a 80MVAr shunt reactor to the 345kV bus. Reactor will have a dedicated breaker. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). | ATC | M2 - Appendix A Approved | 241600000 | 2033-06-01 | Transformer | Transformer New | Sugar Creek |  |  | 765 | 345 |  |  | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50564 | LRTP-31: Sugar Creek - Collins | MVP | 51028 | Line: Sugar Creek - IL/WI State Line - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 211807240 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Sugar Creek | IL/WI State Line |  | 765 |  | 25 | 0 | WI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50564 | LRTP-31: Sugar Creek - Collins | MVP | 51029 | Line: IL/WI State Line - Collins (PJM) - 765 kV | This transmission line will be assigned to a PJM Transmission Owner. Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | ComEd (PJM) | M2 - Appendix A Approved | 521600000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | IL/WI State Line | Collins (PJM) |  | 765 |  | 100 | 0 | IL |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50564 | LRTP-31: Sugar Creek - Collins | MVP | 51030 | Substation - Collins (PJM) | This substation will be assigned to a PJM Transmission Owner. Add 2-765kV ring bus positions: 1) New 765kV transmission line to Woodford County, 2) New 765kV transmission line to IL/WI State Border (Sugar Creek). Add 2-765kV 300MVAr line reactor with dedicated circuit breaker (for each outgoing line to Woodford County and IL/WI State Border (Sugar Creek)). Include two single-phase spare 765kV reactors (one for each outgoing line). | ComEd(PJM) | M2 - Appendix A Approved | 73600000 | 2034-06-01 | Substation | Substation bus upgrade | Collins (PJM) |  |  | 765 |  |  |  | IL |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51031 | Transformer - Denver | Construct new eight-position 345kV breaker-and-a-half bus substation: 1) New 345kV transmission line to Tittabawassee #1, 2) New 345kV transmission line to Tittabawassee #2, 3) New 345kV transmission line to Nelson Road #1, 4) New 345kV transmission line to Nelson Road #2, 5) New 345kV transmission line to Ludington #1, 6) New 345kV transmission line to Ludington #2, 7) 345/138kV 500MVA transformer #1, 8) 345/138kV 500MVA transformer #2. Install 2-345kV 75MVAr line reactors with dedicated circuit breakers (for outgoing lines to Ludington). Add 2-345/138kV 500MVA transformers with 138kV circuit breakers. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 60200000 | 2032-06-01 | Transformer | Transformer New | Denver |  |  | 345 | 138 |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51032 | Line: Denver - Ludington - 345 kV | Construct new 345kV double-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 912900000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denver | Ludington |  | 345 |  | 159 | 0 | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51033 | Substation - Ludington | Add 2-345kV line positions (breaker-and-a-half bus): 1) New 345kV transmission line to Denver #1, 2) New 345kV transmission line to Denver #2. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 7500000 | 2032-06-01 | Substation | Substation bus upgrade | Ludington |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51034 | Line: Denver - Nelson Road - 345 kV | Construct new 345kV double-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 312100000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denver | Nelson Road |  | 345 |  | 55 | 0 | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51035 | Substation - Nelson Road | Add 2-345kV line positions (breaker-and-a-half bus): 1) New 345kV transmission line to Denver #1, 2) New 345kV transmission line to Denver #2. Relocate two existing line terminations into an adjacent row of the Nelson Road bus arrangement. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 14300000 | 2032-06-01 | Substation | Substation bus upgrade | Nelson Road |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51036 | Substation - Salt River | Convert the five-position 138kV ring bus to a seven-position breaker-and-a-half bus arrangement by adding two positions: 1) New 138kV transmission line to Denver #1, 2) New 138kV transmission line to Denver #2. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 5600000 | 2032-06-01 | Substation | Substation bus upgrade | Salt River |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51037 | Line: Salt River - 138 kV | Re-terminate the existing 138kV line to Summerton into an adjacent bus position. | METC | M2 - Appendix A Approved | 2000000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Salt River |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51038 | Line: Denver - Tittabawassee - 345 kV | Construct new 345kV double-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 226700000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denver | Tittabawassee |  | 345 |  | 40 | 0 | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51039 | Substation - Tittabawassee | Add 2-345kV line positions (breaker-and-a-half bus): 1) New 345kV transmission line to Denver #1, 2) New 345kV transmission line to Denver #2. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 7500000 | 2032-06-01 | Substation | Substation bus upgrade | Tittabawassee |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | AMERICAN ELECTRIC POWER SERVICE CORPORATION | Central | 50566 | LRTP-33: Greentown - Sorenson - Lulu | MVP | 51040 | Substation - Greentown | Add 1-765kV double-breaker, double-bus line position: 1) New 765kV transmission line to Gwynneville. Add 1-765kV 300MVAr line reactor with dedicated circuit breaker (for outgoing line to Gwynneville). Include one single-phase spare 765kV reactor. | AEP(MISO) | M2 - Appendix A Approved | 41700000 | 2033-06-01 | Substation | Substation bus upgrade | Greentown |  |  | 765 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50566 | LRTP-33: Greentown - Sorenson - Lulu | MVP | 51041 | Line: Greentown - Sorenson (PJM) - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | AEP(MISO), AEP(PJM) | M2 - Appendix A Approved | 347300000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | Greentown | Sorenson (PJM) |  | 765 |  | 70 | 0 | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50566 | LRTP-33: Greentown - Sorenson - Lulu | MVP | 51042 | Substation - Sorenson (PJM) | This substation will be assigned to a PJM Transmission Owner. Add two new 765kV line positions: 1) New 765kV transmission line to Greentown, 2) New 765kV transmission line to Lulu. Add 2-765kV 300MVAr line reactors with dedicated circuit breaker (one on each outgoing line). Include two single-phase spare 765kV reactors (one for each outgoing line). | AEP(PJM) | M2 - Appendix A Approved | 77800000 | 2033-06-01 | Substation | Substation bus upgrade | Sorenson (PJM) |  |  | 765 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50566 | LRTP-33: Greentown - Sorenson - Lulu | MVP | 51043 | Line: Sorenson (PJM) - IN/MI State Line - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | AEP(PJM), ITCT | M2 - Appendix A Approved | 307700000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | Sorenson (PJM) | IN/MI State Line |  | 765 |  | 62 | 0 | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50566 | LRTP-33: Greentown - Sorenson - Lulu | MVP | 51044 | Line: IN/MI State Line - Lulu - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | AEP(PJM), ITCT | M2 - Appendix A Approved | 359800000 | 2033-06-01 | Line New | New Transmission line, new ROW - may include terminations | IN/MI State Line | Lulu |  | 765 |  | 68 | 0 | MI |  | Shared
MTEP24 | A | ITC | East | 50566 | LRTP-33: Greentown - Sorenson - Lulu | MVP | 51045 | Transformer - Lulu | Add a 765kV double-breaker, double-bus with three positions: 1) New 765kV transmission line to IN/MI State Border (Sorenson), 2) 765/345kV 2250MVA transformer #1, 3) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Add two 345kV double-breaker, double-bus positions: 1) 765/345kV 2250MVA transformer #1, 2) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Re-terminate two existing 345kV line positions to reduce 345kV line crossings. Install 2-765/345kV 2250MVA transformers. Install 1-765kV 300MVAr line reactor with dedicated circuit breaker (for outgoing line to Sorenson). Include one single-phase spare 765/345kV transformer, and one single-phase spare 765kV reactor. | ITCT | M2 - Appendix A Approved | 175200000 | 2033-06-01 | Transformer | Transformer New | Lulu |  |  | 765 | 345 |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51046 | Substation - Oneida | Add one new 345kV position to the existing breaker-and-a-half bus arrangement. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 4200000 | 2032-06-01 | Substation | Substation bus upgrade | Oneida |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51047 | Line: Oneida - Existing 138kV Line Near Williamston - 345 kV | Construct new 345kV single-circuit transmission line from Oneida to the existing 138kV line within approximately four miles of Williamston. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 172100000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Oneida | Existing 138kV Line Near Williamston |  | 345 |  | 32 | 0 | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51048 | Line: Existing 138kV Line Near Williamston - Sabine Lake - 345 kV | Replace existing single-circuit 138kV structures from within approximately four miles of Williamston to Sabine Lake substation with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. The structures being replaced are part of the existing Tihart - Oakland 138kV line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 99600000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Existing 138kV Line Near Williamston | Sabine Lake |  | 345 | 138 | 0 | 18 | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51049 | Substation - Blackfoot | Replace the existing three-position 345kV ring bus with six-position 345kV breaker-and-a-half bus: 1) Cut-in existing Bauer - Pontiac 345kV transmission line #1, 2) Cut-in existing Bauer - Pontiac 345kV transmission line #2, 3) Existing Blackfoot - Madrid 345kV transmission line #1, 4) Cut-in existing Blackfoot - Madrid 345kV transmission line #2, 5) Existing 345kV line to Van Dyke, 6) Existing 345kV line to Pontiac. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 14400000 | 2032-06-01 | Substation | Substation bus upgrade | Blackfoot |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51050 | Line: Blackfoot - 345 kV | Modify the existing Bauer - Pontiac 345kV single-circuit line by constructing structures to cut-in the existing Bauer - Pontiac 345kV line into the Blackfoot substation. | ITCT | M2 - Appendix A Approved | 3100000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Blackfoot |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51051 | Line: Blackfoot - 345 kV | Modify the existing Blackfoot - Madrid 345kV six wired double-circuit 345kV line to cut-in the second Blackfoot - Sabine Lake line into the Blackfoot substation. | ITCT | M2 - Appendix A Approved | 3100000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Blackfoot |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51052 | Line: Blackfoot - Sabine Lake - 345 kV | Modify the existing Blackfoot - Madrid 345kV six wired double-circuit 345kV line to create the two separate Blackfoot - Sabine Lake lines on double-circuit structures. | ITCT, METC | M2 - Appendix A Approved | 7200000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Blackfoot | Sabine Lake |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51053 | Substation - Sabine Lake | Construct new five-position 345kV breaker-and-a-half bus substation: 1) Existing Blackfoot 345kV transmission line #1, 2) Existing Blackfoot 345kV transmission line #2, 3) Existing Madrid 345kV transmission line, 4) New Majestic 345kV transmission line, 5) New 345kV transmission line to Oneida. Location of new substation will be within approximately 13 miles north of the existing Madrid substation. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 21600000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Sabine Lake |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51054 | Line: Sabine Lake - 345 kV | Modify the existing Blackfoot - Madrid 345kV six wired double-circuit 345kV line to cut-in the two circuits to Blackfoot, the circuit to Madrid, and the circuit to Majestic into the Sabine Lake substation. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 12300000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sabine Lake |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51055 | Line: Sabine Lake - I-96 - 345 kV | Modify the existing Blackfoot - Madrid 345kV six wired double-circuit 345kV line to support the two separate Sabine Lake - Madrid lines on double-circuit structures. | ITCT, METC | M2 - Appendix A Approved | 7200000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sabine Lake | I-96 |  | 345 |  | 0 | 8 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51056 | Line: I-96 - Madrid - 345 kV | Increase the nominal operating voltage of existing (currently operated at 40kV) conductors on existing double-circuit structures to 345kV. | ITCT | M2 - Appendix A Approved | 17000000 | 2032-06-01 | Line Upgrade | Line conversion to higher voltage | I-96 | Madrid |  | 345 |  | 0 | 6 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51057 | Line: Madrid - Calla - 345 kV | Increase the nominal operating voltage of existing (currently operated at 120kV) conductors on existing double-circuit structures to 345kV. | ITCT | M2 - Appendix A Approved | 6100000 | 2032-06-01 | Line Upgrade | Line conversion to higher voltage | Madrid | Calla |  | 345 |  | 0 | 14 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51058 | Line: Madrid - Calla - 120 kV | Modify existing 120kV transmission circuit by relocating it from existing double-circuit structures to single-circuit 120kV structures along the existing ROW. (If further analysis shows there is not adequate ROW available, installing the 120kV transmission circuit underground could be considered.) | ITCT | M2 - Appendix A Approved | 28600000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Madrid | Calla |  | 120 |  | 0 | 14 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51059 | Line: Calla - Majestic - 345 kV | Increase the nominal operating voltage of existing (currently operated at 120kV) conductors on existing double-circuit structures to 345kV. | ITCT | M2 - Appendix A Approved | 3100000 | 2032-06-01 | Line Upgrade | Line conversion to higher voltage | Calla | Majestic |  | 345 |  | 0 | 2 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51060 | Line: Calla - Majestic - 120 kV | Modify existing 120kV transmission circuit by relocating it from existing double-circuit structures to single-circuit 120kV structures along the existing ROW. (If further analysis shows there is not adequate ROW available, installing the 120kV transmission circuit underground could be considered.) | ITCT | M2 - Appendix A Approved | 4300000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Calla | Majestic |  | 120 |  | 0 | 2 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51061 | Substation - Majestic | Add 1-345kV line position (breaker-and-a-half bus). | ITCT | M2 - Appendix A Approved | 7800000 | 2032-06-01 | Substation | Substation bus upgrade | Majestic |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51062 | Line: Van Dyke - 345 kV | Modify the existing Thetford - Jewell 345kV single-circuit line by constructing structures to cut-in the existing Thetford - Jewell 345kV line into the Van Dyke substation. | ITCT | M2 - Appendix A Approved | 7000000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Van Dyke |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51063 | Line: Van Dyke - 345 kV | Modify the existing Blackfoot - Fitz 345kV single-circuit line by constructing structures to cut-in the existing Blackfoot - Fitz 345kV line into the Van Dyke substation. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 6800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Van Dyke |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51064 | Line: Van Dyke - 345 kV | Modify the existing Fitz - Pontiac 345kV single-circuit line by constructing structures to cut-in the existing Fitz - Pontiac 345kV line into the Van Dyke substation. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 6800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Van Dyke |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51065 | Substation - Van Dyke | Construct new six-position 345kV breaker-and-a-half bus substation: 1) Existing 345kV line to Fitz #1, 2) Existing 345kV line to Fitz #2, 3) Existing 345kV line to Thetford, 4) Existing 345kV line to Blackfoot, 5) Existing 345kV line to Jewell #1, 6) Existing 345kV line to Jewell #2. Location of new substation is within approximately one mile of junction of the existing Thetford - Jewell, Blackfoot - Fitz, and Fitz - Pontiac 345kV lines. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 25800000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Van Dyke |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51066 | Substation - Crimson | Add three new 345kV positions to the existing three position ring bus arrangement which will result in a six-position breaker-and-a-half arrangement: 1) Existing 345kV Pontiac #1 transmission line, 2) New 345kV Pontiac #2 transmission line, 3) Existing 345kV Jewell #1 transmission line, 4) New 345kV Jewell #2 transmission line, 5) Existing 345kV Belle River transmission line, 6) New 345kV line to Puttygut. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 14600000 | 2032-06-01 | Substation | Substation bus upgrade | Crimson |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51067 | Line: Crimson - 345 kV | Modify the existing Pontiac - Fitz 345kV single-circuit line by constructing structures to cut-in the existing Pontiac - Fitz 345kV line into the Crimson substation. Construct one approximately 1200' line entrance to Crimson substation. Make line reconnections of existing lines to the south and southeast of Crimson. Relocate line positions and structures as necessary. The final arrangement will result in the following six circuits leaving Crimson: Pontiac #1, Pontiac #2, Jewell #1, Jewell #2, Puttygut, and Belle River. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 28800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Crimson |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51068 | Line: Crimson - Jewell - 345 kV | Replace approximately four miles of 120kV double-circuit structures. Convert de-energized 120kV line to energized line. | ITCT | M2 - Appendix A Approved | 4000000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Crimson | Jewell |  | 345 |  | 0 | 4 | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51069 | Substation - Pontiac | Replace the bus and switches on the Crimson #2 345kV line termination to achieve 1700MVA capability. | ITCT | M2 - Appendix A Approved | 3700000 | 2032-06-01 | Substation | Substation bus upgrade | Pontiac |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51070 | Line: Pontiac - Crimson #2 - 345 kV | Replace 1000' of double-circuit line leaving the Pontiac substation. Perform sag remediation at three locations. | ITCT | M2 - Appendix A Approved | 5500000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Pontiac | Crimson #2 |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51071 | Substation - Jewell | Add three new 345kV positions to the existing six breaker-and-a-half bus positions for a total of nine breaker-and-a-half bus positions: 1) Existing 345kV Crimson #1 line, 2) New 345kV Crimson #2 line, 3) Existing 345kV Van Dyke line termination #1, 4) Existing 345kV Van Dyke line termination #2, 5) Existing 345kV line to Lennox, 6) Existing 345kV line to Bismark, 7) Existing 345kV line to Stephens, 8) New 345kV St. Clair line termination, 9) New 345kV Stephens line termination. Note that the two existing 345/230kV transformers will remain tapped off of the main 345kV busses and several lines will be re-terminated to minimize line crossings. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 15700000 | 2032-06-01 | Substation | Substation bus upgrade | Jewell |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51072 | Line: Jewell - 345 kV | Modify the existing Stephens - St. Clair 345kV line by constructing structures to cut-in the existing Stephens - St. Clair 345kV line into Jewell substation. Construct approximately 1200' 120kV line entrance to Jewell. Relocate line positions and structures as necessary. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 19400000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Jewell |  |  | 345 | 120 |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51073 | Substation - Wayne | Add two new 345kV positions to the existing breaker-and-a-half bus arrangement. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 7200000 | 2032-06-01 | Substation | Substation bus upgrade | Wayne |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51074 | Line: Wayne - 345 kV | Modify the existing Monroe 34 - Coventry 345kV single-circuit line by constructing structures to cut-in the existing Monroe 34 - Coventry 345kV line into the Wayne substation. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 3100000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Wayne |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51075 | Substation - Laplaisance Creek | Construct a new substation with a six-position breaker-and-a-half 345kV bus arrangement: 1) Existing 345kV line to Lulu #1, 2) Existing 345kV line to Lulu #2, 3) Existing 345kV line to Monroe 12, 4) Existing 345kV line to Monroe 34, 5) Existing 345kV line to Lemoyne, 6) Existing 345kV line to Lallendorf. | ITCT | M2 - Appendix A Approved | 25700000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Laplaisance Creek |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50567 | LRTP-34: Oneida - Sabine Lake - Blackfoot & Majestic | MVP | 51076 | Line: Laplaisance Creek - 345 kV | Modify the planned Lulu - Monroe 345kV, planned Lulu - Lemoyne 345kV, and existing Monroe - Lallendorf 345kV circuits by constructing new structures to cut lines into the Laplaisance Creek substation. | ITCT, METC | M2 - Appendix A Approved | 14400000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Laplaisance Creek |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51077 | Substation - Sullivan (PJM) | This substation will be assigned to a PJM Transmission Owner. Add 2-345kV line positions (breaker-and-a-half bus): 1) Cut-in to existing Fairbanks - Dresser 345kV transmission line #1, 2) Cut-in to existing Fairbanks - Dresser 345kV transmission line #2. | AEP(PJM) | M2 - Appendix A Approved | 8300000 | 2032-06-01 | Substation | Substation bus upgrade | Sullivan (PJM) |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51078 | Line: Sullivan (PJM) - 345 kV | This transmission line will be assigned to a PJM Transmission Owner. Modify the existing Fairbanks - Dresser 345kV single-circuit line by constructing structures to cut-in the existing Fairbanks - Dresser 345kV line into the Sullivan substation. | AEP(PJM), DEI | M2 - Appendix A Approved | 4700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sullivan (PJM) |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51079 | Line: Merom - 345 kV | Modify the existing Petersburg - Sullivan 345kV single-circuit line by constructing structures to cut-in the existing Petersburg - Sullivan 345kV line into the Merom substation. | IPL | M2 - Appendix A Approved | 4700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Merom |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | HOOSIER ENERGY | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51080 | Substation - Merom | Add 2-345kV positions (breaker-and-a-half bus): 1) Cut-in to existing Petersburg - Sullivan 345kV transmission line #1, 2) Cut-in to existing Petersburg - Sullivan 345kV transmission line #2. | HE | M2 - Appendix A Approved | 7200000 | 2032-06-01 | Substation | Substation bus upgrade | Merom |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | HOOSIER ENERGY | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51081 | Substation - Worthington | Replace the existing 345kV straight bus with a five-position breaker-and-a-half bus arrangement: 1) Existing 345kV line to Merom, 2) Existing 345kV line to Bloomington North, 3) Cut-in to existing Edwardsport - Amo 345kV transmission line, 4) Cut-in to existing Edwardsport - Amo 345kV transmission line, 5) Existing 345/138kV transformer. | HE | M2 - Appendix A Approved | 22500000 | 2032-06-01 | Substation | Substation bus upgrade | Worthington |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51082 | Line: Worthington - 345 kV | Modify the existing Edwardsport - Amo 345kV single-circuit line by constructing structures to cut-in the existing Edwardsport - Amo 345kV line into the Worthington substation. Re-terminate the existing 345kV Merom line and the existing 345kV Bloomington North line into the breaker-and-a-half bus arrangement. Re-route one mile of 69kV line to make room for the substation expansion. | DEI | M2 - Appendix A Approved | 13900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Worthington |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51083 | Substation - Indian Creek | Construct new six-position 345kV breaker-and-a-half bus substation: 1) Cut-in existing Gibson - Merom 345kV transmission line #1, 2) Cut-in existing Gibson - Merom 345kV transmission line #2, 3) Cut-in existing Edwardsport - Wheatland 345kV transmission line #1, 4) Cut-in existing Edwardsport - Wheatland 345kV transmission line #2, 5) Cut-in existing Petersburg - Sullivan 345kV transmission line #1, 6) Cut-in existing Petersburg - Sullivan 345kV transmission line #2. Location of new substation is within approximately one mile of the existing Gibson - Merom, Sullivan - Petersburg, and Edwardsport - Wheatland 345kV crossing. | DEI | M2 - Appendix A Approved | 22700000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Indian Creek |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51084 | Line: Indian Creek - 345 kV | Modify the existing Gibson - Merom 345kV single-circuit line by constructing structures to cut-in the existing Gibson - Merom 345kV line into the Indian Creek substation. | DEI | M2 - Appendix A Approved | 6700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Indian Creek |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51085 | Line: Indian Creek - 345 kV | Modify the existing Edwardsport - Wheatland 345kV single-circuit line by constructing structures to cut-in the existing Edwardsport - Wheatland 345kV line into the Indian Creek substation. | DEI | M2 - Appendix A Approved | 6700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Indian Creek |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51086 | Line: Indian Creek - 345 kV | Modify the existing Petersburg - Sullivan 345kV single-circuit line by constructing structures to cut-in the existing Petersburg - Sullivan 345kV line into the Indian Creek substation. | IPL | M2 - Appendix A Approved | 6700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Indian Creek |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51087 | Transformer - AB Brown | Add 1-345kV ring bus position: 1) 345/138kV 448MVA transformer. Add 1-345/138kV 448MVA transformer. Add 1-138kV breaker-and-a-half bus position: 1) 345/138kV 448MVA transformer connection. Add 1-138kV 2000A series reactor located on the 138kV side of the 345/138kV transformer. | CPEI (SIGE) | M2 - Appendix A Approved | 14700000 | 2027-07-01 | Transformer | Transformer New | AB Brown |  |  | 345 | 138 |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51088 | Transformer - Pike County | Construct new four-position 765kV double-breaker, double-bus and seven-position 345kV breaker-and-a-half bus substation. 765kV bus positions: 1) Cut-in to existing Sullivan - Rockport 765kV transmission line #1, 2) Cut-in to existing Sullivan - Rockport 765kV transmission line #2, 3) 765/345kV 2250MVA transformer #1, 4) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. 345kV breaker-and-a-half bus positions: 1) New 345kV transmission line to Petersburg #1, 2) New 345kV transmission line to Petersburg #2, 3) Cut-in existing Bedford - Gibson 345kV transmission line, 4) Cut-in existing Bedford - Gibson 345kV transmission line, 4) New 345kV transmission line to Duff. Note: All of these positions have a minimum 3000A rating. 345kV double-breaker, double-bus position: 6) 765/345kV 2250MVA transformer #1, 7) 765/345kV 2250MVA transformer #2. Note: This position has a minimum 4000A rating. Install 2-765/345kV 2250MVA transformers. Install 2-765kV 300MVAr line reactors with dedicated circuit breaker (for each outgoing line to Sullivan and Rockport). Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). The location of the substation is within approximately one mile of the existing Sullivan - Rockport 765kV line and I-69 crossing. | AEP (PJM), DEI | M2 - Appendix A Approved | 238200000 | 2032-06-01 | Transformer | Transformer New | Pike County |  |  | 765 | 345 |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51089 | Line: Pike County - 765 kV | This transmission line will be assigned to a PJM Transmission Owner. Modify the existing Sullivan - Rockport 765kV single-circuit line by constructing structures to cut-in the existing Sullivan - Rockport 765kV line into the Pike County substation. | AEP (PJM) | M2 - Appendix A Approved | 9000000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Pike County |  |  | 765 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51090 | Line: Pike County - 345 kV | Modify the existing Bedford - Gibson 345kV single-circuit line by constructing structures to cut-in the existing Bedford - Gibson 345kV line into the Pike County substation. | DEI | M2 - Appendix A Approved | 25300000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Pike County |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51091 | Line: Pike County - Petersburg - 345 kV | Construct new 345kV double-circuit transmission line. | DEI, IPL | M2 - Appendix A Approved | 15900000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Pike County | Petersburg |  | 345 |  | 3 | 0 | IN |  | Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51092 | Substation - Petersburg | Add 2-345kV line positions (double-breaker, double-bus): 1) New 345kV transmission line to Pike County #1, 2) New 345kV transmission line to Pike County #2. | IPL | M2 - Appendix A Approved | 9000000 | 2032-06-01 | Substation | Substation bus upgrade | Petersburg |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51093 | Line: Pike County - Duff - 345 kV | Construct new 345kV single-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 61500000 | 2030-10-01 | Line New | New Transmission line, new ROW - may include terminations | Pike County | Duff |  | 345 |  | 20 | 0 | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51094 | Line: Duff - 345 kV | Re-terminate two existing 345kV lines to accommodate the replacement of the 345kV ring bus with a breaker-and-a-half arrangement. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 5600000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Duff |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51095 | Substation - Duff | Add 2-345kV line positions (replace existing ring bus with breaker-and-a-half bus). | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 14600000 | 2029-12-31 | Substation | Substation bus upgrade | Duff |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51096 | Line: Duff - Culley 345kV - 345 kV | Construct new 345kV single-circuit transmission line. | CPEI(SIGE) | M2 - Appendix A Approved | 110700000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Duff | Culley 345kV |  | 345 |  | 36 | 0 | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51097 | Transformer - Culley 345kV | Add 4-345kV line positions (ring bus): 1) New 345kV transmission line to Duff, 2) New 345kV transmission line to IN/KY State Border (Reid EHV), 3) 345/138kV 448MVA transformer #1, 4) 345/138kV 448MVA transformer #2. Add 2-345/138kV 448MVA transformers each with a 138kV breaker. Add 2-138kV line terminations: 1) 138kV line to Darlington, 2) 138kV line to Warrick North. Add 2-138kV 2000A series reactors. | CPEI(SIGE) | M2 - Appendix A Approved | 32900000 | 2029-12-31 | Transformer | Transformer New | Culley 345kV |  |  | 345 | 138 |  |  | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51098 | Line: Culley 345kV - IN/KY State Line - 345 kV | Construct new 345kV single-circuit transmission line. | CPEI(SIGE) | M2 - Appendix A Approved | 2800000 | 2029-07-01 | Line New | New Transmission line, new ROW - may include terminations | Culley 345kV | IN/KY State Line |  | 345 |  | 1 | 0 | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51099 | Line: Culley 345kV - Darlington - 138 kV | Construct new 138kV single-circuit transmission line. | CPEI(SIGE) | M2 - Appendix A Approved | 5500000 | 2029-07-01 | Line New | New Transmission line, new ROW - may include terminations | Culley 345kV | Darlington |  | 138 |  | 3 | 0 | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51100 | Line: Culley 345kV - Warrick North - 138 kV | Construct new 138kV single-circuit transmission line. | CPEI(SIGE) | M2 - Appendix A Approved | 5500000 | 2029-04-01 | Line New | New Transmission line, new ROW - may include terminations | Culley 345kV | Warrick North |  | 138 |  | 3 | 0 | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51101 | Substation - Darlington | Add one 138kV line position to the existing breaker-and-a-half bus arrangement: 1) 138kV line to Culley 345/138kV Switching Station. | CPEI(SIGE) | M2 - Appendix A Approved | 2000000 | 2028-07-01 | Substation | Substation bus upgrade | Darlington |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51102 | Substation - Warrick North | Add one 138kV line position to the existing breaker-and-a-half bus arrangement: 1) 138kV line to Culley 345/138kV Switching Station. | CPEI(SIGE) | M2 - Appendix A Approved | 2000000 | 2028-07-01 | Substation | Substation bus upgrade | Warrick North |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | REPUBLIC TRANSMISSION, LLC | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51103 | Line: IN/KY State Line - Reid EHV - 345 kV | Construct new 345kV single-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 85853895 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | IN/KY State Line | Reid EHV |  | 345 |  | 22 | 0 | KY |  | Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 50568 | LRTP-35: Southwest Indiana-Kentucky | MVP | 51104 | Substation - Reid EHV | Add 1-345kV line position (ring bus): 1) New 345kV transmission line to IN/KY State Border (Culley 345kV). | BREC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Substation | Substation bus upgrade | Reid EHV |  |  | 345 |  |  |  | KY |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51105 | Substation - Greensboro | Replace the existing 345kV straight bus arrangement with a three-position ring bus: 1) Existing 345kV line to Gwynneville, 2) Existing 345/138kV transformer, 3) New 345kV line to Madison County. | DEI | M2 - Appendix A Approved | 12700000 | 2032-06-01 | Substation | Substation bus upgrade | Greensboro |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51106 | Line: Greensboro - Madison County - 345 kV | Construct new 345kV single-circuit transmission line. | DEI | M2 - Appendix A Approved | 37400000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Greensboro | Madison County |  | 345 |  | 13 | 0 | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51107 | Substation - Madison County | Construct new five-position 345kV breaker-and-a-half bus substation: 1) New 345kV transmission line to Greensboro, 2) Cut-in to existing Fall Creek - Noblesville 345kV transmission line #1, 3) Cut-in to existing Fall Creek - Noblesville 345kV transmission line #2, 4) Cut-in to existing Fall Creek - Sunnyside 345kV transmission line #1, 5) Cut-in to existing Fall Creek - Sunnyside 345kV transmission line #2. The location of the substation is within approximately one mile of the existing Fall Creek - Noblesville and Fall Creek - Sunnyside 345kV junction. | DEI, IPL | M2 - Appendix A Approved | 20800000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Madison County |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51108 | Line: Madison County - 345 kV | Modify the existing Fall Creek - Noblesville 345kV single-circuit line by constructing structures to cut-in the existing Fall Creek - Noblesville 345kV line into the Madison County substation. | AEP(PJM), DEI, IPL | M2 - Appendix A Approved | 6700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Madison County |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51109 | Line: Madison County - 345 kV | Modify the existing Fall Creek - Sunnyside 345kV single-circuit line by constructing structures to cut-in the existing Fall Creek - Sunnyside 345kV line into the Madison County substation. | AEP(PJM), IPL | M2 - Appendix A Approved | 6700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Madison County |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51110 | Transformer - Gwynneville | Add 4-765kV double-breaker, double-bus line positions: 1) Cut-in existing Greentown - Jefferson 765kV transmission line #1, 2) Cut-in existing Greentown - Jefferson 765kV transmission line #2, 3) 765/345kV 2250MVA transformer #1, 4) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Add 2-765/345kV 2250MVA transformers. Add 2-765kV 300MVAr line reactor with dedicated circuit breaker (one on each outgoing line). Replacing existing four-position 345kV ring bus with eight-position breaker-and-a-half bus: 1) Cut-in existing Hanna - Tanners Creek 345kV transmission line #1, 2) Cut-in existing Hanna - Tanners Creek 345kV transmission line #2, 3) Existing 345kV line to Prescott, 4) Existing 345/69kV transformer, 5) Existing 345kV transmission line to Greensboro, 6) Existing 345kV transmission line to Sunnyside. Note: All of these positions have a minimum 3000A rating. 2-345kV double-breaker, double-bus positions: 7) New 765/345kV 2250MVA transformer #1, 8) New 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). | DEI | M2 - Appendix A Approved | 240200000 | 2032-06-01 | Transformer | Transformer New | Gwynneville |  |  | 765 | 345 |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51111 | Line: Gwynneville - 765 kV | This transmission line will be assigned to a PJM Transmission Owner. Modify the existing Jefferson - Greentown 765kV single-circuit line by constructing structures to cut-in the existing Jefferson - Greentown 765kV line into the Gwynneville substation. | AEP(PJM) | M2 - Appendix A Approved | 9000000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gwynneville |  |  | 765 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51112 | Line: Gwynneville - 345 kV | This transmission line will be assigned to a PJM Transmission Owner. Modify the existing Hanna - Tanners Creek 345kV single-circuit line by constructing structures to cut-in the existing Hanna -Tanners Creek 345kV line into the Gwynneville substation. | AEP(PJM) | M2 - Appendix A Approved | 6700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gwynneville |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51113 | Line: Gwynneville - 345 kV | Modify the existing Gwynneville - Greensboro 345kV single-circuit line by constructing structures to cut-in the existing Gwynneville - Greensboro 345kV line into the Gwynneville substation. | DEI | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gwynneville |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51114 | Line: Gwynneville - 345 kV | Modify the existing Gwynneville - Sunnyside 345kV single-circuit line by constructing structures to cut-in the existing Gwynneville - Sunnyside 345kV line into the Gwynneville substation. | IPL | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gwynneville |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51115 | Line: Gwynneville - 345 kV | Modify the existing Gwynneville - Prescott 345kV single-circuit line by constructing structures to cut-in the existing Gwynneville - Prescott 345kV line into the Gwynneville substation. | DEI, IPL | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gwynneville |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51116 | Substation - Decatur County | Replace substation bus and equipment to achieve 2000A rating for outgoing 138kV line to Greensburg. | DEI | M2 - Appendix A Approved | 8700000 | 2032-06-01 | Substation | Substation bus upgrade | Decatur County |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51117 | Substation - Greensburg | Replace substation bus and equipment to achieve 2000A rating for the outgoing 138kV line to Decatur County. | DEI | M2 - Appendix A Approved | 3400000 | 2032-06-01 | Substation | Substation bus upgrade | Greensburg |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51118 | Line: Decatur County - Greensburg - 138 kV | Replace existing Decatur County - Greensburg 138kV single-circuit transmission line with 138kV single-circuit structures. | DEI | M2 - Appendix A Approved | 8700000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Decatur County | Greensburg |  | 138 |  | 0 | 5 | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51119 | Substation - Batesville | Replace the nine-position 138kV straight bus arrangement with a 138kV breaker-and-a-half bus with 10 positions: 1) New 138kV transmission line to Sutton Ridge substation, 2) 138kV lead line to the existing 138/69kV transformer #1, 3) 138kV lead line to 138/69kV transformer #2, 4) Existing 345/138kV transformer, 5) Existing 138kV capacitor bank, 6) Existing 138kV transmission line to Greensburg, 7) Existing 138kV transmission line to Laurel, 8) Existing 138kV transmission line to Hubbel, 9) Existing 138kV transmission line to Napoleon, 10) Existing 138kV transmission line to Columbus. Replace substation bus and equipment to achieve 2000A rating for the existing outgoing 138kV line to Hubbell. | DEI | M2 - Appendix A Approved | 32100000 | 2032-06-01 | Substation | Substation bus upgrade | Batesville |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51120 | Substation - Batesville | Add 2-345kV line positions (ring bus): 1) Cut-in to existing Tanners Creek - Hanna 345kV transmission line #1, 2) Cut-in to existing Tanners Creek - Hanna 345kV transmission line #2. | DEI | M2 - Appendix A Approved | 5700000 | 2032-06-01 | Substation | Substation bus upgrade | Batesville |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51121 | Line: Batesville - 345 kV | This transmission line will be assigned to a PJM Transmission Owner. Modify the existing Tanners Creek - Hanna 345kV single-circuit line by constructing double-circuit structures to cut-in the existing Tanners Creek - Hanna 345kV line into the Batesville substation. | AEP(PJM) | M2 - Appendix A Approved | 41100000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Batesville |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51122 | Line: Batesville - 138 kV | Modify the existing Batesville - Greensburg 138kV single-circuit line by constructing single-circuit structures to cut-in the existing Batesville - Greensburg 138kV line into the Batesville substation. | DEI | M2 - Appendix A Approved | 1700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Batesville |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51123 | Line: Batesville - 138 kV | Modify the existing Batesville - Laurel 138kV single-circuit line by constructing single-circuit structures to cut-in the existing Batesville - Laurel 138kV line into the Batesville substation. | DEI | M2 - Appendix A Approved | 1700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Batesville |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51124 | Line: Batesville - 138 kV | Modify the existing Batesville - Napolean 138kV single-circuit line by constructing single-circuit structures to cut-in the existing Batesville - Napolean 138kV line into the Batesville substation. | DEI | M2 - Appendix A Approved | 1700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Batesville |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51125 | Line: Batesville - 138 kV | Modify the existing Batesville - Columbus 138kV single-circuit line by constructing single-circuit structures to cut-in the existing Batesville - Columbus 138kV line into the Batesville substation. | DEI | M2 - Appendix A Approved | 1700000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Batesville |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51126 | Line: Batesville - Hubbell - 138 kV | Replace existing double-circuit 138kV structures on the Batesville - Hubbell 138kV line with double-circuit 138kV structures that have a rating of 478MVA per circuit. | DEI | M2 - Appendix A Approved | 27900000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Batesville | Hubbell |  | 138 |  | 0 | 9 | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51127 | Line: Weisburg - 138 kV | Replace existing 138kV line switches and bus at Weisburg substation to achieve 2000A capability and cut-in the rebuilt line to Weisburg substation. | DEI | M2 - Appendix A Approved | 4900000 | 2032-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Weisburg |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | HOOSIER ENERGY | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51128 | Substation - Hubbell | Replace substation bus and equipment to achieve 2000A rating for outgoing lines to Batesville and Greendale. | HE | M2 - Appendix A Approved | 4400000 | 2032-06-01 | Substation | Substation bus upgrade | Hubbell |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51129 | Line: Hubbell - Greendale - 138 kV | Replace existing double-circuit 138kV structures on the Hubbell - Greendale 138kV line with double-circuit 138kV structures that have a rating of 478MVA per circuit. Replace existing 138kV line switches with switches having a 2000A rating capability. | HE, IMPA | M2 - Appendix A Approved | 49300000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Hubbell | Greendale |  | 138 |  | 0 | 15 | IN |  | Shared
MTEP24 | A | HOOSIER ENERGY | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51130 | Line: Hidden Valley - 138 kV | Replace existing 138kV line switches at the Hidden Valley substation and cut-in rebuilt line to Hidden Valley substation. | HE | M2 - Appendix A Approved |  | 2032-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Hidden Valley |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | INDIANA MUNICIPAL POWER AGENCY | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51131 | Substation - Greendale | Replace substation bus and equipment to achieve 2000A rating for outgoing lines to Hubbell and Miami Fort. | IMPA | M2 - Appendix A Approved | 2600000 | 2032-06-01 | Substation | Substation bus upgrade | Greendale |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51132 | Substation - Sutton Ridge | Construct new five-position 138kV breaker-and-a-half bus substation: 1) Cut-in to existing Wilmington Junction - Wilmington 138kV transmission line, 2) Cut-in to existing Wilmington Junction - Greendale 138kV transmission line, 3) Cut-in to existing Wilmington Junction - Hubbell 138kV line, 4) Cut-in to new Sutton Ridge - Miami Fort 138kV line, 5) Cut-in to new Sutton Ridge - Batesville 138kV line. The location of the new substation is within approximately one mile of the existing Wilmington Junction 3-way tap. | DEI | M2 - Appendix A Approved | 11200000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Sutton Ridge |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51133 | Line: Sutton Ridge - 138 kV | Modify the existing Wilmington Junction - Wilmington 138kV line by constructing structures to cut-in the Wilmington Junction - Wilmington 138kV line into the new Sutton Ridge substation. | DEI | M2 - Appendix A Approved | 1800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sutton Ridge |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51134 | Line: Sutton Ridge - 138 kV | Modify the existing Wilmington Junction - Greendale 138kV line by constructing structures to cut-in the Wilmington Junction - Greendale 138kV line into the new Sutton Ridge substation. | DEI, IMPA | M2 - Appendix A Approved | 1800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sutton Ridge |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51135 | Line: Sutton Ridge - 138 kV | Modify the existing Wilmington Junction - Hubbell 138kV line by constructing structures to cut-in the Wilmington Junction - Hubbell 138kV line into the new Sutton Ridge substation. | DEI, HE | M2 - Appendix A Approved | 1800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sutton Ridge |  |  | 138 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51136 | Line: Greendale - IN/OH State Line - 138 kV | Replace existing double-circuit 138kV structures on the Greendale - Miami Fort 138kV line with double-circuit 138kV structures that have a rating of 478MVA per circuit. | DEI | M2 - Appendix A Approved | 9700000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Greendale | IN/OH State Line |  | 138 |  | 0 | 3 | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51137 | Line: IN/OH State Line - Miami Fort (PJM) - 138 kV | This transmission line will be assigned to a PJM Transmission Owner. Replace existing double-circuit 138kV structures on the Greendale - Miami Fort 138kV line with double-circuit 138kV structures that have a rating of 478MVA per circuit. | DEO(PJM) | M2 - Appendix A Approved | 3100000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | IN/OH State Line | Miami Fort (PJM) |  | 138 |  | 0 | 1 | OH |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50569 | LRTP-36: Southeast Indiana | MVP | 51138 | Substation - Miami Fort (PJM) | This substation will be assigned to a PJM Transmission Owner. Add 1-138kV line position in the existing straight bus. Replace substation bus and equipment to achieve 2000A rating for outgoing 138kV line to Greendale. | DEO(PJM) | M2 - Appendix A Approved | 2200000 | 2032-06-01 | Substation | Substation bus upgrade | Miami Fort (PJM) |  |  | 138 |  |  |  | OH |  | Shared
MTEP24 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51139 | Substation - Maywood | Add one 345kV line position to the existing breaker-and-a-half bus arrangement. | ATXI | M2 - Appendix A Approved | 3300000 | 2032-06-01 | Substation | Substation bus upgrade | Maywood |  |  | 345 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51140 | Line: Maywood - Palmyra - 345 kV | Construct new 345kV single-circuit transmission line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Maywood | Palmyra |  | 345 |  | 3 | 0 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51141 | Line: Palmyra - Spalding - 345 kV | Replace existing single-circuit 161kV structures with double-circuit structures that have one circuit operating at 161kV and one circuit operating at 345kV**. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Palmyra | Spalding |  | 345 | 161 | 0 | 16 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51142 | Line: Spalding - Finn Tap - 345 kV | Construct new 345kV single-circuit transmission line. | AMMO, MJMEUC | M2 - Appendix A Approved | 0 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Spalding | Finn Tap |  | 345 |  | 3 | 0 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51143 | Line: Finn Tap - Belleau - 345 kV | Replace existing single-circuit 161kV structures with double-circuit structures that have one circuit operating at 161kV and one circuit operating at 345kV**. | AMMO, MJMEUC | M2 - Appendix A Approved | 495100000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Finn Tap | Belleau |  | 345 | 161 | 0 | 68 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51144 | Line: Hannibal West - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hannibal West |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51145 | Line: Spalding - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Spalding |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51146 | Line: Peno Creek EC - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Peno Creek EC |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51147 | Line: Pike - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Pike |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51148 | Line: Cyrene - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Cyrene |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51149 | Line: New Hope - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | New Hope |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51150 | Line: Troy - 161 kV | Replace existing 161kV cut-ins with cut-ins to the co-located 161kV line. | AMMO | M2 - Appendix A Approved | 4200000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Troy |  |  | 161 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51151 | Substation - Belleau | Modify the existing 345kV three-position straight bus by adding three positions and creating 6-345kV ring bus positions: 1) Existing 345/138kV transformer #1, 2) Existing 345kV Root Beer transmission line, 3) Existing 345kV MRPD transmission line #1, 4) New 345kV Maywood transmission line, 5) New 345kV MRPD transmission line #2, 6) New 345/138kV transformer #2. Add a 50MVAr switchable shunt reactor connected to the Maywood line termination. Add a 700MVA 345/138kV transformer and add a 138kV position to the existing 138kV bus arrangement. | AMMO | M2 - Appendix A Approved | 23800000 | 2032-06-01 | Substation | Substation bus upgrade | Belleau |  |  | 345 | 138 |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51152 | Line: Belleau - MRPD - 345 kV | Replace existing single-circuit 138kV structures with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. | AMMO | M2 - Appendix A Approved | 94000000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Belleau | MRPD |  | 345 | 138 | 0 | 15 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51153 | Line: Fort Zumwalt - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Fort Zumwalt |  |  | 138 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51154 | Line: McClay - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | McClay |  |  | 138 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51155 | Line: Huster - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Huster |  |  | 138 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51156 | Line: Fountain Lakes - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMMO | M2 - Appendix A Approved | 1800000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Fountain Lakes |  |  | 138 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51157 | Substation - MRPD | Construct new five-position 345kV breaker and a half substation: 1) New 345kV transmission line to Belleau, 2) New 345kV transmission line to Sioux, 3) New 345kV transmission line to Bugle, 4) Cut-in to existing Belleau - Sioux 345kV transmission line #1, 5) Cut-in to existing Belleau - Sioux 345kV transmission line #2. The location of the substation is within approximately one mile of the existing Herleman - Bugle and Belleau - Sioux 138/345kV crossing. | AMMO | M2 - Appendix A Approved | 20800000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | MRPD |  |  | 345 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51158 | Line: MRPD - 345 kV | Modify the existing Belleau - Sioux 345kV single-circuit line by constructing structures to cut-in the existing Belleau - Sioux 345kV line into the MRPD substation. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | MRPD |  |  | 345 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51159 | Line: MRPD - 3-Way Junction - 345 kV | Decommission two de-energized double-circuit 138kV lines and construct a new line of double-circuit 345kV structures (one circuit to Sioux and the other circuit to Bugle) from MRPD substation to the 3-way junction approximately three miles southeast of MRPD substation. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | MRPD | 3-Way Junction |  | 345 |  | 4 | 0 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51160 | Line: 3-Way Junction - Sioux - 345 kV | Increase the nominal operating voltage of existing (currently operated at 138kV) conductors on existing double-circuit structures to 345kV. Replace existing 138kV line with single-circuit 138kV structures from the 3-way junction approximately three miles southeast of MRPD substation to Sioux substation. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line conversion to higher voltage | 3-Way Junction | Sioux |  | 345 |  | 0 | 8 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51161 | Substation - Sioux | Add 1-345kV bus position (ring bus). Relocate two existing 345kV line connections at Sioux to accommodate the new Sioux-MRPD line. Remove one 138kV line termination. | AMMO | M2 - Appendix A Approved | 8300000 | 2032-06-01 | Substation | Substation bus upgrade | Sioux |  |  | 345 |  |  |  | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51162 | Line: 3-Way Junction - Bugle - 345 kV | Decommission existing 138kV single-circuit structures from the 3-way junction approximately three miles southeast of MRPD substation to Bugle substation and construct a new line of single-circuit 345kV structures. | AMMO | M2 - Appendix A Approved | 97400000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | 3-Way Junction | Bugle |  | 345 |  | 14 | 0 | MO |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51163 | Transformer - Bugle | Add 5-345kV ring bus positions: 1) New 345kV transmission line to MRPD, 2) New 345kV Roxford line, 3) New 345kV Gateway line, 4) New 345/138kV 700MVA transformer #1, 5) New 345/138kV 700MVA transformer #2. Remove the 138kV Sioux line termination. Add 2-345/138kV 700MVA transformer. Add 2-138kV bus positions: 1) 345/138kV 700MVA transformer #1, 2) 345/138kV 700MVA transformer #2. | AMMO | M2 - Appendix A Approved | 38800000 | 2032-06-01 | Transformer | Transformer New | Bugle |  |  | 345 | 138 |  |  | MO |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51164 | Line: Bugle - IL/MO State Line - 345 kV | Replace two existing 138kV single-circuit lines by replacing both lines of single-circuit 138kV structures with two lines of double-circuit structures that each have one circuit operating at 138kV and one circuit operating at 345kV**. | AMIL, AMMO | M2 - Appendix A Approved | 99600000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Bugle | IL/MO State Line |  | 345 |  | 0 | 16 | MO |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51165 | Line: IL/MO State Line - Roxford/Gateway - 345 kV | Modify the existing Roxford - Gateway 345kV single-circuit line by constructing double-circuit structures to cut-in the existing Roxford - Gateway 345kV line into the Bugle substation. | AMIL, AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | IL/MO State Line | Roxford/Gateway |  | 345 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50570 | LRTP-37: Maywood - Belleau - MRPD - Sioux - Bugle | MVP | 51166 | Line: Euclid - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMMO | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Euclid |  |  | 138 |  |  |  | MO |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51167 | Line: East Adair - Marshalltown (Twinkle) - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 566200000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | East Adair | Marshalltown (Twinkle) |  | 765 |  | 109 | 0 | IA |  | Shared
MTEP24 | A | ITC MIDWEST | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51168 | Transformer - Marshalltown (Twinkle) | Add 5-765kV double-breaker, double-bus line positions: 1) New 765kV transmission line to East Adair, 2) New 765kV transmission line to Sub T, 3) 765/345kV 2250MVA transformer #1, 4) 765/345kV 2250MVA transformer #2, 5) 300MVAr Reactor position with future 765kV line position. Note: All of these positions have a minimum 4000A rating. Add 2-765/345kV 2250MVA transformers. Add 3-765kV 300MVAr line reactors with dedicated circuit breakers (for each outgoing line to East Adair and Sub T). Add 4-345kV breaker-and-a-half bus positions: 1) New 345kV transmission line to Montezuma #1, 2) New 345kV transmission line to Montezuma #2, 3) New 345kV transmission line to Lehigh, 4) New 345kV transmission line to Franklin North. Note: All of these positions have a minimum 3000A rating. Add 2-345kV double-breaker, double-bus positions: 1) 765/456kV 2250MVA transformer #1, 2) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). | ITCM | M2 - Appendix A Approved | 286900000 | 2034-06-01 | Transformer | Transformer New | Marshalltown (Twinkle) |  |  | 765 | 345 |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51169 | Line: Marshalltown (Twinkle) - Sub T - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 439400000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Marshalltown (Twinkle) | Sub T |  | 765 |  | 87 | 0 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51170 | Transformer - Sub T | Add 3-765kV double-breaker, double-bus line position: 1) New 765kV transmission line to Marshalltown (Twinkle), 2) New 765kV transmission line to Woodford County, 3) 765/345kV 2250MVA transformer. Note: All of these positions have a minimum 4000A rating. Add 1-765/345kV 2250MVA transformer. Add 2-765kV 300MVAr line reactors with dedicated circuit breakers (for each outgoing line to Marshalltown (Twinkle) and Woodford County). Replace existing three-position 345kV ring bus with five-position 345kV breaker-and-a-half bus: 1) Cut-in to existing 345kV transmission line to Louisa, 2) Cut-in to existing 345kV line to Skunk River, 3) Cut-in to existing 345kV transmission line to Hills #1, 4) Cut-in to new 345kV transmission line to Hills #2. Note: All of these positions have a minimum 3000A rating. 345kV double-breaker, double-bus position: 5) 765/345kV 2250MVA transformer. Note: This position has a minimum 4000A rating. Include one single-phase spare 765/345kV transformer. Include two single-phase spare 765kV reactors (one for each outgoing line). | MEC | M2 - Appendix A Approved | 181700000 | 2033-06-01 | Transformer | Transformer New | Sub T |  |  | 765 | 345 |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51171 | Line: Sub 93 Louisa - IA/IL State Line - 345 kV | Replace existing Sub 93 Louisa - Oak Grove 345kV single-circuit transmission line with 345kV single-circuit structures and conductors to achieve a 3000A rating. | ITCM, MEC | M2 - Appendix A Approved | 5900000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Sub 93 Louisa | IA/IL State Line |  | 345 |  | 0 | 1 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51172 | Substation - Sub 93 Louisa | Replace existing 345kV substation bus and equipment to achieve 3000A rating for the outgoing Oak Grove 345kV transmission line. | MEC | M2 - Appendix A Approved | 1300000 | 2032-06-01 | Substation | Substation bus upgrade | Sub 93 Louisa |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51173 | Line: Hills - 345 kV | Modify the existing Hills - Tiffin 345kV single-circuit line by constructing transmission structures to cut-in the existing Hills - Tiffin 345kV line into the Hills substation to an adjacent position from the existing position. | MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hills |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51174 | Line: Hills - 345 kV | Modify the existing Hills - Diamond Trail 345kV single-circuit line by constructing transmission structures to cut-in the existing Hills - Diamond Trail 345kV line into the Hills substation to an adjacent position from the existing position. | MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hills |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | AMEREN MISSOURI | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51175 | Line: Hills - Sub T - 345 kV | Replace existing single-circuit 345kV transmission line with double-circuit structures that have one circuit operating at 345kV and one circuit operating at 345kV**. | Ameren | M2 - Appendix A Approved | 90000000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Hills | Sub T |  | 345 |  | 0 | 17 | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51176 | Substation - Lehigh | Add 1-345kV bus position (ring bus) and replace existing 345kV substation equipment to achieve 3000A rating for the outgoing Twinkle 345kV transmission line. Re-terminate the Webster 345kV transmission line into a new position. | MEC | M2 - Appendix A Approved | 10900000 | 2032-06-01 | Substation | Substation bus upgrade | Lehigh |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51177 | Line: Lehigh - Marshalltown (Twinkle) - 345 kV | Construct new 345kV single-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 284200000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Lehigh | Marshalltown (Twinkle) |  | 345 |  | 90 | 0 | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51178 | Substation - Franklin North | Add 1-345kV line position (breaker-and-a-half bus). Install 1-345kV 50MVAr shunt reactor with dedicated circuit breaker on one of the 345kV busses. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 8400000 | 2032-06-01 | Substation | Substation bus upgrade | Franklin North |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51179 | Line: Marshalltown (Twinkle) - Montezuma - 345 kV | Construct new 345kV double-circuit transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 208400000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Marshalltown (Twinkle) | Montezuma |  | 345 |  | 40 | 0 | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51180 | Substation - Montezuma | Replace existing four-position 345kV ring bus with six-position breaker-and-a-half bus: 1) Cut-in to existing 345kV transmission line to Bondurant, 2) Cut-in to existing 345kV to Diamond Trail, 3) Cut-in to existing 345kV line to Ottumwa, 4) Cut-in existing 345kV line to North English, 5) New 345kV transmission line to Marshalltown (Twinkle) #1, 6) New 345kV transmission line to Marshalltown (Twinkle) #2. Install 1-345kV 50MVAr shunt reactor with dedicated circuit breaker on one of the 345kV busses. | ITCM, MEC | M2 - Appendix A Approved | 26700000 | 2032-06-01 | Substation | Substation bus upgrade | Montezuma |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51181 | Line: Montezuma - 345 kV | Modify the existing Montezuma - Bondurant 345kV single-circuit line by constructing transmission structures to cut-in the Montezuma - Bondurant 345kV line into the Montezuma substation. | MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Montezuma |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51182 | Line: Montezuma - 345 kV | Modify the existing Montezuma - Diamond Trail 345kV single-circuit line by constructing transmission structures to cut-in the Montezuma - Diamond Trail 345kV line into the Montezuma substation. | MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Montezuma |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51183 | Line: Montezuma - 345 kV | Modify the existing Montezuma - Ottumwa 345kV single-circuit line by constructing transmission structures to cut-in the Montezuma - Ottumwa 345kV line into the Montezuma substation. | ITCM, MEC | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Montezuma |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51184 | Line: Sub T - IA/IL State Line - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved |  | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Sub T | IA/IL State Line |  | 765 |  | 26 | 0 | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51185 | Line: IA/IL State Line - Oak Grove - 345 kV | Replace existing Sub 93 Louisa - Oak Grove 345kV single-circuit transmission line with 345kV single-circuit structures to achieve a 3000A rating. | ITCM, MEC | M2 - Appendix A Approved | 79700000 | 2034-06-01 | Line Upgrade | Line rebuild on existing ROW | IA/IL State Line | Oak Grove |  | 345 |  | 0 | 27 | IL |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51186 | Substation - Oak Grove | Replace existing 345kV substation equipment to achieve 3000A rating for the outgoing Sub 93 Louisa 345kV transmission line. | MEC | M2 - Appendix A Approved | 1300000 | 2034-06-01 | Substation | Substation bus upgrade | Oak Grove |  |  | 345 |  |  |  | IL |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51187 | Line: IA/IL State Line - Woodford County - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 787800000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | IA/IL State Line | Woodford County |  | 765 |  | 151 | 0 | IL |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51188 | Transformer - Woodford County | Construct new five-position 765kV double-breaker, double-bus and eight-position 345kV breaker-and-a-half bus substation. 765kV bus positions: 1) New 765kV transmission line to IL/IA State Border (Sub T), 2) New 765kV transmission line to Collins, 3) New 765kV transmission line to IL/IN State Border (Reynolds), 4) 765/345kV 2250MVA transformer #1, 5) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. 345kV breaker-and-a-half bus positions: 1) New 345kV transmission line to Radbourn, 2) New 345kV transmission line to Powerton #1, 3) New 345kV transmission line to Powerton #2, 4) New 345kV transmission line to Fargo, 5) New 345kV transmission line to Nevada, 6) New 345kV transmission line to Katydid Road. Note: All of these positions have a minimum 3000A rating. 345kV double-breaker, double-bus positions: 7) 765/345kV 2250MVA transformer #1, 8) 765/345kV 2250MVA transformer #2. Note: All of these positions have a minimum 4000A rating. Install 2-765/345kV 2250MVA transformers. Install 3-765kV 300MVAr line reactors with dedicated circuit breaker (for each outgoing line to IL/IA State Border (Sub T), Collins, and IL/IN State Border (Reynolds)). Include one single-phase spare 765/345kV transformer. Include three single-phase spare 765kV reactors (one for each outgoing line). The location of the substation is within approximately one mile of the existing Goodings Grove - Powerton and Oglesby - McLean 345/138kV crossing. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 299500000 | 2034-06-01 | Transformer | Transformer New | Woodford County |  |  | 765 | 345 |  |  | IL |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51190 | Line: Woodford County - IL/IN State Line - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 413100000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Woodford County | IL/IN State Line |  | 765 |  | 81 | 0 | IL |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51191 | Line: IL/IN State Line - Reynolds - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. | NIPSCO | M2 - Appendix A Approved | 189000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | IL/IN State Line | Reynolds |  | 765 |  | 38 | 0 | IN |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51192 | Transformer - Reynolds | Add 1-765kV double-breaker, double-bus line position: 1) New 765kV transmission line to IL/IN State Border (Woodford County). Note: This position has a minimum 4000A rating. Add 1-765/345kV 2250MVA transformer which will be connected to the 765kV south bus. Add 1-765kV circuit breaker for the new Transformer. Add 1-765kV 300MVAr line reactor with dedicated circuit breaker (for outgoing line to Woodford County). Add 2-765kV breakers to the existing Greentown line termination. Add 1-345kV line position: 1) 765/345kV 2250MVA transformer. Note: This position has a minimum 4000A rating. Remove the existing 765kV bus-tie breaker located between transformer 3 and transformer 4. Include one single-phase spare 765kV reactor (existing single-phase spare transformer already exists on site). | NIPSCO | M2 - Appendix A Approved | 103300000 | 2034-06-01 | Transformer | Transformer New | Reynolds |  |  | 765 | 345 |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51193 | Line: Woodford County - 345 kV | Modify the existing Powerton - Nevada and Powerton - Katydid Road 345kV double-circuit lines by constructing structures to cut-in the existing Powerton - Nevada and Powerton - Katydid Road 345kV lines into the Woodford County substation. | ComEd(PJM) | M2 - Appendix A Approved | 7000000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Woodford County |  |  | 345 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51194 | Line: Woodford County - Woodhall - 345 kV | Construct new 345kV single-circuit transmission line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Woodford County | Woodhall |  | 345 |  | 18 | 0 | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51195 | Line: Woodhall - Fargo - 345 kV | Replace existing single-circuit 138kV structures with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. The structures being replaced are part of the existing Woodhall - Fargo 138kV line. | AMIL | M2 - Appendix A Approved | 212600000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Woodhall | Fargo |  | 345 | 138 | 0 | 28 | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51196 | Line: Alta - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Alta |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51197 | Line: Mossville - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mossville |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51198 | Line: Hallock - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hallock |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51199 | Line: Woodhall - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Woodhall |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51200 | Substation - Fargo | Add 1-345kV line position (ring bus): 1) New 345kV transmission line to Woodford County. | AMIL | M2 - Appendix A Approved | 2900000 | 2032-06-01 | Substation | Substation bus upgrade | Fargo |  |  | 345 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51201 | Line: Woodford County - Near Woodford County - 345 kV | Construct new 345kV single-circuit transmission line from Woodford County substation to within approximately one mile of the existing Goodings Grove - Powerton and Oglesby - McLean 345/138kV crossing. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Woodford County | Near Woodford County |  | 345 |  | 1 | 0 | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51202 | Line: Near Woodford County - Radbourn - 345 kV | Replace existing single-circuit 138kV structures from within approximately one mile of the existing Goodings Grove - Powerton and Oglesby - McLean 345/138kV crossing to Radbourn substation with double-circuit structures that have one circuit operating at 138kV and one circuit operating at 345kV**. The structures being replaced are part of the existing Woodford County - McLean County 138kV line, McLean County - Normal East 138kV line, and Normal East - Radbourn 138kV line. | AMIL | M2 - Appendix A Approved | 195100000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Near Woodford County | Radbourn |  | 345 |  | 0 | 37 | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51203 | Line: McLean - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | McLean |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51204 | Line: East Normal - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | East Normal |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51205 | Line: Towanda - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Towanda |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51206 | Line: Brokaw - 138 kV | Replace existing 138kV cut-ins with cut-ins to the co-located 138kV line. | AMIL | M2 - Appendix A Approved | 0 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Brokaw |  |  | 138 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50574 | LRTP-41: Woodford County - Fargo & Radbourn | MVP | 51207 | Substation - Radbourn | Add 1-345kV line position (breaker-and-a-half bus): 1) New 345kV transmission line to Woodford County. | AMIL | M2 - Appendix A Approved | 4200000 | 2032-06-01 | Substation | Substation bus upgrade | Radbourn |  |  | 345 |  |  |  | IL |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50575 | LRTP-42: Burr Oak - Schahfer | MVP | 51208 | Substation - Babcock | Add 4-345kV line positions (breaker-and-a-half bus): 1) Cut-in to existing 345kV Olive - University Park transmission line #1, 2) Cut-in to existing 345kV Olive - University Park transmission line #2, 3) Cut-in to existing 345kV Olive - Green Acres transmission line, 4) Cut-in to existing 345kV Olive - Green Acres transmission line. | NIPSCO | M2 - Appendix A Approved | 15900000 | 2032-06-01 | Substation | Substation bus upgrade | Babcock |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50575 | LRTP-42: Burr Oak - Schahfer | MVP | 51209 | Line: Babcock - 345 kV | This transmission line will be assigned to a PJM Transmission Owner. Modify the existing Olive - University Park and Olive - Green Acres 345kV double-circuit lines by constructing structures to cut-in the existing Olive - University Park and Olive - Green Acres 345kV lines into the Babcock substation. | AEP(PJM), ComEd(PJM) | M2 - Appendix A Approved | 9400000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Babcock |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50575 | LRTP-42: Burr Oak - Schahfer | MVP | 51210 | Substation - Burr Oak | Add 1-345kV line position (breaker-and-a-half bus): 1) New 345kV transmission line to Schahfer. | NIPSCO | M2 - Appendix A Approved | 6800000 | 2032-06-01 | Substation | Substation bus upgrade | Burr Oak |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50575 | LRTP-42: Burr Oak - Schahfer | MVP | 51211 | Line: Burr Oak - 345 kV | Re-terminate each of the two existing 345kV Reynolds lines one bay to the east to free up a position for the second 345kV circuit to Schahfer. | NIPSCO | M2 - Appendix A Approved | 4200000 | 2032-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Burr Oak |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50575 | LRTP-42: Burr Oak - Schahfer | MVP | 51212 | Substation - Schahfer | Terminate the new 345kV circuit to Burr Oak into a 345kV bus position vacated by the retirement of a local generator. | NIPSCO | M2 - Appendix A Approved | 5400000 | 2032-06-01 | Substation | Substation bus upgrade | Schahfer |  |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 50899 | Line: Cass County - Red River - 115 kV | Replace existing Cass County - Red River 115kV single-circuit transmission line with 115kV single-circuit structures and conductor to achieve 3000A rating. | XEL | M2 - Appendix A Approved | 5400000 | 2032-06-01 | Line Upgrade | Line rebuild on existing ROW | Cass County | Red River |  | 115 |  |  | 3 | ND |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 50148 | Havana-Puro 138 kV1422 MPFCA | GIP | 50242 | Havana-Puro-1422 138 kV | Rebuild the 138 kV Havana-Puro 1422 transmission line with new wood H frame structures, steel structures, OPGW and 1200 A conductor. Affected J#s include: J1408, J1453, J1454 |  | M2 - Appendix A Approved | 13200000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Havana | Puro |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | METC | East | 50151 | Sphinx 138 kV Station | Other | 50246 | Sphinx New 138 kV Station | Build a new 138 kV four-row breaker-and-a-half configuration station Sphinx. Install twelve 138 kV, 3000 A breakers with at least 40 kA interrupting capability and install all associated equipment capable of at least 3000A SE. |  | M2 - Appendix A Approved | 13900000 | 2027-03-31 | Substation | Substation (breakers only, no transformer) | Sphinx |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 50151 | Sphinx 138 kV Station | Other | 50247 | Gaines-Sphinx 1 and 2 138 kV Lines and OPGW | Rebuild approx. 2.5 mile of Gaines – Plaster Creek 138 kV line to double circuit structures 1431 ACSS and create two new circuits Gaines – Sphinx #1 and #2 138 kV lines and install OPGW. Remove temporary feed equipment (from phase 1) as necessary. |  | M2 - Appendix A Approved | 9430000 | 2027-02-26 | Line Upgrade | Line rebuild on existing ROW | Gaines | Sphinx | 1 & 2 | 138 |  | 2.5 |  | MI |  | Not Shared
MTEP24 | A | METC | East | 50151 | Sphinx 138 kV Station | Other | 50248 | Gaines Station Rows Expansion | Expand Gaines 138 kV station rows 7 and 11 to accommodate the new line. Install five 138 kV standard 3000 A 63 kA breakers. |  | M2 - Appendix A Approved | 4900000 | 2026-03-31 | Substation | Substation (breakers only, no transformer) | Gaines |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 50151 | Sphinx 138 kV Station | Other | 50249 | Sphinx - Plaster Creek 138 kV Line (Cut-in) | Redirect line from East Paris into the new station Sphinx utilizing 1431 ACSS conductor and replace OPGW. |  | M2 - Appendix A Approved | 4400000 | 2026-05-15 | Line Upgrade | Generic transmission line project (try not to use the generic) | Sphinx | Plaster Creek | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 50151 | Sphinx 138 kV Station | Other | 50250 | Plaster Creek - Install WM13 Communications | Install a rack mounted patch panel for termination of new fiber cable from the Plaster Creek – East Paris Line. Install and terminate new underground cable from the patch panel to splice closure on the Plaster Creek – East Paris Line. |  | M2 - Appendix A Approved | 55000 | 2026-05-15 | Misc. | Relaying, protection, RTU and SCADA equipment | Plaster Creek |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 50151 | Sphinx 138 kV Station | Other | 50251 | East Paris - Install Communications | Install 2 wall mounted patch panels for termination of new fiber cable from the the East Paris – Plaster Creek, and the East Paris – Gaines Line. Install and terminate 2 new underground cables from the patch panels to splice closures on the East Paris – Plaster Creek and East Paris Gaines Lines. |  | M2 - Appendix A Approved | 125000 | 2026-03-31 | Misc. | Relaying, protection, RTU and SCADA equipment | East Paris |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50152 | Ellendale load 3 addition | Other | 50253 | 230 kV Transmission line | This is a new 230 kV transmission line between the Ellendale sub and the Ellendale Data Center Sub. |  | M2 - Appendix A Approved | 2265527 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Ellendale | Ellendale Data Center |  | 230 |  | 1 |  | ND |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50152 | Ellendale load 3 addition | Other | 50254 | Ellendale Data Center Sub additions | Additions to the Ellendale Data Center Sub for the additional load. Add transformer, breakers and switches. |  | M2 - Appendix A Approved | 7310211 | 2027-12-31 | Substation | Substation bus upgrade | Ellendale Data Center Sub |  |  | 230 | 34 |  |  | ND |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 50152 | Ellendale load 3 addition | Other | 50255 | Ellendale Substation Additions | Adding breakers and switches at the Ellendale sub for the new 230 kV line. |  | M2 - Appendix A Approved | 3000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Ellendale |  |  | 230 |  |  |  | ND |  | Not Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 50263 | Dorset | Install FOC jumpers |  | M2 - Appendix A Approved | 25506 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Dorset |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 50264 | Spruce | Install FOC jumpers |  | M2 - Appendix A Approved | 25506 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Spruce |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 50265 | Lark | Install FOC jumpers |  | M2 - Appendix A Approved | 25506 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Lark |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | ENTERGY MISSISSIPPI, LLC. | South | 50160 | J1672 Network Upgrades: Gerald Andrus 230kV Auto | GIP | 50288 | 2nd Andrus 230/115 Autotransformer | Install second 230/115 kV 392 MVA Autotransformer. |  | M2 - Appendix A Approved | 19750000 | 2028-06-15 | Transformer | Transformer New | Andrus 230 | Andrus 115 | 1 | 230 | 115 |  |  | MS |  | Not Shared
MTEP24 | A | METC | East | 15831 | Alma - Regal #2 138 kV Rebuild | BRP | 23880 | 23880-Alma-Regal | Rebuild the entire ~5.8 mile-long Alma – Regal 2 138 kV line by replacing the existing assets (all structures, 336 ACSR conductor, and the 336 ACSR line entrance at Alma) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. | METC | M2 - Appendix A Approved | 10617000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Alma | Regal | 2 | 138 |  |  | 3.8 | MI |  | Not Shared
MTEP24 | A | METC | East | 15831 | Alma - Regal #2 138 kV Rebuild | BRP | 23884 | 23884-Alma- | Upgrade the 336 ACSR line entrance at Alma. | METC | M2 - Appendix A Approved | 694000 | 2028-06-01 | Substation | Small miscellaneous substation equipment | Alma |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 24462 | Grassmere - J1525 TOIF - Install Position CQ and switch CQA | GIP | 27949 | 27949-Grassmere- | Install Grassmere switch CQA and line entrance structure at position CQ for generator interconnection. | ITCT | M2 - Appendix A Approved | 0 | 2026-03-27 | Substation | Small miscellaneous substation equipment | Grassmere |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 24463 | Greenwood-Rapson#1 - J1557 Generator Interconnection (Cribbins) - Network Upgrade | GIP | 27950 | 27950-Greenwood-Rapson | Construct a new 345kV ring bus station with three 40kA breakers for the J1557 interconnection | ITCT | M2 - Appendix A Approved | 12408239 | 2028-08-14 | Substation | Switching station (breakers only, no transformer) | Greenwood | Rapson |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 24463 | Greenwood-Rapson#1 - J1557 Generator Interconnection (Cribbins) - Network Upgrade | GIP | 27951 | 27951-Greenwood-Rapson | Extend the Greenwood-Rapson #1 345kV line to loop in the J1557 interconnection 345kV station. | ITCT | M2 - Appendix A Approved | 1586250 | 2028-08-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Greenwood | Rapson |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 24494 | Cribbins-J1557 TOIF- Install position CQ and switch CQA | GIP | 27952 | 27952-Cribbins- | Install Cribbins position CQ line entrance structure and switch CQA for generator interconnection. | ITCT | M2 - Appendix A Approved | 0 | 2028-08-14 | Substation | Small miscellaneous substation equipment | Cribbins |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 24450 | J1516 Generator Interconnection Network Upgrades | GIP | 27987 | 27987-FItz- | Install breaker position HF and disconnect switches HH and HD. | ITCT | M2 - Appendix A Approved | 52496 | 2026-08-03 | Substation | Substation (breakers only, no transformer) | FItz |  |  | 120 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 24451 | J1516 Generator Interconnection TOIF | GIP | 27988 | 27988-Fitz- | Install line entrance structure and disconnect switch. Install position HI at Fitz to interconnect J1516 generator. | ITCT | M2 - Appendix A Approved | 18378 | 2026-08-03 | Substation | Small miscellaneous substation equipment | Fitz |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 24533 | J1526 Generator Interconnection Network Upgrades | GIP | 27989 | 27989-Greenwood- | Install 345 kV BKR KT at Greenwood. Replace Annunciator panel with RTU panel. | ITCT | M2 - Appendix A Approved | 1364741 | 2026-05-13 | Substation | Substation (breakers only, no transformer) | Greenwood |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 24534 | J1526 Generator Interconnection TOIF | GIP | 27990 | 27990-Greenwood- | Install line entrance structures and disconnect switch. Install position KQ at Greenwood to interconnect J1526 generation. | ITCT | M2 - Appendix A Approved | 0 | 2026-05-13 | Substation | Small miscellaneous substation equipment | Greenwood |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 24535 | J1553 Generator Interconnection Network Upgrades | GIP | 27991 | 27991-Bingham- | Expand Bingham station. Extend Blue bus and move the capacitor. Install Row 4 and install breaker 8W8, 8B7, 4B7, and 4M9. Reterminate the Cornell - Bingham line at position BM4. | METC | M2 - Appendix A Approved | 5488031 | 2027-03-31 | Substation | Substation (breakers only, no transformer) | Bingham |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24535 | J1553 Generator Interconnection Network Upgrades | GIP | 27992 | 27992-Bingham- | Reterminate the Bingham - Cornell 138kV line at position BM4 | METC | M2 - Appendix A Approved | 712500 | 2028-04-28 | Substation | Small miscellaneous substation equipment | Bingham |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24515 | J1553 Generator Interconnection TOIF | GIP | 27993 | 27993-Bingham- | Install required entrance structures and disconnect switch as TOIF. Install position WM6 at Bingham to interconnect J1553 generator. | METC | M2 - Appendix A Approved | 0 | 2027-03-31 | Substation | Small miscellaneous substation equipment | Bingham |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 24516 | J1571 Generator Interconnection Network Upgrades | GIP | 27994 | 27994-Beecher-Pixley | Construct new breaker and a half 138kV station Rouget in a ring bus configuration with three, 138kV, 40kA minimum capability breakers and associated disconnects. | METC | M2 - Appendix A Approved | 7887399 | 2028-04-03 | Substation | Substation (breakers only, no transformer) | Beecher | Pixley |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24516 | J1571 Generator Interconnection Network Upgrades | GIP | 27995 | 27995-Beecher-Pixley | Loop in the Beecher – Pixley (Beecher – Morocco #1) 138kV circuit to the new J1571 station ~2.8 miles from Beecher 138kV station near structure 017B5283 utilizing conductor rated at least that of 954 ACSR 54/7. | METC | M2 - Appendix A Approved | 687500 | 2028-02-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Beecher | Pixley |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24536 | J1571 Generator Interconnection TOIF | GIP | 27996 | 27996-Beecher-Pixley | Install required entrance structures and disconnect switch as TOIF. Install position BM8 at Rouget to interconnect J1571 generator. | METC | M2 - Appendix A Approved | 0 | 2028-04-03 | Substation | Small miscellaneous substation equipment | Beecher | Pixley |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 24553 | J1659 Generator Interconnection Network Upgrades | GIP | 28005 | 28005-Dorset- | Install tie-bkr HG at Dorset. | ITCT | M2 - Appendix A Approved | 922579 | 2026-04-01 | Substation | Substation (breakers only, no transformer) | Dorset |  |  | 120 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 24554 | J1659 Generator Interconnection TOIF | GIP | 28006 | 28006-Dorset- | Install an entrance structure, one BKR, and two disconnect switches as TOIF. Install position HK at Dorset to interconnect J1659 generator. | ITCT | M2 - Appendix A Approved | 0 | 2026-04-01 | Substation | Small miscellaneous substation equipment | Dorset |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24274 | New - 138 kV Maloney-Reservoir Loop | Other | 28012 | 28012-Rockville-Maloney | New 8.45 mile 138 kV transmission line and ROW to serve customer load in Brownsburg. | IPL | M2 - Appendix A Approved | 14600000 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | Rockville | Maloney | 93 | 138 |  | 7.8 |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24274 | New - 138 kV Maloney-Reservoir Loop | Other | 28013 | 28013-Maloney- | New breaker-and-a-half (3 bays, 6 positions) 138 kV substation to serve customer load | IPL | M2 - Appendix A Approved | 13500000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Maloney |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24274 | New - 138 kV Maloney-Reservoir Loop | Other | 28014 | 28014-Maloney-Reservoir | A 4 mile 138 kV transmission line to serve load in Boone County. | IPL | M2 - Appendix A Approved | 7500000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Maloney | Reservoir | 92 | 138 |  | 4 |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24274 | New - 138 kV Maloney-Reservoir Loop | Other | 28015 | 28015-Reservoir- | A 138 kV breaker-and-a-half substation (4 bays, 8 positions) dedicated to serve REMC and IOU customer load in Boone County | IPL | M2 - Appendix A Approved | 16500000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Reservoir |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | METC | East | 24556 | J1586 Generator Interconnection Network Upgrades | GIP | 28017 | 28017-Oxby- | Construct J1586 POI station as a breaker and half 345kV station with three 50kA breakers. | METC | M2 - Appendix A Approved | 12667183 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Oxby |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24556 | J1586 Generator Interconnection Network Upgrades | GIP | 28018 | 28018-Argenta-Tompkins | Extend the Argenta - Tompkins 345kV line 0.2 miles by adding 2-1431 ACSR to loop in J1586 POI 345kV station. | METC | M2 - Appendix A Approved | 1820400 | 2027-01-21 | Line Upgrade | Generic transmission line project (try not to use the generic) | Argenta | Tompkins |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24557 | J1586 Generator Interconnection TOIF | GIP | 28021 | 28021-Oxby- | Install a line entrance structure and disconnect as TOIF. Install position RH31 at Oxby to interconnect J1586 generator. | METC | M2 - Appendix A Approved | 0 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Oxby |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 24558 | J1658 Generator Interconnection Network Upgrades | GIP | 28022 | 28022-Cronk- | Construct J1658 Interconnection 138kV station as a breaker and half station with three 40kA breakers in a ring bus configuration. | METC | M4 - Project in Service | 6800964 | 2025-12-12 | Substation | Substation (breakers only, no transformer) | Cronk |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24558 | J1658 Generator Interconnection Network Upgrades | GIP | 28023 | 28023-Coldwater-Moore Road | Extend the Coldwater - Moore Road line and loop in the J1658 Station. Extend fiber path to J1658 POI, Coldwater, and Moore Rd stations. | METC | M4 - Project in Service | 12137500 | 2025-11-13 | Line Upgrade | Generic transmission line project (try not to use the generic) | Coldwater | Moore Road |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24558 | J1658 Generator Interconnection Network Upgrades | GIP | 28024 | 28024-Coldwater- | Install a SEL2506 at Coldwater for island mitigation. | METC | M4 - Project in Service | 338050 | 2025-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Coldwater |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24558 | J1658 Generator Interconnection Network Upgrades | GIP | 28025 | 28025-Moore Road- | Install a SEL2506 at Moore Road for island mitigation | METC | M2 - Appendix A Approved | 384456 | 2026-03-02 | Misc. | Relaying, protection, RTU and SCADA equipment | Moore Road |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25285 | 0891 West St Cloud - Crossroads Rebuild | Other | 28426 | 28426-West St Cloud-Crossroads | Rebuild 4.1 miles 115 kV from West St. Cloud - Crossroads with new structures and new OPGW shield wire. | XEL | M2 - Appendix A Approved | 3500000 | 2026-11-01 | Line Upgrade | Line rebuild on existing ROW | West St Cloud | Crossroads | 1 | 115 |  |  | 4.1 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25286 | 0754 Buffalo - Maple Lake Rebuild | Other | 28429 | 28429-Buffalo-Maple Lake | Rebuild 8.2 miles 69 kV from Buffalo - Maple Lake with new structures, new OPGW shield wire, and new conductor. | XEL | M2 - Appendix A Approved | 6000000 | 2027-12-15 | Line Upgrade | Line rebuild on existing ROW | Buffalo | Maple Lake | 1 | 69 |  |  | 8.2 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25287 | W3402 Loyal - Spokesville Rebuild | Other | 28430 | 28430-Loyal-Spokesville | Rebuild 8 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | XEL | M2 - Appendix A Approved | 6866139 | 2028-05-31 | Line Upgrade | Line rebuild on existing ROW | Loyal | Spokesville | 1 | 69 |  |  | 8 | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25288 | 0774 Goodview - Str 444 Rebuild | Other | 28431 | 28431-Goodview-Goodview Tap | Rebuild 3 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | XEL | M2 - Appendix A Approved | 6000000 | 2026-03-31 | Line Upgrade | Line rebuild on existing ROW | Goodview | Goodview Tap | 1 | 69 |  |  | 3 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25270 | 0760 Redwing - Lake City - Str 217 Rebuild | Other | 28434 | 28434-Redwing-Lake City | Rebuild 18 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | XEL | M2 - Appendix A Approved | 10000000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Redwing | Lake City | 1 | 69 |  |  | 18 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25258 | Prior TR02 And Feeder | Other | 28438 | 28438-Prior- | Install second 115/13.8 kV transformer and associated equipment. | XEL | M2 - Appendix A Approved | 10500000 | 2026-10-25 | Substation | Substation (breakers only, no transformer) | Prior |  |  | 115 | 14 |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25272 | MNN MOD Installation | Other | 28441 | 28441-Monticello- | Install new MOD transmission line switches at Monticello. Potential for new pole and substation fence expansion. | XEL | M2 - Appendix A Approved | 1898712 | 2027-06-30 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Monticello |  |  | 345 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25273 | Bateman Substation Breaker Upgrade | Other | 28442 | 28442-Bateman- | Project to convert 69kV switch 4E442 to a circuit breaker and upgrade and bus relaying scheme at the Bateman substation. | XEL | M2 - Appendix A Approved | 1300000 | 2026-10-15 | Substation | Substation (breakers only, no transformer) | Bateman |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25323 | St Croix Valley Upgrades | Other | 28447 | 28447-South Hudson- | Build a new South Hudson substation. | XEL | M2 - Appendix A Approved | 15000000 | 2029-09-30 | Substation | Substation (breakers only, no transformer) | South Hudson |  |  | 115 | 24 |  |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25323 | St Croix Valley Upgrades | Other | 28448 | 28448-Willow River- | Add bus and breaker at Willow River to accommodate the new 115kV transmission line | XEL | M2 - Appendix A Approved | 2000000 | 2029-09-30 | Substation | Substation (breakers only, no transformer) | Willow River |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25323 | St Croix Valley Upgrades | Other | 28449 | 28449-Willow River- | Replace the two 70 MVA TR’s at Willow River. | XEL | M2 - Appendix A Approved | 8000000 | 2029-09-30 | Transformer | Transformer New | Willow River |  |  | 115 | 24 |  |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25323 | St Croix Valley Upgrades | Other | 28450 | 28450-Junction Mill-South Hudson | New 115kV transmission line from the proposed Junction Mill substation in River Falls to a new South Hudson substation. | XEL | M2 - Appendix A Approved | 12000000 | 2029-09-30 | Line New | New Transmission line, new ROW - may include terminations | Junction Mill | South Hudson | 1 | 115 |  | 6 |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25323 | St Croix Valley Upgrades | Other | 28451 | 28451-South Hudson-Willow River | New 115kV transmission line from new South Hudson substation to Willow River substation. | XEL | M2 - Appendix A Approved | 8000000 | 2029-09-30 | Line New | New Transmission line, new ROW - may include terminations | South Hudson | Willow River | 1 | 115 |  | 4 |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25295 | 2023 Line Clearance Mitigations | Other | 28453 | 28453-Raptor-Red Rock | Replace structures at 1 clearance limited span between Raptor - Red Rock. | XEL | M4 - Project in Service | 261043 | 2025-03-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Raptor | Red Rock | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25295 | 2023 Line Clearance Mitigations | Other | 28455 | 28455-St Augusta-Wakefield | Replace structures at 1 clearance limited span between St Augusta - Wakefield. | XEL | M4 - Project in Service | 317817 | 2023-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | St Augusta | Wakefield | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25295 | 2023 Line Clearance Mitigations | Other | 28456 | 28456-North Rochester-Prairie Island | Replace structures at 3 clearance limited span between North Rochester - Prairie Island. | XEL | M3 - Under Construction | 1111422 | 2026-05-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | North Rochester | Prairie Island | 1 | 345 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25295 | 2023 Line Clearance Mitigations | Other | 28457 | 28457-Monticello-Oakwood | Replace structures at 3 clearance limited span between Monticello - Oakwood. | XEL | M4 - Project in Service | 150000 | 2023-09-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Monticello | Oakwood | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25297 | Blue Heron Second Transformer | Other | 28459 | 28459-Blue Heron- | Install new 69/13.8 kV transformer with LTC at Blue Heron substation. | XEL | M2 - Appendix A Approved | 10000000 | 2028-05-31 | Transformer | Transformer New | Blue Heron |  |  | 69 | 14 |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25340 | Albany Second Transformer | Other | 28460 | 28460-Albany- | Install new Albany TR3 69/12.5 kV transformer and replace existing TR2 both with 14 MVA transformers on the West side of the Albany substation yard. | XEL | M2 - Appendix A Approved | 5000000 | 2029-09-28 | Transformer | Transformer New | Albany |  |  | 69 | 13 |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25340 | Albany Second Transformer | Other | 28461 | 28461-Albany- | Rebuild and relocate NSP's facilities on the west side of the Albany substation yard. | XEL | M2 - Appendix A Approved | 500000 | 2029-09-28 | Substation | Substation bus upgrade | Albany |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25324 | Downing Substation | Other | 28462 | 28462-Downing- | Install new distribution substation in the Downing area. | XEL | M2 - Appendix A Approved | 4000000 | 2027-12-17 | Substation | Substation (breakers only, no transformer) | Downing |  |  | 69 | 24 |  |  | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25325 | 0986 K Frame Replacement | Other | 28463 | 28463-Prairie Island-Red Rock | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0986. | XEL | M2 - Appendix A Approved | 12147306 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Prairie Island | Red Rock | 2 | 345 |  |  | 31 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25341 | 0987 K Frame Replacement | Other | 28464 | 28464-Red Rock-Prairie Island | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0987. | XEL | M2 - Appendix A Approved | 13047661 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Red Rock | Prairie Island | 1 | 345 |  |  | 31 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25342 | Missouri Creek Substation | Other | 28465 | 28465-Missouri Creek- | Rebuild Eau Galle distribution substation as new Missouri Creek substation and convert existing Eau Galle distribution to 23.9kV. | XEL | M2 - Appendix A Approved | 9000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Missouri Creek |  |  | 69 | 24 |  |  | WI |  | Not Shared
MTEP24 | A | METC | East | 25275 | METC SPOF Blanket | BRP | 28478 | 28478-Throughout METC system- | System violations throughout METC system that are caused by single point of failure (SPOF) contingencies. | METC | M2 - Appendix A Approved | 19500000 | 2029-06-01 | Substation | Small miscellaneous substation equipment | Throughout METC system |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 25276 | Conway 138kV Add Breakers and Aging Infrastructure | Other | 28479 | 28479-Conway- | Add interrupting devices on XFMRs 1,2,3,4 Add Line BKRs to MASN-WLDW-1&2, CNWY-TYSN-3&4 Aging infrastructure replacements | AmerenMO | M2 - Appendix A Approved | 2500000 | 2027-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Conway |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP24 | A | METC | East | 25277 | METC Customer Interconnections - 2027 | Other | 28480 | 28480-METC Facilities- | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | METC | M2 - Appendix A Approved | 2500000 | 2027-12-31 | Substation | Small miscellaneous substation equipment | METC Facilities |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25327 | METC Asset Replacement Program - 2026 | Other | 28482 | 28482-METC Facilities- | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. | METC | M2 - Appendix A Approved | 53960000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | METC Facilities |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 28484 | 28484-St Louis County-New 345/230kV Substation | New 345/230kV Substation, 1x 345kV line entrance, 1000 MVA transformer, 2x 230kV line entrances (includes 345 kV line from HVDC station) | MP | M2 - Appendix A Approved | 45000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | St Louis County | New 345/230kV Substation |  | 345 | 230 | 0.5 |  | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 28485 | 28485-St Louis County-Arrowhead Ckts 1&2 | Two new 230 kV lines from St Louis County to existing Arrowhead 230 kV bus | MP | M2 - Appendix A Approved | 5000000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | St Louis County | Arrowhead Ckts 1&2 |  | 230 |  | 1 |  | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 28487 | 28487-Arrowhead-230kV Line Entrances | Upgrade existing 230kV HVDC bus and equipment from line entrances to existing Pole 1 & 2 line entrance positions. Capacity increased to 1000MVA | MP | M2 - Appendix A Approved | 5000000 | 2028-12-31 | Substation | Substation bus upgrade | Arrowhead | 230kV Line Entrances |  | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 28489 | 28489-Nelson Lake-345-230kV Sub Expansion | Expand planned Nelson Lake Substation to include 345/230kV transformer (1000MVA) and 1x 345 kV line entrance | MP | M2 - Appendix A Approved | 30000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Nelson Lake | 345-230kV Sub Expansion |  | 345 | 230 |  |  | ND |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 25279 | Replace Pole and Insulator Program - MTEP24 | Other | 28491 | 28491-Multiple- | Replace Pole and Insulators | AmerenIL, AmerenMO | M2 - Appendix A Approved | 20000000 | 2026-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Multiple |  |  | 345 | 138 |  |  | IL | MO | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 4295 | HVDC Modernization Project | TDSP | 28492 | 28492-East Oliver-Nelson Lake 345kV | New double-circuit capable 345kV line connecting HVDC to Nelson Lake | MP | M2 - Appendix A Approved | 10000000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | East Oliver | Nelson Lake 345kV |  | 345 |  | 3.5 |  | ND |  | Not Shared
MTEP24 | A | ITC | East | 25363 | ITCT SPOF Blanket | BRP | 28494 | 28494-Throughout ITC System- | 2029 blanket for projects to address locations where single point of failure (SPOF) are identified that cause system issues. | ITCT | M2 - Appendix A Approved | 12100000 | 2029-06-01 | Substation | Small miscellaneous substation equipment | Throughout ITC System |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 25362 | Replace Breakers and Relays Program - MTEP24 | Other | 28495 | 28495-All- | Miscellaneous breaker and relay replacements. | AmerenIL, AmerenMO | M2 - Appendix A Approved | 5000000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | All |  |  | 345 | 138 |  |  | MO | IL | Not Shared
MTEP24 | A | ITC | East | 25364 | ITCT Customer Interconnections - 2027 | Other | 28496 | 28496-ITCT Facilities- | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | ITCT | M2 - Appendix A Approved | 2500000 | 2027-12-31 | Substation | Small miscellaneous substation equipment | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 25366 | ITCTransmission Asset Replacement Program - 2026 | Other | 28498 | 28498-ITCT Facilities- | Replace aging and outdated equipment at a pace that will ensure each type of equipment is replaced near its projected end of life. | ITCT | M2 - Appendix A Approved | 60700000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25345 | ITCM Cleveland to Sheas Lake Rebuild | Other | 28500 | 28500-Cleveland-Sheas Lake | The ITCM portion of the Cleveland – Sheas Lake 69 kV line was originally constructed in the 1960’s and is at end of life and is approaching eminent failure condition. In addition, this line has been identified as needing to have it’s thermal rating increased and also due to it connecting between two areas with 115 kV infrastructure, it should be built to allow for future conversion to 115 kV operation if/as needed. | ITCM | M2 - Appendix A Approved | 22306250 | 2029-12-30 | Line Upgrade | Line rebuild on existing ROW | Cleveland | Sheas Lake | 1 | 69 | 69 |  |  | MN |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25346 | ITCM Walcott 80 Substation Interconnection | Other | 28501 | 28501-Walcott 80-Substation | IPL has notified ITC that they will be constructing a new Walcott 80 Substation which will replace their existing Walcott and Walcott North substations. The new substations will initially connect at 34.5 kV and then be converted to 69 kV as part of the Fulton – Dixon 69 kV conversion. IPL has requested ITC install two 69 kV busses with two line breakers and a bus tie breaker. New line taps for Walcott 80 substation to be constructed with T2-4/0 ACSR conductor. While operating at 34.5 kV, one new breaker looking toward Calamus 3350 should be operated as the new normal open point, with PTS 3372 becoming normally closed to allow the Walcott 80 load to be switched between the two 34.5 kV sources. Existing taps to Walcott and Walcott North to be retired under separate future EI Sketches prior to 69 kV conversion. | ITCM | M2 - Appendix A Approved | 3685151 | 2026-12-30 | Substation | Substation (breakers only, no transformer) | Walcott 80 | Substation |  | 69 | 34 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25346 | ITCM Walcott 80 Substation Interconnection | Other | 28502 | 28502-Walcott 80-Line Taps | IPL has notified ITC that they will be constructing a new Walcott 80 Substation which will replace their existing Walcott and Walcott North substations. The new substations will initially connect at 34.5 kV and then be converted to 69 kV as part of the Fulton – Dixon 69 kV conversion. IPL has requested ITC install two 69 kV busses with two line breakers and a bus tie breaker. New line taps for Walcott 80 substation to be constructed with T2-4/0 ACSR conductor. While operating at 34.5 kV, one new breaker looking toward Calamus 3350 should be operated as the new normal open point, with PTS 3372 becoming normally closed to allow the Walcott 80 load to be switched between the two 34.5 kV sources. Existing taps to Walcott and Walcott North to be retired under separate future EI Sketches prior to 69 kV conversion. | ITCM | M2 - Appendix A Approved | 347500 | 2026-12-30 | Line New | New Transmission line, new ROW - may include terminations | Walcott 80 | Line Taps |  | 69 | 34 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25346 | ITCM Walcott 80 Substation Interconnection | Other | 28503 | 28503-Walcott 80-Substation Conversion to 69 kV | Covert the 34 kV operated sub to 69 kV operation along with the Dixon-Fulton conversion. | ITCM | M2 - Appendix A Approved | 442821 | 2029-12-30 | Substation | Substation (breakers only, no transformer) | Walcott 80 | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25348 | Saratoga – 7 Mile Creek 138 kV, Construct New Line | Other | 28505 | Saratoga – 7 Mile Creek Line Work | • Construct a new Saratoga – 7 Mile Creek (X-New) 138-kV line, double-circuiting it with existing Saratoga – ACEC Grant (Y-301) 69-kV line. • At 7 Mile Creek SS, relocate existing 7 Mile Creek – Sand Lake (X-11) 138-kV line to connect the new line at existing X-11’s terminal. In addition, construct a new section of approx. 0.05 miles on X-11 for its interconnection to bus 4, eliminating the need for 138-kV crossings. | ATC | M3 - Under Construction | 4200000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Saratoga | 7 Mile Creek |  | 138 | 69 | 1.1 |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25348 | Saratoga – 7 Mile Creek 138 kV, Construct New Line | Other | 28506 | Saratoga – 7 Mile Creek SS Work | • At 7 Mile Creek SS, relocate existing 7 Mile Creek – Sand Lake (X-11) 138-kV line to connect the new line at existing X-11’s terminal. In addition, construct a new section of approx. 0.05 miles on X-11 for its interconnection to bus 4, eliminating the need for 138-kV crossings. Finally, install new 138 kV substation equipment (breaker and switch) at 7 Mile Creek to complete its 4-position ring bus. • At Saratoga SS, install one 138-kV line circuit breaker with manual line and bus-side disconnect switches for the new line. In addition, install a new 138-kV bus-tie breaker and replace Saratoga – Badger West (X-43) 138-kV line jumpers, and buses 1 and 2 jumpers, to allow higher ratings on existing facilities. Finally, reroute X-159 line preventing it from being above the new line’s terminal. • After Northern Adams County Area Network Improvement Project is placed in service in 2027, retire Saratoga 138/69-kV T33 transformer and re-terminate the new line with this vacated position. | ATC | M3 - Under Construction | 4200000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Saratoga | 7 Mile Creek |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25332 | WVPA Pike 69kV Line Rebuild | Other | 28508 | 28508-WVPA Pike 69kV Line Rebuild- | WVPA Pike 69kV Line Rebuild - Rebuild 69kV line feeding Pike substation | DEI | M2 - Appendix A Approved | 15000000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | WVPA Pike 69kV Line Rebuild |  |  | 69 |  |  | 7.9 | IN |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25333 | Westfield 156th St 69/12kV Sub | Other | 28509 | 28509-Westfield 156th St 69/12kV Sub- | Westfield 156th St 69/12kV Sub (new sub) - Loop 69142 line through Sub; transfer 69155 wire to 5 new poles | DEI | M3 - Under Construction | 3442000 | 2026-06-19 | Substation | Distribution substation - may include trans high side | Westfield 156th St 69/12kV Sub |  |  | 69 | 12 | 0.5 | 0.25 | IN |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25334 | Kokomo Webster St Ckt Brkr Replacements | Other | 28510 | 28510-Kokomo Webster St-230 CBs | Kokomo Webster St Ckt Brkr Replacements - 230kV: replace (2) oil CBs (23022-20 and 230B2-22) and their disconnect switches (motorize); replace all 230kV relays; install SCADA controlled line disconnect switches (23016, 23020 & 23022) and upgrade wave traps as needed; Upgrade RTU and DC power supply systems | DEI | M2 - Appendix A Approved | 2800000 | 2027-12-16 | Substation | Circuit Breaker (replacement at existing substation) | Kokomo Webster St | 230 CBs |  | 230 |  |  |  | IN |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25334 | Kokomo Webster St Ckt Brkr Replacements | Other | 28511 | 28511-Kokomo Webster St-69 CBs | Kokomo Webster St Ckt Brkr Replacements - 69kV: Replace (4) oil CBs (69173, 69174, 6912-1 and 69230-2) and their disconnect switches as needed; replace all 69kV relays | DEI | M2 - Appendix A Approved | 3500000 | 2027-05-27 | Substation | Circuit Breaker (replacement at existing substation) | Kokomo Webster St | 69 CBs |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25368 | W3418 Insulator Replacement And Refurb | Other | 28517 | 28517-Owen Area Substation-Lakehead Pump | W3418 line refurb on 2.8 miles from structures 716-762. | XEL | M2 - Appendix A Approved | 500000 | 2026-04-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Owen Area Substation | Lakehead Pump | 1 | 69 |  |  | 2.8 | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25370 | W3401 Insulator Replacement And Refurb | Other | 28519 | 28519-Blair-Alma Center | W3401 line refurb on 18.8 miles from Alma Center to Blair. | XEL | M2 - Appendix A Approved | 1000000 | 2026-02-10 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Blair | Alma Center | 1 | 69 |  |  | 18.8 | WI |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25350 | New Waynesville 345kV Station | Other | 28523 | 28523-08BEDFRD-08COLMBU | 345 kV ring bus substation with 4 breakers and two 345 kV :69 kV transformers. A 69kV ring-bus station one the low-side. | HE | M2 - Appendix A Approved | 33000000 | 2028-05-31 | Substation | Substation (breakers only, no transformer) | 08BEDFRD | 08COLMBU |  | 345 | 69 |  |  | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25350 | New Waynesville 345kV Station | Other | 28524 | 28524-Waynesville-Ogilville | New ~4.5 mile, 69kV, line from Waynesville to Ogilville | HE | M2 - Appendix A Approved | 8000000 | 2028-05-31 | Line New | New Transmission line, new ROW - may include terminations | Waynesville | Ogilville |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25350 | New Waynesville 345kV Station | Other | 28525 | 28525-Ogilville Jct-Ogilville | Rebuild 1.75-mile, 69kV line from Ogilville Jct to Ogilville sub | HE | M2 - Appendix A Approved | 4000000 | 2028-05-31 | Line Upgrade | Line rebuild on existing ROW | Ogilville Jct | Ogilville |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25350 | New Waynesville 345kV Station | Other | 28526 | 28526-Waynesville-Walesboro | New ~4.5 mile, 69kV line, from Waynesville Station to Walesboro | HE | M2 - Appendix A Approved | 11000000 | 2028-05-31 | Line New | New Transmission line, new ROW - may include terminations | Waynesville | Walesboro |  | 69 |  | 4.5 |  | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25350 | New Waynesville 345kV Station | Other | 28527 | 28527-Walesboro Jct-Woodside | New 1.2-mile, 69kV line | HE | M2 - Appendix A Approved | 2160000 | 2028-05-31 | Line New | New Transmission line, new ROW - may include terminations | Walesboro Jct | Woodside |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25381 | Long Siding - Princeton Area Projects | Other | 28529 | 28529-Long Siding-Milaca | Rebuild Long Siding - Milaca | GRE | M2 - Appendix A Approved | 4449792 | 2027-12-19 | Line Upgrade | Line rebuild on existing ROW | Long Siding | Milaca | 1 | 69 |  |  | 8.6 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25381 | Long Siding - Princeton Area Projects | Other | 28530 | 28530-Long Siding-Princeton | Rebuild Long Siding to Princeton | GRE | M2 - Appendix A Approved | 924029 | 2027-12-19 | Line Upgrade | Line rebuild on existing ROW | Long Siding | Princeton | 1 | 69 |  |  | 1.6 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25381 | Long Siding - Princeton Area Projects | Other | 28531 | 28531-Long Siding- | Replace Long Siding tap switch | GRE | M2 - Appendix A Approved | 354937 | 2027-12-19 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Long Siding |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25337 | Meadowbrook to Side Lake Area Projects | Other | 28532 | 28532-Meadowbrook-Side Lake | Rebuild Meadowbrook to Side Lake | GRE | M2 - Appendix A Approved | 14750435 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Meadowbrook | Side Lake | 1 | 69 |  |  | 15 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25338 | Victor to Woodland Rebuild Projects | Other | 28533 | 28533-Victor-Woodland | Rebuild Victor to Woodland. | GRE | M2 - Appendix A Approved | 5905484 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Victor | Woodland | 1 | 69 |  |  | 8.6 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25338 | Victor to Woodland Rebuild Projects | Other | 28534 | 28534-Woodland-DX Line | Rebuild Woodland to DX line. | GRE | M2 - Appendix A Approved | 6374506 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Woodland | DX Line | 1 | 69 |  |  | 5.8 | MN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25372 | New 345-138 kV Monrovia Substation | Other | 28536 | Monrovia Substation | 2 bay 345/138 kV breaker-and-a-half substation with 2 40 MVA transformers. | IPL | M2 - Appendix A Approved | 35348000 | 2031-06-30 | Substation | Substation (breakers only, no transformer) | Monrovia |  |  | 345 | 138 |  |  | IN |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25352 | J1833 Generator Interconnection | GIP | 28537 | 28537-Leeville- | Supporting the interconnection of Gas Generator (J1833) at the Leeville 115 kV station. | Entergy-LA | M2 - Appendix A Approved | 17825000 | 2027-04-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Leeville |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25353 | Replace Southwest 138 kV #1 Breaker | Other | 28539 | Southwest Substation | Replacement of 1 138 kV breaker at Southwest. Breaker #1. | IPL | M3 - Under Construction | 900000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Southwest |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25383 | Replace South 138 kV Breakers | Other | 28540 | 28540-South-Substation | Replace 3 breakers. #1, #2, and #3 | IPL | M2 - Appendix A Approved | 2700000 | 2026-11-30 | Substation | Circuit Breaker (replacement at existing substation) | South |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25384 | Replace East 138 kV Breakers | Other | 28541 | 28541-East-Substation | Replace 5 138 kV breakers. #1, #2, #4, #5, and #7. | IPL | M2 - Appendix A Approved | 4500000 | 2026-08-31 | Substation | Circuit Breaker (replacement at existing substation) | East |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25354 | Replace Parker 138 kV Breakers | Other | 28542 | 28542-Parker-Substation | Replace 3 138 kV breakers. #1, #2, and #3. | IPL | M2 - Appendix A Approved | 2700000 | 2026-09-30 | Substation | Circuit Breaker (replacement at existing substation) | Parker |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25402 | Replace Petersburg 138 kV #4 Breaker | Other | 28545 | Petersburg Substation | Replace 1 138 kV breaker at Petersburg. Breaker #4. | IPL | M2 - Appendix A Approved | 900000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Petersburg |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25385 | Replace Petersburg 345 kV Breakers | Other | 28546 | 28546-Petersburg-Substation | Replace 6 345 kV breakers. #3A, #3B, #3C, #4A, #4B, and #4C. | IPL | M2 - Appendix A Approved | 5400000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Petersburg |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25386 | Replace North 138 kV Breakers | Other | 28547 | 28547-North-Substation | Replace 2 138 kV breakers. #3 and #4. | IPL | M2 - Appendix A Approved | 1800000 | 2026-09-25 | Substation | Circuit Breaker (replacement at existing substation) | North |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25387 | Replace Prospect 138 kV #2 Breaker | Other | 28548 | 28548-Prospect-Substation | Replace 1 138 kV breaker at Prospect. Breaker #2. | IPL | M2 - Appendix A Approved | 716236 | 2026-05-31 | Substation | Circuit Breaker (replacement at existing substation) | Prospect |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25389 | Replace Northeast 138 kV Breakers | Other | 28549 | 28549-Northeast-Substation | Replace 2 138 kV breakers. #1 and #3. | IPL | M2 - Appendix A Approved | 1800000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Northeast |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25388 | Cleveland Breaker Replacement | Other | 28550 | 28550-Cleveland- | Replace breakers at Cleveland substation. | GRE | M2 - Appendix A Approved | 1367918 | 2026-06-30 | Substation | Circuit Breaker (replacement at existing substation) | Cleveland |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25390 | Replace Brookwood 138 kV Breakers | Other | 28551 | 28551-Brookwood-Substation | Replace 2 138 kV breakers. #1 and #2 | IPL | M2 - Appendix A Approved | 1800000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Brookwood |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25391 | Mud Lake to Riverton 230 kV Upgrade | Other | 28552 | 28552-Mud Lake-Riverton | Upgrade Mud Lake - Riverton 230 kV line. | GRE | M2 - Appendix A Approved | 1146876 | 2027-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mud Lake | Riverton | 1 | 230 |  |  | 5.6 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25374 | Blackberry Area Rebuild Projects | Other | 28555 | 28555-Arbo Switch-Gunn | Rebuild from 1.1 miles of the line from Arbo Switch to just south of Gunn substation. | GRE | M2 - Appendix A Approved | 1377043 | 2025-11-17 | Line Upgrade | Line rebuild on existing ROW | Arbo Switch | Gunn | 1 | 69 |  |  | 1.1 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25374 | Blackberry Area Rebuild Projects | Other | 28556 | 28556-Blackberry-Enbridge Blackberry Tap | Rebuild 1.07 miles of the Blackberry to Enbridge Blackberry Tap line. | GRE | M2 - Appendix A Approved | 3074573 | 2025-10-31 | Line Upgrade | Line rebuild on existing ROW | Blackberry | Enbridge Blackberry Tap | 1 | 69 |  |  | 1.07 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25374 | Blackberry Area Rebuild Projects | Other | 28557 | 28557-Enbridge Blackberry-Enbridge Blackberry Tap | Rebuild 0.76 miles of the Enbridge Blackberry to Enbridge Blackberry Tap line. | GRE | M2 - Appendix A Approved | 1256824 | 2025-11-10 | Line Upgrade | Line rebuild on existing ROW | Enbridge Blackberry | Enbridge Blackberry Tap | 1 | 69 |  |  | 0.76 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25374 | Blackberry Area Rebuild Projects | Other | 28560 | 28560-Enbridge Blackberry Tap-Warba | Rebuild 3.76 miles of the Enbridge Blackberry Tap to Warba line. | GRE | M2 - Appendix A Approved | 4726830 | 2027-04-30 | Line Upgrade | Line rebuild on existing ROW | Enbridge Blackberry Tap | Warba | 1 | 69 |  |  | 3.76 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25374 | Blackberry Area Rebuild Projects | Other | 28561 | 28561-Goodland-Warba | Rebuild 7.4 miles of the Goodland to Warba line. | GRE | M2 - Appendix A Approved | 5876908 | 2027-12-10 | Line Upgrade | Line rebuild on existing ROW | Goodland | Warba | 1 | 69 |  |  | 7.4 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25357 | BYN-NRH Pilot Channel Replacement | Other | 28562 | 28562-Byron-North Rochester | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | XEL | M2 - Appendix A Approved | 242000 | 2026-06-12 | Misc. | Communication equipment | Byron | North Rochester | 1 | 345 |  |  | 14 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25375 | W3415 EGA-DUR-ARK Insulator Replacement and Refurbishment | Other | 28563 | 28563-Eau Galle-Durand | Line W3415 refurb and insulator replacement on 5.9 miles between Eau Galle - Durand. | XEL | M2 - Appendix A Approved | 1000000 | 2027-04-15 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Eau Galle | Durand | 1 | 69 |  |  | 5.9 | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25375 | W3415 EGA-DUR-ARK Insulator Replacement and Refurbishment | Other | 28564 | 28564-Durand-Arkansas | Line W3415 refurb and insulator replacement on 5.5 miles between Durand - Arkansas. | XEL | M2 - Appendix A Approved | 1000000 | 2027-04-15 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Durand | Arkansas | 1 | 69 |  |  | 5.5 | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25376 | Line 0876 Redwood Falls Tap Switch Replacement | Other | 28565 | 28565-Redwood Falls- | Line 0876 Switch 278 replacement at SMMPA Redwood Falls tap. | XEL | M2 - Appendix A Approved | 350000 | 2027-10-29 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Redwood Falls |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25378 | Gaylord Substation Rebuild | Other | 28567 | 28567-Dryden 69kV Substation | Rebuild Gaylord substation as Dryden substation at a new location, converting 4.16kV feeders to 13.8kV. | XEL | M2 - Appendix A Approved | 1733000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Gaylord |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25379 | Rebuild Wabasha Substation | Other | 28568 | 28568-Wabasha- | Rebuild Wabasha substation at a nearby location due to flooding concerns. | XEL | M2 - Appendix A Approved | 10000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Wabasha |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25422 | Airport Substation Breaker Addition | Other | 28571 | 28571-Airport Substation- | Add 3 breakers to Airport substation. | GRE | M2 - Appendix A Approved | 5692565 | 2026-09-30 | Substation | Switching station (breakers only, no transformer) | Airport Substation |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25423 | Fox Lake Area Upgrades | Other | 28572 | 28572-Dunnel-Fox Lake Tap | Rebuild the Dunnel to Fox Lake tap line. | GRE | M2 - Appendix A Approved | 5255229 | 2027-09-30 | Line Upgrade | Line rebuild on existing ROW | Dunnel | Fox Lake Tap | 1 | 69 |  |  | 4 | MN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25403 | Replace Newtonville T2 and T3 Transformers and Circuit Breakers | Other | 28573 | 28573-Newtonville- | Replacing 161/138kV transformer, 138/69kV transformer and circuit breakers. | SIGE | M2 - Appendix A Approved | 18500000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Newtonville |  |  | 161 |  |  |  | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25423 | Fox Lake Area Upgrades | Other | 28574 | 28574-Fox Lake-Fox Lake Tap | Rebuild 6 miles of the Fox Lake to Fox Lake tap. | GRE | M2 - Appendix A Approved | 7214678 | 2027-06-30 | Line Upgrade | Line rebuild on existing ROW | Fox Lake | Fox Lake Tap | 1 | 69 |  |  | 6 | MN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25406 | Replace Santa Claus Substation 69 kV Protection | Other | 28576 | 28576-Santa Claus- | Replace high side transformer fuse and switch number 199 with a circuit switcher. | SIGE | M2 - Appendix A Approved | 1500000 | 2027-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Santa Claus |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25407 | Replace Angel Mounds 138 kV Circuit Breakers and Switches | Other | 28578 | 28578-Angel Mounds- | Replacing several 138kV circuit breakers and switches | SIGE | M2 - Appendix A Approved | 3000000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Angel Mounds |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25393 | Replace Chrisney Substation Circuit Breakers and Switches | Other | 28579 | 28579-Chrisney- | Replace existing circuit breakers ‘188’ and ‘288’ and their associated foundations, disconnect switches, and protective relaying. Replace existing regulators with new 600A regulators. | SIGE | M2 - Appendix A Approved | 2740000 | 2026-10-01 | Substation | Circuit Breaker (replacement at existing substation) | Chrisney |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25359 | Louis Allis Switch Replacement | Other | 28580 | 28580-Louis Allis- | Replacing several switches and distribution breakers | SIGE | M2 - Appendix A Approved | 2300000 | 2029-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Louis Allis |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25394 | Midway 69/2.4kV Transformer Replacement | Other | 28581 | 28581-Midway- | Replacing several 69/2.4kV transformers and switches | SIGE | M2 - Appendix A Approved | 2000000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Midway |  |  | 69 | 2 |  |  | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25395 | Replace Oakland City 69/15 kV Transformer and Substation Circuit Breakers | Other | 28582 | 28582-Oakland City- | Replacing 69/15kV transformer and 69kV circuit breakers | SIGE | M3 - Under Construction | 2700000 | 2026-06-15 | Substation | Substation (breakers only, no transformer) | Oakland City |  |  | 69 | 15 |  |  | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25442 | Rebuild Line Z91-1 NW - Pigeon Creek Transmission | Other | 28585 | 28585-NW-Pigeon Creek | Rebuilding ~3 miles of 138kV line from 795 to 954 | SIGE | M3 - Under Construction | 11000000 | 2026-06-15 | Line Upgrade | Line reconductor | NW | Pigeon Creek | 91-1 | 138 |  |  | 3 | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25443 | Rebuild Z84-1 Culley - Dubois 138 kV Line | Other | 28586 | 28586-Culley-Tennyson | Replacing ~20 miles of poles for the 138kV line from Culley to Tennyson | SIGE | M2 - Appendix A Approved | 27500000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Culley | Tennyson | 84-1 | 138 |  |  | 20 | IN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25443 | Rebuild Z84-1 Culley - Dubois 138 kV Line | Other | 28587 | 28587-Tennyson-Dubois | Replace ~13 miles of poles on the 138kV line from Tennyson to Dubois | SIGE | M2 - Appendix A Approved | 20000000 | 2027-09-01 | Line Upgrade | Line rebuild on existing ROW | Tennyson | Dubois | 84-1 | 138 |  |  | 13 | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25358 | Burnsville Area Projects | Other | 28588 | 28588-Burnsville- | Expand Burnsville substation 115 kV bus. | GRE | M2 - Appendix A Approved | 21509092 | 2030-03-15 | Substation | Substation bus upgrade | Burnsville |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25212 | ITC Midwest Asset Replacement Program 2026 | Other | 28589 | 28589-ITCM Asset Blanket for 2026-Throughout system | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | ITCM | M2 - Appendix A Approved | 52625000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | ITCM Asset Blanket for 2026 | Throughout system |  | 345 | 69 |  |  | IA | MN | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25213 | ITC Midwest SCADA Controlled Motor Operated Switch Addition Program 2025 | Other | 28590 | 28590-Blanket for SCADA M.O. Switches for2025-Throughout system | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be utilized to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | ITCM | M2 - Appendix A Approved | 3125000 | 2026-07-30 | Line New | New Transmission line, new ROW - may include terminations | Blanket for SCADA M.O. Switches for2025 | Throughout system |  | 69 | 69 |  |  | IA | MN | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25396 | Otsego Area Rebuilds | Other | 28592 | 28592-Albertville-Black Lake Tap | Rebuild 12 miles of the Albertville to Black Lake tap line. | GRE | M2 - Appendix A Approved | 17075410 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Albertville | Black Lake Tap | 1 | 69 |  |  | 12 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25396 | Otsego Area Rebuilds | Other | 28593 | 28593-Albertville-Otsego | Rebuild 8 miles of the Albertville to the double circuit EMX line east of the Otsego substation. | GRE | M2 - Appendix A Approved | 14820167 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Albertville | Otsego | 1 | 69 |  |  | 8 | MN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25397 | New Tepe Park 138/15 kV Distribution Transformer | Other | 28594 | 28594-Tepe Park- | Replacing 138/15kV transformer and breakers | SIGE | M3 - Under Construction | 4000000 | 2026-07-15 | Substation | Substation (breakers only, no transformer) | Tepe Park |  |  | 138 | 15 |  |  | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25396 | Otsego Area Rebuilds | Other | 28595 | 28595-Black Lake Tap-Maple Lake | Rebuild 5 miles of the Black Lake tap to Maple Lake line. | GRE | M2 - Appendix A Approved | 8182839 | 2029-02-28 | Line Upgrade | Line rebuild on existing ROW | Black Lake Tap | Maple Lake | 1 | 69 |  |  | 5 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25445 | Prairie Woods to Sunburg Rebuild | Other | 28597 | 28597-Prairie Woods Tap-Sunburg | Rebuild 7.2 miles of the Prairie Woods tap to Sunburg line. | GRE | M2 - Appendix A Approved | 7649388 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Prairie Woods Tap | Sunburg | 1 | 69 |  |  | 7.2 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28606 | 28606-Jamestown Tap GRE-Jamestown Tap Xcel | Rebuild from 2.8 miles of the GRE Jamestown Tap to the Xcel Jamestown Tap line. | GRE | M2 - Appendix A Approved | 3265967 | 2028-02-01 | Line Upgrade | Line rebuild on existing ROW | Jamestown Tap GRE | Jamestown Tap Xcel | 1 | 69 |  |  | 2.8 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28607 | 28607-St. Thomas Tap-Sheas Lake | Rebuild 3.43 miles from the St. Thomas Tap (AKA ITC Le Center Tap) switch to the Sheas Lake double circuit line. | GRE | M2 - Appendix A Approved | 3293491 | 2027-04-22 | Line Upgrade | Line rebuild on existing ROW | St. Thomas Tap | Sheas Lake | 1 | 69 |  |  | 3.43 | MN |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25447 | Forest & Vermont Breaker Replacements | Other | 28608 | 28608-Forest & Vermont- | Replace overdutied 69 kV breakers | MEC | M2 - Appendix A Approved | 2400000 | 2026-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Forest & Vermont |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25448 | Browns Woods Substation and 161 kV lines | Other | 28609 | 28609-Browns Woods- | Construct new 161-13 kV substation | MEC | M2 - Appendix A Approved | 3500000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Browns Woods |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25448 | Browns Woods Substation and 161 kV lines | Other | 28610 | 28610-Browns Woods-Ashawa | Tap Ashawa-16th & Wabash 161 kV | MEC | M2 - Appendix A Approved | 4750000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Browns Woods | Ashawa | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25448 | Browns Woods Substation and 161 kV lines | Other | 28611 | 28611-Browns Woods-16th & Wabash | Tap Ashawa-16th & Wabash 161 kV | MEC | M2 - Appendix A Approved | 4750000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Browns Woods | 16th & Wabash | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25448 | Browns Woods Substation and 161 kV lines | Other | 28612 | 28612-63rd & Park-Monarch Tap | 63rd & Park Substation and associated 69 kV lines will be retired | MEC | M2 - Appendix A Approved | 200000 | 2026-12-01 | Misc. | Remove existing branch from model | 63rd & Park | Monarch Tap | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25448 | Browns Woods Substation and 161 kV lines | Other | 28613 | 28613-63rd & Park-West Des Moines | 63rd & Park Substation and associated 69 kV lines will be retired | MEC | M2 - Appendix A Approved | 200000 | 2026-12-01 | Misc. | Remove existing branch from model | 63rd & Park | West Des Moines | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28614 | 28614-Cleveland-End of Double Circuit | Rebuild the 1.6 miles of double circuit line from Cleveland substation to the end of the double circuit and interconnection with ITC & Xcel lines. | GRE | M2 - Appendix A Approved | 3455298 | 2027-04-22 | Line Upgrade | Line rebuild on existing ROW | Cleveland | End of Double Circuit |  | 69 |  |  | 1.6 | MN |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25449 | Norwoodville Substation and 69 kV lines | Other | 28615 | 28615-Norwoodville- | Construct new 69 kV switching substation | MEC | M2 - Appendix A Approved | 12900000 | 2028-10-01 | Substation | Substation (breakers only, no transformer) | Norwoodville |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25449 | Norwoodville Substation and 69 kV lines | Other | 28616 | 28616-Norwoodville-E. 46th & Jefferson | Norwoodville-E. 46th & Jefferson 69 kV line | MEC | M2 - Appendix A Approved | 1000000 | 2028-10-01 | Line New | New Transmission line, new ROW - may include terminations | Norwoodville | E. 46th & Jefferson | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25449 | Norwoodville Substation and 69 kV lines | Other | 28617 | 28617-Norwoodville-E. 29th & Hubbell | Norwoodville-E. 29th & Hubbell 69 kV line | MEC | M2 - Appendix A Approved | 1000000 | 2028-10-01 | Line New | New Transmission line, new ROW - may include terminations | Norwoodville | E. 29th & Hubbell | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 28618 | 28618-Pleasant Valley- | Replace breakers and wave trap at Pleasant Valley on the Pleasant Valley - Byron 161 kV line. | GRE | M2 - Appendix A Approved | 1400000 | 2027-08-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Pleasant Valley |  |  | 161 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 3856 | HVDC 900MW Transmission Line Upgrades | TDSP | 20819 | 20819-HVDC Line-MN Structure Upgrades | Structure Upgrades in Minnesota to increase capacity | MP | M2 - Appendix A Approved | 26000000 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | HVDC Line | MN Structure Upgrades |  | 250 |  | 0 | 0 | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 3856 | HVDC 900MW Transmission Line Upgrades | TDSP | 20820 | 20820-HVDC Line-ND Structure Upgrades | Structure Upgrades in North Dakota to increase capacity | MP | M2 - Appendix A Approved | 26000000 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | HVDC Line | ND Structure Upgrades |  | 250 |  | 0 | 0 | ND |  | Not Shared
MTEP24 | A | METC | East | 20034 | Sag Remediate Higgins - Mio Dam 138 kV | BRP | 25732 | 25732-Higgins-Mio Dam | The proposed solution is ITC is to remove the sag limit on the 266.8 ACSR on the Higgins – Mio Dam 138kV line up to the conductor’s limit. | METC | M2 - Appendix A Approved | 2800000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Higgins | Mio Dam | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 20119 | Sag Remediate Claremont - Cornell #2 138 kV | BRP | 25823 | 25823-Claremont-Cornell #2 | METC is to raise the sag limit on the 477 ACSR to 257F and 795 ACSR to 178F on the Bell Road – Cornell section of the Claremont - Cornell #2 138 kV Line | METC | M2 - Appendix A Approved | 1263000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Claremont | Cornell #2 | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25104 | 2nd St. Tap - 30th Ave. 69 kV (N-14), Partial Rebuild | Other | 28235 | 2nd St. Tap - 30th Ave. 69 kV (N-14), Partial Rebuild | Rebuild and install OPGW on approximately 1.5 miles of N-14 from Structure 145364 to 30th Ave. | ATC | M2 - Appendix A Approved | 7500000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | 2nd St. Tap | 30th Ave. | N-14 | 69 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25164 | Menominee - 30th Ave. 69 kV (Y-199), Rebuild | Other | 28236 | Menominee - 30th Ave. 69 kV (Y-199), Rebuild | Rebuild and install OPGW on approximately 1.3 miles of line Y-199 from Menominee SS to 30th Ave. SS. | ATC | M2 - Appendix A Approved | 8400000 | 2029-02-02 | Line Upgrade | Line rebuild on existing ROW | Menominee | 30th Ave. | Y-199 | 69 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25165 | Glory Road - Oak St. 69 kV (GLNY41), Partial Rebuild | Other | 28237 | Glory Road - Oak St. 69 kV (GLNY41), Partial Rebuild | Rebuild and install OPGW on approximately 0.7 miles of line GLNY41 from Glory Rd SS towards Oak St SS. | ATC | M2 - Appendix A Approved | 6000000 | 2029-09-14 | Line Upgrade | Line rebuild on existing ROW | Glory Road | Oak St | GLYN4 | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25181 | J1190 GIA TOIF Calamus East 161 kV Terminal Addition | GIP | 28247 | 28247-Calamus East-Substation | TOIF includes facilities including, 161 kV breaker, switches, dead-end, and equipment at Calamus East substation dedicated to the 161 kV radial line and Generating Facility | ITCM | M2 - Appendix A Approved | 803119 | 2026-10-01 | Line New | New Transmission line, new ROW - may include terminations | Calamus East | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25200 | J1190 GIA NU Calamus East 161 kV Bus Expansion | GIP | 28248 | 28248-Calamus East-Substation | A 161 kV straight bus expansion at the Calamus East station will be constructed for the interconnection of project J1190. | ITCM | M2 - Appendix A Approved | 155146 | 2026-10-01 | Substation | Substation bus upgrade | Calamus East | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25182 | J1313 GIA TOIF Karma 161 kV Terminal Addition | GIP | 28249 | 28249-Karma-Subustation | Transmission Owner Interconnection Facilities include equipment (dead-end, insulators, switch, CCVTs, etc.) dedicated to the J1313 Generating Facility | ITCM | M2 - Appendix A Approved | 427809 | 2028-06-20 | Substation | Small miscellaneous substation equipment | Karma | Subustation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25183 | J1313 GIA NU Karma 161 kV Ring Bus Expansion | GIP | 28250 | 28250-Karma-Substation | Add a 161 kV breaker position in the Karma Substation | ITCM | M2 - Appendix A Approved | 556081 | 2028-04-27 | Substation | Substation (breakers only, no transformer) | Karma | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25202 | J1325 GIA NU Magnolia 161 kV Bus Expansion | GIP | 28251 | 28251-Magnolia-Substation | Expand Magnolia 161 kV substation from a 4-terminal, 4 breaker, ring-bus substation to a 5 terminal ring bus substation. | ITCM | M2 - Appendix A Approved | 486788 | 2026-11-20 | Substation | Substation (breakers only, no transformer) | Magnolia | Substation |  | 161 | 161 |  |  | MN |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25201 | J1325 GIA TOIF Magnolia 161 kV Terminal Addition | GIP | 28252 | 28252-Magnolia-Substation | TOIF includes facilities and equipment dedicated to the Generating Facility including; dead-end, switch, relay panel, CCVTs, etc. | ITCM | M2 - Appendix A Approved | 417240 | 2026-08-31 | Substation | Substation (breakers only, no transformer) | Magnolia | Substation |  | 161 | 161 |  |  | MN |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25220 | Cuba City South, DIC, Sub Expansion | Other | 28253 | Cuba City South, DIC, Sub Expansion | • ATC will construct 0.63 miles of new 69 kV line around the space-constrained Gro Alliance area. • ATC will rebuild 1.12 miles of the existing Cuba City South Tap as a new double circuit 69 kV line to provide a loop-through connection to the Cuba City South Substation. • ATC will construct a loop-through, straight bus substation with two 69 kV line breakers. • Cuba City will install a 69/12.47 kV transformer at Cuba City South. | ATC | M3 - Under Construction | 11000000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Cuba City South |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25221 | J1432 GIA TOIF New Bryant 345 kV Terminal | GIP | 28259 | 28259-Bryant-Substation | TOIF includes facilities and equipment at the Bryant 345 kV switching station dedicated to the 345 kV radial line and Generating Facility | ITCM | M2 - Appendix A Approved | 716244 | 2028-09-01 | Substation | Substation (breakers only, no transformer) | Bryant | Substation |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25222 | J1432 GIA NU New Bryant 345 kV Switch Station | GIP | 28260 | 28260-Bryant-Substation | A new Bryant 345 kV, 3 breaker, ring-bus switching station will be constructed for the interconnection of project J1432. | ITCM | M2 - Appendix A Approved | 8987360 | 2028-09-01 | Substation | Switching station (breakers only, no transformer) | Bryant | Substation |  | 345 | 345 |  |  | IA |  | Shared
MTEP24 | A | ITC MIDWEST | West | 25222 | J1432 GIA NU New Bryant 345 kV Switch Station | GIP | 28261 | 28261-Rock-Salem | The Salem to Rock Creek 345 kV line will be opened and 2 dead-end structures will be installed to allow the line to be looped through the Bryant 345 kV switching station. | ITCM | M2 - Appendix A Approved | 1726000 | 2028-09-01 | Line New | New Transmission line, new ROW - may include terminations | Rock | Salem | 1 | 345 | 345 |  |  | IA |  | Shared
MTEP24 | A | ITC MIDWEST | West | 25222 | J1432 GIA NU New Bryant 345 kV Switch Station | GIP | 28262 | 28262-Rock Creek-Substation | Network upgrades required to install fiber at Rock Creek. | ITCM | M2 - Appendix A Approved | 121752 | 2028-09-01 | Substation | Small miscellaneous substation equipment | Rock Creek | Substation |  | 345 | 345 |  |  | IA |  | Shared
MTEP24 | A | ITC MIDWEST | West | 25222 | J1432 GIA NU New Bryant 345 kV Switch Station | GIP | 28263 | 28263-Bryant-Rock Creek | Install the dual OPGW on the Bryant to Rock Creek 345 kV line. | ITCM | M2 - Appendix A Approved | 1952000 | 2028-09-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Bryant | Rock Creek | 1 | 345 | 345 |  |  | IA |  | Shared
MTEP24 | A | ITC MIDWEST | West | 25205 | ITCM Meservey 69 kV Tap Rebuild | Other | 28268 | 28268-Meservey Tap-Meservey | The radial 6.9 miles Meservey Tap 69 kV line is at the end of its useful life and needs to be rebuilt for continued use. | ITCM | M2 - Appendix A Approved | 4766250 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Meservey Tap | Meservey | 1 | 69 | 69 |  | 6.9 | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25188 | ITCM Boone South 69 kV Substation Interconnection | Other | 28269 | 28269-Boone South-Substation | Build 69kV portion of future IPL Boone South substation | ITCM | M2 - Appendix A Approved | 3761163 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Boone South | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25188 | ITCM Boone South 69 kV Substation Interconnection | Other | 28270 | 28270-Boone South-Substation | Install line taps for the new Boone South substation. | ITCM | M2 - Appendix A Approved | 436250 | 2026-03-31 | Line New | New Transmission line, new ROW - may include terminations | Boone South | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25188 | ITCM Boone South 69 kV Substation Interconnection | Other | 28271 | 28271-Boone Southeast Tap-Boone Southeast | Retire tap and PTSs to existing Boone Southeast station | ITCM | M2 - Appendix A Approved | 166250 | 2026-03-31 | Line New | New Transmission line, new ROW - may include terminations | Boone Southeast Tap | Boone Southeast |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25206 | ITCM Lime Creek 161/69 kV Transformer Replacement | Other | 28272 | 28272-Lime Creek-Substation | Replacing both aging transformers with one new transformer of 150MVA will allow for the same loading on the system. The transformer will only be tied to the L2 bus on the 161kV side, but to both the J1 and the J2 bus on the 69kV side. This is a lower cost option than rebuilding the 161kV into a breaker and a half or adding back in two transformers. | ITCM | M2 - Appendix A Approved | 5690194 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Lime Creek | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25241 | ITCM Newton 8th St Control Enclosure, Relay, and SCADA Replacement | Other | 28273 | 28273-Newton 8th Street-Substation | Replace the existing relaying and SCADA at Leon by ITC installing a new ITC owned control building. IPL owns and maintains this building. Separating the buildings by owner lines up with the current substation standards. | ITCM | M2 - Appendix A Approved | 2655119 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Newton 8th Street | Substation |  | 161 |  |  |  | IA |  | Not Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 28279 | 28279-Lulu- | Construct Lulu 345 kV switching station | ITCT | M2 - Appendix A Approved | 20342722 | 2026-09-01 | Substation | Switching station (breakers only, no transformer) | Lulu |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 28280 | 28280-Maple- | Upgrade line position CI relaying | ITCT | M2 - Appendix A Approved | 300084 | 2028-05-09 | Substation | Small miscellaneous substation equipment | Maple |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 28281 | 28281-Monroe-Milan | Cut the Milan-Monroe-Morcco 345 kV line into the Lulu switchyard | ITCT | M2 - Appendix A Approved | 4768750 | 2026-11-13 | Line New | New Transmission line, new ROW - may include terminations | Monroe | Milan |  | 345 |  | 0.6 |  | MI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25190 | Badger SS Control House, Breaker, and Relay Asset Renewal | Other | 28282 | Badger SS Control House, Breaker, and Relay Asset Renewal | - Replace control building and contents - Replace 138 kV circuit breaker | ATC | M3 - Under Construction | 7875000 | 2026-12-14 | Substation | Substation (breakers only, no transformer) | Badger |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 28284 | 28284-Lemoyne-Majestic | Cut the Lemoyne-Majestic 345 kV line into the Lulu switchyard | ITCT | M2 - Appendix A Approved | 3551250 | 2026-11-13 | Line New | New Transmission line, new ROW - may include terminations | Lemoyne | Majestic |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 28285 | 28285-Milan- | Upgrade position CM, CQ, and CT relaying | ITCT | M2 - Appendix A Approved | 607350 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Milan |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | GIP | 28286 | 28286-Monroe- | Upgrade Monroe position MI relaying | ITCT | M2 - Appendix A Approved | 270254 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Monroe |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 25243 | Rockwood 138kV Aging Infrastructure and Line Breaker Addition | Other | 28288 | 28288-Rockwood- | At Rockwood 138/34.5 kV substation, install three 138 kV line breakers on the Rockwood-Big River-1 line position H2, Gray-Rockwood-3 position H6, Gray-Rockwood-4 position H10 having a 2000 A continuous capability. | AmerenMO | M2 - Appendix A Approved | 4500000 | 2030-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Rockwood |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP24 | A | METC | East | 25244 | Morocco - Replace RH34 Relaying - Multiple Generator Network Upgrade | GIP | 28289 | 28289-Morocco- | Replace position RH34 relaying | METC | M2 - Appendix A Approved | 319323 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Morocco |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | AMEREN MISSOURI | Central | 25225 | Maurer Lake 161 Aging Infrastructure | Other | 28290 | 28290-Maurer Lake- | Replace breaker H9 Bus Tie (G735) and associated switches (G734 and G736) Add disconnect switch and breaker to XFMR 1 and 2 | AmerenMO | M3 - Under Construction | 2400000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Maurer Lake |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21786 | Vestaburg 69kV Relocation | Other | 28292 | 28292-Vestaburg- | In conjunction with the planned relocation of the Vestaburg 69kV station, redesign and install new line exits | WPSC | M2 - Appendix A Approved | 1000000 | 2026-12-31 | Misc. | Line relocation (road move) | Vestaburg |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 25191 | Leroy to South Boardman DC Line Rebuild | Other | 28293 | 28293-Cadillac-South Boardman | Rebuild and upgrade 23 miles of 69 kV line from Cadillac to South Boardman to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | WPSC | M2 - Appendix A Approved | 27600000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Cadillac | South Boardman | 1 | 138 |  |  | 23 | MI |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 25191 | Leroy to South Boardman DC Line Rebuild | Other | 28294 | 28294-Cadillac-Richland | Rebuild and upgrade 5 miles of 69 kV line to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | WPSC | M2 - Appendix A Approved | 6500000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Cadillac | Richland | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 25191 | Leroy to South Boardman DC Line Rebuild | Other | 28295 | 28295-Richland-Leroy | -Rebuild and upgrade 15 miles of 69 kV line to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | WPSC | M2 - Appendix A Approved | 18000000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Richland | Leroy | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25247 | ITCM Abbott - Marshalltown 161 kV Rebuild | Other | 28298 | 28298-Abbott-Marshalltown | ITC will rebuild the Pheonix/SD and Rail portions of Abbott – Marshalltown 161kV circuit with T2-Grosbeak. | ITCM | M2 - Appendix A Approved | 10762500 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Abbott | Marshalltown | 1 | 161 | 161 |  | 7.41 | IA |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25226 | Union Townline, DIC, Sub Expansion | Other | 28300 | Union Townline, DIC, Sub Expansion | • ATC will construct an approximately 0.08 mile 69 kV transmission line extension from the Bass Creek-Sheepskin 69 kV line (Y-158) to the Union Townline substation for a networked substation feed. • ATC will construct a 69 kV loop-through straight bus with line breakers, associated switches, and space reserved for a potential bus-tie breaker. • Evansville Water & Light (WPPI) to install a second 69/12.47 kV transformer with high side circuit switcher protection and necessary low side bus equipment. | ATC | M2 - Appendix A Approved | 6900000 | 2027-05-03 | Substation | Distribution substation - may include trans high side | Union Townline |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | METC | East | 25194 | Cronk-Moore Road Rebuild & Station Equipment Upgrades (J1550, J1635, J1658) - Network Upgrade | GIP | 28301 | 28301-Cronk-Moore Road | Rebuild the Cronk-Moore Road 138 kV circuit utilizing conductor rated at least that of 1431 ACSR. | METC | M2 - Appendix A Approved | 10900000 | 2026-05-15 | Line Upgrade | Line rebuild on existing ROW | Cronk | Moore Road |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25194 | Cronk-Moore Road Rebuild & Station Equipment Upgrades (J1550, J1635, J1658) - Network Upgrade | GIP | 28302 | 28302-Moore Road- | Replace Moore Road conductor and equipment to achieve a rating at least that of 348 MVA SE. | METC | M2 - Appendix A Approved | 423126 | 2026-05-22 | Substation | Small miscellaneous substation equipment | Moore Road |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 25208 | Brownstown #304 345-120 kV Transformer Replacement | Other | 28304 | 28304-Brownstown- | Replace Brownstown 304 345/120kV Transformer. | ITCT | M2 - Appendix A Approved | 6572000 | 2027-11-15 | Transformer | Transformer New | Brownstown |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25209 | Battle Creek-Oneida and Argenta-Tompkins Line Upgrades (J1586) - Network Upgrade | GIP | 28307 | 28307-Battle Creek-Oneida | Cut the Battle Creek-Oneida 345 kV circuit into Oxby station using a conductor rated at least that of 2-1431 ACSR. | METC | M2 - Appendix A Approved | 2263750 | 2026-11-10 | Line Upgrade | Generic transmission line project (try not to use the generic) | Battle Creek | Oneida |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25209 | Battle Creek-Oneida and Argenta-Tompkins Line Upgrades (J1586) - Network Upgrade | GIP | 28308 | 28308-Oxby- | Install Row 31, install 3-345 kV breakers and associated disconnects at positions 31R8, 31H9, and 31F7. Install breakers 29R8 and 33F7 and associated disconnects. | METC | M2 - Appendix A Approved | 8274863 | 2027-02-01 | Substation | Substation (breakers only, no transformer) | Oxby |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25209 | Battle Creek-Oneida and Argenta-Tompkins Line Upgrades (J1586) - Network Upgrade | GIP | 28309 | 28309-Oxby-Oneida | Remediate the sag on the Oxby - Oneida 345 kV line to achieve a rating of at least 1327 MVA SN and 1327 MVA SE | METC | M2 - Appendix A Approved | 2196250 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Oxby | Oneida |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25209 | Battle Creek-Oneida and Argenta-Tompkins Line Upgrades (J1586) - Network Upgrade | GIP | 28310 | 28310-Oxby-Tompkins | Reconductor Oxby-Tompkins 345 kV line with OPGW using 2-1431 ACSR conductor. Approximately 15.7 miles of this reconductor will be completed under LRTP. | METC | M2 - Appendix A Approved | 3443750 | 2026-12-31 | Line Upgrade | Line reconductor | Oxby | Tompkins |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25210 | Replace Moore Road WM33 Trainer (J1658) - Network Upgrade | GIP | 28311 | 28311-Moore Road- | Replace Moore Road WM33 477 ACSR 26/7 trainer with 1590 ACSR to raise rating to 209 MVA SN and 237 MVA SE. | METC | M2 - Appendix A Approved | 27635 | 2026-02-02 | Substation | Small miscellaneous substation equipment | Moore Road |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25227 | Dowling Junction-Knowles Sag Remediation (J1658) - Network Upgrade | GIP | 28312 | 28312-Beecher-Knowles | Remediate Knowles - Dowling Junction sag limit to achieve a rating of at least 240 MVA SN and 266 MVA SE. | METC | M2 - Appendix A Approved | 1098750 | 2026-04-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Beecher | Knowles |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 25195 | MCV 345-138 kV Transformer Addition | BRP | 28313 | MCV - Expand 345 kV and 138 kV Yards | Install six 345 kV breakers to convert the 345 kV side to ring-bus. Expand MCV 138 kV buses, replace 10 existing breakers, and install 3 additional breakers to the west as depicted in the diagram to accommodate the 3rd XFMR at MCV. | METC | M2 - Appendix A Approved | 28000000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | MCV |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25195 | MCV 345-138 kV Transformer Addition | BRP | 28314 | MCV - Install 345-138 kV Transformer #3 | Install a new 345/138 kV transformer and terminated it at the newly created 345 & 138 kV positions. | METC | M2 - Appendix A Approved | 6500000 | 2028-06-01 | Transformer | Transformer New | MCV |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 25228 | DBGEN 41 120 kV Station Rebuild | Other | 28316 | 28316-DBGEN 41- | New station constructed as five rows of breaker and a half 120 kV station. | ITCT | M2 - Appendix A Approved | 62000000 | 2029-03-01 | Substation | Substation (breakers only, no transformer) | DBGEN 41 |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 25228 | DBGEN 41 120 kV Station Rebuild | Other | 28317 | 28317-DBGEN 41- | Reterminate all DB041 lines into the new locations at DBGEN 41 station. | ITCT | M2 - Appendix A Approved | 2200000 | 2029-03-01 | Line New | New Transmission line, new ROW - may include terminations | DBGEN 41 |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25195 | MCV 345-138 kV Transformer Addition | BRP | 28321 | MCV-Tittabawassee #1_Relocate Structure | Relocate a structure to accommodate 345 kV station expansion. | METC | M2 - Appendix A Approved | 1125000 | 2028-06-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | MCV | Tittabawassee | 1 | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25195 | MCV 345-138 kV Transformer Addition | BRP | 28322 | MCV-Tittabawassee #2_Relocate Structure | Relocate a structure to accommodate 345 kV station expansion. | METC | M2 - Appendix A Approved | 1125000 | 2028-06-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | MCV | Tittabawassee | 2 | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25215 | Andes 500/230 kV Substation | Other | 28330 | 28330-Mantero- | Mantero230 kV Substation will connect to the new Andes 500/230 kV station by 2 short transmission lines. | Entergy-MS | M3 - Under Construction | 1 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Mantero |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25215 | Andes 500/230 kV Substation | Other | 28331 | 28331-Andes- | New Andes 500/230 kV station will cut in on the Lakeover - McAdams 500 kV transmission line and feed the Soldiers 230 kV substation. | Entergy-MS | M3 - Under Construction | 158000000 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | Andes |  |  | 500 | 230 |  |  | MS |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25215 | Andes 500/230 kV Substation | Other | 28332 | 28332-Andes- | 2x500/230 kV 720 MVA autotransformers will be installed at the new Andes 500/230 kV station. | Entergy-MS | M3 - Under Construction | 1 | 2027-06-01 | Transformer | Transformer New | Andes |  |  | 500 | 230 |  |  | MS |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50710 | JTIQ Lyon Co - Lakefield Junction | GIP | 51457 | Lyon Co - Lakefield Junction 345kV Line | 345kV line from Lyon County - Lakefield Junction for JTIQ portfolio. |  | M2 - Appendix A Approved | 396000000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Lyon County | Lakefield Junction | 1 | 345 |  | 108.5 |  | MN |  | Not Shared
MTEP24 | A | ITC | East | 50060 | Bismarck - Macomb 120 kV Line | BRP | 50098 | Bismarck-Macomb_ Construct New 120 kV Circuit | Construct a new 120 kV circuit (~6.7 miles) from Bismarck to Macomb. |  | M2 - Appendix A Approved | 8700000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Bismarck | Macomb | 1 | 120 |  | 3.9 | 2.8 | MI |  | Not Shared
MTEP24 | A | ITC | East | 50060 | Bismarck - Macomb 120 kV Line | BRP | 50099 | Bismarck - Add Position JK | Install a new 120 kV breaker at Bismarck position "JK" to terminate the new Bismarck - Macomb 120 kV line. |  | M2 - Appendix A Approved | 1100000 | 2028-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Bismarck |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 50060 | Bismarck - Macomb 120 kV Line | BRP | 50100 | Macomb - Add Position HC | Install a new 120 kV breaker at Macomb position "HC" to terminate the new Bismarck - Macomb 120 kV line. |  | M2 - Appendix A Approved | 1360000 | 2028-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Macomb |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50061 | CAPX Fargo-TC OPWG Replacement | Other | 50101 | Fargo - Twin Cities OPGW Replacement | Replace damaged OPGW on lines 0973 MNN-QRY, 0954 QRY-RVV, 0954 ALS-RVV |  | M2 - Appendix A Approved | 6100000 | 2026-12-15 | Misc. | Communication equipment | Monticello | Alexandria | 1 | 345 |  |  |  | MN | ND | Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 50065 | J1576 Generator Interconnection on the Adams Creek - Angie 230 kV | GIP | 50106 | J1576 Interconnection Adams Creek - Angie | This construction of a new station on the Adams Creek - Angie 230 kV line to accommodate the interconnection of a solar facility (J1576) |  | M2 - Appendix A Approved | 19725228 | 2028-11-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Adams Creek | Angie |  | 230 |  |  |  | LA |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 50068 | HE Taylorsville 69/12kV Sub | Other | 50108 | HE Taylorsville 69/12kV Sub | HE Taylorsville 69/12kV Sub: construct new 22MVA sub at the same location as existing HE Taylorsville sub; to be served radially off the DEI 69146 ckt.; load at HE Taylorsville will be transferred from Edinburgh sub 69/12kV bank #2 = 3MW+/- |  | M3 - Under Construction | 900000 | 2026-06-02 | Substation | Distribution substation - may include trans high side | HE Taylorsville 69/12kV Sub | new distribution sub |  | 69 | 12 | 0 | 0 | IN |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 50086 | Load addition at Montgomery 161 kV Substation | Other | 50126 | Montgomery 161 kV Substation with a new straight bus and terminal | This project will facilitate the connection of a 250 MW datacenter load at Montgomery (161 kV) Substation with a new straight bus and terminal |  | M2 - Appendix A Approved | 2500000 | 2026-12-01 | Substation | Substation bus upgrade | Montgomery |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP24 | A | CLECO POWER LLC | South | 50087 | J1673&J1759 Ft. Jessup Substation | GIP | 50127 | Ft. Jessup Substation | New Ft Jessup substation tapped into the future Marthaville to Belmont 230 kV line 6.8 miles from Marthaville. |  | M2 - Appendix A Approved | 4070667 | 2026-09-01 | Substation | Substation (breakers only, no transformer) | Marthaville | Belmont | 1 | 230 | 230 |  |  | LA |  | Not Shared
MTEP24 | A | ENTERGY ARKANSAS, LLC | South | 50090 | Wheatley 500kV: New POI J1710 J1819 J1820 J1821 | GIP | 50134 | Wheatley 500kV | A new 500kV generator point of interconnection on the Keo - Heth 500kV line. |  | M3 - Under Construction | 32354000 | 2026-09-13 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Wheatley |  |  | 500 |  |  |  | AR |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50091 | Milwaukee County, New DIC | Other | 50136 | Milwaukee County, New DIC | Tap Oak Creek-Oakview 138 kV line to serve new interconnection request. |  | M3 - Under Construction | 3900000 | 2026-11-10 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Oak Creek | Oakview | 836 | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | ENTERGY ARKANSAS, LLC | South | 50093 | Galet 500/230kV New Substation | Other | 50139 | Galet 500/230kV | A new 500/230kV four breaker ring bus substation with two 1200MVA autotransformers and two 230kV lines extending to the customer stations. Two 81 MVAR cap banks will be installed in the 230kV station. |  | M3 - Under Construction | 182000000 | 2027-06-15 | Substation | Distribution substation - may include trans high side | Galet 500/230kV |  |  | 500 | 230 |  |  | AR |  | Not Shared
MTEP24 | A | METC | East | 25522 | Oakland 138 kV Station Rebuild | Other | 50141 | Halsey - Replace Relay Panel | Replace relay panel at Halsey |  | M2 - Appendix A Approved | 294000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Halsey |  | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25454 | East Chain Tie Line Projects | Other | 50142 | East Chain Tie Line | Construct a tie line between East Chain municipal and GRE’s FE-WB (East Chain to Wilbert) line. |  | M2 - Appendix A Approved | 3000000 | 2028-10-06 | Line New | New Transmission line, new ROW - may include terminations | East Chain | East Chain Tap |  | 69 | 69 | 1.75 |  | MN |  | Not Shared
MTEP24 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50094 | Northstar | Other | 50143 | Northstar 115 kV interconnection | Construct 115 kV main & transfer bus with line breakers as per Entergy standards to interconnect. |  | M2 - Appendix A Approved | 3000000 | 2026-09-01 | Substation | Switching station (breakers only, no transformer) | New interconnection |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP24 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50094 | Northstar | Other | 50144 | Northstar substation | Construct 115/13.2 kV, 20 MVA substation. |  | M2 - Appendix A Approved | 4000000 | 2026-09-01 | Substation | Distribution substation - may include trans high side | New interconnection |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50095 | Upgrade Stout CT - CT 4 and 5 Relaying | Other | 50145 | CT 4 Relaying | Relay packages for CT 4 and its GSU |  | M2 - Appendix A Approved | 150000 | 2026-09-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Stout CT |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50095 | Upgrade Stout CT - CT 4 and 5 Relaying | Other | 50146 | CT 5 Relaying | Relay packages for CT 5 and its GSU |  | M2 - Appendix A Approved | 150000 | 2026-09-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Stout CT |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 50096 | Upgrade Stout CT - CT Bus Relaying | Other | 50147 | Stout CT Bus | Relay packages for Stout CT bus section |  | M2 - Appendix A Approved | 125000 | 2026-09-30 | Misc. | Relaying, protection, RTU and SCADA equipment | Stout CT |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 50098 | Hagensville Junction Interconnection | BRP | 50148 | Hagensville Junction to Hagensville | Install 5.7 miles of 795ACSS from Wolverine's Hagensville Junction location to near METC's Hagensville Tap location. |  | M2 - Appendix A Approved | 8550000 | 2025-11-01 | Line New | New Transmission line, new ROW - may include terminations | Hagensville Junction | TBD | 1 | 138 | 138 | 7 |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50184 | Elm Road Generation POI Relocation Project | GIP | 50321 | Elm Road 345 kV Substation expansion | Driven by WEC’s Generating Facility Modification Request to relocate Elm Road generation POIs, this project will expand Elm Road 345 kV substation breaker and a half configuration with three new rungs and six new 345kV breakers. |  | M3 - Under Construction | 18850000 | 2026-08-29 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Elm Road |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | ITC MIDWEST | West | 25307 | ITCM State Center Rural 69 kV Interconnection | Other | 50322 | State Center Rural 69kV Sub | Construct transmission portion of new State Center Rural substation |  | M2 - Appendix A Approved | 2613014 | 2026-12-15 | Substation | Substation (breakers only, no transformer) | State Center Rural | State Center Rural |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ENTERGY ARKANSAS, LLC | South | 50197 | West Memphis 500/161kV Auto Replacement MPFCA | GIP | 50345 | West Memphis 500/161kV Auto Replacement | The existing 500/161kV autotransformer at West Memphis will be replaced with a new 600MVA rated autotransformer. Also, the existing 161kV breaker B2600 will be replaced. |  | M2 - Appendix A Approved | 39117346 | 2027-11-30 | Transformer | Transformer Replacement | West Memphis EHV |  |  | 500 | 161 |  |  | AR |  | Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25399 | Congestion Mitigation Projects | Other | 50360 | Cleveland-Jamestown Tap | Rebuild Cleveland - Jamestown Tap 8.7 miles |  | M2 - Appendix A Approved | 7819920 | 2027-06-30 | Line Upgrade | Line rebuild on existing ROW | Cleveland | Jamestown Tap | 1 | 69 |  |  | 8.7 | MN |  | Not Shared
MTEP24 | A | LAFAYETTE UTILITIES SYSTEM | South | 50139 | J1818 Generator Interconnection at Moss 69kV Station | GIP | 50219 | J1818 69kV Interconnection Facilities | Transmission Owner Interconnection Facilities will consist of a new 69kV rated 4” aluminum IPS bus, 69kV gas circuit breaker, bus support structures, 69kV center break disconnect switches, and incoming transmission line single bay dead end. A revenue accuracy metering panel with power quality monitor will be installed. A line protection panel and breaker control panel will also be installed. |  | M2 - Appendix A Approved | 993000 | 2028-06-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Moss |  |  | 69 |  |  |  | LA |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 24922 | Forest Junction SS and Remote End Relay Asset Renewal | Other | 50220 | Forest Junction SS and Remote End Relay Asset Renewal | Scope of work combines work at Forest Junction with remote end work at Kaukauna Central, Lake Park, Melissa, and Tecumseh Rd. Forest Junction: Replacement of various line relay panels, various 138 kV breaker protection and control panels, various 345 kV breaker protection and control panels, and RTUs. Kaukauna Central: Replacement of one circuit breaker and one line relay panel for line 971K11, one bus protection panel, and GPS Clock. Lake Park: Replacement of 728K21 line protection panel, RTU, and GPS clock. Melissa: Replacement of 971K11 line protection panel. Tecumseh Rd: Replacement of 971K11 and X-106 line projection panels, RTU, two 138 kV and three 69 kV disconnect switches, and three 138 kV bus potential transformers. |  | M2 - Appendix A Approved | 6480000 | 2028-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Forest Junction |  |  | 345 | 69 |  |  | WI |  | Not Shared
MTEP24 | A | METC | East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Other | 50221 | Shale-Twining_Install Cottage Grove Tap & PTS | Install tap structure with two 1-way PTS to connect Cottage Grove to the Shale – Twining 138 kV line (near structure #005F1454). |  | M2 - Appendix A Approved | 1500000 | 2028-09-29 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Cottage Grove | Relocated Line |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25198 | Port Calcite 138 kV Station Rebuild | Other | 50238 | Port Calcite - Rockport 138 kV Line Retermination | Redirect line from Rockport into the new station utilizing 954 ACSR Conductor. |  | M2 - Appendix A Approved | 580000 | 2030-03-05 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Port Calcite | Rockport |  | 138 |  | 1.5 |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25198 | Port Calcite 138 kV Station Rebuild | Other | 50239 | Port Calcite - Riggsville 138 kV Line Retermination | Redirect line from Rockport into the new station utilizing 954 ACSR Conductor. |  | M2 - Appendix A Approved | 580000 | 2030-03-05 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Port Calcite | Riggsville |  | 138 |  | 1.5 |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25198 | Port Calcite 138 kV Station Rebuild | Other | 50240 | Port Calcite - Remove Station Equipment | Remove transmission equipment at Port Calcite. |  | M2 - Appendix A Approved | 551000 | 2030-03-05 | Substation | Small miscellaneous substation equipment | Port Calcite |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | NORTHWESTERN WISCONSIN ELECTRIC CO. | West | 50147 | Frederic To Lewis - 69 KV - Clam Falls Drive Section | Other | 50241 | Frederic To Lewis - 69 KV - Clam Falls Drive Section | Upgrade structure design and wire size |  | M2 - Appendix A Approved | 660000 | 2027-05-01 | Line Upgrade | Line rebuild on existing ROW | Frederic | Lewis |  | 69 |  |  | 2.5 | WI |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50552 | LRTP-19: Bison - Alexandria | MVP | 51213 | Line: Alexandria - MN/ND State Line - 345 kV | Install second 345kV circuit on existing spare position. | GRE, MP, MRES, OTP, XEL | M2 - Appendix A Approved | 176000000 | 2032-06-01 | Line Upgrade | 2nd circuit on existing spare position | Alexandria | MN/ND State Line |  | 345 |  | 0 | 102 | MN |  | Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 50558 | LRTP-25: Pleasant Valley - North Rochester - Hampton Corner | MVP | 51214 | Line: North Rochester - Hampton Corner - 345 kV | Install davit arms, insulators, and conductor for the second 345kV circuit on existing spare position. | DPC, RPU, SMMPA, XEL | M2 - Appendix A Approved | 74000000 | 2032-06-01 | Line Upgrade | 2nd circuit on existing spare position | North Rochester | Hampton Corner |  | 345 |  | 0 | 38 | MN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51215 | Line: Denver - Salt River - 138 kV | Construct one new 138kV line #1 to connect the adjacent Denver and Salt River substations. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 2000000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denver | Salt River |  | 138 |  | 2 | 0 | MI |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | East | 50565 | LRTP-32: Ludington - Denver - Tittabawassee & Nelson Road | MVP | 51216 | Line: Denver - Salt River - 138 kV | Construct one new 138kV line #2 to connect the adjacent Denver and Salt River substations. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 2000000 | 2032-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denver | Salt River |  | 138 |  | 2 | 0 | MI |  | Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 50571 | LRTP-38: East Adair - Marshalltown - Sub T | MVP | 51217 | Substation - Hills | Add 1-345kV bus position (breaker-and-a-half bus). | MEC | M2 - Appendix A Approved | 5400000 | 2032-06-01 | Substation | Substation bus upgrade | Hills |  |  | 345 |  |  |  | IA |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | West | 50572 | LRTP-39: Lehigh - Marshalltown - Franklin North & Montezuma | MVP | 51218 | Line: Marshalltown (Twinkle) - Franklin North - 345 kV | Install second 345kV circuit on existing spare position on existing structures on existing Marshalltown (Twinkle) - Franklin North 345kV transmission line. | Local TO(s) / To Be Determined | M2 - Appendix A Approved | 41000000 | 2032-06-01 | Line Upgrade | 2nd circuit on existing spare position | Marshalltown (Twinkle) | Franklin North |  | 345 |  | 0 | 69 | IA |  | Shared
MTEP24 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 50575 | LRTP-42: Burr Oak - Schahfer | MVP | 51219 | Line: Burr Oak - Schahfer - 345 kV | Install second 345kV circuit on existing spare position on existing structures on existing Burr Oak - Schahfer 345kV transmission line. | NIPSCO | M2 - Appendix A Approved | 26000000 | 2032-06-01 | Line Upgrade | 2nd circuit on existing spare position | Burr Oak | Schahfer |  | 345 |  | 0 | 33 | IN |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51480 | Line: Woodford County - Near Woodford County - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. This is the MISO portion of the original line (facility #51189). | MISO | M2 - Appendix A Approved | 5000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Woodford County | Near Woodford County |  | 765 |  | 1 | 0 | IL |  | Shared
MTEP24 | A | Midcontinent Independent System Operator, Inc. | Central | 50573 | LRTP-40: Sub T - Woodford County - Collins & Reynolds | MVP | 51481 | Line: Near Woodford County - Collins (PJM) - 765 kV | Construct new 765kV single-circuit transmission line. Minimum Surge Impedance Loading (SIL) should be 2400 MW. This is the PJM portion of the original line (facility #51189) | ComEd(PJM) | M2 - Appendix A Approved | 267000000 | 2034-06-01 | Line New | New Transmission line, new ROW - may include terminations | Near Woodford County | Collins (PJM) |  | 765 |  | 52 | 0 | IL |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 3856 | HVDC 900MW Transmission Line Upgrades | TDSP | 7379 | 7379-HVDC Line-ND Reconductor | Short segment of reconductor in ND to increase capacity | MP | M2 - Appendix A Approved | 6000000 | 2027-12-31 | Line Upgrade | Line reconductor | HVDC Line | ND Reconductor | 1 | 250 |  | 0 | 1.5 | ND | MN | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 21900 | Mullet River Area Reliability Project | BRP | 26490 | Mullet River SS Work | • Retire existing Mullet River and North Mullet River. • Build new 138 kV / 69 kV substation. • 8 position 138 kV breaker and a half yard expandable to 10 positions. o 3 position segmented 69 kV straight bus expandable to 5 positions. o 138/69 kV LTC transformer o 69 kV cap bank o Provisions for series reactors or other flow control devices on the 8241 and LYNG11 line exits. | ATC | M2 - Appendix A Approved | 35550000 | 2031-05-28 | Substation | Substation (breakers only, no transformer) | Mullet River |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23426 | New Rushville-Quaker 69 kV Line | Other | 27071 | New Rushville-Astoria 69 kV line | New Rushville-Astoria 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 9425000 | 2029-12-01 | Line New | New Transmission line, new ROW - may include terminations | Rushville | Astoria | 1 | 69 | 69 | 14.5 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23373 | New Industry-Ipava 69 kV Line | Other | 27072 | New Industry-Table Grove 69 kV Line | New Industry-Table Grove 336 ACSR 69 kV Line | PPI | M2 - Appendix A Approved | 7500000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Industry | Table Grove | 1 | 69 | 69 | 13.6 |  | IL |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 24960 | Legend to Sandling 230 kV Circuit 2 Project | BRP | 28145 | 28145-Legend-Sandling | Construct a new Legend to Sandling 230 kV Ckt 2 | Entergy-TX | M2 - Appendix A Approved | 87600000 | 2027-05-30 | Line New | New Transmission line, new ROW - may include terminations | Legend | Sandling | 2 | 230 |  |  |  | TX |  | Not Shared
MTEP24 | A | ITC | East | 24998 | Pontiac 345 kV Station - Extend Buses and Add A Row | Other | 28147 | Pontiac - Extend 345 kv Bus 301 and 303 and Add A Row | Extend bus 303 and construct a fifth breaker and a half row for terminating Transformer 301 and Transformer 303 into breaker and a half positions. All breakers should be 3000 A, 63 kA breakers. Transformer 301 will be terminated at Pos AI. Transformer 303 will be terminated at Pos BQ. Rename AD switch to AA and rename AV switch to AZ. | ITCT | M2 - Appendix A Approved | 5900000 | 2027-03-15 | Substation | Substation (breakers only, no transformer) | Pontiac |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 24998 | Pontiac 345 kV Station - Extend Buses and Add A Row | Other | 28148 | PONTC-FITZ_Reterminate at position AQ | Fitz-Pontiac 345kV line termination will be moved from position BQ to position AQ. | ITCT | M2 - Appendix A Approved | 144000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Pontiac |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 24921 | New Steamboat 138 kV Ringbus for Babylon 138 kV Sub for PPI Connection | Other | 28150 | 28150-Steamboat- | Prairie Power Incorporated (PPI) 138 kV delivery point substation to supply a new bulk distribution transformer at the PPI Ellisville tap on the Ameren Castro-Galesburg Monmouth Blvd-1427 138 kV line | AmerenIL | M2 - Appendix A Approved | 9700000 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | Steamboat |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 24980 | Pioneer SS Breaker Relay and Remote Ends Asset Renewal | Other | 28154 | Pioneer SS Breaker Relay Asset Renewal | Pioneer SS Breaker Relay Asset Renewal | ATC | M2 - Appendix A Approved | 3600000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Pioneer |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 24980 | Pioneer SS Breaker Relay and Remote Ends Asset Renewal | Other | 28155 | Stiles SS Breaker Relay and Remote Ends Asset Renewal | Stiles SS Breaker Relay and Remote Ends Asset Renewal | ATC | M2 - Appendix A Approved | 200000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Stiles |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25000 | Lakefront SW YD – Revere Dr 69 kV (D-104), Partial Rebuild | Other | 28171 | Lakefront SW YD - Revere Dr 69 kV (D-104), Rebuild | Rebuild and install OPGW on approximately 1.84 miles of D-104 from Lakefront to Revere Dr. | ATC | M2 - Appendix A Approved | 9000000 | 2031-02-25 | Line Upgrade | Line rebuild on existing ROW | Lakefront | Revere Dr | D-104 | 69 |  |  | 1.84 | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 24983 | Hilltop – Council Creek 69 kV (Y-74), Rebuild & OPGW | Other | 28174 | Hilltop – Council Creek 69 kV (Y-74), Rebuild & OPGW | Rebuild and install OPGW on approximately 29 miles of 69 kV line Y-74 from Hilltop Substation to Council Creek Substation and rebuild ~0.5 miles of Camp Douglas Tap. | ATC | M3 - Under Construction | 48800000 | 2026-10-15 | Line Upgrade | Line rebuild on existing ROW | Hilltop | Council Creek | Y-74 | 69 |  |  | 29 | WI |  | Not Shared
MTEP24 | A | AMEREN MISSOURI | Central | 25039 | Taum Sauk 138 kV Upgrade for 60MW Hydro (J1213) | GIP | 28188 | 28188-Taum Sauk- | MISO project J1213, will add 60 MW to the existing Hydro Energy Generating Facility, Transmission Owner will modify the 138 kV bus at its existing Taum Sauk 138 kV substation. | AmerenMO | M2 - Appendix A Approved | 100000 | 2026-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Taum Sauk |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP24 | A | ITC | East | 24998 | Pontiac 345 kV Station - Extend Buses and Add A Row | Other | 28193 | Pontiac - Reconfigure E-Row | Remove breakers EM and ET Remove KK disconnect switch and move existing breaker KM to ET position. Extend bus 303 to connect E Row and remove bus 305 Replace disconnect switches EO, ER, and EV with new standard disconnect switches Upgrade relaying as necessary to accommodate new configuration | ITCT | M2 - Appendix A Approved | 2230000 | 2027-05-14 | Substation | Substation (breakers only, no transformer) | Pontiac |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 25081 | J1450 Webster County Switching Station for POI | GIP | 28196 | 28196-Webster County- | New Switching Station | BREC | M2 - Appendix A Approved | 0 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Webster County |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 25081 | J1450 Webster County Switching Station for POI | GIP | 28197 | 28197-Hopkins County-Webster County | 4.23 mile of OPGW and related equipment. | BREC | M2 - Appendix A Approved | 0 | 2026-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hopkins County | Webster County | 1 | 161 |  |  |  | KY |  | Not Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 25081 | J1450 Webster County Switching Station for POI | GIP | 28198 | 28198-Webster County-Reid EHV | 18 miles of OPGW and related equipment. | BREC | M2 - Appendix A Approved | 0 | 2026-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Webster County | Reid EHV | 1 | 161 |  |  |  | KY |  | Not Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 25081 | J1450 Webster County Switching Station for POI | GIP | 28199 | 28199-Hopkins- | Upgrade relaying to accommodate the new Webster County switching station. | BREC | M2 - Appendix A Approved | 0 | 2026-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Hopkins |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 25081 | J1450 Webster County Switching Station for POI | GIP | 28200 | 28200-Reid EHV- | Upgrade relaying at Reid EHV to accommodate the new switching station Webster County. | BREC | M2 - Appendix A Approved | 0 | 2026-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Reid EHV |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP24 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 25120 | J1466 Reid EHV 161 kV Terminal Addition | GIP | 28201 | 28201-Reid EHV- | Add terminal on the 161 kV bus for POI of J1466. | BREC | M2 - Appendix A Approved | 0 | 2025-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Reid EHV |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 25042 | Supernova 345 kV Substation for Perry County Solar (J1306) | GIP | 28203 | 28203-Supernova- | This project will install a new 345 kV line position to serve as the Point of Interconnection for Perry County under GIA J1306, within the new 3-position ring bus named Supernova. | AmerenIL | M2 - Appendix A Approved | 11000000 | 2027-12-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Supernova |  |  | 345 |  |  |  | IL |  | Shared
MTEP24 | A | AMEREN ILLINOIS | Central | 25043 | Moose 138 kV Substation for Albion PV1 (J1422) | GIP | 28204 | 28204-Moose- | This project will install a new 138 kV line position to serve as the Point of Interconnection for Albion PV 1, LLC under GIA J1422, within the new 3-position ring bus named Moose. | AmerenIL | M2 - Appendix A Approved | 8400000 | 2026-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Moose |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP24 | A | ITC | East | 24574 | J1664 Generator Interconnection Network Upgrades | GIP | 28206 | 28206-Carrigan- | Expand station to extend bus 102 and begin row "J". Install breaker position GF and disconnect switches at positions GD and JH | ITCT | M2 - Appendix A Approved | 1969214 | 2028-01-03 | Substation | Substation (breakers only, no transformer) | Carrigan |  |  | 120 |  |  |  | MI |  | Shared
MTEP24 | A | ITC | East | 25082 | J1664 Generator Interconnection TOIF | GIP | 28207 | 28207-Carrigan- | Install line entrance structures and disconnect switch. Install position KQ at Greenwood to interconnect J1526 generation. | ITCT | M2 - Appendix A Approved | 0 | 2028-01-03 | Substation | Small miscellaneous substation equipment | Carrigan |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 25141 | Arrowhead 115kV SPF Upgrade | BRP | 28212 | 28212-Arrowhead 115kV- | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Arrowhead 115kV buses. | MP | M2 - Appendix A Approved | 250000 | 2026-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Arrowhead 115kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 25142 | Forbes 115kV SPF Upgrade | BRP | 28213 | 28213-Forbes- | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Forbes 115kV buses. | MP | M2 - Appendix A Approved | 250000 | 2026-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Forbes |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 25147 | Mead Johnson 69/12kV Transformer Replacement | Other | 28221 | 28221-Mead Johnson- | Replacement of 69/12kV transformer and several breakers | SIGE | M2 - Appendix A Approved | 3800000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Mead Johnson |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25160 | Weston - Morrison Ave 115kV (Z-52), Reconductor | Other | 28223 | Weston - Morrison Ave 115kV (Z-52), Reconductor | Reconfigure Weston - Sherman Street (O-41) line terminal to new position on West bus and relocate the Weston - Morrison Ave (Z-52) line terminal to the vacated position. Z-52 to be reconductored from Weston to Morrison Ave. Install upgraded communication equipment at remote ends. | ATC | M3 - Under Construction | 3700000 | 2026-06-01 | Line Upgrade | Line reconductor | Weston | Morrison Ave | Z-52 | 115 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25162 | Milwaukee Leased Dark Fiber Retirement Plan | Other | 28226 | Milwaukee Leased Dark Fiber Retirement Plan | Installation of 8+ miles of ATC Owned Underground (UG) Fiber to replace leased UG Fiber with Midwest Fiber Networks in Milwaukee Metro Area. | ATC | M2 - Appendix A Approved | 6000000 | 2027-12-31 | Misc. | Communication equipment | Milwaukee Metro Area |  |  | 0 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 25163 | Freeman - Presque Isle (PI605), OPGW Addition | Other | 28227 | Freeman - Presque Isle (PI605), OPGW Addition | Installation of 7.5 miles of OPGW to provide an alternate fiber path establishing two diverse fiber routes connecting into ATC larger OPGW Network Infrastructure. | ATC | M2 - Appendix A Approved | 5300000 | 2027-07-09 | Misc. | Communication equipment | Freeman | Presque Isle | PI605 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 9997 | OTP Rolette 230 kV Substation | Other | 21422 | 21422-Rolette 230kV- | Install one 230 kV breaker, two 230 kV line switches, and one 69 kV breaker. Install one 230/115/69 kV Transformer (140 MVA) leaving the 115 kV winding disconnected. | OTP | M2 - Appendix A Approved | 8700000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Rolette 230 kV |  |  | 230 | 69 |  |  | ND |  | Not Shared
MTEP24 | A | OTTER TAIL POWER COMPANY | West | 10001 | OTP Voltaire 115 kV Substation | Other | 21424 | 21424-Voltaire 115 kV- | Tap Xcel's 115 kV line between GRE McHenry and Magic City and build a new 115/41.6 kV substation in the Voltaire area. Install three 115 kV breakers and three 41.6 kV breakers. Install one 56 MVA 115/41.6 kV transformer. | OTP | M2 - Appendix A Approved | 8100000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Voltaire 115 kV |  |  | 115 | 42 |  |  | ND |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23374 | New Babylon 138/69 kV Substation and Lines | Other | 27075 | New Babylon 138/69 kV Substation | New Babylon 138/69 kV Substation | PPI | M2 - Appendix A Approved | 7325000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Babylon |  |  | 138 | 69 |  |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23375 | Upgrade Babylon 138/69 kV Transformer | Other | 27077 | Upgrade Babylon 138/69 kV Transformer | Upgrade Babylon 138/69 kV Transformer with 84 MVA | PPI | M2 - Appendix A Approved | 2600000 | 2029-12-01 | Transformer | Transformer Replacement | Babylon |  | 1 | 138 | 69 |  |  | IL |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 23910 | Eden – Rock Branch 69kV (Y-106), Rebuild & OPGW | Other | 27599 | Eden – Rock Branch 69kV (Y-106), Rebuild | Eden – Rock Branch 69kV (Y-106), Rebuild | ATC | M2 - Appendix A Approved | 67900000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Eden | Rock Branch | Y-106 | 69 |  |  |  | WI |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 23851 | Stanton Breaker Replacement | Other | 27653 | 27653-Stanton- | Replace Stanton oil breakers 31RB1, 2, 3, 4 & 6. | GRE | M2 - Appendix A Approved | 2179821 | 2026-11-05 | Substation | Circuit Breaker (replacement at existing substation) | Stanton |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 13905 | Burnside Tap (Audubon) 230-115 kV Autotransformer | BRP | 22988 | 22988-Burnside- | 1) Construct a 3 breaker 230 kV ring bus at Burnside, Minimum of 2000 Amp equipment. 2) Cut in and out the Conway to Panama 230 kV line. 3) Install 300 MVA 230-115 kV Autotransformer, similar to the current Sorrento 230-115 kV Autotransformer. 4) Install 115 kV low side breaker at Burnside | Entergy-LA | M2 - Appendix A Approved | 34260000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Burnside |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP24 | A | METC | East | 18072 | Sag Remediation Hubbard Lake – Spruce Road 138 kV | BRP | 24855 | 24855-Hubbard Lake-Spruce Road | Completely remediate the sag on the Hubbard Lake – Spruce Road section of the Alpena – Iosco 138kV line. | METC | M2 - Appendix A Approved | 700000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hubbard Lake | Spruce Road |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 21900 | Mullet River Area Reliability Project | BRP | 26496 | Mullet River Project Line Work | • Rebuild X-57 from the existing Mullet River site to the new substation site as a double circuit to route X-89 and X-97 into the new yard. • Build new double circuit taps to tie 8241 and LYNG11 into the new site. • Build new segment for Y-50 to tie it into the new site. • Build new double circuit connection for X-57 operated as a bifurcated single circuit to the new site. • Retire Y-50 from North Mullet River to connection with new tap to the new site | ATC | M2 - Appendix A Approved | 35550000 | 2029-05-28 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mullet River |  | X-57 | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | METC | East | 21968 | Delaney 138 kV Station Rebuild | Other | 26593 | 26593-New Station- | The new Delaney 138 kV station will be rebuilt as a compressed four breaker ring bus configuration. Install new control house. Install (3) 138 kV, 3000 A breakers with at least 40 kA interrupting. The summer emergency rating of all new equipment should be no less than 644 MVA/2693 amps. | METC | M2 - Appendix A Approved | 5686000 | 2029-05-01 | Substation | Substation (breakers only, no transformer) | New Station |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 21968 | Delaney 138 kV Station Rebuild | Other | 26594 | 26594-Delaney-Thetford | Reterminate the existing Delaney-Thetford 138kV line into the new station configuration. | METC | M2 - Appendix A Approved | 1473000 | 2029-05-01 | Line New | New Transmission line, new ROW - may include terminations | Delaney | Thetford | 1 | 138 |  | 1.1 |  | MI |  | Not Shared
MTEP24 | A | METC | East | 21968 | Delaney 138 kV Station Rebuild | Other | 26595 | 26595-Delaney-Hemphill | Reterminate the existing Delaney-Helphill 138kV line into the new station configuration. | METC | M2 - Appendix A Approved | 1473000 | 2029-05-01 | Line New | New Transmission line, new ROW - may include terminations | Delaney | Hemphill | 1 | 138 |  | 1.1 |  | MI |  | Not Shared
MTEP24 | A | MINNKOTA POWER COOPERATIVE, INC | West | 24375 | Center-Maple River 345 kV Foundation Restoration | Other | 27847 | 27847-Bison-Maple River | Maple River - Bison 345 KV | MPC | M2 - Appendix A Approved | 400000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Bison | Maple River |  | 345 |  |  |  | ND |  | Not Shared
MTEP24 | A | METC | East | 24477 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) TOIF | GIP | 27912 | 27912-Peddler- | Install position WM6 at the new station for J1292 generator to connect. | METC | M2 - Appendix A Approved | 0 | 2028-06-01 | Substation | Small miscellaneous substation equipment | Peddler |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 24440 | Van Tyle - J1603 NU - Install breaker 4B7 and switches 4M5 and 4B3 | GIP | 27931 | 27931-Van Tyle- | Complete Row 4, install 1-138kV breaker at position 4B7 with minimum 40kA interrupting capability. Install 138kV 3000A disconnect switches 4B3 and 4M5 | METC | M2 - Appendix A Approved | 1122500 | 2027-05-14 | Substation | Substation (breakers only, no transformer) | Van Tyle |  |  | 138 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24442 | Van Tyle-J1603 TOIF-Install position BM4 and switch 177 | GIP | 27932 | 27932-Van Tyle- | Install Van Tyle line position BM4 and switch 177 for generator interconnect. | METC | M2 - Appendix A Approved | 0 | 2027-05-14 | Substation | Small miscellaneous substation equipment | Van Tyle |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 24443 | Tallmadge-Argenta - J1663 Generator Interconnection (Gordon) - Network Upgrade | GIP | 27933 | 27933-Argenta-Tallmadge | Construct J1663 as a 345kV breaker and half station with three 50kA breakers. | METC | M2 - Appendix A Approved | 12721682 | 2028-03-01 | Substation | Substation (breakers only, no transformer) | Argenta | Tallmadge |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24443 | Tallmadge-Argenta - J1663 Generator Interconnection (Gordon) - Network Upgrade | GIP | 27934 | 27934-Argenta-Tallmadge | Extend the Argenta-Tallmadge 345kV line to loop in J1663 POI station. | METC | M2 - Appendix A Approved | 1175000 | 2028-03-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Argenta | Tallmadge |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24443 | Tallmadge-Argenta - J1663 Generator Interconnection (Gordon) - Network Upgrade | GIP | 27935 | 27935-Argenta- | Upgrade position FH30 relaying at Argenta 345kV | METC | M2 - Appendix A Approved | 457185 | 2028-03-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Argenta |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24443 | Tallmadge-Argenta - J1663 Generator Interconnection (Gordon) - Network Upgrade | GIP | 27936 | 27936-Tallmadge- | Upgrade Position RH31 relaying at Tallmadge 345kV. | METC | M2 - Appendix A Approved | 457185 | 2028-03-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Tallmadge |  |  | 345 |  |  |  | MI |  | Shared
MTEP24 | A | METC | East | 24479 | Gordon-J1663 TOIF-Install position RH29 and switch 177 | GIP | 27937 | 27937-Gordon- | Install Gordon line entrance structure at position RH29 and switch 177 for generator interconnection. | METC | M2 - Appendix A Approved | 0 | 2028-03-01 | Substation | Small miscellaneous substation equipment | Gordon |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25215 | Andes 500/230 kV Substation | Other | 28333 | 28333-Andes-Mantero | 2x230 kV short transmission lines will interconnect the Mantero 230 kV substation to the Andes 500/230 kV station. | Entergy-MS | M3 - Under Construction | 1 | 2027-06-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Andes | Mantero |  | 230 |  |  |  | MS |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25215 | Andes 500/230 kV Substation | Other | 28334 | 28334-Andes- | 2x230 kV Autotransformers will be installed at the new Andes 500/230 kV station. | Entergy-MS | M3 - Under Construction | 1 | 2027-06-01 | Transformer | Transformer New | Andes |  |  | 500 | 230 |  |  | MS |  | Not Shared
MTEP24 | A | ENTERGY SERVICES, LLC. | South | 25215 | Andes 500/230 kV Substation | Other | 28335 | 28335-Andes-Mantero | 2x230 kV short transmission lines will connect the Mantero 230 kV substation to Andes 500/230 kV station. | Entergy-MS | M3 - Under Construction | 1 | 2027-06-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Andes | Mantero | 2 | 230 |  |  |  | MS |  | Not Shared
MTEP24 | A | METC | East | 25216 | Gaines - Caledonia Jct. 138 kV Sag Remediation | BRP | 28336 | 28336-GAINS-CALEDONIA_ Sag Remediation | Remediate sag on the 795 ACSS up to 153 MVA (summer ratings) on the Gaines – Caledon J. section of the Thompson Road – Gaines 138 kV circuit. | METC | M2 - Appendix A Approved | 520000 | 2026-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gaines | Caledonia Jct. | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25230 | Manning #2 345-138 kV Transformer Replacement | Other | 28337 | 28337-Manning- | Replace the Manning #2 345/138 kV transformer with at least 650 MVA (2718 Amps) summer emergency rated transformer. Also install a new high side 3000 Amps disconnect switch. | METC | M2 - Appendix A Approved | 7060000 | 2027-12-31 | Transformer | Transformer New | Manning |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25217 | Blendon 138 KV Capacitor | BRP | 28338 | 28338-Blendon - Install Capacitor | Install (1) 33.33 MVAR capacitor bank with associated 138kV, 40 kA synchronous breakers and disconnect switch at the Blendon 138kV substation. The proposed capacitor will be connected to bus 40 and Transformer 1 will be moved to Bus 50. | METC | M2 - Appendix A Approved | 3400000 | 2028-06-01 | Voltage Device | Capacitor (switched capacitor) | Blendon |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25217 | Blendon 138 KV Capacitor | BRP | 28339 | 28339-BLNDN- NRIDG (FOUMI)_Swap Termination with BLNDN - ZEELAND RILEY | Relocate the existing Blendon- Northridge (formerly Four Mile) 138kV line termination from bus 20 to bus 10. Also, relocate the existing Blendon-Zeeland Riley 138kV line termination from bus 10 to bus 20. | METC | M2 - Appendix A Approved | 860000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Blendon |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | ITC | East | 25218 | Sterling #201 230-120 kV Transformer Replacement | Other | 28340 | 28340-Sterling- | Replace the Sterling #201 230/120 kV transformer with a transformer of at least 728 MVA (3503 Amps) summer emergency rating. Install a breaker and associated equipment on the high side of the transformer. | ITCT | M2 - Appendix A Approved | 7950000 | 2028-04-28 | Substation | Substation (breakers only, no transformer) | Sterling |  |  | 230 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25211 | ITCM Customer Interconnects with short lead time 2026 | Other | 28343 | 28343-Blanket for Customer Interconnections under $1 million for 2026- | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | ITCM | M2 - Appendix A Approved | 3750000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Blanket for Customer Interconnections under $1 million for 2026 |  |  | 345 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | METC | East | 25198 | Port Calcite 138 kV Station Rebuild | Other | 28344 | Port Calcite - Station Rebuild (NEW STATION) | METC: Rebuild Port Calcite into a four (4) position ring bus configuration that can be converted to Breaker and a half in the future. Arrange the four breaker ring bus so that the positions alternate between transformers and lines. All new 138 kV breakers should be standard 3000 A 40 kA breakers. The new substation is located to the Northwest of existing station. All new equipment should have a minimum summer emergency rating of 364 MVA. CE: Install circuit switcher or high side breaker on CE Transformer 1 & 2. | METC | M2 - Appendix A Approved | 8100000 | 2030-03-05 | Substation | Switching station (breakers only, no transformer) | Port Calcite |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 25199 | Fairmont 10th St 69kV Substation Modernization | Other | 28349 | 28349-Fairmont 10th St- | Replacing 4 69kV circuit breakers and associated equipment. | SMMPA | M2 - Appendix A Approved | 1800000 | 2026-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Fairmont 10th St |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 25260 | Loon Lake 69kV Substation Modernization | Other | 28350 | 28350-Loon Lake Substation- | Replacing 4 69kV circuit breakers and associated equipment. | SMMPA | M2 - Appendix A Approved | 1800000 | 2026-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Loon Lake Substation |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25280 | HE_J1354_Decatur_Battery | GIP | 28352 | 28352-Decatur Switch Station 138kV | Construct Transmission Owner’s Interconnection Facilities at Decatur Substation. | HE | M2 - Appendix A Approved | 3248872 | 2026-11-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Decatur Switch Station 138kV |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25300 | Nobles County Third Transformer | BRP | 28353 | 28353-Nobles County- | Install third 345/115 kV transformer at Nobles County | XEL | M2 - Appendix A Approved | 12500000 | 2028-05-01 | Transformer | Transformer New | Nobles County |  | 11 | 345 | 115 |  |  | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25300 | Nobles County Third Transformer | BRP | 28354 | 28354-Nobles County- | Add 50 MVAR tertiary reactor to new 345/115 kV transformer | XEL | M2 - Appendix A Approved | 750000 | 2028-05-01 | Voltage Device | Reactor or Inductor | Nobles County |  |  | 345 | 115 |  |  | MN |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25301 | Leola load addition | Other | 28355 | 28355-Leola- | Add 2-10 Mvar capacitors to the 115 kV bus at Leola. | MDU | M2 - Appendix A Approved | 1000000 | 2026-12-31 | Voltage Device | Capacitor (switched capacitor) | Leola |  |  | 115 |  |  |  | SD |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25301 | Leola load addition | Other | 28356 | 28356-Leola- | Add breaker and switches to the 41.6 kV portion of the substation. | MDU | M2 - Appendix A Approved | 2600000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Leola |  |  | 42 |  |  |  | SD |  | Not Shared
MTEP24 | A | MIDAMERICAN ENERGY CO. | West | 25302 | Hills 69 kV Breaker Replacement | Other | 28357 | 28357-Hills- | Replace the Hills 69 kV breaker 514 with a breaker that has interrupting rating of 40kA. | MEC | M3 - Under Construction | 500000 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Hills |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25303 | HE_J1027_Ratts2_Solar | GIP | 28358 | 28358-Petersburg/Ratts 161 kV- | Construct Transmission Owner’s Interconnection Facilities at Petersburg Substation. | HE | M2 - Appendix A Approved | 3636500 | 2026-10-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Petersburg/Ratts 161 kV |  |  | 161 |  |  |  | IN |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25306 | ITCM Burlington 4th Street Control Enclosure & 69 kV Tie Breaker Addition | Other | 28367 | 28367-Burlington 4th Street-Substation | IPL has notified ITC that they will be rebuilding their Burlington 4th Street sub and installing a 2nd 20/26/33 MVA transformer; as well as, replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Burlington 4th Street sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | ITCM | M2 - Appendix A Approved | 1984333 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Burlington 4th Street | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25253 | ITCM Flint Ridge Control Enclosure & 69 kV Tie Breaker Addition | Other | 28368 | 28368-Flint Ridge-Substation | IPL has notified ITC that they will be rebuilding their Flint Ridge sub and installing a 2nd 20/26/33 MVA transformer. This rebuild will also be replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Flint Ridge sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | ITCM | M2 - Appendix A Approved | 2160171 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Flint Ridge | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25307 | ITCM State Center Rural 69 kV Interconnection | Other | 28369 | 28369-State Center Rural Tap-State Center Rural | Line Taps for new State Center Rural Substation Interconnection | ITCM | M2 - Appendix A Approved | 297500 | 2026-12-15 | Line New | Install tap (typically a pole a switch or in-and-out loop) | State Center Rural | State Center Rural | 1 | 69 | 69 | 0.1 |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | Other | 28370 | 28370-Leon Rodeo-Substation | ITCM will build the 69 kV portion of a new Leon Rodeo sub with 2 line breakers and a bus tie breaker. | ITCM | M2 - Appendix A Approved | 4118979 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Leon Rodeo | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | Other | 28371 | 28371-Grand River-Leon Rodeo | ITCM will construct new line taps for the new Leon Rodeo sub and retire any existing 69 kV line no longer needed. | ITCM | M2 - Appendix A Approved | 130000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Grand River | Leon Rodeo | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | Other | 28372 | 28372-Leon Rodeo-Sailing | ITCM will construct new line taps for the new Leon Rodeo sub and retire any existing 69 kV line no longer needed. | ITCM | M2 - Appendix A Approved | 127500 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Leon Rodeo | Sailing | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | ITC MIDWEST | West | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | Other | 28373 | 28373-Leon-Substation | Retire the Leon substation after the Leon Rodeo sub is online. | ITCM | M2 - Appendix A Approved | 484263 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Leon | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP24 | A | MINNESOTA POWER INC. | West | 25311 | Stinson PST Retirement | Other | 28385 | 28385-Stinson- | Retire Stinson 115 kV PST. | MP | M2 - Appendix A Approved | 1000000 | 2032-12-31 | Misc. | Phase angle regulating transformer (phase shifter) | Stinson |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP24 | A | CLECO POWER LLC | South | 25313 | J1599 Daspit Substation | GIP | 28394 | 28394-Daspit- | Build a new Daspit substation tapped into the Hopkins to Morbihan 138 kV line. This project is needed for J1599 generator. | CLECO | M2 - Appendix A Approved | 16236000 | 2027-04-01 | Substation | Substation (breakers only, no transformer) | Daspit |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25268 | Replace 345-138 kV Petersburg East & West Autos | BRP | 28396 | 28396-Petersburg-Petersburg | Replace Petersburg E auto | IPL | M2 - Appendix A Approved | 15182115 | 2028-12-31 | Transformer | Transformer New | Petersburg | Petersburg | E | 345 | 138 |  |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 25268 | Replace 345-138 kV Petersburg East & West Autos | BRP | 28397 | 28397-Petersburg-Petersburg | Replace Petersburg W autotransformer. | IPL | M2 - Appendix A Approved | 6000000 | 2028-12-31 | Transformer | Transformer New | Petersburg | Petersburg | W | 345 | 138 |  |  | IN |  | Not Shared
MTEP24 | A | CLECO POWER LLC | South | 25283 | Dolet Solar Replacement R1004 | GIP | 28402 | 28402-Dolet Hills- | Upgrade terminal equipment for R1004 | CLECO | M2 - Appendix A Approved | 1956770 | 2025-12-15 | Substation | Substation (breakers only, no transformer) | Dolet Hills |  |  | 345 |  |  |  | LA |  | Not Shared
MTEP24 | A | CLECO POWER LLC | South | 25283 | Dolet Solar Replacement R1004 | GIP | 28403 | 28403-Dolet Hills-Dolet Solar | Generation Tie line from Dolet Hills to Solar Site | CLECO | M2 - Appendix A Approved | 17730535 | 2026-12-15 | Line New | New Transmission line, new ROW - may include terminations | Dolet Hills | Dolet Solar | 1 | 345 |  | 7.7 |  | LA |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23373 | New Industry-Ipava 69 kV Line | Other | 28404 | New Table Grove-Ipava 69 kV Line | New Table Grove-Ipava 336 ACSR 69 kV Line | PPI | M2 - Appendix A Approved | 8200000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Table Grove | Ipava |  | 69 | 69 | 12 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23374 | New Babylon 138/69 kV Substation and Lines | Other | 28405 | New Babylon-WeeMaTuk 69 kV Line | New Babylon-WeeMaTuk 69 kV Line | PPI | M2 - Appendix A Approved | 8970000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Babylon | Canton |  | 69 | 69 | 13.8 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23374 | New Babylon 138/69 kV Substation and Lines | Other | 28406 | New Babylon-Ellisville/Smithfield 69 kV Line | New Babylon-Ellisville/Smithfield 69 kV Line double-circuit | PPI | M2 - Appendix A Approved | 625000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Babylon | Ellisville/Smithfield |  | 69 | 69 | 0.5 | 0.5 | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23426 | New Rushville-Quaker 69 kV Line | Other | 28407 | New Astoria-Quaker 69 kV line | New Astoria-Quaker 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 6760000 | 2029-12-01 | Line New | New Transmission line, new ROW - may include terminations | Astoria | Quaker |  | 69 |  | 10.4 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25316 | New Plymouth-Macomb 69 kV Line | Other | 28412 | New Plymouth 69kV Breaker Station | New Plymouth 69kV Breaker Station located near Plymouth, IL in WIEC | PPI | M2 - Appendix A Approved | 3400000 | 2029-12-01 | Substation | Switching station (breakers only, no transformer) | Plymouth |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25316 | New Plymouth-Macomb 69 kV Line | Other | 28413 | New Plymouth-Colmar 69 kV Line | New Plymouth-Colmar 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 4680000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Plymouth | Colmar |  | 69 | 69 | 7.2 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25316 | New Plymouth-Macomb 69 kV Line | Other | 28414 | New Colmar-Fandon 69 kV Line | New Colmar-Fandon 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 4550000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Colmar | Fandon |  | 69 | 69 | 7 |  | IL |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25317 | Wakefield Protection Upgrade | Other | 28415 | 28415-Wakefield- | Upgrade system protection equipment at Wakefield 115 kV substation. | XEL | M2 - Appendix A Approved | 450000 | 2027-08-11 | Misc. | Relaying, protection, RTU and SCADA equipment | Wakefield |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25316 | New Plymouth-Macomb 69 kV Line | Other | 28416 | New Fandon-Colchester 69 kV Line | New Fandon-Colchester 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 3380000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Fandon | Colchester |  | 69 | 69 | 5.2 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25316 | New Plymouth-Macomb 69 kV Line | Other | 28417 | New Colchester-Macomb 69 kV Line | New Colchester-Macomb 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 3055000 | 2030-12-01 | Line New | New Transmission line, new ROW - may include terminations | Colchester | Macomb |  | 69 | 69 | 4.7 |  | IL |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 25318 | Upgrade Winchester 138/69 kV Transformer | Other | 28418 | Upgrade Winchester 138/69 kV Transformer | Upgrade Winchester 138/69 kV Transformer with 84 MVA | PPI | M2 - Appendix A Approved | 3500000 | 2026-05-01 | Transformer | Transformer Replacement | Winchester |  |  | 138 | 69 |  |  | IL |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25322 | 0890 Granite City - Crossroads Rebuild | Other | 28424 | 28424-Granite City-Crossroads | Rebuild 3.7 miles 115 kV line from Granite City - Crossroads with new structures and new OPGW shield wire. | XEL | M2 - Appendix A Approved | 5845170 | 2028-05-15 | Line Upgrade | Line rebuild on existing ROW | Granite City | Crossroads | 1 | 115 |  |  | 3.7 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25471 | St. Clair Tap Rebuild | Other | 28722 | 28722-St. Clair-St. Clair Tap | Rebuild 4.5 miles from St. Clair to the St. Clair Tap. | GRE | M2 - Appendix A Approved | 4728756 | 2027-12-30 | Line Upgrade | Line rebuild on existing ROW | St. Clair | St. Clair Tap | 1 | 69 |  |  | 4.5 | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25469 | Silver Lake Transformer Replacement | Other | 28726 | 28726-Silver Lake- | Replace the Silver Lake transformer. | GRE | M2 - Appendix A Approved | 4646984 | 2027-12-31 | Transformer | Transformer New | Silver Lake |  |  | 230 | 42 |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25453 | Medina Breaker Addition and Replacement | Other | 28728 | 28728-Medina- | Replace and add breakers at Medina substation. | GRE | M2 - Appendix A Approved | 1509395 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Medina |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25452 | Dickinson Breaker Replacement | Other | 28729 | 28729-Dickinson- | Replace 3 breakers at Dickinson substation. | GRE | M2 - Appendix A Approved | 2847337 | 2027-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Dickinson |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | ITC | East | 25478 | ITCT Line Relocation - 2025 | Other | 28730 | 28730-ITCT Facilities- | Relocation portions of transmission lines located in public right of way at the government entities mandate. | ITCT | M2 - Appendix A Approved | 2500000 | 2025-12-31 | Misc. | Line relocation (road move) | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25500 | METC Line Relocation - 2025 | Other | 28731 | 28731-METC Facilities- | Relocation portions of transmission lines located in public right of way at the government entities mandate. | METC | M2 - Appendix A Approved | 2500000 | 2025-12-31 | Misc. | Line relocation (road move) | METC Facilities |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25416 | Lucedale 69kV Switching Station | Other | 28733 | 28733-Lucedale- | In order to serve the member delivery points of North Lucedale and South Lucedale economically and reliably a new 69kV switching will be constructed at near Lucedale, MS. | SMEPA | M2 - Appendix A Approved | 2860000 | 2028-03-01 | Substation | Switching station (breakers only, no transformer) | Lucedale |  |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25523 | J1348 Brouilletts Creek Solar POI | GIP | 28735 | 28735-Brouilletts Creek Solar-J1348 POI | J1348 200MW Brouilletts Creek Solar, LLC: Provide construction oversite for new switching station constructed by the IPP; relaying upgrades at Cayuga CT and Sugar Creek (34513 ckt); Loop 34513 in and out of new substation | DEI | M2 - Appendix A Approved | 8372617 | 2027-12-15 | Misc. | Generator | Brouilletts Creek Solar | J1348 POI |  | 345 |  |  |  | IN |  | Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25542 | J1357 Williams Power POI | GIP | 28737 | 28737-Madison 138- | J1357 150MW Williams Power, LLC battery storage (600MWh): Madison 138 - add breaker (straight bus config) and line terminal on bus section #1 | DEI | M3 - Under Construction | 5680572 | 2026-10-13 | Misc. | Generator | Madison 138 |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25503 | MDU Network and Interconnection Upgrades - J1040 | GIP | 28739 | 28739-Wishek- | Wishek substation - terminal equipment to interconnect project (PCB, Disconnects, bus work) | MDU | M2 - Appendix A Approved | 3600000 | 2026-10-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Wishek |  |  | 230 |  |  |  | ND |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25503 | MDU Network and Interconnection Upgrades - J1040 | GIP | 28740 | 28740-Mandan-Napoleon | Mandan-Napoleon 230 kV line - terminal equipment (Re-tap CTs Mandan and jumpers at Napoleon) | MDU | M2 - Appendix A Approved | 75000 | 2026-10-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Mandan | Napoleon |  | 230 |  |  |  | ND |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25503 | MDU Network and Interconnection Upgrades - J1040 | GIP | 28741 | 28741-Wishek-Merricourt | reconductor and pole replacement | MDU | M2 - Appendix A Approved | 12800000 | 2026-10-01 | Line Upgrade | Line rebuild on existing ROW | Wishek | Merricourt |  | 230 |  |  |  | ND |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25503 | MDU Network and Interconnection Upgrades - J1040 | GIP | 28742 | 28742-Merricourt- | Add another breaker and re-terminate one of the 230 kV lines | MDU | M2 - Appendix A Approved | 1500000 | 2026-10-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Merricourt |  |  | 230 |  |  |  | ND |  | Not Shared
MTEP24 | A | MONTANA-DAKOTA UTILITIES CO. | West | 25503 | MDU Network and Interconnection Upgrades - J1040 | GIP | 28743 | 28743-Ellendale- | 115 kV terminal equipment for line to Aberdeen | MDU | M2 - Appendix A Approved | 140000 | 2026-10-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Ellendale |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP24 | A | METC | East | 25522 | Oakland 138 kV Station Rebuild | Other | 28744 | Oakland - 138 kV Station Rebuild | New station constructed as a four breaker ring bus configuration. All 138 kV breakers should be standard 3000 A, 40 kA breakers. Terminate 138 kV lines into new Oakland station | METC | M2 - Appendix A Approved | 6500000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | Oakland |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | METC | East | 25522 | Oakland 138 kV Station Rebuild | Other | 28745 | Oakland - Install Capacitor Banks | Replace existing 50 MVAR with two (2) 25 MVAR cap banks on separate buses with new synchronous breakers. | METC | M2 - Appendix A Approved | 1500000 | 2027-12-31 | Voltage Device | Capacitor (switched capacitor) | Oakland |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25459 | Line 35 Rebuild | Other | 28746 | 28746-Benndale-Lucedale | To ensure reliable service a complete rebuild of L35 (Lucedale – Benndale 11.37 miles) is recommended. | SMEPA | M2 - Appendix A Approved | 9000000 | 2028-03-01 | Line Upgrade | Line rebuild on existing ROW | Benndale | Lucedale |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25543 | J1381 Locomotive Solar POI | GIP | 28747 | 28747-Greentown 230-J1381 POI | J1381 200MW net Locomotive Solar, LLC: Greentown 230 - Expand 230 kV ring bus and add line terminal equipment between AEP Bk2 and 23021 (Peru SE) | DEI | M2 - Appendix A Approved | 6666686 | 2026-12-01 | Misc. | Generator | Greentown 230 | J1381 POI |  | 230 |  |  |  | IN |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25520 | South Lucedale 69kV Delivery Point | Other | 28749 | 28749-Lucedale-South Lucedale | In order to serve the member delivery point economically and reliably, a new 2.7-mile radial line will be constructed from the Lucedale 69kV Switching Station to the member delivery. | SMEPA | M2 - Appendix A Approved | 3800000 | 2028-03-01 | Line New | New Transmission line, new ROW - may include terminations | Lucedale | South Lucedale |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25520 | South Lucedale 69kV Delivery Point | Other | 28750 | 28750-South Lucedale- | Upgrade member high side substation equipment to accommodate the 69kV service. | SMEPA | M2 - Appendix A Approved | 2477100 | 2028-03-01 | Substation | Distribution substation - may include trans high side | South Lucedale |  |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25545 | J1390 Lowland Solar Park POI | GIP | 28751 | 28751-Lowland Solar-J1390 POI | J1390 150MW net Lowland Solar Park, LLC - Oversite of Self-Build Switching Station by developer (3-CB ring); inserted in the 23004 Gallagher to Columbus ckt; includes relay upgrades on the remote ends, 23004 loop-through line work; and reroute of the 23005 around the new switching station | DEI | M2 - Appendix A Approved | 6843406 | 2028-10-31 | Misc. | Generator | Lowland Solar | J1390 POI |  | 230 |  |  |  | IN |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25489 | North Lucedale 69kV Delivery Point | Other | 28752 | 28752-North Lucedale GOAB-North Lucedale | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | SMEPA | M2 - Appendix A Approved | 3675000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | North Lucedale GOAB | North Lucedale |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25489 | North Lucedale 69kV Delivery Point | Other | 28753 | 28753-North Lucedale GOAB- | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | SMEPA | M2 - Appendix A Approved | 125000 | 2027-12-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | North Lucedale GOAB |  |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25546 | J1388 Galea Springs SPV POI | GIP | 28754 | 28754-Galea Springs SPV-J1388 POI | J1388 - 150MW Galea Springs SPV - solar farm - construct new switching station (3-CB ring) in the radial Oakland City 13862 ckt. - includes Oakland City relay upgrades and rebuilding 6.75 miles of 138kV line from POI to Oakland City | DEI | M2 - Appendix A Approved | 52928159 | 2027-06-01 | Misc. | Generator | Galea Springs SPV | J1388 POI |  | 138 |  |  | 6.75 | IN |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25504 | J1481 Emerald Green Solar POI | GIP | 28755 | 28755-Greentown 230-J1481 POI | J1481 200MW net Emerald Green Solar LLC: Greentown 230 - Expand 230 kV sub by adding a new CB that will share the existing ring bus terminal of the 23022 line and add line terminal equipment | DEI | M2 - Appendix A Approved | 8535044 | 2026-12-31 | Misc. | Generator | Greentown 230 | J1481 POI |  | 230 |  |  |  | IN |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25489 | North Lucedale 69kV Delivery Point | Other | 28756 | 28756-North Lucedale- | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | SMEPA | M2 - Appendix A Approved | 2599100 | 2027-12-01 | Substation | Distribution substation - may include trans high side | North Lucedale |  |  | 69 |  |  |  | MS |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25419 | Hermanville 115kV Delivery Point | Other | 28761 | 28761-Hermanville GOAB-Hermanville | In order to serve the member delivery point, tap Utica Loop line with a 115kV Goab and construct a new line to the delivery point. | Entergy-MS | M2 - Appendix A Approved | 500000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Hermanville GOAB | Hermanville |  | 115 |  |  |  | MS |  | Not Shared
MTEP24 | A | COOPERATIVE ENERGY | South | 25419 | Hermanville 115kV Delivery Point | Other | 28762 | 28762-Hermanville GOAB- | In order to serve the member delivery point, tap Utica Loop line with a 115kV Goab and construct a new line to the delivery point. | Entergy-MS | M2 - Appendix A Approved | 200000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Hermanville GOAB |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP24 | A | DAIRYLAND POWER COOPERATIVE | West | 25498 | J898 Generation Interconnection Network Upgrades | GIP | 28766 | 28766-Beaver Creek- | New 4-breaker ring, 161 kV switching station at POI and 6.0 miles of 161 kV on New Right-of-way | DPC | M2 - Appendix A Approved | 19574516 | 2027-09-01 | Substation | Switching station (breakers only, no transformer) | Beaver Creek | Harmony | 1 | 161 |  | 6 |  | MN |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25525 | Kokomo Project Fusion Phase 2 - 230/69kV Sub | Other | 28781 | 28781-Kokomo Fusion - Phase 2-xfmr and CBs | Kokomo Fusion Phase 2 (StarPlus Energy) - 155MW/51MVAR addition; relocate 23022, 69172, and 69174 lines away from StarPlus Energy Phase 2 facilities; add (1) 150MVA 230/69kV transformer; add (2) 230CBs; add (4) 60MVA 69/34kV transformers | DEI | M2 - Appendix A Approved | 14000000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Kokomo Fusion - Phase 2 | xfmr and CBs |  | 230 | 69 |  |  | IN |  | Not Shared
MTEP24 | A | CITY OF HENDERSON, KY, UTILITY COMMISSION, DBA HENDERSON MUNICIPAL POWER AND LIGHT (BA) | Central | 25499 | Reconductor HMPL Sub 2 to HMPL Sub 5 69kV line | Other | 28782 | 28782-HMPL Sub 2-HMPL Sub 5 | Reconductor 69kV line | HMPL | M3 - Under Construction | 1036568 | 2026-07-31 | Line Upgrade | Line reconductor | HMPL Sub 2 | HMPL Sub 5 | 1 | 69 |  |  |  | KY |  | Not Shared
MTEP24 | A | DUKE ENERGY INDIANA, LLC | Central | 25526 | Terre Haute Project Tonic Water | Other | 28783 | 28783-Terre Haute Tonic Water-new switching station | Terre Haute new load - Tonic Water: located north of the Vigo Co. Industrial Park in the 13821 ckt; new 138kV line loop to be 954ACSS@200C - 3.26 mi. west side / 2.17 mi. east side; 138kV sub to be 7 breakers in a breaker and 1/2 layout; (2) dedicated customer-owned 138kV outlet lines to their load; Load ramp: 33MW/11MVAR each step - 7/1/25; 7/1/26; 11/1/26; 31MW/10MVAR - 3/1/27; (2) 36MVAR - 138kV capacitors | DEI | M3 - Under Construction | 35777500 | 2029-03-19 | Substation | Substation (breakers only, no transformer) | Terre Haute Tonic Water | new switching station |  | 138 |  | 5.43 |  | IN |  | Not Shared
MTEP24 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24274 | New - 138 kV Maloney-Reservoir Loop | Other | 28785 | 28785-Teppco-Rockville | Reconductor 138kV line from Teppco to Rockville | IPL | M2 - Appendix A Approved | 700000 | 2028-12-31 | Line Upgrade | Line reconductor | Teppco | Rockville |  | 138 |  |  | 2 | IN |  | Not Shared
MTEP24 | A | GREAT RIVER ENERGY | West | 25547 | Blind Lake sub - install Statcom and breaker | Other | 28787 | 28787-Blind Lake- | Remove switch 58NSM4 and replace with a circuit breaker. Replace existing breakers B1 and B2. Add a second 6.12 MVAR capacitor bank or replace cap bank with 18 mVAR statcom. | GRE | M2 - Appendix A Approved | 8777667 | 2028-02-10 | Voltage Device | Capacitor (switched capacitor) | Blind Lake |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Other | 28788 | 28788-HE Wilbur-DEI Centerton | New 5.8 miles 69kV line, 795 ACSR | HE | M2 - Appendix A Approved | 12000000 | 2025-09-30 | Line New | New Transmission line, new ROW - may include terminations | HE Wilbur | DEI Centerton |  | 69 |  | 5.8 |  | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Other | 28789 | 28789-MooresJct-WilburJct | Rebuild 2.3 miles of 69kV line from Wilbur Jct to Mooresville Jct | HE | M2 - Appendix A Approved | 2300000 | 2025-05-31 | Line Upgrade | Line rebuild on existing ROW | MooresJct | WilburJct |  | 69 |  |  | 2.3 | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Other | 28790 | 28790-Wilbur-Nelson | Rebuild 6.9 miles of 69kV line | HE | M2 - Appendix A Approved | 7500000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Wilbur | Nelson |  | 69 |  |  | 6.9 | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Other | 28791 | 28791-Nelson-WilburJct | Rebuild 3.45 miles of 69kV line | HE | M2 - Appendix A Approved | 3400000 | 2026-04-01 | Line Upgrade | Line rebuild on existing ROW | Nelson | WilburJct |  | 69 |  |  | 3.45 | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Other | 28792 | 28792-MooresJct-EastMad | Rebuild 2.7 miles 69kV line | HE | M2 - Appendix A Approved | 4450000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | MooresJct | EastMad |  | 69 |  |  |  | IN |  | Not Shared
MTEP24 | A | HOOSIER ENERGY | Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Other | 28793 | 28793-Wilbur Jct-ToytJct | Rebuild 3 miles of 69kV line | HE | M2 - Appendix A Approved | 5000000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Wilbur Jct | ToytJct |  | 69 |  |  | 3 | IN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25506 | Inver Grove – Inver Hills 115 kV Rebuild to Double Circuit 115 kV | Other | 28794 | 28794-Inver Grove-Inver Hills | Rebuild 2.2 miles 115 kV line 5507 to double circuit from Inver Grove - Inver Hills. Expand Inver Hills substation. | XEL | M2 - Appendix A Approved | 18800000 | 2028-12-15 | Line Upgrade | Line rebuild on existing ROW | Inver Grove | Inver Hills | 1 | 115 |  |  | 2.2 | MN |  | Not Shared
MTEP24 | A | NORTHERN STATES POWER COMPANY | West | 25506 | Inver Grove – Inver Hills 115 kV Rebuild to Double Circuit 115 kV | Other | 28795 | 28795-Umore Park- | Add 1 breaker at Umore substation. | XEL | M2 - Appendix A Approved | 2000000 | 2027-11-30 | Substation | Substation (breakers only, no transformer) | Umore Park |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP24 | A | METC | East | 20017 | Reconductor Alma (Cheesman) - Regal #1 138 kV Line | BRP | 25698 | 25698-Alma-Regal | ITC is to reconductor the approximately 1.34 miles of the Alma – Regal #1 138kV with 954 ACSR conductor. Line entrances at Regal will be upgraded with 954 ACSR or greater. | METC | M2 - Appendix A Approved | 1725000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Alma | Regal | 1 | 138 |  |  | 1.34 | MI |  | Not Shared
MTEP24 | A | PRAIRIE POWER, INC. | Central | 23374 | New Babylon 138/69 kV Substation and Lines | Other | 27226 | New Ameren Steamboat-Babylon 138 kV Line | New Ameren Steamboat-Babylon 138 kV Line | PPI | M2 - Appendix A Approved | 1400000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Ameren Steamboat | Babylon | 1 | 138 | 138 | 1.4 |  | IL |  | Not Shared
MTEP24 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50164 | Woodberry Load Addition | Other | 50310 | Woodberry 69kV Substation | New substation that is needed to serve a new 26MW load on the Summerville 69kV system. |  | M2 - Appendix A Approved | 8200000 | 2026-08-01 | Substation | Distribution substation - may include trans high side | Woodberry |  |  | 69 |  |  |  | AR |  | Not Shared
MTEP24 | A | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | South | 50164 | Woodberry Load Addition | Other | 50311 | Woodberry Cap Banks | 2 new cap banks will be added to the Summerville 69kV substation to support contingency voltage issues. |  | M2 - Appendix A Approved | 2000000 | 2026-08-01 | Voltage Device | Capacitor (switched capacitor) | Summerville |  |  | 69 |  |  |  | AR |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50107 | J1513 Clintonville Swt St Network Upgrades and Interconnection Facilities | GIP | 50164 | J1513 Clintonville Switching Station | Add one (1) new 138kV bus tie breaker and one (1) new CCVT, wave trap, and line tuner will be installed on the 86502 Line to Badger. Four (4) new relay panels will be added to the existing control house for protection of the new bus section and Generator Lead Line. |  | M2 - Appendix A Approved | 1501000 | 2029-06-01 | Substation | Switching station (breakers only, no transformer) | Clintonville |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50107 | J1513 Clintonville Swt St Network Upgrades and Interconnection Facilities | GIP | 50165 | 138kV Badger Substation Remote End | 138kV Badger Substation Remote End |  | M2 - Appendix A Approved | 458000 | 2029-06-01 | Substation | Small miscellaneous substation equipment | Badger |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50107 | J1513 Clintonville Swt St Network Upgrades and Interconnection Facilities | GIP | 50166 | 138kV Werner West Substation Remote End | 138kV Werner West Substation Remote End |  | M2 - Appendix A Approved | 146000 | 2029-06-01 | Substation | Small miscellaneous substation equipment | Werner West |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50107 | J1513 Clintonville Swt St Network Upgrades and Interconnection Facilities | GIP | 50167 | J1513 138kV Interconnection Substation Interconnection Facilities | J1513 138kV Interconnection Substation Interconnection Facilities |  | M2 - Appendix A Approved | 1063000 | 2029-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Clintonville |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50108 | J1573 Plover SS Network Upgrades and Interconnection Facilities | GIP | 50168 | J1573 115kV Interconnection Station | Existing Plover Substation will add one (1) new 138kV bus tie breaker and three (3) bus VTs to the existing bus configuration. Three (3) new relay panels will be added to the existing control house for protecting the new buses and Generator Lead Line. |  | M2 - Appendix A Approved | 1735000 | 2028-09-10 | Substation | Small miscellaneous substation equipment | Plover |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50108 | J1573 Plover SS Network Upgrades and Interconnection Facilities | GIP | 50169 | J1573 115kV Interconnection Facilities | J1573 115kV Interconnection Facilities |  | M2 - Appendix A Approved | 898000 | 2028-09-10 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Plover |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50109 | J1814 Nordic SS Network Upgrades and Interconnection Facilities | GIP | 50170 | J1814 138kV Interconnection Station | Existing Nordic Substation will add a new Generator Lead Line terminal with one (1) new 138kV line breaker (included in TOIF) and one (1) line VT. One (1) new relay panel will be added to the existing control house for protecting the new Generator Lead Line. |  | M2 - Appendix A Approved | 1059000 | 2027-08-02 | Substation | Small miscellaneous substation equipment | Nordic |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50109 | J1814 Nordic SS Network Upgrades and Interconnection Facilities | GIP | 50171 | J1814 138kV Interconnection Facilities | J1814 138kV Interconnection Facilities |  | M2 - Appendix A Approved | 1091000 | 2027-08-02 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Nordic |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | GIP | 50172 | J1751 138kV Interconnection Station | J1751 138kV Interconnection Station |  | M2 - Appendix A Approved | 7873000 | 2028-01-30 | Substation | Switching station (breakers only, no transformer) | Young St |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | GIP | 50173 | 138kV Transmission Line Modifications | The X-43 138 kV Transmission Line Loop-In project will consist of two (2) horizontal monopole dead-end structures routing the line through the Transmission Owner’s new substation, segmenting X-43 between the Badger West and Saratoga substations. Line renaming will be required and determined in detailed design. |  | M2 - Appendix A Approved | 849000 | 2028-01-30 | Line Upgrade | Generic transmission line project (try not to use the generic) | Badger West | Saratoga | X-43 | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | GIP | 50174 | Saratoga Substation remote end work | Saratoga Substation remote end work |  | M2 - Appendix A Approved | 235000 | 2028-01-30 | Substation | Small miscellaneous substation equipment | Saratoga |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | GIP | 50175 | Petenwell Substation remote end work | Petenwell Substation remote end work |  | M2 - Appendix A Approved | 250000 | 2028-01-30 | Substation | Small miscellaneous substation equipment | Petenwell |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | GIP | 50176 | J1751 138kV Interconnection Substation Interconnection Facilities | J1751 138kV Interconnection Substation Interconnection Facilities |  | M2 - Appendix A Approved | 496000 | 2028-01-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Young St |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50111 | J1773 Edmund Swt St Network Upgrades and Interconnection Facilities | GIP | 50178 | J1773 345 kV Interconnection Substation | J1773 345 kV Interconnection Substation |  | M2 - Appendix A Approved | 15994000 | 2028-05-01 | Substation | Switching station (breakers only, no transformer) | Edmund |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50111 | J1773 Edmund Swt St Network Upgrades and Interconnection Facilities | GIP | 50179 | W-18 345 kV Transmission Line Modifications | The W-18 345 kV Transmission Line Loop-In project will consist of two (2) vertical dead-end structures routing the line through the Transmission Owner’s new substation, segmenting W-18 between the Hill Valley and Cardinal substations. Line renaming will be required and determined in detailed design. |  | M2 - Appendix A Approved | 2300000 | 2028-05-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Hill Valley | Cardinal | W-18 | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50111 | J1773 Edmund Swt St Network Upgrades and Interconnection Facilities | GIP | 50180 | J1773 345 kV Interconnection Substation Interconnection Facilities | J1773 345 kV Interconnection Substation Interconnection Facilities |  | M2 - Appendix A Approved | 1399000 | 2028-05-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Edmund |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50112 | J1781 Hill Valley SS Network Upgrades and Interconnection Facilities | GIP | 50181 | J1781 Interconnection Switching Station | The facility upgrades required to support J1781 consists of modifying Hill Valley Substation to add a fifth 345 kV terminal position and making it a breaker and a half configuration to accommodate new interconnection facilities. Relay protection and control will be added for the new bus, breakers and line position. The Transmission Owner will maintain ownership of all work at Hill Valley Substation up to the PCO near the POI for the Interconnection Customer’s generation collection facility transmission line. |  | M2 - Appendix A Approved | 5829000 | 2031-08-25 | Substation | Switching station (breakers only, no transformer) | Hill Valley |  |  | 345 |  |  |  | WI |  | Shared
MTEP24 | A | AMERICAN TRANSMISSION COMPANY | West | 50112 | J1781 Hill Valley SS Network Upgrades and Interconnection Facilities | GIP | 50182 | J1781 345kV Interconnection Substation Interconnection Facilities | J1781 345kV Interconnection Substation Interconnection Facilities |  | M2 - Appendix A Approved | 1390000 | 2031-08-25 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Hill Valley |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP23 | A | CITIZENS ELECTRIC CORPORATION 1 | Central | 51104 | New Kinsey 69/12 kV Substation | Other | 52045 | New Kinsey 69/12 kV Substation | Construct New Kinsey 69/12 kV Substation (5/7 MVA). |  | M2 - Appendix A Approved | 1200000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Kinsey 69kV |  |  | 69 | 69 |  |  | MO |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23803 | Big Swan Ring Bus and Capacitor Bank Addition | BRP | 50021 | Big Swan 115 kV Ring Bus | Replace the existing Big Swan 115 kV bus with a new 5 position ring bus. |  | M2 - Appendix A Approved | 7826624 | 2026-12-31 | Substation | Substation bus upgrade | Big Swan |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | ITC | East | 23828 | Hurst 120 kV 33.3 MVAR Capacitor | BRP | 50068 | 50068-GENOA - HURST 120kV_Retermination | Relocate Genoa - Hurst 120 kV from current location to the relocated H-Frame position. |  | M2 - Appendix A Approved | 0 | 2025-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | HURST |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 15654 | Delhi - Tallulah 115 kV rebuild | BRP | 23667 | 23667-Delhi-Tallulah | Rebuild 20.8 miles of 115kV line from Delhi to Tallulah with a minimum through-path rating of 259 MVA (1300A). | Entergy-LA | M2 - Appendix A Approved | 31700000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Delhi | Tallulah | 1 | 115 |  |  | 20.8 | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 15654 | Delhi - Tallulah 115 kV rebuild | BRP | 23668 | 23668-Delhi- | Upgrading terminal equipment at Delhi to 1300 amps | Entergy-LA | M2 - Appendix A Approved | 1 | 2026-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Delhi |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 15654 | Delhi - Tallulah 115 kV rebuild | BRP | 23669 | 23669-Tallulah- | Upgrading terminal equipment at Tallulah to 1300 amps minimum | Entergy-LA | M2 - Appendix A Approved | 1 | 2026-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Tallulah |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 15654 | Delhi - Tallulah 115 kV rebuild | BRP | 23670 | 23670-Delhi-Tallualh | Upgrading relaying to 1300 amps minimum | Entergy-LA | M2 - Appendix A Approved | 1 | 2026-12-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Delhi | Tallualh | 1 | 115 |  |  |  | LA |  | Not Shared
MTEP23 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 19007 | Upgrade Kansas 69 kV line | Other | 25368 | 25368-Kansas (BREC)-Kansas tap | Rebuild 5.1 mile 69 kV radial as double circuit 69 kV line. | BREC | M2 - Appendix A Approved | 900000 | 2030-01-01 | Line Upgrade | Line rebuild on existing ROW | Kansas (BREC) | Kansas tap | 1 | 69 |  |  | 5.1 | KY |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 20201 | Small Capital Project and Asset Renewal Program 2024 | Other | 26316 | Small Capital Project and Asset Renewal Program 2024 | See project description. | ATC | M3 - Under Construction | 47000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Various Sites |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 20204 | Load Interconnection Program 2024 | Other | 26319 | Load Interconnection 2024 | See project description. | ATC | M3 - Under Construction | 16000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Various Sites |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP23 | A | ITC | East | 21725 | Horn - Trenton Channel 120 kV Sag Remediation | BRP | 26334 | 26334-Horn-Trenton Channel | fully remediate the sag on the Horn – Trenton Channel 120 kV circuit up to the conductor limit. | ITCT | M4 - Project in Service | 74000 | 2025-01-07 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Horn | Trenton Channel | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 21725 | Horn - Trenton Channel 120 kV Sag Remediation | BRP | 26335 | 26335-Trenton Channel- | Upgrade 750 CU bus at Trenton Channel 120 kV position HG | ITCT | M3 - Under Construction | 246000 | 2032-12-01 | Substation | Small miscellaneous substation equipment | Trenton Channel |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 21985 | Chandler-Delta 69 kV (Delta1), Rebuild and OPGW | Other | 26628 | 26628-Chandler-Delta | Rebuild approximately 5.5 miles of 69 kV line Delta1 and install OPGW. | ATC | M3 - Under Construction | 16300000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Chandler | Delta |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23728 | Owen Area Substation | Other | 27464 | 27464-Owen Area Substation- | Install new Owen Area Substation and convert Owen Distribution to 23.9 kV. | XEL | M2 - Appendix A Approved | 7854000 | 2026-10-15 | Substation | Substation (breakers only, no transformer) | Owen Area Substation |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | METC | East | 23743 | Deja Junction - Vestaburg 138 kV Rebuild | BRP | 27467 | 27467-Deja Junction-Vestaburg | Rebuild 4.3 miles section between Deja Jct. and Vestaburg of the Eureka - Vestaburg 138kV line using 1431 ACSR with standard double circuit structures. | METC | M2 - Appendix A Approved | 8822000 | 2029-04-05 | Line Upgrade | Line rebuild on existing ROW | Deja Junction | Vestaburg | 1 | 138 |  |  | 4.3 | MI |  | Not Shared
MTEP23 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 23756 | Replace Yankeetown 69/12 kV Transformer | Other | 27481 | 27481-Yankeetown-Yankeetown | Replace 69/12 kV T1 due to age and condition | SIGE | M3 - Under Construction | 1102500 | 2026-06-01 | Transformer | Transformer New | Yankeetown | Yankeetown | T1 | 69 | 12 |  |  | IN |  | Not Shared
MTEP23 | A | MINNESOTA POWER INC. | West | 23707 | Maturi Substation Expansion | Other | 27487 | 27487-Maturi- | Rebuild and expand existing Maturi Substation. Project will add three breaker to allow for the transmission line to be looped in and out of the substation. | MP | M2 - Appendix A Approved | 3580000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Maturi |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | MINNESOTA POWER INC. | West | 23708 | Mahtowa Substation Expansion | Other | 27488 | 27488-Mahtowa- | Add three 115 kV Breakers to reconfigure the Mahtowa Substation into a 3 position ring bus. | MP | M2 - Appendix A Approved | 6737242 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Mahtowa |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | METC | East | 23709 | Campbell – Blendon 138kV Loop Into Tyler | BRP | 27489 | 27489-Campbell-Blendon | Loop the Campbell - Blendon 138kV line into Tyler to create Campbell - Tyler and Tyler - Blendon 138kV lines. | METC | M3 - Under Construction | 1245000 | 2028-03-28 | Line Upgrade | Generic transmission line project (try not to use the generic) | Campbell | Blendon | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23709 | Campbell – Blendon 138kV Loop Into Tyler | BRP | 27491 | 27491-Tyler- | Extend White and Blue Buses and install (5) 138 kV, 3000 A continuous, 50 kA min. interruptible breakers at Tyler 138kV | METC | M3 - Under Construction | 4371321 | 2028-03-28 | Substation | Substation (breakers only, no transformer) | Tyler |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23709 | Campbell – Blendon 138kV Loop Into Tyler | BRP | 27492 | 27492-Campbell-Port Sheldon | Install OGPW/Fiber from Port Sheldon to Campbell use existing fiber paths to get to Tyler, CE to upgrade relaying at Port Sheldon | METC | M3 - Under Construction | 730000 | 2028-03-28 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Campbell | Port Sheldon | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 23697 | Beck - Stephens 120 kV Sag Remediation | BRP | 27499 | 27499-Beck-Stephens | Remediate the sag limit on the Beck - Stephens 120 kV circuit up to a minimum summer emergency rating of 242 MVA. | ITCT | M2 - Appendix A Approved | 540000 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Beck | Stephens | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 15872 | Brownstown-Monroe #2 345 kV Sag Remediation | Other | 27518 | 27518-Monroe- | Upgrade switches at Monroe positions FT and FM to raise rating to at least 1400 MVA (2343A). | ITCT | M2 - Appendix A Approved | 1253000 | 2028-06-30 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Monroe |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 23825 | Reconfigure Rockville 138 kV substation | BRP | 27520 | 27520-Rockville-Substation | Conversion to Ring Bus | IPL | M2 - Appendix A Approved | 8500000 | 2026-12-01 | Substation | Substation bus upgrade | Rockville |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP23 | A | GRIDLIANCE HEARTLAND LLC | Central | 23765 | Rebuild Joppa-Joppa TS-Grahamville 161 line (854) | Other | 27521 | 27521-Joppa-Grahamville | Rebuild GridLiance Heartland portion of Joppa - Joppa TS - Grahamville ckt 854 tie line to LG&E. | GLH | M2 - Appendix A Approved | 21900000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Joppa | Grahamville |  | 161 |  |  | 10.4 | KY | IL | Not Shared
MTEP23 | A | GRIDLIANCE HEARTLAND LLC | Central | 23826 | Rebuild Joppa - Grahamville 161 line (804) | Other | 27522 | 27522-Joppa-Grahamville | Rebuild the GridLiance Heartland portion of Joppa - Grahamville 161 kV Ckt 804 tie line to LG&E | GLH | M2 - Appendix A Approved | 21900000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Joppa | Grahamville |  | 161 |  |  | 10.1 | KY | IL | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23786 | Ft Redwood - Rawhide 115kV Line | BRP | 27523 | 27523-Ft Redwood-Rawhide | Construct a new 115kV line from a new Cooperative Energy owned 115kV switching station near the FT Redwood substation to the new Cooperative Energy owned 115kV switching station near Rawhide Road. | Entergy-MS | M2 - Appendix A Approved | 7000000 | 2029-01-01 | Line New | New Transmission line, new ROW - may include terminations | Ft Redwood | Rawhide | 1 | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23786 | Ft Redwood - Rawhide 115kV Line | BRP | 27524 | 27524-Ft Redwood- | Construct a new 115kV line from the Entergy Mississippi LLC owned Flowers 115kV station to a new Cooperative Energy owned 115kV switching station near the FT Redwood substation. | Entergy-MS | M2 - Appendix A Approved | 2860000 | 2029-01-01 | Substation | Switching station (breakers only, no transformer) | Ft Redwood |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23786 | Ft Redwood - Rawhide 115kV Line | BRP | 27525 | 27525-Redwood-Ft Redwood | Rebuild the existing Cooperative Energy owned Redwood - Ft Redwood 115kV line. | Entergy-MS | M2 - Appendix A Approved | 772500 | 2029-01-01 | Line Upgrade | Line rebuild on existing ROW | Redwood | Ft Redwood |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23786 | Ft Redwood - Rawhide 115kV Line | BRP | 27526 | 27526-Rawhide- | Tap the Entergy MS owned Flowers - Tinsley 115kV line and construct a new Cooperative Energy owned 115kV breaker switching station near Rawhide Road in Warren, MS. | Entergy-MS | M2 - Appendix A Approved | 2860000 | 2029-01-01 | Substation | Switching station (breakers only, no transformer) | Rawhide |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | GRIDLIANCE HEARTLAND LLC | Central | 23827 | New 3-breaker ring bus substation | Other | 27527 | 27527-Heath- | Build a new 3-ring breaker switching station near Health, KY bisecting Joppa - Shawnee Ckt 1 and allowing 1-161 kV terminal for connection with Big Rivers Electric McCracken station. | GLH | M2 - Appendix A Approved | 15900000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Heath |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP23 | A | GRIDLIANCE HEARTLAND LLC | Central | 23827 | New 3-breaker ring bus substation | Other | 27528 | 27528-Joppa-Joppa TS | Looping Joppa - Joppa TS - Shawnee 161 kV three terminal portion of ckt in and out of Joppa TS station. | GLH | M2 - Appendix A Approved | 1 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Joppa | Joppa TS | 1 | 161 |  | 0.4 |  | IL |  | Not Shared
MTEP23 | A | ITC | East | 23828 | Hurst 120 kV 33.3 MVAR Capacitor | BRP | 27529 | 27529-Hurst- Install 33.3 MVAR Capacitor | Install a 33.3 MVAR capacitor at bus 102, position HJ, with a new 120 kV, 40 kA synchronous breaker and associated disconnect switch. Install a 3000 A, 40 kA breaker at position HK on the Hurst – Genoa 120 kV circuit. | ITCT | M2 - Appendix A Approved | 3125000 | 2026-06-01 | Voltage Device | Capacitor (switched capacitor) | Hurst |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | GRIDLIANCE HEARTLAND LLC | Central | 23827 | New 3-breaker ring bus substation | Other | 27530 | 27530-Joppa TS- | Add one breaker and equipment for additional position at Joppa TS | GLH | M2 - Appendix A Approved | 1 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Joppa TS |  |  | 161 |  |  |  | IL |  | Not Shared
MTEP23 | A | METC | East | 23829 | Tompkins 345/138 kV Transformer #1 Replacement | Other | 27535 | 27535-Tompkins- | Replace the 345/138 KV transformer #1 at Tompkins with a new, standard transformer of similar size. | METC | M3 - Under Construction | 5231640 | 2027-01-29 | Transformer | Transformer New | Tompkins |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 15752 | Redstone – Tittabawassee 138 kV Rebuild | BRP | 27541 | 27541-Redstone- | Terminate OPGW at Redstone position WM6. | METC | M2 - Appendix A Approved | 100000 | 2028-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Redstone |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23807 | Alma - Vestaburg 138 kV Reconductor | BRP | 27542 | 27542-Alma-Vestaburg | Reconductor from Vestaburg to structure #2W8472 (~16.24 miles) from 954 ACSR to 954 ACSS. | METC | M2 - Appendix A Approved | 16330000 | 2028-06-01 | Line Upgrade | Line reconductor | Alma | Vestaburg | 1 | 138 |  |  | 16.24 | MI |  | Not Shared
MTEP23 | A | METC | East | 23807 | Alma - Vestaburg 138 kV Reconductor | BRP | 27543 | 27543-Alma- | Upgrade 1590 SAC buses and 1200A switches at Alma position “477” to at least 455 MVA for summer emergency rating. | METC | M2 - Appendix A Approved | 330000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Alma |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23830 | MCV 138 kV Station Equipment Upgrade | BRP | 27544 | 27544-MCV- | Upgrade thermal relay at position "3141" to at least 620 MVA. | METC | M2 - Appendix A Approved | 190000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | MCV |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23784 | Blackberry Breaker Addition | Other | 27545 | 27545-Blackberry- | Remove existing switch 20NSM1 from Blackberry and replace with a circuit breaker and disconnect. OR Retain existing switch 20NSM1 at Blackberry and add a circuit breaker between the 115/69 kV transformer and switch 20NSM1. | GRE | M3 - Under Construction | 1189145 | 2026-04-20 | Substation | Substation (breakers only, no transformer) | Blackberry |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23782 | Dotson Corners Breaker Replacement | Other | 27546 | 27546-Dotson Corners- | Replace 69kv oil breakers 860, 861, and 862 and associated equipment. | GRE | M2 - Appendix A Approved | 1090436 | 2026-07-18 | Substation | Circuit Breaker (replacement at existing substation) | Dotson Corners |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23822 | Matawan - St. Olaf Lake 69 kV Rebuild | Other | 27547 | 27547-Matawan-St. Olaf Lake | Rebuild SW-MB line segments 1 and 2 (11.01 miles) (Matawan switches to St. Olaf Lake switches) to 69 kV minimum conductor size 477 ACSR would meet voltage and thermal considerations per planning. | GRE | M2 - Appendix A Approved | 9807002 | 2026-10-23 | Line Upgrade | Line rebuild on existing ROW | Matawan | St. Olaf Lake | 1 | 69 |  |  | 11 | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23763 | Laketown Substation Tap | Other | 27548 | 27548-Laketown-Laketown Tap | Install 3-way MOD 2000 A 115 kV switch on GRE’s MV-VTT and construct about 3 mile 115 kV transmission line from the three way switch to the high side of MVEC’s Laketown distribution substation. | GRE | M2 - Appendix A Approved | 13904910 | 2028-09-26 | Substation | Distribution substation - may include trans high side | Laketown | Laketown Tap | 1 | 115 |  | 3 |  | MN |  | Not Shared
MTEP23 | A | ITC | East | 23853 | Wayne Transformer 301 Replacement | Other | 27549 | 27549-Wayne- | Replace 345/120kV transformer 301 at Wayne with a new transformer rated at least 750 MVA for summer emergency. | ITCT | M2 - Appendix A Approved | 5635000 | 2026-04-30 | Transformer | Transformer New | Wayne |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23872 | Kraft 138 kV Station Equipment Upgrade | Other | 27550 | 27550-Kraft- | Upgrade existing 500 circuit switcher, 2 line switches with new breakers at Kraft 138kV station | METC | M2 - Appendix A Approved | 5226528 | 2029-02-14 | Substation | Substation (breakers only, no transformer) | Kraft |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23872 | Kraft 138 kV Station Equipment Upgrade | Other | 27551 | 27551-Spaulding-Broadmoor | Remove N.O. 3317 PTS | METC | M2 - Appendix A Approved | 116250 | 2029-02-14 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Spaulding | Broadmoor | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23804 | Kimball Substation Tap | Other | 27558 | 27558-Kimball-Kimball Tap | Construct approximately 4 miles of 115 kV line with 477 ACSR conductor to the high side of Meeker Energy’s new Kimball distribution substation. | GRE | M2 - Appendix A Approved | 4768766 | 2027-09-27 | Substation | Distribution substation - may include trans high side | Kimball | Kimball Tap | 1 | 115 |  | 4 |  | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23803 | Big Swan Ring Bus and Capacitor Bank Addition | BRP | 27559 | 27559-Big Swan- | Add a new 40 MVAr capacitor on the extended 115-kV bus and replace 69-kV bus relaying, station power, and battery bank. | GRE | M2 - Appendix A Approved | 750000 | 2026-12-31 | Voltage Device | Capacitor (switched capacitor) | Big Swan |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23802 | West Otsego Substation Tap | Other | 27560 | 27560-West Otsego-West Otsego Tap | Install a 3-way 69 kV switch on GRE’s Otsego to Albertville 69 kV line and construct about 0.5 miles of 69 kV tap line to the high side of Wright Hennepin’s West of Otsego area substation. | GRE | M2 - Appendix A Approved | 1283329 | 2027-06-30 | Substation | Distribution substation - may include trans high side | West Otsego | West Otsego Tap | 1 | 69 |  | 0.5 |  | MN |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24575 | DPC Clearfield Jct Tap, New T-T | Other | 28046 | DPC Clearfield Jct Tap, New T-T | New T-T interconnection to Council Creek-Hilltop 69 kV (Y-74), and constructing a new 69 kV loop-through substation near New Lisbon Tap with three line breakers to replace an existing three-way GOAB. | ATC | M3 - Under Construction | 11100000 | 2028-11-16 | Line New | New Transmission line, new ROW - may include terminations | Council Creek | Hilltop | Y-74 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | ITC | East | 24593 | GM Orion Plant Expansion | Other | 28048 | 28048-Sunbird- | Install a 120 kV Section Breaker, 3-120 kV line breakers, and create Bus 103 at Sunbird substation. | ITCT | M4 - Project in Service | 7650000 | 2024-04-18 | Substation | Substation (breakers only, no transformer) | Sunbird |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 24593 | GM Orion Plant Expansion | Other | 28049 | 28049-Pontiac-Sunbird | Rebuild segments to double circuit structures and reconductor portions of the existing Pontiac-Sunbird #1 and Pontiac-Walton #1 lines. Install OPGW between Pontiac and Sunbird. Install PTS on Colorado tap of the line | ITCT | M4 - Project in Service | 9500000 | 2025-05-20 | Line Upgrade | Line rebuild on existing ROW | Pontiac | Sunbird | 1 | 120 |  |  | 2.67 | MI |  | Not Shared
MTEP23 | A | ITC | East | 24593 | GM Orion Plant Expansion | Other | 28050 | 28050-Pontiac-Sunbird | Create a second Pontiac-Sunbird 120 kV line by rebuilding existing lines to double circuit structures between the 2 substations. | ITCT | M4 - Project in Service | 5901000 | 2025-05-20 | Line New | New Transmission line, new ROW - may include terminations | Pontiac | Sunbird | 2 | 120 |  | 2.67 |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 24593 | GM Orion Plant Expansion | Other | 28051 | 28051-Bloomfiled-Sunbird | Add 120 kV pole top switch on the tap side of the Colorado 2 tap. | ITCT | M2 - Appendix A Approved | 1260000 | 2026-12-03 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Bloomfiled | Sunbird | 1 | 120 |  |  | 0.1 | MI |  | Not Shared
MTEP23 | A | ITC | East | 24593 | GM Orion Plant Expansion | Other | 28052 | 28052-Bloomfield- | Upgrade relaying at Bloomfield to accommodate the changes at Sunbird substation. | ITCT | M4 - Project in Service | 524000 | 2025-10-30 | Substation | Small miscellaneous substation equipment | Bloomfield |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 24593 | GM Orion Plant Expansion | Other | 28053 | 28053-Pontiac- | Install 1-120 kV line breaker, replace existing 120 kV station equipment, and bypass the 120 kV reactor at the Pontiac 120 kV substation. | ITCT | M4 - Project in Service | 961000 | 2025-03-21 | Substation | Substation (breakers only, no transformer) | Pontiac |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 28060 | 28060-Delhi- | Remove fiber connections from Nokias to Churchill MOABs | METC | M2 - Appendix A Approved | 48580 | 2028-01-26 | Substation | Small miscellaneous substation equipment | Delhi |  |  | 138 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 28061 | 28061-Tompkins- | Remove fiber connections from Nokias to Churchill MOABs | METC | M2 - Appendix A Approved | 58713 | 2028-01-26 | Substation | Small miscellaneous substation equipment | Tompkins |  |  | 138 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 28062 | 28062-Delhi-Tompkins | Remove pole top switch controllers (SEL-2411) at switch locations 3535 & 3527 | METC | M2 - Appendix A Approved | 12500 | 2028-01-26 | Line Upgrade | Generic transmission line project (try not to use the generic) | Delhi | Tompkins |  | 138 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 28063 | 28063-Delhi-Tompkins | Remove pole mounted CTs and control boxes on switches 3435 and 3527 | METC | M2 - Appendix A Approved | 258750 | 2028-01-26 | Line Upgrade | Generic transmission line project (try not to use the generic) | Delhi | Tompkins |  | 138 |  |  |  | MI |  | Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 24695 | New Fauna 345 kV Sub for Flora Solar (J1679) | GIP | 28065 | 28065-Fauna- | 125 MW solar electric generation project. That will interconnect at Fauna sub on Xenia - Mt Vernon West 345 kV Line 4591 | AmerenIL | M2 - Appendix A Approved | 11000000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Fauna |  |  | 345 |  |  |  | IL |  | Shared
MTEP23 | A | AMEREN MISSOURI | Central | 24696 | New Vanhorn 345 kV Substation for Wolf Creek Solar (J1352) | GIP | 28066 | 28066-Vanhorn- | Construct the Interconnection Facilities at the J1352 Interconnection Switching Station, line cut-in and relay upgrades. Vanhorn sub on Montgomery-Spencer Creek 345 kV line. | AmerenMO | M2 - Appendix A Approved | 11000000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Vanhorn |  |  | 345 |  |  |  | MO |  | Shared
MTEP23 | A | ENTERGY ARKANSAS, LLC | South | 24697 | Aurelle 115kV: POI for J1612 | GIP | 28067 | 28067-Aurelle 115kV- | New point of interconnection for J1612 100 MW solar project. | Entergy-AR | M2 - Appendix A Approved | 13031000 | 2028-01-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Aurelle 115kV |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24740 | Commercial (JCE) 69 kV Substation | Other | 28072 | 28072-Commercial (JCE)-Substation | ITC’s portion of the Commercial Substation ITC will install a new 69 kV substation with 2 69 kV line breakers, one distribution transformer position, and one mobile transformer position. All the ITC equipment will be capable of 600A or greater. | ITCM | M3 - Under Construction | 3878272 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Commercial (JCE) | Substation |  | 69 | 69 |  |  | IL |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24740 | Commercial (JCE) 69 kV Substation | Other | 28073 | 28073-Commercial (JCE)-Savanna | Line tap for the new Commercial (JCE) Substation. | ITCM | M4 - Project in Service | 725000 | 2026-04-30 | Line New | New Transmission line, new ROW - may include terminations | Commercial (JCE) | Savanna | 1 | 69 | 69 |  |  | IL |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | GIP | 28077 | 28077-North Arlington Swt St- | J1410 J1411 North Arlington Swt St Network Upgrades | ATC | M3 - Under Construction | 15552396 | 2026-06-03 | Substation | Substation (breakers only, no transformer) | North Arlington Swt St |  |  | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | GIP | 28078 | 28078-Columbia-North Madison | J1410 J1411 TL Modification (W31) | ATC | M3 - Under Construction | 4680062 | 2026-06-03 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Columbia | North Madison | LCOL2 | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | GIP | 28079 | 28079-North Madison- | J1410 J1411 North Madison Relay Panel | ATC | M3 - Under Construction | 242888 | 2026-06-03 | Misc. | Relaying, protection, RTU and SCADA equipment | North Madison |  |  | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | GIP | 28080 | 28080-Columbia- | J1410 J1411 Columbia SS Relay Panel | ATC | M3 - Under Construction | 283940 | 2026-06-03 | Misc. | Relaying, protection, RTU and SCADA equipment | Columbia |  |  | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24758 | J1410 J1411 North Arlington Swt St MPFCA & Network Upgrades | GIP | 28081 | 28081-North Arlington Swt St- | J1410 J1411 North Arlington Swt St Interconnection Facilities | ATC | M3 - Under Construction | 1229118 | 2026-06-03 | Substation | Points of Interconnection for generators (User TAP for dist subs) | North Arlington Swt St |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP23 | A | METC | East | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | GIP | 28082 | 28082-Stable-Substation | Install SEL-2506 relaying at Stable to mitigate islanding scenarios. | METC | M2 - Appendix A Approved | 44963 | 2026-05-29 | Misc. | Relaying, protection, RTU and SCADA equipment | Stable | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24799 | J1377 Blitz SS Network Upgrades and Interconnection Facilities | GIP | 28088 | 28088-Blitz- | J1377 Blitz SS Network Upgrades | ATC | M3 - Under Construction | 10516164 | 2030-03-20 | Substation | Substation (breakers only, no transformer) | Blitz |  |  | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24799 | J1377 Blitz SS Network Upgrades and Interconnection Facilities | GIP | 28089 | 28089-Rockdale- | Rockdale SS Relay | ATC | M3 - Under Construction | 239432 | 2030-03-20 | Misc. | Relaying, protection, RTU and SCADA equipment | Rockdale |  |  | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24799 | J1377 Blitz SS Network Upgrades and Interconnection Facilities | GIP | 28090 | 28090-Blitz-Rockdale | W32 (345kV)-Loop-in New SS | ATC | M3 - Under Construction | 3181676 | 2030-03-20 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Blitz | Rockdale | W-32 | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24799 | J1377 Blitz SS Network Upgrades and Interconnection Facilities | GIP | 28091 | 28091-Blitz- | J1377 Blitz SS Interconnection Facilities | ATC | M3 - Under Construction | 637088 | 2030-03-20 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Blitz |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23629 | Charles City South-Nashua Tap 69 kV Rebuild | Other | 28093 | 28093-Charles City South- | Replace 69 kV line breaker 6210, line breaker 6350 and associated line relaying, and 69 kV bus differential relaying. | MEC | M2 - Appendix A Approved | 1600000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Charles City South |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 24780 | Fayetteville Bee Hollow Substation (J1311) | GIP | 28094 | 28094-Fayetteville Bee Hollow- | The Fayetteville Bee Hollow Substation will be rebuilt to a 4 position (6 position ultimate) 138kV ring bus for J1311 | AmerenIL | M3 - Under Construction | 8000000 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Fayetteville Bee Hollow |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24783 | Hodag SS, DIC, Add Additional Transformer | Other | 28112 | Hodag SS DIC, Add Additional Transformer | Add additional transformer, expand and reconfigure substation to a loop through straight bus configuration | ATC | M3 - Under Construction | 3700000 | 2026-05-01 | Substation | Distribution substation - may include trans high side | Hodag |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24785 | Pleasant Prairie 345 kV Capacitor Bank Addition | Other | 28114 | 28114-Pleasant Prairie- | Install four 75 Mvar 345 kV Capacitor Banks | ATC | M3 - Under Construction | 9500000 | 2026-02-15 | Voltage Device | Capacitor (switched capacitor) | Pleasant Prairie |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24819 | Racine 345 kV Capacitor Bank Addition | Other | 28115 | 28115-Racine- | Install two 75 Mvar 345 kV Capacitor Banks | ATC | M3 - Under Construction | 11900000 | 2026-06-26 | Voltage Device | Capacitor (switched capacitor) | Racine |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24838 | J1316 Paris SS Network Upgrades | GIP | 28116 | 28116-North Appleton-Fox River | NAPL121 345kV Transmission Line Reconductor (J1316) | ATC | M2 - Appendix A Approved | 22347091 | 2028-12-29 | Line Upgrade | Line reconductor | North Appleton | Fox River |  | 345 |  |  | 8 | WI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24838 | J1316 Paris SS Network Upgrades | GIP | 28117 | 28117-Fox River- | Fox River SS Jumper Replacement | ATC | M2 - Appendix A Approved | 85375 | 2028-12-29 | Substation | Small miscellaneous substation equipment | Fox River |  |  | 345 |  |  |  | WI |  | Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 24052 | New Nile 138 kV Substation for J1208-J1209 Chariot Solar I & ll | GIP | 28119 | 28119-Nile- | Construct a ring bus arrangement with four-line terminal positions and provisions for two additional future terminal positions. Cut existing Crab Orchard-Muddy 138 kV transmission line. | AmerenIL | M2 - Appendix A Approved | 9250000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Nile |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 24878 | Ashley-IL 138 kV New Position for Ashley Solar (J1216) | GIP | 28120 | 28120-Ashley-IL- | This project will tap into the existing Ashley 138 kV 3-position ring bus to serve as the Point of Interconnection for the Interconnection Customer's Generating Facility, Ashley Solar, LLC | AmerenIL | M2 - Appendix A Approved | 1000000 | 2027-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Ashley-IL |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24861 | J1583 Interconnection on Evergreen to Donaldsonville 230 kV | GIP | 28123 | 28123-Evergreen-Donaldsonville | Interconnection facilities for J1583 | Entergy-LA | M2 - Appendix A Approved | 5000000 | 2027-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Evergreen | Donaldsonville |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24839 | J1671 230 kV Interconnection Project(Rocky Creek to Veteran) | GIP | 28124 | 28124-Rocky Creek-Veteran | Interconnection for J1671 | Entergy-TX | M2 - Appendix A Approved | 18847000 | 2026-11-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Rocky Creek | Veteran |  | 230 |  |  |  | TX |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24862 | J1644 Generator Interconnection on Champagne to Plaisance 138 kV | GIP | 28125 | 28125-Champagne-Plaisance | Solar Interconnection station | Entergy-LA | M2 - Appendix A Approved | 4329000 | 2026-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Champagne | Plaisance |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24899 | Twinkletown 230 kV: Solar Interconnection (J1748) | GIP | 28136 | 28136-Twinkletown- | The generation facility intends to connect adjacent to the current solar facility located at Twinkletown 230 kV substation. | Entergy-MS | M2 - Appendix A Approved | 672000 | 2027-05-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Twinkletown |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24880 | Cotton Blossom 230 kV: Solar Interconnection (J1747) | GIP | 28137 | 28137-Cotton Blossom- | The generation facility intends to connect adjacent to the current solar facility located at Cotton Blossom 230 kV substation. | Entergy-MS | M2 - Appendix A Approved | 724000 | 2027-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Cotton Blossom |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 22587 | North Central WI Reliability Project | BRP | 26802 | North Central WI Reliability Project | New project scope will require CPCN filing due to routing and siting a new line after constructability concerns were identified with the double circuit build. System Planning has revised the project scope to construct a greenfield 115kV circuit to avoid highly limited outage windows associated with the previous double circuit rebuild scope. Address reliability concerns in the 115kV system in North Central Wisconsin for multiple P6 outage combinations. Scope: • Construct new 115kV source between Hilltop and Pine substations • OPGW to be installed on new line • Asset renewal work on relays at Hilltop, Maine, and Pine substation • Upgrade Pine SS Bus #51 to match rating of new line | ATC | M2 - Appendix A Approved | 71200000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | In development |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22667 | New PPI - Forest City 138 kV Interconnection | Other | 26823 | 26823-Havana-Cincinnati | Construct a new 138 kV substation in ring bus configuration on the existing Ameren Havana-Cincinnati-1352 138 kV line. A position will feed PPI Forest City 138/69 kV | AmerenIL | M2 - Appendix A Approved | 8500000 | 2028-06-01 | Substation | Switching station (breakers only, no transformer) | Havana | Cincinnati |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 22809 | J1058 Network Upgrades 345 kV | GIP | 26840 | 26840-NEW J1058- | New double breaker double bus 345kV sub on the Schahfer to St. John line | NIPS | M2 - Appendix A Approved | 20996953 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | NEW J1058 |  |  | 345 |  |  |  | IN |  | Shared
MTEP23 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 22809 | J1058 Network Upgrades 345 kV | GIP | 26841 | 26841-Schahfer-St. John | Connection of Schahfer to St. John line | NIPS | M2 - Appendix A Approved | 3063450 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | Schahfer | St. John |  | 345 |  |  |  | IN |  | Shared
MTEP23 | A | ITC | East | 22847 | Kings Point - New DTE 120kV Interconnection | Other | 26845 | 26845-New 120kV Substation- | Construct Kings Point 120kV station as a straight bus station with one 40kA section breaker and two 40kA line breakers | ITCT | M2 - Appendix A Approved | 4200000 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | New 120kV Substation |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 22847 | Kings Point - New DTE 120kV Interconnection | Other | 26846 | 26846-Boyne-Golf | Cut the Boyne – Golf 120kV line into the new 120kV substation to provide transmission service to a new LDC Kings Point. Relocate a ~ 2.1 miles section of the Boyne-Golf 120kV circuit by utilizing DTE’s existing 40kV circuit on the North side of 21 Mile Rd, East side of N. Gratiot Ave, and South side of Hall Rd to rebuild this ~2.1 miles to 120kV with 40kV underbuilding to loop the Boyne-Golf line into the new 120kV substation. | ITCT | M2 - Appendix A Approved | 12800000 | 2029-11-16 | Misc. | Line relocation (road move) | Boyne | Golf | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 22847 | Kings Point - New DTE 120kV Interconnection | Other | 26847 | 26847-Boyne-New 120kV Sub | Install OPGW from Boyne – New 120kV Substation for relay communication. | ITCT | M2 - Appendix A Approved | 680000 | 2029-11-16 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Boyne | New 120kV Sub |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 22847 | Kings Point - New DTE 120kV Interconnection | Other | 26848 | 26848-New Substation-Golf | Install OPGW from New 120kV Substation - Golf for relay communication. | ITCT | M2 - Appendix A Approved | 1400000 | 2030-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | New Substation | Golf | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 22847 | Kings Point - New DTE 120kV Interconnection | Other | 26849 | 26849-Boyne- | Identify any necessary relaying required for the protection at Boyne HE Pos | ITCT | M2 - Appendix A Approved | 600000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Boyne |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 22847 | Kings Point - New DTE 120kV Interconnection | Other | 26850 | 26850-Golf- | Identify any necessary relaying required for the protection at Golf HD Pos | ITCT | M2 - Appendix A Approved | 320000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Golf |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22801 | Rebuild Sioux-Meppen North-Hull 138 kV line | Other | 26865 | 26865-Sioux-Meppen North | Rebuild the Sioux-Meppen North-4 from Str. 180-Meppen North and the entire Meppen North-Hull-1494 138 kV line to upgrade aging infrastructure and improve system reliability. | AmerenMO | M3 - Under Construction | 77700000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Sioux | Meppen North |  | 138 |  |  |  | MO | IL | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22846 | Upgrade Sioux 138 kV Substation | Other | 26872 | 26872-Sioux- | Add interrupting device on 14H (Starting XFMR 1) Upgrade 15H posn to higher ampacity to increase available capacity of the 700MVA Auto XFMR Aging infrastructure | AmerenMO | M3 - Under Construction | 24800000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Sioux |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22813 | Reconductor Coffeen North-Roxford 345 kV line | Other | 26874 | 26874-Coffeen North-Roxford | Reconductor the 51 mile Coffeen North-Roxford-4551 345 kV line with conductor capable of carrying 3,000 amps during Summer Emergency conditions. | AmerenIL | M2 - Appendix A Approved | 141600000 | 2027-06-01 | Line Upgrade | Line reconductor | Coffeen North | Roxford | 1 | 345 |  |  | 51 | IL |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22815 | Upgrade Hunter 161 kV substation | Other | 26876 | 26876-Hunter- | Maintenance: BKR H7 Bus Tie 2-3, Line relays on H6 and H2 Bus Relays on Bus 2 BKR relays on bus ties 1-2 and 2-3 Operations: Line breakers on H2 and H10 High Side Interrupting Devices on XFMR 1, 2, 3 | AmerenMO | M2 - Appendix A Approved | 3000000 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Hunter |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22817 | Rebuild Mount Vernon West-Xenia 345 kV line (4591) | Other | 26878 | 26878-Mount Vernon-Xenia | Rebuild the existing 37 mile Mount Vernon West-Xenia-4591 345 kV line due to replace decayed and severely woodpecker damaged wood poles. Newly rebuilt line will utilize conductors capable of 3000 amps at Summer Emergency conditions and 2 OPGW's. | AmerenIL | M2 - Appendix A Approved | 96000000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Mount Vernon | Xenia |  | 345 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 23006 | Upgrade Pilot Knob 161 kV substation | Other | 26879 | 26879-Pilot Knob- | Add circuit switcher for XFMR 1 and line breaker for 161 kV FLET –PKNB -2 | AmerenMO | M2 - Appendix A Approved | 4000000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Pilot Knob |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22866 | Upgrade St Francois 345 kV substation | Other | 26880 | 26880-St. Francois- | Install a new circuit breaker at St. Francois Sub position V43 to complete the ring bus. Add a new breaker at position V45. | AmerenMO | M2 - Appendix A Approved | 25300000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | St. Francois |  |  | 345 | 138 |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22869 | Rebuild Clark 138/161 kV Substation to 138 kV BAAH | BRP | 26890 | 26890-Clark- | Rebuild Clark 138/161 kV Substation to have a 138 kV BAAH bus with 8 positions (4 existing lines, 2 XFMRs, bring in RIV-ALFM-6636) and a 161 kV ring bus with 6 positions (2 existing lines, 2 XFMRs, and new line position to Viburnum). Rebuild the existing Clark-Viburnum 161 kV line to be double circuit 161 kV lines. Add a 161 kV terminal at Viburnum Substation. Route the RIV-ALFM-6636 138 kV line into the new Clark 138 kV BAAH bus. | AmerenMO | M2 - Appendix A Approved | 34200000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Clark |  |  | 161 | 138 |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22890 | Upgrade Selma 161 kV substation | Other | 26891 | 26891-Selma- | Add line breakers to Selma-Rivermines-2 & DPFE-Selma-1 Add High Side Interrupting devices to XFMR 1 & 2 | AmerenMO | M2 - Appendix A Approved | 3000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Selma |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22870 | Reconfigure Mason-Carrollton-Sioux 138 kV lines | Other | 26892 | 26892-Carrollton- | Split the ~2 mile Mason-Carrollton-8/Carrollton-Sioux-8 138 kV lines into two separate circuits to avoid the loss of a single structure causing a long-term outage on both Carrollton supplies. | AmerenMO | M2 - Appendix A Approved | 7500000 | 2029-12-01 | Misc. | Line relocation (road move) | Carrollton |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22787 | Upgrade Warson 161 kV substation | Other | 26893 | 26893-Warson- | Line BKRs on 4 line terminals, High Side interrupting devices on XFMRs 1,2,3,4 Add bus tie 2-3 BKR | AmerenMO | M2 - Appendix A Approved | 8000000 | 2029-12-01 | Substation | Substation (breakers only, no transformer) | Warson |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22789 | Upgrade Canton South 138 kV substation | Other | 26901 | 26901-Canton- | New Ring bus | AmerenIL | M2 - Appendix A Approved | 10300000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Canton |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22927 | Convert Viaduct 115 kV facilities to 161 kV | Other | 26902 | 26902-Viaduct- | Convert 115 kV facilities at Viaduct to 161 kV. Eliminate Viaduct 161 to 115kV transformer T1 by bypassing it, and by changing the taps on Viaduct XFMR 1 from 115 to 161kV. Replace 115kV OCB #5210 with a 161kV puffer breaker. | AmerenMO | M2 - Appendix A Approved | 5000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Viaduct |  |  | 161 | 115 |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22790 | Reconfigure Moreau 161 kV substation (Jays) | Other | 26903 | 26903-Moreau- | Construct a four position (six ultimate) 161 kV ring bus at Moreau | AmerenMO | M2 - Appendix A Approved | 8500000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Moreau |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22873 | Upgrade Oran 161 kV substation | Other | 26906 | 26906-Oran- | Add 161 kV ring bus to split the Kelso- Morley-3 line into two lines | AmerenMO | M2 - Appendix A Approved | 7800000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Oran |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22947 | Upgrade Lakeshire 138 kV substation | Other | 26909 | 26909-Lakeshire- | Add line breaker to Pos. J (Baum-Wat-1) | AmerenIL | M2 - Appendix A Approved | 3400000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Lakeshire |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22791 | New McBaine 161 kV substation | Other | 26912 | 26912-Mcbaine Tap- | New switching station at McBaine tap off LYMT-OVRT-3 | AmerenMO | M2 - Appendix A Approved | 14400000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Mcbaine Tap |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22966 | New Baldwin Area Reactive Support | Other | 26932 | 26932-Turkey Hill- | Add 250 MVAR STATCOM at Turkey Hill | AmerenIL | M4 - Project in Service | 37300000 | 2025-11-25 | Voltage Device | Static Var Compensator (STATCOM) | Turkey Hill |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23026 | New South Central Illinois Transmission Expansion | Other | 26941 | 26941-Reifen- | Construct a new 138 kV substation as an ultimate six-position ring bus requiring one 3000 A 138 kV breaker initially adjacent to the Continental Tire facility. Add breaker position to Mt Vernon 42 2nd street substation | AmerenIL | M3 - Under Construction | 15200000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Reifen |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23026 | New South Central Illinois Transmission Expansion | Other | 26942 | 26942-Reifen-Mt Vernon 42 2nd | Construct a ~3.5 mile 138 kV line from Mt. Vernon 42nd St. to the new substation | AmerenIL | M3 - Under Construction | 18500000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Reifen | Mt Vernon 42 2nd |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23072 | Rebuild Newton-Tanner 345 kV line | Other | 26958 | 26958-Newton-Tanner | Rebuild the Newton-Tanner 345 kV line with conductors capable of 3000 amps Summer Emergency rating and two OPGWs. | AmerenIL | M2 - Appendix A Approved | 29000000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Newton | Tanner |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 19947 | New Allen-Mason City 69 kV Line | Other | 25630 | New Allen-Mason City 69 kV Line | New Allen-Mason City 69 kV Line with 556 ACSR | PPI | M2 - Appendix A Approved | 6367500 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Allen | Mason City |  | 69 |  | 9 |  | IL |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23464 | Abbott-Traer 161kV 15 mile Rebuild | Other | 27269 | 27269-Abbott-Trear | Rebuild the Abbott-Traer 161kV line to using T2 Grosbeak. | ITCM | M2 - Appendix A Approved | 16836000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Abbott | Trear | 1 | 161 | 161 |  | 15 | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23546 | Jefferson County 161kV Substation Rebuild | Other | 27271 | 27271-Jefferson County-Substation | Rebuilding the 161 kV bus into a ring bus configuration will increase the reliability of the system reliability of the area and modernize the existing substation originally built in 1970 without a full substation replacement. In addition, the project will replace some existing infrastructure at the substation which is at the end of its useful life and in need or replacement. A ring bus configuration will increase operational flexibly for the area by allowing increased ability to reconfigure the system during certain outage conditions. | ITCM | M2 - Appendix A Approved | 6443395 | 2026-07-30 | Substation | Substation (breakers only, no transformer) | Jefferson County | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23546 | Jefferson County 161kV Substation Rebuild | Other | 27272 | 27272-Jefferson County-Woody | Line work associated with the 161kV bus conversion to a ring on the Jefferson County-Woody 161kV line. | ITCM | M2 - Appendix A Approved | 736800 | 2026-07-30 | Line New | New Transmission line, new ROW - may include terminations | Jefferson County | Woody | 1 | 161 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23546 | Jefferson County 161kV Substation Rebuild | Other | 27273 | 27273-Henry County-Jefferson County | Line work associated with the 161kV bus conversion to a ring on the Henry County-Jefferson County 161kV line. | ITCM | M2 - Appendix A Approved | 742800 | 2026-07-30 | Line New | New Transmission line, new ROW - may include terminations | Henry County | Jefferson County | 1 | 161 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | Other | 27275 | 27275-Grinnell South-Substation | Rebuild the Grinnell South sub in a new location directly south of the existing sub and add a new 20MVAR cap bank. | ITCM | M2 - Appendix A Approved | 4691139 | 2027-12-07 | Substation | Substation (breakers only, no transformer) | Grinnell South | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | Other | 27276 | 27276-Grinnell South-Substation | Retire the old Grinnell South sub after completion of the new one. | ITCM | M2 - Appendix A Approved | 631261 | 2028-06-03 | Substation | Substation (breakers only, no transformer) | Grinnell South | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | Other | 27277 | 27277-Grinnell-Grinnell South | Grinnell-Grinnell South 69kV line tap work for new Grinnell South sub. | ITCM | M2 - Appendix A Approved | 182500 | 2027-04-22 | Line New | New Transmission line, new ROW - may include terminations | Grinnell | Grinnell South | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23511 | Grinnell South 69kV Substation & 20MVAR Cap | Other | 27278 | 27278-Grinnell South-Powesheik County | Grinnell South-Powesheik County 69kV line tap work associated with new Grinnell South sub. | ITCM | M2 - Appendix A Approved | 132500 | 2027-04-22 | Line New | New Transmission line, new ROW - may include terminations | Grinnell South | Powesheik County | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23512 | Prairie View Substation | Other | 27279 | 27279-Prairie View- | Rebuild the Wheaton Substation on a new location with a 4-row breaker and a half 161 kV configuration in order to separate it from the Generation facility. | XEL | M2 - Appendix A Approved | 35093561 | 2029-05-31 | Substation | Switching station (breakers only, no transformer) | Prairie View |  |  | 161 |  |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23479 | Iron River Substation Rebuild | Other | 27282 | 27282-Iron River- | Rebuild the existing Iron River substation to include a 115 kV ring bus and new 115/34.5 kV transformer. | XEL | M2 - Appendix A Approved | 13000000 | 2026-07-27 | Substation | Substation bus upgrade | Iron River |  |  | 115 | 35 |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23513 | Emerald Substation | Other | 27283 | 27283-Emerald- | Line W3209 – Replace 3 way switch with new 161kv to 115kv substation. | XEL | M2 - Appendix A Approved | 30976287 | 2029-12-14 | Substation | Substation (breakers only, no transformer) | Emerald |  |  | 161 | 115 |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23513 | Emerald Substation | Other | 27284 | 27284-Emerald-Pine Lake | Rebuild 1 mile of double circuit 161-115kv line to single circuit 115kv line. | XEL | M2 - Appendix A Approved | 2000000 | 2025-06-15 | Line Upgrade | Line reconductor | Emerald | Pine Lake | 1 | 161 | 115 |  | 1 | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23513 | Emerald Substation | Other | 27285 | 27285-Pine Lake- | Retire Pine Lake 161kv to 115kv yard. | XEL | M2 - Appendix A Approved | 1000000 | 2025-06-15 | Misc. | Remove existing branch from model | Pine Lake |  |  | 161 | 115 |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23515 | Eau Claire TR09 Replacement | Other | 27288 | 27288-Eau Claire- | Upgrade Eau Claire TR09. | XEL | M2 - Appendix A Approved | 10700000 | 2026-03-31 | Transformer | Transformer New | Eau Claire |  |  | 345 | 161 |  |  | WI |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23483 | J1174 GIA - Bluebill TOIF | GIP | 27308 | 27308-Bluebill-Switch Station | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. | ITCM | M2 - Appendix A Approved | 864989 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Bluebill | Switch Station |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23484 | J1175 GIA - Bluebill TOIF | GIP | 27309 | 27309-Bluebill-Switch Station | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. The TOIF will include dead-end, disconnect switch, arresters, PT’s, relay panel, and associated equipment. | ITCM | M2 - Appendix A Approved | 864989 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Bluebill | Switch Station |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23485 | J1174 & J1175 MPFCA - Network Upgrades | GIP | 27310 | 27310-Bluebill-Switch Station | A new Bluebill 345 kV switching station will be constructed to interconnect projects J1174 and J1175. ITC will TO self-fund the Network Upgrades and will earn a return of and return on investment under a FSA for 90% of the cost. 10% of the Network Upgrades costs will be recovered under Attachment GG. | ITCM | M2 - Appendix A Approved | 13816106 | 2026-06-30 | Substation | Switching station (breakers only, no transformer) | Bluebill | Switch Station |  | 345 | 345 |  |  | IA |  | Shared
MTEP23 | A | ITC MIDWEST | West | 23485 | J1174 & J1175 MPFCA - Network Upgrades | GIP | 27311 | 27311-Bison-Colby | The Bison – Colby 345 kV line will be tapped and re-routed to new positions in the Bluebill station. ITC will TO self-fund the Network Upgrades and will earn a return of and return on investment under a FSA for 90% of the cost. 10% of the Network Upgrades costs will be recovered under Attachment GG. | ITCM | M2 - Appendix A Approved | 2400000 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Bison | Colby | 1 | 345 | 345 |  |  | IA |  | Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23026 | New South Central Illinois Transmission Expansion | Other | 27312 | 27312-Kays- | New Kays Substation | AmerenIL | M2 - Appendix A Approved | 16000000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Kays |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23532 | New Pleasant View-Ishi 69 kV Line | Other | 27313 | New Pleasant View-Moweaqua 69 kV line | New Pleasant View-Moweaqua 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 4375000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Pleasant View | Moweaqua | 1 | 69 | 69 | 3.5 |  | IL |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23567 | Relocate Pearl-Kampsville 69 kV Line | Other | 27316 | Relocate Pearl-Kampsville 69 kV Line | Relocate Pearl-Kampsville 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 7285000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Pearl | Kampsville |  | 69 |  | 8.5 |  | IL |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23532 | New Pleasant View-Ishi 69 kV Line | Other | 27317 | New Moweaqua-Yantisville 69 kV line | New Moweaqua-Yantisville 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 14046500 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Moweaqua | Yantisville | 1 | 69 | 69 | 12.1 | 9.51 | IL |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23532 | New Pleasant View-Ishi 69 kV Line | Other | 27318 | New Yantisville-Henton 69 kV line | New Yantisville-Henton 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 5076500 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Yantisville | Henton | 1 | 69 | 69 | 7.81 |  | IL |  | Not Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 23568 | Replace Southwest 138 kV #16 Breaker | BRP | 27319 | 27319-Southwest-Substation | Replacement of one (1) 138 kV breaker #6 at Southwest | IPL | M2 - Appendix A Approved | 380948 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Southwest |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP23 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 23569 | New [BREC] McCracken-[GLH] Joppa 161 kV Tie Line | Other | 27321 | 27321-McCracken- | BREC McCracken to new GLH switching station. | BREC | M2 - Appendix A Approved | 4300000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | McCracken |  | 1 | 161 |  |  |  | KY |  | Not Shared
MTEP23 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 23569 | New [BREC] McCracken-[GLH] Joppa 161 kV Tie Line | Other | 27322 | 27322-McCracken- | Add new 161 kV terminal. | BREC | M2 - Appendix A Approved | 1000000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | McCracken |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23609 | Delaware Substation 161 kV Line Breakers | Other | 27324 | 27324-Delaware- | Install 161 kV line breakers and associated relaying | MEC | M2 - Appendix A Approved | 2200000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Delaware |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23570 | Valley Trail 161 kV Substation | Other | 27326 | 27326-Valley Trail- | Construct new 161 - 13.2 kV substation | MEC | M2 - Appendix A Approved | 9500000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Valley Trail |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23590 | Granger Substation 161 kV Line Breakers | Other | 27327 | 27327-Granger- | Install 161 kV line breakers and associated relaying | MEC | M2 - Appendix A Approved | 2100000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Granger |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23571 | Humboldt 69 kV Reconfiguration | Other | 27328 | 27328-Humboldt East- | Replace 69 kV breaker 6890 and modify 69 kV line relaying on breakers 6890 and 7130 to accommodate lines from Humboldt Central Substation and Weaver Switching Station, respectively. | MEC | M2 - Appendix A Approved | 2300000 | 2027-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Humboldt East |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23571 | Humboldt 69 kV Reconfiguration | Other | 27329 | 27329-Humboldt East-Humboldt Central | T90W7: Build approximately 1/4 mile of 69 kV line to form the Humboldt East-Humboldt Central 69 kV line. | MEC | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Humboldt East | Humboldt Central |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23571 | Humboldt 69 kV Reconfiguration | Other | 27330 | 27330-Humboldt East-Humboldt (Corn Belt) | T90W8: Remove approximately 1 miles section of 69 kV line. Remove 69 kV line switch 7108. | MEC | M2 - Appendix A Approved | 100000 | 2027-12-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Humboldt East | Humboldt (Corn Belt) |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23571 | Humboldt 69 kV Reconfiguration | Other | 27331 | 27331-Humboldt Central- | Replace 69 kV breakers 7110 and 7120 and add 69 kV line relaying on breakers 7110 and 7120 to accommodate lines from Corn Belt's Humboldt Substation and Humboldt East Substation, respectively. Add 69 kV bus and 69-13 kV transformer differential relaying. None of this is Transmission. | MEC | M2 - Appendix A Approved | 0 | 2027-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Humboldt Central |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23571 | Humboldt 69 kV Reconfiguration | Other | 27332 | 27332-Humboldt East-Weaver Switching Station | Rebuild due to condition and to support networked operation. | MEC | M2 - Appendix A Approved | 6000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Humboldt East | Weaver Switching Station | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23628 | Waverly Junction: Reconfigure 69 kV Terminals | Other | 27334 | 27334-Waverly Junction- | Reconfigure 69 kV line terminals to eliminate tapped substation transformer | MEC | M2 - Appendix A Approved | 2500000 | 2029-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Waverly Junction |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23629 | Charles City South-Nashua Tap 69 kV Rebuild | Other | 27335 | 27335-Charles City South-Nashua Tap | Rebuild Charles City South-Nashua Tap 69 kV Line on new Right of Way | MEC | M2 - Appendix A Approved | 6100000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Charles City South | Nashua Tap | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23591 | Nashua Tap-Plainfield Junction 69 kV Rebuild | Other | 27336 | 27336-Nashua Tap-Plainfield Junction | Replace conductor on section of Nashua Tap-Plainfield Junction 69 kV line using existing right of way | MEC | M2 - Appendix A Approved | 5300000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Nashua Tap | Plainfield Junction | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23610 | Washburn: 161-69 kV, 125 MVA Transformer | Other | 27339 | 27339-Washburn- | Replace existing 161-69 kV, 50 MVA Transformer with a 161-69 kV, 125 MVA Transformer | MEC | M2 - Appendix A Approved | 7500000 | 2028-12-31 | Transformer | Transformer New | Washburn |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23573 | Black Hawk: 161-69 kV, 167 MVA Transformer | Other | 27341 | 27341-Black Hawk- | Replace existing 161-69 kV, 50 MVA Transformer with a 161-69 kV, 167 MVA Transformer | MEC | M2 - Appendix A Approved | 9000000 | 2027-12-01 | Transformer | Transformer New | Black Hawk |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23593 | Charles City North add 69 kV Breakers | Other | 27342 | 27342-Charles City North- | Charles City North Add 69 kV Breakers | MEC | M2 - Appendix A Approved | 800000 | 2027-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Charles City North |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22966 | New Baldwin Area Reactive Support | Other | 27343 | 27343-Moro- | Add 250 MVAR STATCOM at Moro | AmerenIL | M3 - Under Construction | 42500000 | 2027-06-01 | Voltage Device | Static Var Compensator (STATCOM) | Moro |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22966 | New Baldwin Area Reactive Support | Other | 27344 | 27344-Jarvis- | Add 250 MVAR STATCOM at Jarvis 138 kV | AmerenIL | M3 - Under Construction | 42500000 | 2027-06-01 | Voltage Device | Static Var Compensator (STATCOM) | Jarvis |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 22966 | New Baldwin Area Reactive Support | Other | 27345 | 27345-Granite City 23rd street- | Add 250 MVAR STATCOM to Centerville 138 kV substation | AmerenIL | M4 - Project in Service | 39300000 | 2025-11-12 | Voltage Device | Static Var Compensator (STATCOM) | Granite City 23rd street |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23612 | Altona Protection System Upgrade | Other | 27356 | 27356-Altona- | Replace the control building to install modern digital relays and install an additional circuit breaker to increase reliability on Altona to Morley transmission line. | WPSC | M2 - Appendix A Approved | 1500000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Altona |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23614 | Casnovia to Cedar Springs Rebuild | Other | 27358 | 27358-Casnovia-Cedar Springs | Rebuild and upgrade 11 miles of 69kV line to 138 kV standard with steel poles, 795ACSS conductor, and OPGW. | WPSC | M2 - Appendix A Approved | 9250000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Casnovia | Cedar Springs |  | 69 |  |  | 11 | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23615 | Copemish Protection System Upgrade | Other | 27359 | 27359-Copemish- | Replace the circuit breaker and its associated controls and protective relaying, bringing the station to Wolverine’s standard for 138kV transmission operation. | WPSC | M2 - Appendix A Approved | 1500000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Copemish |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23616 | Gaylord Protection System Upgrade | Other | 27360 | 27360-Gaylord- | Upgrade existing electromechanical relays with digital relays. | WPSC | M2 - Appendix A Approved | 800000 | 2026-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Gaylord |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23617 | Hayes Junction to Hayes Rebuild | Other | 27361 | 27361-Hayes Junction-Hayes | Rebuild and upgrade 12 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. | WPSC | M2 - Appendix A Approved | 12000000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Hayes Junction | Hayes |  | 69 |  |  | 12 | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23619 | Mulliken Jct to Grand Ledge Rebuild | Other | 27363 | 27363-Mulliken Jct-Grand Ledge | Rebuild and upgrade 4 miles of 69kV line to 138 kV standard with wood poles, 336ACSS conductor, and OPGW. | WPSC | M2 - Appendix A Approved | 4250000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Mulliken Jct | Grand Ledge |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23620 | North Shade Protection System Upgrade | Other | 27364 | 27364-North Shade- | Upgrade existing electromechanical relays with digital relays. | WPSC | M2 - Appendix A Approved | 1250000 | 2026-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | North Shade |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23574 | Pellston to Cross Village | Other | 27365 | 27365-Pellston-Cross Village | Rebuild and upgrade 9 miles of 69kV line to 138 kV standard with steel poles, 336ACSS conductor, and OPGW. | WPSC | M2 - Appendix A Approved | 10000000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Pellston | Cross Village |  | 69 |  |  | 9 | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23575 | Pellston Relocation and Upgrades | Other | 27366 | 27366-Pellston- | Project will replace capacity limiting equipment and existing protection system at the Pellston substation and relocate the Pellston to Cross Village line to improve reliability on that line. | WPSC | M2 - Appendix A Approved | 1600000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Pellston |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23631 | Petosky Protection System Upgrade | Other | 27367 | 27367-Petoskey- | Upgrade existing electromechanical relays with digital relays. | WPSC | M2 - Appendix A Approved | 1000000 | 2026-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Petoskey |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23953 | Rebuild WVPA Greencastle 69/12kV Substation | Other | 27656 | 27656-WVPA Greencastle- | WVPA Greencastle 69/12kV Substation Rebuild: Rebuild the existing 69-12.47 kV Greencastle Substation with 69 kV flow-through in another location due to size of site. Replace bank with 14.4 MVA. | DEI | M3 - Under Construction | 4828000 | 2026-10-01 | Substation | Substation (breakers only, no transformer) | WVPA Greencastle |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP23 | A | METC | East | 23709 | Campbell – Blendon 138kV Loop Into Tyler | BRP | 27760 | 27760-Campbell- | Replace 138kV Pos. 188 Relaying at Campbell | METC | M3 - Under Construction | 321430 | 2028-03-28 | Misc. | Relaying, protection, RTU and SCADA equipment | Campbell |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23709 | Campbell – Blendon 138kV Loop Into Tyler | BRP | 27761 | 27761-Blendon- | Replace Section 30 Line Relaying at Blendon | METC | M3 - Under Construction | 248766 | 2028-03-28 | Misc. | Relaying, protection, RTU and SCADA equipment | Blendon |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23942 | OTP Gackle - Jamestown 41.6 kV | Other | 27663 | 27663-Jamestown 41.6 kV-Gackle 41.6 kV | Reconductor and rebuild sections of the 41.6 kV line between Gackle 41.6 kV and Jamestown 41.6 kV. | OTP | M2 - Appendix A Approved | 1000000 | 2029-12-31 | Line Upgrade | Line reconductor | Jamestown 41.6 kV | Gackle 41.6 kV |  | 42 |  |  |  | ND |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23941 | Silver Creek Delivery Point | Other | 27664 | 27664-Silver Creek- | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. | SMEPA | M2 - Appendix A Approved | 200000 | 2027-01-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Silver Creek |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 24232 | ALP SE Substation | Other | 27765 | 27765-ALEXNOKO-ALEXAND7 | Alexandria Light & and Power (ALP) will build a new distribution substation on the southeast part of town. The substation will tap and existing 115 kV line with an in and out substation. The substation will have a 115 kV to distribution transformer. | MRES | M2 - Appendix A Approved | 1842000 | 2029-06-30 | Substation | Distribution substation - may include trans high side | ALEXNOKO | ALEXAND7 |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23941 | Silver Creek Delivery Point | Other | 27665 | 27665-Silver Creek- | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. | SMEPA | M2 - Appendix A Approved | 150000 | 2027-01-01 | Line New | New Transmission line, new ROW - may include terminations | Silver Creek |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23943 | OTP Pickert - McVille 41.6 kV | Other | 27666 | 27666-Pickert 41.6 kV-McVille 41.6 kV | Rebuild portions of the 41.6 kV line between Pickert 41.6 kV and McVille 41.6 kV. | OTP | M2 - Appendix A Approved | 3800000 | 2027-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Pickert 41.6 kV | McVille 41.6 kV |  | 42 |  |  |  | ND |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23944 | OTP Wabek - Parshall 41.6 kV | Other | 27667 | 27667-Parshall 41.6 kV-Wabek 41.6 kV | Rebuild and Reconductor the 41.6 kV line between Parshall 41.6 kV and Wabek 41.6 kV | OTP | M2 - Appendix A Approved | 930000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Parshall 41.6 kV | Wabek 41.6 kV | 1 | 42 |  |  |  | ND |  | Not Shared
MTEP23 | A | MINNESOTA POWER INC. | West | 23877 | Nelson Lake 230 kV Substation | Other | 27668 | 27668-Nelson Lake- | New 230 kV Substation, 5 position breaker+half | GRE, MP | M2 - Appendix A Approved | 18000000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | Nelson Lake |  |  | 230 |  | 0 | 0 | ND |  | Not Shared
MTEP23 | A | MINNESOTA POWER INC. | West | 23877 | Nelson Lake 230 kV Substation | Other | 27669 | 27669-Nelson Lake-Square Butte East / Bison | Tie in existing MP Square Butte East - Bison 230 kV Line and build a second Nelson Lake - Square Butte East line parallel to existing | MP | M2 - Appendix A Approved | 5000000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Nelson Lake | Square Butte East / Bison |  | 230 |  | 2 |  | ND |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24272 | J1421 230 kV Interconnection Project | GIP | 27770 | 27770-J1421- | Construct station for new interconnect customer | Entergy-LA | M3 - Under Construction | 32259000 | 2027-09-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | J1421 |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | MINNESOTA POWER INC. | West | 23877 | Nelson Lake 230 kV Substation | Other | 27670 | 27670-Nelson Lake-Square Butte / Stanton | Tie in existing GRE Square Butte - Stanton 230 kV Line | GRE | M2 - Appendix A Approved | 2000000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Nelson Lake | Square Butte / Stanton |  | 230 |  | 0.5 |  | ND |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24272 | J1421 230 kV Interconnection Project | GIP | 27771 | 27771-Moler- | add four breakers to Moler to create a four breaker ring bus. | Entergy-LA | M3 - Under Construction | 1 | 2027-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Moler |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24272 | J1421 230 kV Interconnection Project | GIP | 27772 | 27772-Moler-Coly | Upgrade Coly to Moler 230 kV line. | Entergy-LA | M3 - Under Construction | 1 | 2027-06-01 | Line Upgrade | Line reconductor | Moler | Coly |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24273 | New - 138kV - Airtech Substation | Other | 27773 | 27773-Airtech | New 138kV, two 20 MVA transformer, three-breaker substation | IPL | M2 - Appendix A Approved | 10700000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Thompson | United MOC | 77 | 138 | 12 | 0 | 0 | IN |  | Not Shared
MTEP23 | A | ITC | East | 23947 | 2026 ITCT Customer Interconnections | Other | 27673 | 27673-ITCT Facilitates- | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2 Million a separate project will be submitted for approval. | ITCT | M2 - Appendix A Approved | 2500000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | ITCT Facilitates |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 24293 | New - 138 kV - New Pleasant Acres Substation | Other | 27774 | 27774-PleasantAcres-Substation | New 138 kV, two 40 MVA transformers, 4 breaker, ring bus substation to serve WVPA load | IPL | M2 - Appendix A Approved | 10000000 | 2026-05-15 | Substation | Substation (breakers only, no transformer) | Winding Ridge |  |  | 138 | 12 |  |  | IN |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 12210 | South Hattiesburg Industrial Delivery Point | Other | 27675 | 27675-South Hattiesburg Industrial- | In order to serve the South Hattiesburg and Hattiesburg Industrial delivery points economically and reliably, service will be established by constructing a 161kV breaker switching station. | SMEPA | M2 - Appendix A Approved | 3789500 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | South Hattiesburg Industrial |  |  | 161 |  |  |  | MS |  | Not Shared
MTEP23 | A | ITC | East | 24313 | Greenwood-Rapson(Banner)-J1196 GIA(Wedge) NU | GIP | 27776 | 27776-Wedge-Substation | J1196 is a generation interconnection request for a 200 MW Solar Power Plant proposing to connect to the ITCT Greenwood - Rapson (Banner) 345 kV circuit.J1196 generation is queued within the DPP 2019 Cycle 1. | ITCT | M2 - Appendix A Approved | 11387184 | 2027-03-04 | Substation | Substation (breakers only, no transformer) | Wedge | Substation |  | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | ITC | East | 24313 | Greenwood-Rapson(Banner)-J1196 GIA(Wedge) NU | GIP | 27777 | 27777-Greenwood-Rapson | Loop the Greenwood-Rapson #1 345kV circuit into the new J1196 switching station. | ITCT | M2 - Appendix A Approved | 1233600 | 2027-03-04 | Line New | New Transmission line, new ROW - may include terminations | Greenwood | Rapson | 1 | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 23941 | Silver Creek Delivery Point | Other | 27677 | 27677-Silver Creek- | In order to serve the Silver Creek delivery point economically and reliably, service will be established by tapping the Cooperative Energy owned Line 571 115kV line. A 115kV GOAB will be installed at the tap point and a new 115kV tap line will be constructed to the delivery point. | SMEPA | M2 - Appendix A Approved | 1725000 | 2027-01-01 | Substation | Distribution substation - may include trans high side | Silver Creek |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | ITC | East | 23884 | 2025 ITCTransmission Asset Replacement Program | Other | 27678 | 27678-ITCT Facilities- | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | ITCT | M2 - Appendix A Approved | 60370000 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | ITCT Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24314 | Thetford-J1203 GIA NU | GIP | 27779 | 27779-Thetford-Substation | Complete Thetford 345kV Row 29. Install breakers 29F7, 29H9, and 29R8 including any required disconnects for new breakers. | METC | M2 - Appendix A Approved | 4245703 | 2028-03-01 | Substation | Substation (breakers only, no transformer) | Thetford | Substation |  | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 23948 | 2025 METC Asset Replacement Program | Other | 27679 | 27679-METC Facilities- | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | METC | M2 - Appendix A Approved | 49570000 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | METC Facilities |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24294 | Mio Dam - Twining - J1210 GIA (Quarry) - NU | GIP | 27780 | 27780-Quarry-Substation | Install a new 138 kV station with 5-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | METC | M2 - Appendix A Approved | 7133994 | 2027-08-02 | Substation | Substation (breakers only, no transformer) | Quarry | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 23949 | METC Pole Top Switch Additions/Replacement Program 2025 | Other | 27680 | 27680-METC 138 kV Lines- | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | METC | M2 - Appendix A Approved | 2400000 | 2025-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | METC 138 kV Lines |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24294 | Mio Dam - Twining - J1210 GIA (Quarry) - NU | GIP | 27781 | 27781-Mio Dam-Twining | Loop the Mio Dam - Twining 138kV circuit into the new J1210 switching station. Install fiber on the J1210-Twining circuit. | METC | M2 - Appendix A Approved | 2204400 | 2027-05-03 | Line New | New Transmission line, new ROW - may include terminations | Mio Dam | Twining | 1 | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24294 | Mio Dam - Twining - J1210 GIA (Quarry) - NU | GIP | 27782 | 27782-Iosco-Karn | Loop the Iosco-Karn 138kV circuit into the new J1210 switching station. | METC | M2 - Appendix A Approved | 1357200 | 2027-05-03 | Line New | New Transmission line, new ROW - may include terminations | Iosco | Karn | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 23885 | 2026 METC Customer Interconnections | Other | 27682 | 27682-METC Faciltiies- | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2026 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval | METC | M2 - Appendix A Approved | 2500000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | METC Faciltiies |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24294 | Mio Dam - Twining - J1210 GIA (Quarry) - NU | GIP | 27783 | 27783-Twining-Substation | Remove sparing from Twining breaker position 177. Upgrade position 177 line relays. Upgrade RTU, router, and switch. Extend T1 telecom service from Twining to J1210 Station. | METC | M2 - Appendix A Approved | 354342 | 2026-05-29 | Substation | Substation (breakers only, no transformer) | Twining | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | ITC | East | 24333 | Majestic-Milan - J1224 & J1329 GIA (Neblo) NU | GIP | 27784 | 27784-Neblo-Substation | Construct the new station as a 345kV station breaker and half station with three 40kA breakers in ring bus station. | ITCT | M2 - Appendix A Approved | 10631002 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Neblo | Substation |  | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | ITC | East | 24333 | Majestic-Milan - J1224 & J1329 GIA (Neblo) NU | GIP | 27785 | 27785-Majestic-Milan | Extend the Majestic - Milan 345kV line by adding 0.2 miles of 1431ACSR to loop in the New Station. | ITCT | M2 - Appendix A Approved | 1678800 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | Majestic | Milan | 1 | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | ITC | East | 24333 | Majestic-Milan - J1224 & J1329 GIA (Neblo) NU | GIP | 27786 | 27786-Majestic-Substation | Upgrade relaying at Majestic 345kV position AQ. | ITCT | M2 - Appendix A Approved | 426272 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Majestic | Substation |  | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | ITC | East | 24333 | Majestic-Milan - J1224 & J1329 GIA (Neblo) NU | GIP | 27787 | 27787-Milan-Substation | Upgrade relaying at Milan 345kV position CI. | ITCT | M2 - Appendix A Approved | 420320 | 2029-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Milan | Substation |  | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24275 | Morocco - J1226 GIA NU | GIP | 27788 | 27788-Morocco-Substation | Complete 345kV rows 34 and 36. Install 345kV breakers 34R8, 36R8, and 36F7. Install 345kV disconnects 34R2, 36R4, 36H6, and 36F1. | METC | M2 - Appendix A Approved | 4260888 | 2028-04-03 | Substation | Substation (breakers only, no transformer) | Morocco | Substation |  | 345 | 345 |  |  | MI |  | Shared
MTEP23 | A | ITC | East | 23976 | ITCT Pole Top Switch Additions/Replacement Program 2025 | Other | 27689 | 27689-ITCT 138 kV Lines- | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | ITCT | M2 - Appendix A Approved | 2400000 | 2025-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | ITCT 138 kV Lines |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | GIP | 27789 | 27789-Bearcat-Substation | Construct the New Station as a breaker and half station with three 40kA breakers in a ring bus configuration | METC | M2 - Appendix A Approved | 6421627 | 2026-05-29 | Substation | Substation (breakers only, no transformer) | Bearcat | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23685 | Neal North-Southbridge Tap-Knox-State Steel Tap 69 kV Line Rebuild | Other | 27690 | 27690-Neal North-Southbridge Tap | Rebuild line | MEC | M2 - Appendix A Approved | 2500000 | 2030-12-20 | Line Upgrade | Line rebuild on existing ROW | Neal North | Southbridge Tap |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | METC | East | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | GIP | 27790 | 27790-Marshall-Blackstone | Extend the Marshall - Blackstone (Stable) 138kV line 0.2 miles to loop in the New Station. | METC | M2 - Appendix A Approved | 3170400 | 2026-06-26 | Line New | New Transmission line, new ROW - may include terminations | Marshall | Blackstone | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | GIP | 27791 | 27791-Marshall-Substation | Upgrade Marshall section 30 relaying. | METC | M2 - Appendix A Approved | 37218 | 2026-05-29 | Substation | Substation (breakers only, no transformer) | Marshall | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23978 | New Bargersville North 69kV Switching Station | Other | 27692 | 27692-Bargersville North Switching Station-new sub - ring bus | Build new Bargersville North 69kV three breaker ring bus switching station in the 69102 line | DEI | M2 - Appendix A Approved | 11659302 | 2028-11-07 | Substation | Switching station (breakers only, no transformer) | Bargersville North Switching Station | new sub - ring bus |  | 69 |  |  |  | IN |  | Not Shared
MTEP23 | A | METC | East | 24295 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) NU | GIP | 27792 | 27792-Brook Industrial-Substation | Upgrade Brooks Industrial position WM14 Relaying | METC | M2 - Appendix A Approved | 37218 | 2026-05-29 | Substation | Substation (breakers only, no transformer) | Brook Industrial | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23979 | New Trafalgar 69 kV Ring Bus | Other | 27693 | 27693-Trafalgar-ring bus | Convert the existing Trafalgar 69 kV switching station to a three breaker ring bus | DEI | M2 - Appendix A Approved | 9980000 | 2029-06-01 | Substation | Switching station (breakers only, no transformer) | Trafalgar | ring bus |  | 69 |  |  |  | IN |  | Not Shared
MTEP23 | A | METC | East | 24276 | Vergennes - Marquette - J1255 GIA (Hawley) NU | GIP | 27793 | 27793-Hawley-Substation | Construct a new 138kV station as a breaker and half station with three breakers in a ring bus configuration. | METC | M2 - Appendix A Approved | 6393380 | 2028-09-28 | Substation | Substation (breakers only, no transformer) | Hawley | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24276 | Vergennes - Marquette - J1255 GIA (Hawley) NU | GIP | 27794 | 27794-Marquette-Vergennes | Extend the Vergennes - Marquette 138kV line to loop in the J1255 Generator | METC | M2 - Appendix A Approved | 546000 | 2028-09-28 | Line New | New Transmission line, new ROW - may include terminations | Marquette | Vergennes | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24277 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) NU | GIP | 27795 | 27795-Gains-Thompson Road | Extend the Thompson Road - Gaines 138kV line to loop in the J1292 | METC | M2 - Appendix A Approved | 541200 | 2028-06-01 | Substation | Small miscellaneous substation equipment | Gains | Thompson Road | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24277 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) NU | GIP | 27796 | 27796-Peddler-Substation | Construct a new 138kV station as a breaker and half station with three breakers in a ring bus configuration. | METC | M2 - Appendix A Approved | 6393380 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Peddler | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23962 | Rebuild 6958 Line 69 kV for FAA | Other | 27698 | 27698-HE Whitehall Switch Pole-structure 815-1069-01 | 6958 Line Rbld as required by FAA - Rebuild 39 Structures and replace conductor from HE Whitehall to structure 815-1069-01. Replace individual poles 815-1060 and 815-1061. Install monitored FAA warning lights on 37 of the poles. Install 36 marker balls on the static wire. | DEI | M2 - Appendix A Approved | 3385000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | HE Whitehall Switch Pole | structure 815-1069-01 |  | 69 |  |  | 2.13 | IN |  | Not Shared
MTEP23 | A | METC | East | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | GIP | 27798 | 27798-Hathon-Substation | Construct a new 138kV station as a breaker and half station with five 40kA breakers in a ring bus configuration. | METC | M2 - Appendix A Approved | 8318370 | 2029-12-28 | Substation | Substation (breakers only, no transformer) | Hathon | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | GIP | 27799 | 27799-Cornell-Goss | Extend the Cornell - Goss 138kV line to loop in J1297 | METC | M2 - Appendix A Approved | 3981600 | 2029-12-28 | Line New | New Transmission line, new ROW - may include terminations | Cornell | Goss |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | GIP | 27800 | 27800-Cornell-Substation | Upgrade Positions 177 relays at the Cornell Substation. | METC | M2 - Appendix A Approved | 256477 | 2029-12-28 | Substation | Substation (breakers only, no transformer) | Cornell | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23964 | New Kokomo Fusion Phase 1 - 230/69 kV Sub | Other | 27700 | 27700-Kokomo Fusion - Phase 1-new sub | Kokomo Project Fusion Phase 1: new 230/69kV substation for new large customer load inserted in the 23022 ckt. with breaker and 1/2 layout (between Greentown and Kokomo Webster St.); (2) 150MVA -230/69kV transformers; (14) 69kV breakers in a breaker and one half layout; loop 69172 ckt. (between Kokomo East and Kokomo Chrysler North) through new sub; also loop the 69174 ckt. (between Kokomo Touby Pike Tap 1 and Chrysler North Jct.); (3) 60MVA - 69/34.5kV transformers; add second parallel 230/69kV xfmr at Kokomo Webster St. | DEI | M3 - Under Construction | 92073454 | 2026-11-30 | Substation | Substation (breakers only, no transformer) | Kokomo Fusion - Phase 1 | new sub |  | 230 | 69 |  |  | IN |  | Not Shared
MTEP23 | A | METC | East | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | GIP | 27801 | 27801-Claremont-Cornell | Extend the Claremont - Cornell 138kV line to loop in J1297 | METC | M2 - Appendix A Approved | 5350800 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Claremont | Cornell | 2 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24279 | Claremont - Cornell #2 - J1297 GIA (Hathon) NU | GIP | 27802 | 27802-Goss-Substation | Upgrade Position WM13 relays at the Goss substation. | METC | M2 - Appendix A Approved | 199390 | 2029-12-28 | Substation | Substation (breakers only, no transformer) | Goss | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23968 | New Greensfork East 69/12kV Sub | Other | 27703 | 27703-Greensfork East-new sub | Greensfork East 69/12kV - 22.4MVA Sub: looped-through feed from 69100 ckt. | DEI | M2 - Appendix A Approved | 1440000 | 2029-06-01 | Substation | Distribution substation - may include trans high side | Greensfork East | new sub |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP23 | A | METC | East | 24317 | DuPont - Cobb - J1375 GIA (Lamos) NU | GIP | 27805 | 27805-J1375 New Station-Substation | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | METC | M2 - Appendix A Approved | 6115758 | 2028-05-01 | Substation | Substation (breakers only, no transformer) | J1375 New Station | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23969 | New Williamsport 69/12kV Sub | Other | 27704 | 27704-Williamsport-new sub | Williamsport new 69/12kV - 22.4MVA sub: looped-through feed from the 6936 ckt. | DEI | M2 - Appendix A Approved | 3152000 | 2028-06-01 | Substation | Distribution substation - may include trans high side | Williamsport | new sub |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP23 | A | METC | East | 24317 | DuPont - Cobb - J1375 GIA (Lamos) NU | GIP | 27806 | 27806-Dupont-Cobb | Loop the Dupont - Cobb 138kV circuit into the new J1375 switching station. | METC | M2 - Appendix A Approved | 652800 | 2028-05-01 | Line New | New Transmission line, new ROW - may include terminations | Dupont | Cobb | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23970 | Rebuild 69100 Greensfork to HE Jacksonburg Jct 69kV | Other | 27705 | 27705-Greensfork-HE Jacksonburg Jct | Rebuild 69100 from Greensfork #1 switch (pole #862-3176) to Jacksonburg Jct switch (pole #862-3074) using light duty steel poles, 477ACSR and OPGW | DEI | M2 - Appendix A Approved | 10800000 | 2026-10-30 | Line Upgrade | Line rebuild on existing ROW | Greensfork | HE Jacksonburg Jct |  | 69 |  |  | 5.08 | IN |  | Not Shared
MTEP23 | A | METC | East | 24317 | DuPont - Cobb - J1375 GIA (Lamos) NU | GIP | 27808 | 27808-White Lake-Substation | Upgrade Bus 1, install new Bus 2, install 138kV tie-breaker, install two 138kV line breakers, reconnect CE Trans 2 at Bus 2. | METC | M2 - Appendix A Approved | 5622349 | 2026-05-01 | Substation | Substation (breakers only, no transformer) | White Lake | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23925 | New Slugger 138kV Load | Other | 27707 | 27707-Slugger 138 load- | (1) 12kV construction load up to 12MWS at River Ridge S. 6955 circuit; (2)138 radial tap from 13898 str. 817-4275 to feed up to 146MWs; (3) build 345/138kV substation to feed up to 407MWs; (4) add remote transfer tripping scheme to Open Speed 345/138 Bk3 for P6 outages of 345 line from Speed to Kenzig Rd + 345 line from Slugger to Trimble Co. | DEI | M2 - Appendix A Approved | 123500000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Slugger 138 load |  |  | 345 | 138 | 16 |  | IN |  | Not Shared
MTEP23 | A | METC | East | 24317 | DuPont - Cobb - J1375 GIA (Lamos) NU | GIP | 27809 | 27809-Dupont-Cobb | Loop the Dupont - Cobb 138kV circuit into the White Lake 138kV station. | METC | M2 - Appendix A Approved | 543600 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Dupont | Cobb |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27810 | 27810-J1379 New Station-Substation | Install a new 138 kV station with 4-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | METC | M2 - Appendix A Approved | 7382677 | 2027-04-06 | Substation | Substation (breakers only, no transformer) | J1379 New Station | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27811 | 27811-Eureka-Vestaburg | Loop the Eureka - Vestaburg 138kV circuit into the new J1379 substation. | METC | M2 - Appendix A Approved | 825600 | 2027-01-15 | Line New | New Transmission line, new ROW - may include terminations | Eureka | Vestaburg | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27812 | 27812-Eureka-Substation | Remove sparing from Eureka breaker positions 288 and 277. Upgrade positions 288 and 277 line relays. Install 2 138kV line CCVTs for line positions 288 and 277. | METC | M2 - Appendix A Approved | 1688183 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Eureka | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27813 | 27813-North Belding-Substation | Remove sparing from North Belding breaker positions 177. Upgrade position 177 line relays. Install Blue bus and 500 tie breaker. | METC | M4 - Project in Service | 2997076 | 2025-05-13 | Substation | Substation (breakers only, no transformer) | North Belding | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27814 | 27814-Deja-Derby | Rebuild approximately 8 miles of 138kV line from Derby - Deja with 954 ACSR 138kV double circuit standards. Reconductor should be where appropriate in the cost estimate. Install circuit from North Belding to the J1379 switching station using the vacant side of double circuit tower using 954 ACSR. | METC | M2 - Appendix A Approved | 12793200 | 2027-04-06 | Line New | New Transmission line, new ROW - may include terminations | Deja | Derby | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27815 | 27815-Derby-Eureka | Rebuild approximately 8.6 miles of 138kV line from Derby to Eureka with 954 ACSR 138kV double circuit standards. Reconductor should be where appropriate in the cost estimate. Install circuit from North Belding to the J1379 switching station using the vacant side of double circuit tower using 954 ACSR. | METC | M2 - Appendix A Approved | 13827600 | 2026-05-05 | Line Upgrade | Line rebuild on existing ROW | Derby | Eureka | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24318 | Eureka - Vestaburg - J1379 GIA NU | GIP | 27816 | 27816-Eureka-North Belding | Rebuild approximately 6 miles of 138kV line from Eureka - North Belding with 954 ACSR 138kV double circuit standards. Install circuit from North Belding to the J1379 switching station using the vacant side of double circuit tower using 954 ACSR. | METC | M2 - Appendix A Approved | 10574400 | 2026-02-17 | Line Upgrade | Line rebuild on existing ROW | Eureka | North Belding |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 27817 | 27817-Delhi-Thompkins | J1399 Interconnection is a 90MW solar project in Lesli Township, MI. Build the J1399 Interconnection station as a breaker and half station with three 40kA breakers in a ring bus configuration. Extend the Delhi – Tompkins 138kV line to loop in the J1399 Interconnection station. J1399 is queued within the DPP 2019 Cycle 1. | METC | M2 - Appendix A Approved | 703200 | 2028-01-26 | Line New | New Transmission line, new ROW - may include terminations | Delhi | Thompkins | 2 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 27818 | 27818-Edgar-Substation | Extend the Delhi-Tompkins #2 138kV line to loop in the station. | METC | M2 - Appendix A Approved | 7446364 | 2028-01-26 | Substation | Substation (breakers only, no transformer) | Edgar | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24319 | Delhi-Thompkins #2 J1399 (Edgar) NU | GIP | 27819 | 27819-Edgar-Churchhill | Disconnect the Churchill tap and add 0.5 miles of 954 ACSR to reterminate the Churchill radial at J1399. | METC | M2 - Appendix A Approved | 1482000 | 2028-01-26 | Line New | New Transmission line, new ROW - may include terminations | Edgar | Churchhill |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24282 | Leoni - Parr Road - J1472 GIA(Vargo) NU | GIP | 27821 | 27821-Leoni-Parr Road | Extend the Leoni - Parr Road 138kV line to loop in the new station. | METC | M2 - Appendix A Approved | 3019000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Leoni | Parr Road | 1 | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24282 | Leoni - Parr Road - J1472 GIA(Vargo) NU | GIP | 27822 | 27822-Vargo-Substation | Construct the new 138kV station as a breaker and half station with three breakers in a ring bus configuration. | METC | M2 - Appendix A Approved | 7133000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Vargo | Substation |  | 138 | 138 |  |  | MI |  | Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24296 | Valders SS, New 138/69 kV Substation | Other | 27823 | Valders SS, New 138/69 kV Substation | Construct New Substation | ATC | M2 - Appendix A Approved | 26300000 | 2029-07-25 | Substation | Substation (breakers only, no transformer) | Valders |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | CLECO POWER LLC | South | 24033 | J1286 Manuel Expansion | GIP | 27724 | 27724-Manuel- | Expand Manuel Substation to interconnect J1286 | CLECO | M2 - Appendix A Approved | 2831239 | 2028-05-01 | Misc. | Generator | Manuel |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24053 | J1431 Interconnection Project at Vacherie 230 kV | GIP | 27725 | 27725-Vacherie- | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1431) | Entergy-LA | M2 - Appendix A Approved | 1420000 | 2026-12-31 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Vacherie |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | METC | East | 23872 | Kraft 138 kV Station Equipment Upgrade | Other | 27729 | 27729-Broadmoor- | Upgrade relay equipment at Spaulding | METC | M2 - Appendix A Approved | 233311 | 2029-02-14 | Misc. | Relaying, protection, RTU and SCADA equipment | Broadmoor |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23872 | Kraft 138 kV Station Equipment Upgrade | Other | 27730 | 27730-Spaulding- | Install relay panel at Spaulding Pos. BM36, 36B7 & 36M9 | METC | M2 - Appendix A Approved | 499016 | 2029-02-14 | Misc. | Relaying, protection, RTU and SCADA equipment | Spaulding |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 24072 | Resource Equipment Removal and Bypass | Other | 27731 | 27731-Resource- | Remove transmission equipment at Resource substation. | ITCT | M2 - Appendix A Approved | 530159 | 2025-12-31 | Substation | Small miscellaneous substation equipment | Resource |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 24072 | Resource Equipment Removal and Bypass | Other | 27732 | 27732-Alfred-Frisbie | Bypass Resource substation to form a direct Alfred-Frisbie 120 kV line. | ITCT | M2 - Appendix A Approved | 6312057 | 2025-12-31 | Line New | New underground transmission line | Alfred | Frisbie | 1 | 120 |  | 0.01 |  | MI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24093 | Rocky Run SS T2 and T4 Power Transformer Replacement | BRP | 27733 | Rocky Run SS T2 and T4 Power Transformer Replacement | Planning Scope: o Remove Rocky Run 345/115kV transformers T2 and T4. Replace with on-site spare 500MVA 345/115kV transformer in the T4 position. o Upgrade two (2) 345kV bus switches and five (5) 115kV bus switches. o Remove breaker 4-2 and shorten 345kV ring bus. o Purchase new 500MVA 345/115kV system spare. Asset Renewal Scope: o Replace W-8 secondary relay SEL-321 (component replacement). o Replace all physical security cameras. | ATC | M3 - Under Construction | 17600000 | 2027-06-01 | Transformer | Transformer Replacement | Rocky Run SS |  |  | 345 | 115 |  |  | WI |  | Not Shared
MTEP23 | A | CLECO POWER LLC | South | 24113 | J1424 Singer Substation | GIP | 27742 | 27742-Cole-Penton | Tap the future Cole to Penton 230 kV line and build a new Substation Singer | CLECO | M2 - Appendix A Approved | 2967565 | 2026-10-15 | Misc. | Generator | Cole | Penton | 1 | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | CLECO POWER LLC | South | 24114 | J1367 Caneland Expansion | GIP | 27743 | 27743-Caneland- | Expand Caneland Substation to interconnect J1367 Generation Plant | CLECO | M2 - Appendix A Approved | 5163000 | 2026-10-24 | Misc. | Generator | Caneland |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 12210 | South Hattiesburg Industrial Delivery Point | Other | 22357 | 22357-South Hattiesburg Industrial- | A new distribution station will be constructed adjacent to the 161kV switching station and the existing distribution feeders from both delivery points will be routed to the new station. | SMEPA | M2 - Appendix A Approved | 8762200 | 2027-06-01 | Substation | Distribution substation - may include trans high side | South Hattiesburg Industrial |  |  | 161 |  |  |  | MS |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 15708 | North Jackson 115 kV: Install Circuit Breakers | Other | 23715 | 23715-North Jackson- | Install Transmission Breakers at North Jackson 115 kV substation. | Entergy-MS | M2 - Appendix A Approved | 7300000 | 2026-12-15 | Substation | Circuit Breaker (replacement at existing substation) | North Jackson |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP23 | A | METC | East | 15752 | Redstone – Tittabawassee 138 kV Rebuild | BRP | 23767 | 23767-Redstone-Tittabawassee | Rebuild ~13.4 miles of the Redstone – Tittabawassee 138 kV line that is comprised of 336 ACSR conductor only utilizing 1431 ACSR conductor. The rebuild is using future double-circuit construction with OPGW. | METC | M2 - Appendix A Approved | 22070000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Redstone | Tittabawassee | 1 | 138 |  |  | 13.4 | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23594 | Scottville RTU Upgrade | Other | 27369 | 27369-Scottville- | Obsolete communication equipment must be replaced with a new RTU. | WPSC | M2 - Appendix A Approved | 40000 | 2026-08-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Scottville |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 23595 | Weidman RTU Upgrade | Other | 27370 | 27370-Weidman- | Replace communication equipment at the Weidman substation. | WPSC | M2 - Appendix A Approved | 40000 | 2026-08-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Weidman |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23026 | New South Central Illinois Transmission Expansion | Other | 27375 | 27375-Reifen-Kays | New 138 kV line from Reifen to Kays | AmerenIL | M2 - Appendix A Approved | 70000000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Reifen | Kays |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23026 | New South Central Illinois Transmission Expansion | Other | 27376 | 27376-Kays-Hamilton | New Kays to Hamilton 138 kV line | AmerenIL | M2 - Appendix A Approved | 51000000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Kays | Hamilton |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23026 | New South Central Illinois Transmission Expansion | Other | 27377 | 27377-Benton NW-Franklin | Benton NW to Franklin 138 kV line | AmerenIL | M2 - Appendix A Approved | 22100000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Benton NW | Franklin |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27378 | 27378-Glenham- | Rebuild of current Glenham substation 230/115/41.6 kV. | MDU | M2 - Appendix A Approved | 19000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Glenham |  |  | 230 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27379 | 27379-Glenham-Greenway | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 600000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Greenway |  | 42 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27380 | 27380-Glenham-Selby | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 600000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Selby |  | 42 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27381 | 27381-Glenham-Mobridge | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 600000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Mobridge |  | 42 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27382 | 27382-Glenham-Bowdle East | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 600000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Bowdle East |  | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27383 | 27383-Glenham-Mobridge | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 600000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Mobridge |  | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27384 | 27384-Glenham-Whitlock | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 750000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Whitlock |  | 230 |  |  |  | SD |  | Not Shared
MTEP23 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23596 | Glenham rebuild | Other | 27385 | 27385-Glenham-Bismarck WAPA | Relocation of line to new sub | MDU | M2 - Appendix A Approved | 750000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Glenham | Bismarck WAPA |  | 230 |  |  |  | SD |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23655 | Shenandoah: Replace 69 kV Breakers 601 & 602 | Other | 27396 | 27396-Shenandoah- | Replace to 69 kV breakers at Shenandoah Substation | MEC | M2 - Appendix A Approved | 600000 | 2027-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Shenandoah |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23675 | Avoca: Install 69 kV Breaker on 161-69 kV Transformer 8T3 and 161 kV & 69 kV Breaker Replacements | Other | 27397 | 27397-Avoca- | Install a 69 kV breaker on the low-side of Avoca 161-69 kV Transformer 8T3, replace/rolocate Avoca Breakers 622 and 623 to accommodate new 69 kV breaker and replace Breakers 801, 802 and 620 due to condition | MEC | M2 - Appendix A Approved | 4100000 | 2030-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Avoca |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23678 | New Duck Creek Solar Interconnection (J1199) | GIP | 27400 | 27400-Duck Creek- | Install one 345 kV terminal in the Duck Creek substation. The terminal will consist of all necessary terminal equipment to connect the J1199 leadline to the Duck Creek substation 345 kV bus. Upgrade control and relay fiber panel at the Duck Creek substations as well as the remote end substati | AmerenIL | M2 - Appendix A Approved | 3000000 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Duck Creek |  |  | 345 |  |  |  | IL |  | Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23699 | Gifford Road 161-13.2 kV Substation and 161 kV Line Taps | Other | 27408 | 27408-Gifford Road- | Construct Gifford Road 161-13.2 kV Sub and Line Taps | MEC | M2 - Appendix A Approved | 5000000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Gifford Road |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23719 | Oakland: Add 69 kV, 12 MVAR Capacitor Bank and 69 kV Line Breakers | Other | 27409 | 27409-Oakland- | Install 69 kV, 12 MVAR capacitor bank and install 69 kV line breakers at Oakland Substation. | MEC | M2 - Appendix A Approved | 6500000 | 2027-06-01 | Voltage Device | Capacitor (switched capacitor) | Oakland |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23699 | Gifford Road 161-13.2 kV Substation and 161 kV Line Taps | Other | 27410 | 27410-CBEC-Gifford Road | Construct Gifford Road 161-13.2 kV Sub and Line Taps | MEC | M2 - Appendix A Approved | 1250000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | CBEC | Gifford Road |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23699 | Gifford Road 161-13.2 kV Substation and 161 kV Line Taps | Other | 27411 | 27411-Indian Creek East-Gifford Road | Construct Gifford Road 161-13.2 kV Sub and Line Taps | MEC | M2 - Appendix A Approved | 1250000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Indian Creek East | Gifford Road |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23685 | Neal North-Southbridge Tap-Knox-State Steel Tap 69 kV Line Rebuild | Other | 27415 | 27415-Southbridge Tap-Knox | Rebuild line | MEC | M2 - Appendix A Approved | 2500000 | 2030-04-19 | Line Upgrade | Line rebuild on existing ROW | Southbridge Tap | Knox | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23685 | Neal North-Southbridge Tap-Knox-State Steel Tap 69 kV Line Rebuild | Other | 27416 | 27416-Knox-State Steel Tap | Rebuild single circuit section of line | MEC | M2 - Appendix A Approved | 6000000 | 2030-06-05 | Line Upgrade | Line rebuild on existing ROW | Knox | State Steel Tap |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23720 | Hickory Avenue-Sioux Center 69 kV Line & Substation Line Terminals | BRP | 27417 | 27417-Hickory Avenue-Sioux Center | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals | MEC | M2 - Appendix A Approved | 7000000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Hickory Avenue | Sioux Center |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23720 | Hickory Avenue-Sioux Center 69 kV Line & Substation Line Terminals | BRP | 27418 | 27418-Hickory Avenue- | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals | MEC | M2 - Appendix A Approved | 3000000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Hickory Avenue |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23720 | Hickory Avenue-Sioux Center 69 kV Line & Substation Line Terminals | BRP | 27419 | 27419-Sioux Center- | Construct new 69 kV line from Hickory Avenue Substation to Sioux Center Substation. Expand Hickory Avenue and Sioux Center Substations to install new 69 kV line terminals | MEC | M2 - Appendix A Approved | 2000000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Sioux Center |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23721 | Monona: Replace 161 kV Transformer | Other | 27420 | 27420-Monona- | Replace the existing Monona 161-69 kV transformer with a 125 MVA unit. Convert Monona 161 kV bus to a ring bus configuration. Also, replace two 69 kV breakers and upgrade associated terminal equipment. | MEC | M2 - Appendix A Approved | 19000000 | 2028-12-01 | Transformer | Transformer New | Monona |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23686 | Obrien County-Hospers 161 kV Line, Obrien County 345-161 kV Transformer Addition & Hospers 161-69 kV Transformer Addition | BRP | 27421 | 27421-Obrien County-Hospers | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus | MEC | M2 - Appendix A Approved | 30000000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Obrien County | Hospers |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23686 | Obrien County-Hospers 161 kV Line, Obrien County 345-161 kV Transformer Addition & Hospers 161-69 kV Transformer Addition | BRP | 27422 | 27422-Obrien County- | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus | MEC | M2 - Appendix A Approved | 15000000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Obrien County |  |  | 345 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23686 | Obrien County-Hospers 161 kV Line, Obrien County 345-161 kV Transformer Addition & Hospers 161-69 kV Transformer Addition | BRP | 27423 | 27423-Hospers- | Construct new 161 kV line from Obrien County Substation to Hospers Substation, expand Obrien County Substation to install 345-161 kV, 560 MVA transformer and 161 kV bus and expand Hospers Substation to install 161-69 kV, 167 MVA transformer and 161 kV bus | MEC | M2 - Appendix A Approved | 9000000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Hospers |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23687 | Storm Lake Industrial 69 kV Line Taps | Other | 27424 | 27424-Storm Lake East-CBPC Storm Lake | Construct 69 kV line taps into new Storm Lake Industrial 69-13.8 kV Substation | MEC | M2 - Appendix A Approved | 800000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Storm Lake East | CBPC Storm Lake |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23688 | Macksburg - Winterset 161 kV Reconductor | BRP | 27425 | 27425-Macksburg-Winterset | Reconductor the 161 kV line from Macksburg to Winterset. | MEC | M2 - Appendix A Approved | 12500000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Macksburg | Winterset |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23690 | Quad Cities Enron Substation: Install 161 kV Line Switches | Other | 27427 | 27427-Quad Cities Enron-161 kV Line Switches | Quad Cities Enron Substation: Install 161 kV Line Switches | MEC | M2 - Appendix A Approved | 500000 | 2028-12-31 | Substation | Small miscellaneous substation equipment | Quad Cities Enron |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23739 | Sub 42: Install 69 kV Line Switches | Other | 27428 | 27428-Sub 42-69 kV Line Switches | Sub 42: Install 69 kV Line Switches | MEC | M2 - Appendix A Approved | 800000 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Sub 42 |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23692 | Sub 28 Add 161 kV Line Breakers and Install New Control Building | Other | 27430 | 27430-Sub 28-Add 161 kV Line Breakers | Sub 28: Add 161 kV line breakers and install new control building. | MEC | M2 - Appendix A Approved | 3700000 | 2029-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Sub 28 |  |  | 161 |  |  |  | IL |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 23701 | J1135 GIA Huntwoods 69 kV TOIF | GIP | 27437 | 27437-Huntwoods-Substation | Install equipment dedicated to the J1135 generating facilities. The J1135 line will be connected to a new breaker position on the Huntwoods 69 kV bus. This work is to install a new 69kV terminal. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. | ITCM | M2 - Appendix A Approved | 558384 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Huntwoods | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23740 | Webster: Replace 161 kV Breaker 9250 | Other | 27438 | 27438-Webster-Replace 161 kV breaker 9250 | Replace 161 kV breaker 9250 in Webster substation | MEC | M2 - Appendix A Approved | 500000 | 2028-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Webster |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23741 | Wright 161 kV Terminal Equipment Upgrades | Other | 27439 | 27439-Wright-161 kV Terminal Equipment Upgrades for LRTP Tranche 1 | Wright 161 kV terminal equipment upgrades | MEC | M2 - Appendix A Approved | 170000 | 2028-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Wright |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23694 | Wall Lake 161 kV Terminal Equipment Upgrades | Other | 27440 | 27440-Wall Lake 161 kV Terminal Equipment Upgrades for LRTP Tranche 1 | Wall Lake 161 kV terminal equipment upgrades | MEC | M2 - Appendix A Approved | 100000 | 2028-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Wall Lake |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23725 | Palo Alto 345 kV Substation Expansion for J877 | GIP | 27442 | 27442-Palo Alto- | Network Upgrades for J877 Palo Alto Solar | MEC | M2 - Appendix A Approved | 3800000 | 2027-10-01 | Substation | Circuit Breaker (replacement at existing substation) | Palo Alto |  |  | 345 |  |  |  | IA |  | Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23703 | J982 POI New 345 kV Interconnection Substation and 345 kV Line Taps | GIP | 27443 | 27443-J982 Sub- | Network Upgrades for J982 Generator (345 kV Interconnection Sub) | MEC | M2 - Appendix A Approved | 17250000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | J982 Sub |  |  | 345 |  |  |  | IA |  | Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23703 | J982 POI New 345 kV Interconnection Substation and 345 kV Line Taps | GIP | 27445 | 27445-Clay County-Palo Alto | Network Upgrades for J982 Generator (345 kV line taps) | MEC | M2 - Appendix A Approved | 4000000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Clay County | Palo Alto |  | 345 |  |  |  | IA |  | Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 23727 | Sub 56 161 kV Substation Expansion for J1131 | GIP | 27452 | 27452-Sub 56- | Network Upgrades for J1131 Solar | MEC | M2 - Appendix A Approved | 2025000 | 2027-09-01 | Substation | Circuit Breaker (replacement at existing substation) | Sub 56 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP23 | A | METC | East | 23704 | Abbe Jct - Mio 138kV Sag Remediation | BRP | 27456 | 27456-Mio Dam-Abbe | Remediate sag on the 266.8 ACSR up to conductor’s limit on the Abbe Jct. – Mio Dam section of the Airport – Mio Dam 138 kV circuit. | METC | M2 - Appendix A Approved | 1700000 | 2026-07-23 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mio Dam | Abbe | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 24285 | Benton County Solar Farm | GIP | 27955 | 27955-Benton County- | The existing 115kV Benton County substation is built as a two row breaker-and-a-half breaker station. A new breaker and a half row would be built out to accommodate the interconnection of the 100 MW solar farm for J1426. The network upgrades at the substation will include the installation of a new 115kV Breaker, Line arrestors, line CCVTs, Primary/Secondary Relay Panels, Metering, new metering CTs, and disconnects in the breaker-and-a-half row. | GRE | M2 - Appendix A Approved | 3263833 | 2027-08-02 | Substation | Circuit Breaker (replacement at existing substation) | Benton County |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27956 | 27956-Sycamore SS- | Asset Renewal | ATC | M2 - Appendix A Approved | 4372716 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | Sycamore SS |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27957 | 27957-Blount SS- | Asset Renewal | ATC | M2 - Appendix A Approved | 5502315 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | Blount SS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27958 | 27958-East Campus- | Asset Renewal | ATC | M2 - Appendix A Approved | 4372716 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | East Campus |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27959 | 27959-Blackhawk(MGE)- | Asset Renewal | ATC | M2 - Appendix A Approved | 1093179 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | Blackhawk(MGE) |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27960 | 27960-Ruskin SS- | Asset Renewal | ATC | M2 - Appendix A Approved | 1093179 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | Ruskin SS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27961 | 27961-Wingra SS- | Asset Renewal | ATC | M2 - Appendix A Approved | 1093179 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | Wingra SS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24447 | J1483 Hill Valley SS Network Upgrades and Interconnection Facilities | GIP | 27967 | 27967-Hill Valley SS- | Interconnection Facilities | ATC | M2 - Appendix A Approved | 639848 | 2027-04-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Hill Valley SS |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24447 | J1483 Hill Valley SS Network Upgrades and Interconnection Facilities | GIP | 27968 | 27968-Hill Valley SS- | Substation Modifications | ATC | M2 - Appendix A Approved | 1613040 | 2027-04-30 | Substation | Substation (breakers only, no transformer) | Hill Valley SS |  |  | 345 | 138 |  |  | WI |  | Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22869 | Rebuild Clark 138/161 kV Substation to 138 kV BAAH | BRP | 27969 | 27969-Clark-Viburnam | Rebuild the existing Clark-Viburnum 161 kV line to be double circuit 161 kV lines. | AmerenMO | M2 - Appendix A Approved | 34350000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Clark | Viburnam |  | 161 |  |  |  | MO |  | Not Shared
MTEP23 | A | METC | East | 24448 | Murphy-Styx - J1389 Generator Interconnection - Network Upgrades | GIP | 27973 | 27973-Murphy-Styx | Install a new 345kV 3 Breaker ring station laid out in a breaker and a half configuration. | METC | M2 - Appendix A Approved | 10855221 | 2026-09-04 | Substation | Substation (breakers only, no transformer) | Murphy | Styx |  | 345 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24448 | Murphy-Styx - J1389 Generator Interconnection - Network Upgrades | GIP | 27974 | 27974-Murphy-Styx | Loop the Murphy - Styx (J984) 345kV circuit (Currently Murphy - Nelson Road 345kV circuit) into the new J1389 Interconnection station. | METC | M2 - Appendix A Approved | 1065000 | 2026-09-04 | Line Upgrade | Generic transmission line project (try not to use the generic) | Murphy | Styx |  | 345 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24448 | Murphy-Styx - J1389 Generator Interconnection - Network Upgrades | GIP | 27975 | 27975-Slate- | Install fiber jumpers at Slate for OPGW Fiber, Change SFP’s at Slate in Nokia. | METC | M2 - Appendix A Approved | 13200 | 2026-09-04 | Substation | Small miscellaneous substation equipment | Slate |  |  | 345 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24448 | Murphy-Styx - J1389 Generator Interconnection - Network Upgrades | GIP | 27976 | 27976-Murphy- | Install C37.94 in Nokia router, Change SFP’s at Murphy in Nokia, Install Orion I/O module. | METC | M2 - Appendix A Approved | 39600 | 2026-09-04 | Substation | Small miscellaneous substation equipment | Murphy |  |  | 345 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24514 | Murphy-Styx - J1389 Generator Interconnection - TOIF | GIP | 27977 | 27977-Palomino- | Install 177 disconnect switch and required entrance structures at position RH31 as TOIF | METC | M2 - Appendix A Approved | 1 | 2026-09-04 | Substation | Small miscellaneous substation equipment | Palomino |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24449 | Nevada Area Load Interconnections | Other | 27978 | 27978-Prairieview Industrial-Substation | Construct ITC portion of new Prairieview Industrial Substation. | ITCM | M2 - Appendix A Approved | 13055400 | 2025-09-26 | Substation | Substation (breakers only, no transformer) | Prairieview Industrial | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24449 | Nevada Area Load Interconnections | Other | 27980 | 27980-Ames-Substation | Rebuild 161 kV portion of Ames transmission substation into a ring bus. | ITCM | M2 - Appendix A Approved | 9431715 | 2025-10-03 | Substation | Substation (breakers only, no transformer) | Ames | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24449 | Nevada Area Load Interconnections | Other | 27981 | 27981-Fernald-Substation | Expand Fernald substation with new 161 kV line terminal. | ITCM | M2 - Appendix A Approved | 1114292 | 2025-09-26 | Substation | Substation (breakers only, no transformer) | Fernald | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24449 | Nevada Area Load Interconnections | Other | 27982 | 27982-Fernald-PVIC | Construct new Fernald - Prairie View Industrial Center 161 kV line. | ITCM | M2 - Appendix A Approved | 15430000 | 2026-01-02 | Line New | New Transmission line, new ROW - may include terminations | Fernald | Teller | 1 | 161 | 161 | 8 |  | IA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 24449 | Nevada Area Load Interconnections | Other | 27984 | 27984-Ames-Prairieview | Construct new Ames Transmission - Prairieview Industrial 161 kV line. | ITCM | M2 - Appendix A Approved | 10091622 | 2026-07-31 | Line New | New Transmission line, new ROW - may include terminations | Ames | Prairieview | 1 | 161 | 161 | 5 |  | IA |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 24465 | Walworth - Brick Church (Y-159), OPGW Addition & Rebuild | Other | 27986 | 27986-Walworth-Brick Church | OPGW Addition & Full Rebuild | ATC | M2 - Appendix A Approved | 9400000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Walworth | Brick Church | Y-159 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | COOPERATIVE ENERGY | South | 12210 | South Hattiesburg Industrial Delivery Point | Other | 28008 | 28008-Purvis Bulk-South Hattiesburg Industrial | In order to serve the South Hattiesburg and Hattiesburg Industrial delivery points economically and reliably, service will be established by tapping L161 and constructing a 161kV breaker switching station. | SMEPA | M2 - Appendix A Approved | 1332500 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | Purvis Bulk | South Hattiesburg Industrial |  | 161 |  |  |  | MS |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 18236 | Winnsboro to Gilbert 115 kV: Rebuild Line | BRP | 25074 | 25074-Winnsboro-Gilbert | Rebuild Winnsboro to Gilbert 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | Entergy-LA | M2 - Appendix A Approved | 20900000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Winnsboro | Gilbert | 1 | 115 |  |  | 9.6 | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 18247 | Gilbert to Wisner 115 kV: Rebuild Line | BRP | 25076 | 25076-Gilbert-Wisner | Rebuild Winnsboro to Gilbert 115 kV line to a minimum of 259 MVA. The line will be built using a double circuit configuration but only strung on one side. The unused side will be reserved for a future 230 kV line. | Entergy-LA | M2 - Appendix A Approved | 11900000 | 2027-12-15 | Line Upgrade | Line rebuild on existing ROW | Gilbert | Wisner | 1 | 115 |  |  | 5 | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 18266 | New Long John to Dayton 138 kV: Rebuild line | BRP | 25101 | 25101-Dayton-New Long John | Rebuild the Dayton to New Long John 138 kV line. | Entergy-TX | M3 - Under Construction | 18100000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Dayton | New Long John |  | 138 |  |  | 7 | TX |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25086 | Tinnin Road 230 kV: Solar Gen Interconnection (J1672) | GIP | 28254 | 28254-Tinnin Road- | The generation facility intends to connect to the existing Tinnin Road 230 kV station. | Entergy-MS | M3 - Under Construction | 5529000 | 2026-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Tinnin Road |  |  | 230 |  |  |  | MS |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25242 | Amite South Reliability Project Phase 1 - alternative | Other | 28274 | 28274-Commodore-Churchill | ~85 mile 500 kV | Entergy-LA | M2 - Appendix A Approved | 1700000000 | 2028-08-01 | Line New | New Transmission line, new ROW - may include terminations | Commodore | Churchill |  | 500 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25242 | Amite South Reliability Project Phase 1 - alternative | Other | 28275 | 28275-Commodore-Waterford | 60 mile 230 kV | Entergy-LA | M2 - Appendix A Approved | 1 | 2028-03-31 | Line New | New Transmission line, new ROW - may include terminations | Commodore | Waterford |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25242 | Amite South Reliability Project Phase 1 - alternative | Other | 28276 | 28276-Commodore- | 500-230 kV substation, including 500-230 kV Auto | Entergy-LA | M2 - Appendix A Approved | 1 | 2028-03-31 | Substation | Substation (breakers only, no transformer) | Commodore |  |  | 500 | 230 |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25242 | Amite South Reliability Project Phase 1 - alternative | Other | 28277 | 28277-Churchill- | 500 kV Station and two 500-230 kV Autos | Entergy-LA | M2 - Appendix A Approved | 1 | 2028-08-01 | Substation | Substation (breakers only, no transformer) | Churchill |  |  | 500 | 230 |  |  | LA |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23207 | Rebuild Mattoon West-Tuscola West 138 kV line | Other | 52079 | Mattoon West-Arland 138 kV Rebuild | Mattoon West-Arland 138 kV Rebuild |  | M2 - Appendix A Approved | 6750000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Mattoon West | Arland | 1 | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 9764 | Dixie Baker to Baker 69 kV: Reconductor Line | Other | 21138 | 21138-Dixie Baker-Baker | Upgrade line | Entergy-LA | M2 - Appendix A Approved | 12800000 | 2026-12-01 | Line Upgrade | Line reconductor | Dixie Baker | Baker | 1 | 69 |  |  |  | LA |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23207 | Rebuild Mattoon West-Tuscola West 138 kV line | Other | 26992 | 26992-Arland-Tuscola West | Rebuild the 24.6 mile Mattoon West-Tuscola West-1 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | AmerenIL | M2 - Appendix A Approved | 11750000 | 2032-12-01 | Line Upgrade | Line rebuild on existing ROW | Arland | Tuscola West |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23286 | New [PPI] Paragon 138 kV substation | Other | 27011 | 27011-Pana- | Add interconnection point to the Pana substation for PPI's new bulk substation which will be called Panther. | AmerenIL | M2 - Appendix A Approved | 900000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Pana |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 23107 | New J993 Brickyard Solar 345 kV | GIP | 27013 | 27013-DEI Whitestown-DEI Hortonville | OPGW Fiber Installation | IPL | M2 - Appendix A Approved | 4000000 | 2028-03-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | DEI Whitestown | DEI Hortonville |  | 345 |  |  |  | IN |  | Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 23107 | New J993 Brickyard Solar 345 kV | GIP | 27014 | 27014-J993 Substation | J993 Substation | IPL | M2 - Appendix A Approved | 16000000 | 2028-03-31 | Substation | Substation (breakers only, no transformer) | DEI Whitestown | DEI Hortonville |  | 345 | 138 |  |  | IN |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23406 | Upgrade Bedford 345 kV - 138 kV Bus 9 | BRP | 27033 | 27033-Bedford 345 KV-bus upgrade | Bedford 345 KV - Upgrade 138KV Bus 9 from (1)954acsr@120C (overhead line rating) to (2)954ACSR@120C | DEI | M2 - Appendix A Approved | 295115 | 2028-05-26 | Substation | Substation bus upgrade | Bedford 345 KV | bus upgrade |  | 138 |  |  |  | IN |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23367 | New Lincoln Land Energy Center 345 kV substation (J955) | GIP | 27036 | 27036-Austin- | Project will connect a 1165 combined cycle generator to the existing Austin substation this requires a new 345 kV breaker position. | AmerenIL | M2 - Appendix A Approved | 2700000 | 2026-12-01 | Misc. | Generator | Austin |  |  | 345 |  |  |  | IL |  | Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23350 | New Forest City-Allen 69 kV Line | Other | 27070 | New Forest City-Allen 69 kV Line | New Forest City-Allen 69 kV Line with 556 ACSR partial line. Ties onto existing Allen Tap Line | PPI | M2 - Appendix A Approved | 2880000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Forest City | Allen |  | 69 |  | 4.4 |  | IL |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24923 | Sidney-Percival 69 kV Line Rebuild | Other | 28159 | 28159-Sidney-Percival | Rebuild Sidney-Percival 69 kV line and replace line structures. | MEC | M2 - Appendix A Approved | 9000000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Sidney | Percival |  | 69 |  |  | 10.11 | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24923 | Sidney-Percival 69 kV Line Rebuild | Other | 28160 | 28160-Sidney- | Replace terminal equipment at Sidney Substation on Sidney-Percival line terminal | MEC | M2 - Appendix A Approved | 100000 | 2028-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Sidney |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28161 | 28161-Southland- | Expand 345 kV bus at existing Southland Substation to serve new customer load. | MEC | M4 - Project in Service | 20000000 | 2024-11-12 | Substation | Substation (breakers only, no transformer) | Southland |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28162 | 28162-Southland- | Expand 345 kV bus at existing Southland Substation to serve new customer load. | MEC | M4 - Project in Service | 4500000 | 2025-02-28 | Substation | Substation (breakers only, no transformer) | Southland |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28163 | 28163-Overland Trail-Pony Creek | Construct a new 345 kV line from Overland Trail Substation to Pony Creek Substation | MEC | M2 - Appendix A Approved | 10500000 | 2027-02-01 | Line New | New Transmission line, new ROW - may include terminations | Overland Trail | Pony Creek | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28164 | 28164-CBEC-Overland Trail | Reroute the CBEC-Overland Trail 345 kV line into new line terminal at Overland Trail Substation | MEC | M2 - Appendix A Approved | 2900000 | 2026-12-01 | Misc. | Line relocation (road move) | CBEC | Overland Trail | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28165 | 28165-Overland Trail- | Expand existing Overland Trail 345 kV bus to install a new 345 kV line terminal. | MEC | M3 - Under Construction | 13500000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Overland Trail |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28166 | 28166-Rolling Hills-Southland | Reroute the existing Pony Creek-Rolling Hills 345 kV line into Southland Substation | MEC | M2 - Appendix A Approved | 4000000 | 2026-12-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Rolling Hills | Southland | 1 | 345 |  |  |  | IA |  | Not Shared
MTEP23 | A | MIDAMERICAN ENERGY CO. | West | 24999 | Southland Expansion & Upgrades | Other | 28167 | 28167-CBEC-Pony Creek | Rebuild the existing CBEC-Pony Creek 345 kV line | MEC | M2 - Appendix A Approved | 11000000 | 2027-06-03 | Line Upgrade | Line rebuild on existing ROW | CBEC | Pony Creek | 1 | 345 |  |  | 2.81 | IA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24984 | J1760 Generator Interconnection on Plum Grove to Colony 230 kV | GIP | 28182 | 28182-Plum Grove-Colony | GI on Plum Grove to Colony | Entergy-TX | M2 - Appendix A Approved | 16300000 | 2028-11-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Plum Grove | Colony |  | 230 |  |  |  | TX |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24985 | J1827 Generator Interconnection Bastrop Tap 115 kV | GIP | 28183 | 28183-Batrop Tap- | GIA 1827 | Entergy-LA | M2 - Appendix A Approved | 18500000 | 2029-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Batrop Tap |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24986 | J1795 Generator Interconnection on Richard to Bayou Cove 138 kV(Ln 258) | GIP | 28184 | 28184-Richard-Bayou Cove | GIA J1795 | Entergy-LA | M2 - Appendix A Approved | 17700000 | 2028-05-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Richard | Bayou Cove |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | ITC MIDWEST | West | 25060 | Grant Milford Interconnection | Other | 28192 | 28192-Grant Tap-Grant Milford | Rebuild existing 4 mile 34.5 kV line to 69 kV construction standards | ITCM | M2 - Appendix A Approved | 3483750 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Grant Tap | Grant Milford |  | 69 | 69 |  | 4 | IA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25083 | J1794 Generator Interconnection on Richard to Scott 138 kV | GIP | 28208 | 28208-Richard-Scott | This construction of a new station on the Richard to Scott 138 kV line to accommodate the interconnection of a solar facility (J1794) | Entergy-LA | M2 - Appendix A Approved | 12840000 | 2027-03-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Richard | Scott |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25140 | J1669 Generator Interconnection on Lake Charles Bulk to Henning 138 kV | GIP | 28209 | 28209-Lake Charles Bulk-Henning | Facilities required to interconnect J1669 Lake Charles Bulk to Henning 138 kV | Entergy-LA | M2 - Appendix A Approved | 16910000 | 2028-03-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Lake Charles Bulk | Henning |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25122 | J1542 Generator Interconnection on Vacherie to Chackbay 230 kV | GIP | 28210 | 28210-Vacherie-Chackbay | This construction of a new station on the Vacherie to Chackbay 230 kV line to accommodate the interconnection of a solar facility (J1542) | Entergy-LA | M2 - Appendix A Approved | 19300000 | 2029-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Vacherie | Chackbay |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25101 | J1564 Generator Interconnection on the Bogalusa to Talisheek 230 kV | GIP | 28211 | 28211-Bogalusa-Talisheek | This construction of a new station on the Bogalusa to Talisheek 230 kV line to accommodate the interconnection of a solar facility (J1564) | Entergy-LA | M2 - Appendix A Approved | 18820000 | 2028-01-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Bogalusa | Talisheek |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 25143 | J1602 Generator Interconnection at Rilla 115 kV | GIP | 28214 | 28214-Rilla- | Facilities required for the interconnection of J1602 at Rilla 115 kV. The J1602 battery will be interconnected behind the main step up transformer for J1239 (Rilla 115 kV POI) | Entergy-LA | M3 - Under Construction | 1 | 2026-06-25 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Rilla |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23427 | New Disco-Carthage 69 kV Line | Other | 27078 | New Disco-Carthage 69 kV Line | New Disco-Carthage 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 8320000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Disco | Carthage |  | 69 |  | 13.1 |  | IL |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 23428 | New Golden-Denver 69 kV Line | Other | 27079 | New Golden-Denver 69 kV line | New Golden-Denver 336 ACSR 69 kV line | PPI | M2 - Appendix A Approved | 12800000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Golden | Denver | 1 | 69 | 69 | 20 |  | IL |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23800 | Gilman - Milaca 69 kV Line Rebuild | Other | 27562 | 27562-Gilman-Milaca | Rebuild the JC line (18.93 miles) and switch SS2888 to 69kV with 477 ACSS. | GRE | M2 - Appendix A Approved | 15282817 | 2026-08-21 | Line Upgrade | Line rebuild on existing ROW | Gilman | Milaca | 1 | 69 |  |  | 18.93 | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23681 | Riverton Breaker Replacement | Other | 27566 | 27566-Riverton- | This project will remove 69kV bus differential relaying, replace GE-T60 with SEL-487E using existing panel 7, protect the 69kV bus zone with the transformer relays, replace Riverton IR8600 RTU with Cybectec RTU, replace Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, and replace the 115-kV 25WB1 oil breaker. In addition to this work there will also be some 69-kV and 115-kV bus work and jumper modifications. | GRE | M3 - Under Construction | 2943580 | 2026-05-29 | Substation | Circuit Breaker (replacement at existing substation) | Riverton |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23892 | Reconfigure Shelbyville Northeast 138kV Ring bus | Other | 27568 | 27568-Shelbyville Northeast- | Shelbyville Northeast: build 138kV ring bus; replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | DEI | M2 - Appendix A Approved | 10800000 | 2027-04-08 | Substation | Substation (breakers only, no transformer) | Shelbyville Northeast |  |  | 138 | 69 |  |  | IN |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23833 | New Edinburgh Industrial Park 69/12kV sub | Other | 27569 | 27569-Edinburgh Industrial Park- | DEI to construct high-side and loop 69kV lines into a new IMPA-owned Edinburgh Industrial Park substation; one 69/12kV 20MVA transformer; SCADA controlled MOLB 69kV line switches; two 69kV buses with a manually operated 69kV bus tie switch; 69kV connections from the 6950 and 69146 ckts. | DEI | M2 - Appendix A Approved | 4570000 | 2027-06-25 | Substation | Distribution substation - may include trans high side | Edinburgh Industrial Park |  |  | 69 | 12 | 1.3 |  | IN |  | Not Shared
MTEP23 | A | ITC | East | 23894 | Jewell 301 Transformer Replacement | Other | 27571 | 27571-Jewell- | Replace the 345/230 KV transformer #301 at Jewell with a new, standard transformer of similar size. | ITCT | M2 - Appendix A Approved | 6600000 | 2027-04-05 | Transformer | Transformer New | Jewell |  |  | 345 | 230 |  |  | MI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23836 | Perch Lake - National 138kV (468), Partial Retirement Project | Other | 27572 | 27572-Perch Lake-National | PR09152: Reconfigure 138kV line 468, from Perch-Lake to Presque Isle, by terminating into National SS to establish a new Perch Lake – National line. The remaining 23mi of line from National to Presque Isle will be retired. PR09140: Perch Lake SS Asset Renewal - Replacement of one oil circuit breaker along with four disconnect switches. This work was formerly in the Small Cap and Asset Renewal Program and is being combined with this project for efficiencies. PR09260: Perch Lake - Presque Isle line 468 Rerate - this rerate project was formerly in the Line Clearance Mitigation Program and is being combined with this project for efficiencies. PR09290: UPPCO to install a new transformer on the existing open position on Bus 3. ATC to retire the 138 kV SSVT on 138 kV Bus 1. | ATC | M3 - Under Construction | 13700000 | 2026-04-15 | Line Upgrade | Generic transmission line project (try not to use the generic) | Perch Lake | National | 468 | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23835 | Pere Marquette Transformer 2 Replacement | Other | 27573 | 27573-Pere Marquette- | Replace 345/138KV transformer 2 at Pere Marquette with a new, standard transformer of similar size. Install a 345 kV breaker and associated switch on the high side of the transformer. Also, install a 138 kV switch on the low side of the transformer. | METC | M3 - Under Construction | 8500000 | 2028-03-01 | Transformer | Transformer New | Pere Marquette |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23895 | McCue SS Control House and Relay Asset Renewal | Other | 27578 | 27578-McCue SS- | Control House and Relay Asset Renewal | ATC | M3 - Under Construction | 6500000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | McCue SS |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23897 | Ohmstead SS Control House and Relay Asset Renewal | Other | 27579 | 27579-Ohmstead SS- | Control House and Relay Asset Renewal | ATC | M2 - Appendix A Approved | 5500000 | 2027-05-03 | Substation | Substation (breakers only, no transformer) | Ohmstead SS |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP23 | A | ENTERGY ARKANSAS, LLC | South | 23898 | McNeil 500kV Relay Improvement SPOF | BRP | 27580 | 27580-Mcneil 500kV- | • Ensure the McNeil – El Dorado 500 kV line, the McNeil 500/115 kV auto and the McNeil – Etta 500 kV line have redundant high-speed protection. • Ensure protection schemes have independent CT and PT winding inputs. • Ensure dual battery installations or monitoring sufficient to FERC 754 guidelines. | Entergy-AR | M2 - Appendix A Approved | 3970000 | 2028-12-15 | Misc. | Relaying, protection, RTU and SCADA equipment | Mcneil 500kV |  |  | 500 |  |  |  | AR |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23855 | Keo 500kV Bus Reconfigure | BRP | 27581 | 27581-Keo- | Reconfigure the Keo 500 kV substation so that the Keo – White Bluff & Keo - Wrightsville 500kV lines are not lost for a P2.3 internal breaker fault. | Entergy-AR | M2 - Appendix A Approved | 10193000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Keo |  |  | 500 |  |  |  | AR |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23896 | OTP Devils Lake, ND 115 kV Delivery | Other | 27584 | 27584-Devils Lake East 115 kV (620265)-Sweetwater (657720) | Tap the Devils Lake East 115 kV to Sweetwater 115 kV line with a two way 115 kV switch. | OTP | M2 - Appendix A Approved | 300000 | 2028-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Devils Lake East 115 kV (620265) | Sweetwater (657720) | 1 | 115 |  |  |  | ND |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23896 | OTP Devils Lake, ND 115 kV Delivery | Other | 27585 | 27585-New Tap along Devils Lake East - Sweetwater 115 kV line-New Devils Lake 115/12.5 kV Distribution Substation | New approximate 2 mile 115 kV line from the new tap along the Devils Lake East - Sweetwater 115 kV to the new 115/12.5 kV distribution substation. Addition of a 115 kV breaker on the high side of the 115/12.5 kV transformer. | OTP | M2 - Appendix A Approved | 1250000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | New Tap along Devils Lake East - Sweetwater 115 kV line | New Devils Lake 115/12.5 kV Distribution Substation | 1 | 115 |  |  |  | ND |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23901 | Shoto SS, Power Transformer Asset Renewal | Other | 27586 | 27586-Shoto SS- | Replace T1 | ATC | M2 - Appendix A Approved | 7500000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Shoto SS |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23856 | Benson Lake SVC SCM Layer Asset Renewal | Other | 27587 | 27587-Benson Lake- | Replace hardware and software of the Benson Lake SVC plant System Control and Monitoring (SCM) Layer with supported hardware and software with a design life of 10 years. | ATC | M2 - Appendix A Approved | 3400000 | 2026-12-01 | Voltage Device | Static Var Compensator (STATCOM) | Benson Lake |  |  | 21 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23903 | North Beaver Dam SS Asset Renewal | Other | 27589 | 27589-North Beaver Dam- | Asset Renewal | ATC | M2 - Appendix A Approved | 16100000 | 2030-08-29 | Substation | Substation (breakers only, no transformer) | North Beaver Dam |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23904 | South Beaver Dam – North Beaver Dam, 69kV (Y-59) Line Rebuild & OPGW | Other | 27590 | 27590-South Beaver Damn-North Beaver Dam | South Beaver Dam – North Beaver Dam, 69kV (Y-59) Line Rebuild | ATC | M2 - Appendix A Approved | 11200000 | 2029-03-16 | Line Upgrade | Line rebuild on existing ROW | South Beaver Damn | North Beaver Dam | Y-59 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23905 | Waupun – Str 127484 69 kV (Y-25), Partial Rebuild & OPGW | Other | 27591 | Waupun - Str 127484 69 kV (Y-25), Partial Rebuild & OPGW | Partial rebuild of line Y-25 from Waupun SS to Structure 127484 and addition of OPGW. | ATC | M3 - Under Construction | 20000000 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Waupun | Structure 127484 | Y-25 | 69 |  |  | 10.5 | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23906 | South Fond du Lac SS, Power Transformer and Breaker Asset Renewal | Other | 27592 | 27592-South Fond du Lac- | South Fond du Lac Asset Renewal | ATC | M2 - Appendix A Approved | 9500000 | 2028-12-30 | Substation | Substation (breakers only, no transformer) | South Fond du Lac |  |  | 345 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23875 | Madison Area Relay Projects | Other | 27596 | 27596-Walnut GIS- | Walnut GIS Asset Renewal | ATC | M2 - Appendix A Approved | 4372716 | 2029-02-16 | Substation | Substation (breakers only, no transformer) | Walnut GIS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23876 | Cornell Tap – Watson Tap 69kV (Chandler), Partial Rebuild | Other | 27597 | Cornell Tap – Watson Tap 69kV (Chandler), Partial Rebuild | Partial rebuild and installation of OPGW on approximately 18 miles of the Chandler line from Cornell SS towards Arnold SS. | ATC | M2 - Appendix A Approved | 41000000 | 2028-11-01 | Line Upgrade | Line rebuild on existing ROW | Cornell Tap | Watson Tap | Chandler | 69 |  |  | 18 | MI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23911 | Shoto – Northeast 69kV (K-11), Rebuild | Other | 27600 | 27600-Shoto-Northeast | Rebuild | ATC | M2 - Appendix A Approved | 12800000 | 2030-10-31 | Line Upgrade | Line rebuild on existing ROW | Shoto | Northeast | K-11 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23837 | Northeast – Revere Dr 69kV (C-103), Uprate or Rebuild | Other | 27601 | 27601-Northeast-Revere Dr | Uprate or Rebuild | ATC | M2 - Appendix A Approved | 8600000 | 2030-01-31 | Line Upgrade | Line rebuild on existing ROW | Northeast | Revere Dr | C-103 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23838 | High Falls – Mountain 69kV (Y-77), Rebuild & OPGW | Other | 27602 | 27602-High Falls-Mountain | Rebuild | ATC | M2 - Appendix A Approved | 33000000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | High Falls | Mountain | Y-77 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23842 | OTP Wilmot - Peever Jct. 41.6 kV | Other | 27607 | 27607-Wilmot 41.6 kV-Peever Jct. 41.6 kV | Rebuild 4 miles of 41.6 kV line between Wilmot 41.6 kV and Peever Jct. 41.6 kV. | OTP | M2 - Appendix A Approved | 1125000 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Wilmot 41.6 kV | Peever Jct. 41.6 kV |  | 42 |  |  |  | SD |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23858 | Wick Drive – Black Earth 69kV (Y-62), OPGW Addition & Partial Rebuild | Other | 27608 | 27608-Wick Drive-Black Earth | OPGW Addition | ATC | M3 - Under Construction | 7000000 | 2029-01-02 | Misc. | Communication equipment | Wick Drive | Black Earth | Y-62 | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23912 | East Krok SS Transformer Replacement | BRP | 27609 | 27609-East Krok- | Transformer Replacement | ATC | M2 - Appendix A Approved | 8700000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | East Krok |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 23913 | Northern Adams County Area Network Improvement Project | Other | 27610 | Northern Adams County Area Network Improvement Project | • Construct 9.2 miles of 69 kV single circuit transmission line (5 miles between Badger West and Y-302, and 4.2 miles between Y-302 and Colburn). • Expand Badger West substation with three 138 kV breakers, a 138/69 kV base transformer, a new ATC control building, and one 69 kV line breaker. • Modify X-43 at Badger West to cross over the new 69kV t-line. | ATC | M3 - Under Construction | 39900000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Colburn |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23917 | OTP Fordville - Fordville Jct. 41.6 kV | Other | 27614 | 27614-Fordville 41.6 kV-Fordville Jct. 4.6 kV | Rebuild of 41.6 kV line between Fordville 41.6 kV and Fordville Jct. 41.6 kV. | OTP | M2 - Appendix A Approved | 1450000 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Fordville 41.6 kV | Fordville Jct. 4.6 kV | 1 | 42 |  |  |  | ND |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 23860 | OTP Hillhead - Veblen 41.6 kV | Other | 27617 | 27617-Hillhead 41.6 kV-Veblen 41.6 kV | Rebuild of 41.6 kV line between Hillhead 41.6 kV and Veblen 41.6 kV. | OTP | M2 - Appendix A Approved | 1700000 | 2030-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hillhead 41.6 kV | Veblen 41.6 kV | 1 | 42 |  |  |  | SD |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23861 | Upgrades Columbus 345 kV Sub Breaker | BRP | 27618 | 27618-Columbus 345-CBs | Columbus 345 Sub Breaker Upgrades: Replace (3) 138kV CBs on Xfmr Banks 1,2, and 3 and (1) 138kV - 13831 ckt. line CB with higher fault interrupting capacity; 2024: added NON-BES / NON-TPL CBs 138TR and 69230-4 | DEI | M2 - Appendix A Approved | 3600000 | 2027-05-07 | Substation | Circuit Breaker (replacement at existing substation) | Columbus 345 | CBs |  | 138 |  |  |  | IN |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23862 | Upgrade Bedford 345 kV Sub - 138-138 Bus Tie | BRP | 27619 | 27619-Bedford 345 KV-bus upgrade | Bedford 345 KV Sub 138-138 bus tie path - Upgrade 138kV bus (increase to 2-1590AL), CTs (reconnect at 2000A:5A ratio), and (2) switches (replace with 3000A) | DEI | M2 - Appendix A Approved | 667000 | 2032-04-01 | Substation | Substation bus upgrade | Bedford 345 KV | bus upgrade |  | 138 |  |  |  | IN |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23863 | Upgrade Cayuga to Nucor 34501 Line Terminal 345 kV | BRP | 27620 | 27620-Cayuga Gen. Sta.-Nucor | Cayuga Gen Station and Nucor 34501 Line Terminal Bus Upgrades (transitions between the line conductors and the ring buses): Upgrade 2500AL and/or 2-954AL bus conductor to 2-1590AL at both line terminal locations. | DEI | M2 - Appendix A Approved | 320000 | 2028-12-04 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Cayuga Gen. Sta. | Nucor | 1 | 345 |  |  |  | IN |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23864 | New Bloomington Area 138kV Source | BRP | 27621 | 27621-West of Bloomington 345 (new)- | Build new 345/138kV substation located in the IPL Petersburg to Frances Crk 345kV line. | IPL | M2 - Appendix A Approved | 35400000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | West of Bloomington 345 (new) |  |  | 345 | 138 |  |  | IN |  | Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 23864 | New Bloomington Area 138kV Source | BRP | 27622 | 27622-West of Bloomington 345 (new)-Bloomington Rogers St. | Build new 138kV line from new West of Bloomington 345 Sub to Rogers St. | DEI | M2 - Appendix A Approved | 18000000 | 2029-06-01 | Line New | New Transmission line, new ROW - may include terminations | West of Bloomington 345 (new) | Bloomington Rogers St. | 1 | 138 |  | 9.14 |  | IN |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23844 | Replace Pole and Insulator Program - MTEP23 | Other | 27623 | 27623-Various- | Pole and Insulator replacements requested by Maintenance (Missouri and Illinois) | AmerenIL, AmerenMO | M3 - Under Construction | 20000000 | 2027-12-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Various |  |  | 345 | 138 |  |  | IL | MO | Not Shared
MTEP23 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 23893 | New Winding Ridge 138 kV Substation | Other | 27625 | 27625-WindingRidge-Substation | New 138 kV, two 40 MVA transformers, 8 breaker, breaker and a half substation to serve AES-IPL customer load and provide transmission service to TOs whom have requested as such | IPL | M2 - Appendix A Approved | 25662753 | 2026-05-15 | Substation | Substation (breakers only, no transformer) | WindingRidge |  |  | 138 | 13 |  |  | IN |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | BRP | 27627 | 27627-Seminary- | Rebuild the 138kV Seminary bus to a ring, the 69 kV to a breaker and a half, and install a cap bank. | WVPA | M2 - Appendix A Approved | 37000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Seminary |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | BRP | 27628 | 27628-Wittenberg- | Install new relaying and breakers for the new 138 kV line to Seminary. | WVPA | M2 - Appendix A Approved | 1000000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Wittenberg |  |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | BRP | 27629 | 27629-Seminary-Wittenberg | Build new ~21.3 miles of 138kV between Seminary and Wittenberg. | WVPA | M2 - Appendix A Approved | 42000000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Seminary | Wittenberg |  | 138 |  |  |  | MO |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | BRP | 27631 | 27631-Grand Tower- | Add line Terminal at Grand Tower for new Grand Tower to Wittenberg line | AmerenIL | M2 - Appendix A Approved | 700000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Grand Tower |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP23 | A | AMEREN ILLINOIS | Central | 23846 | New Seminary - Wittenberg - Grand Tower 138 kV line | BRP | 27633 | 27633-Grand Tower-Wittenberg | Construct a new greenfield line between Wittenberg and Grand Tower. The Grand Tower - Wittenberg line will include a new Mississippi river crossing. | AmerenIL, AmerenMO | M2 - Appendix A Approved | 37200000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Grand Tower | Wittenberg |  | 138 |  |  |  | IL | MO | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23921 | Pilot Knob to Deerwood Area Projects | Other | 27640 | 27640-Pilot Knob- | Rebuild the Pilot Knob Substation to a breaker and a half configuration due to age and condition of the current equipment. Upgrade the DA-PD line from Deerwood to Pilot Knob substation to increase the capacity. Upgrade to be built to 115kV standards but operated at 69kV. Retire the underground portion of the DA-PLX at Pilot Knob and replace with overhead Retire the DA-RE line from Pilot Knob road to Black Hawk Road Retire the DA-PKX from Pilot Knob to Cliff Road Retire SS-2820 and replace with a turning structure. Retire SS-2819 | GRE | M2 - Appendix A Approved | 18553424 | 2027-05-21 | Substation | Substation (breakers only, no transformer) | Pilot Knob |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | GREAT RIVER ENERGY | West | 23921 | Pilot Knob to Deerwood Area Projects | Other | 27641 | 27641-Deerwood-Pilot Knob | Rebuild the Pilot Knob Substation to a breaker and a half configuration due to age and condition of the current equipment. Upgrade the DA-PD line from Deerwood to Pilot Knob substation to increase the capacity. Upgrade to be built to 115kV standards but operated at 69kV. Retire the underground portion of the DA-PLX at Pilot Knob and replace with overhead Retire the DA-RE line from Pilot Knob road to Black Hawk Road Retire the DA-PKX from Pilot Knob to Cliff Road Retire SS-2820 and replace with a turning structure. Retire SS-2819 | GRE | M2 - Appendix A Approved | 11019400 | 2027-04-29 | Line Upgrade | Line rebuild on existing ROW | Deerwood | Pilot Knob | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | METC | East | 23847 | Bingham - Looking Glass 138 kV Rebuild | Other | 27642 | 27642-Bingham-Looking Glass | Rebuild approximately 19.3 miles of the Bingham – Looking Glass 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double- circuit structures with OPGW. Leave the East side of the double-circuit structures vacant. | METC | M2 - Appendix A Approved | 35300000 | 2030-12-31 | Line Upgrade | Line rebuild on existing ROW | Bingham | Looking Glass | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 23847 | Bingham - Looking Glass 138 kV Rebuild | Other | 27643 | 27643-Bingham- | Connect OPGW at Bingham 138 kV position WM6. | METC | M2 - Appendix A Approved | 95000 | 2030-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Bingham |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | DUKE ENERGY INDIANA, LLC | Central | 3382 | Vincennes Vigo St. 138kV Dist Sub | Other | 6255 | 6255-Vincennes Vigo St.-convert distribution sub | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV | DEI | M2 - Appendix A Approved | 10932000 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Vincennes Vigo St. | convert distribution sub | 1 | 138 | 12 | 2.3 |  | IN |  | Not Shared
MTEP23 | A | ITC | Central | 15872 | Brownstown-Monroe #2 345 kV Sag Remediation | Other | 23965 | 23965-Brownstown-Monroe | Raise the sag limit on Brownstown – Monroe #2 345 kV line to at least 1361 MVA. | ITCT | M2 - Appendix A Approved | 1329000 | 2028-06-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Brownstown | Monroe | 2 | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | AMEREN MISSOURI | Central | 22066 | Replace Mason 345/138 kV Transformer No. 1 | Other | 26704 | 26704-Mason- | Replace Mason 345/138 kV xfmr #1 with a 700 MVA unit | AmerenMO | M3 - Under Construction | 48200000 | 2027-06-01 | Transformer | Transformer New | Mason |  |  | 345 | 138 |  |  | MO |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 24298 | J1442 Interconnection Project on Livingston to Rich 138 kV line | GIP | 27874 | 27874-Rich-Livingston | Project to support interconnection of J1442 on the Livingston to Rich 138 kV line. | Entergy-TX | M2 - Appendix A Approved | 15590000 | 2028-05-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Rich | Livingston |  | 138 |  |  |  | TX |  | Not Shared
MTEP23 | A | CLECO POWER LLC | South | 24416 | Rosepine Substation | BRP | 27875 | 27875-Rosepine- | Tap the existing Leesville to Cooper 138 kV line 11.4 miles from Leesville with a new Rosepine Substation | CLECO | M2 - Appendix A Approved | 20585000 | 2028-10-01 | Substation | Substation (breakers only, no transformer) | Rosepine |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | CLECO POWER LLC | South | 24416 | Rosepine Substation | BRP | 27876 | 27876-Rosepine-Deridder | Build a new 3.4 mile 230 kV line from Rosepine to Deridder energized at 138 kV. | CLECO | M2 - Appendix A Approved | 12000000 | 2027-07-15 | Line Upgrade | Generic transmission line project (try not to use the generic) | Rosepine | Deridder | 1 | 138 |  | 3.4 |  | LA |  | Not Shared
MTEP23 | A | CLECO POWER LLC | South | 24416 | Rosepine Substation | BRP | 27877 | 27877-Deridder- | Add a new 138 kV Terminal at Deridder | CLECO | M2 - Appendix A Approved | 3000000 | 2027-07-15 | Substation | Substation (breakers only, no transformer) | Deridder |  |  | 138 |  |  |  | LA |  | Not Shared
MTEP23 | A | ITC | East | 24299 | J1196 Generator Interconnection TOIF | GIP | 27878 | 27878-Wedge- | Install position DI at Wedge to interconnect J1196 generator. | ITCT | M2 - Appendix A Approved | 0 | 2027-03-04 | Substation | Small miscellaneous substation equipment | Wedge |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | ITC | East | 24376 | Majestic-Milan - J1224 & J1329 GIA (Neblo) TOIF | GIP | 27879 | 27879-Neblo- | Install entrance structure and disconnect as TOIF to interconnect J1224 & J1329 | ITCT | M2 - Appendix A Approved | 0 | 2029-06-01 | Substation | Small miscellaneous substation equipment | Neblo |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24396 | J1210 Generator Interconnection TOIF | GIP | 27893 | 27893-Quarry- | Install position WM14 at Quarry to interconnect J1210 generator. | METC | M2 - Appendix A Approved | 0 | 2027-05-03 | Substation | Small miscellaneous substation equipment | Quarry |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24301 | Leoni - Parr Road - J1472 GIA(Vargo) TOIF | GIP | 27894 | 27894-Vargo- | Install position WM13 for the J1472 generator to connect. | METC | M2 - Appendix A Approved | 1 | 2027-12-01 | Substation | Small miscellaneous substation equipment | Vargo |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24433 | Vergennes - Marquette - J1255 GIA (Hawley) TOIF | GIP | 27895 | 27895-Hawley- | Install position WM12 at the new station for J1255 generator to connect. | METC | M2 - Appendix A Approved | 1 | 2028-09-28 | Substation | Small miscellaneous substation equipment | Hawley |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24453 | Hawley-Peddler - New Circuit #1 and #2 (J1255, J1292) - Common Use Network Upgrade | GIP | 27904 | 27904-Hawley-Peddler | Install about 12 miles of 954 ACSR to connect J1255-J1292 forming circuit #1 | METC | M2 - Appendix A Approved | 12099600 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Hawley | Peddler |  | 138 |  | 15 |  | MI |  | Shared
MTEP23 | A | METC | East | 24453 | Hawley-Peddler - New Circuit #1 and #2 (J1255, J1292) - Common Use Network Upgrade | GIP | 27905 | 27905-Hawley-Peddler | Install about 12 miles of 954 ACSR to connect J1255-J1292 forming circuit #2 | METC | M2 - Appendix A Approved | 12099600 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Hawley | Peddler |  | 138 |  | 15 |  | MI |  | Shared
MTEP23 | A | METC | East | 24453 | Hawley-Peddler - New Circuit #1 and #2 (J1255, J1292) - Common Use Network Upgrade | GIP | 27906 | 27906-Hawley- | Expand J1255 station by installing breakers 8W2 and 10B7. terminate the J1255-J1292 #1 line at position WM8. Terminate the J1255-J1292 #2 line at position BM10. | METC | M2 - Appendix A Approved | 1758504 | 2028-09-28 | Substation | Small miscellaneous substation equipment | Hawley |  |  | 138 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24453 | Hawley-Peddler - New Circuit #1 and #2 (J1255, J1292) - Common Use Network Upgrade | GIP | 27907 | 27907-Peddler- | Expand J1292 station by installing breakers 8B7 and 8W8. terminate the J1255-J1292 #1 line at position BM6. Terminate the J1255-J1292 #2 line at position BM8. | METC | M2 - Appendix A Approved | 1758504 | 2028-06-01 | Substation | Small miscellaneous substation equipment | Peddler |  |  | 138 |  |  |  | MI |  | Shared
MTEP23 | A | METC | East | 24434 | J1203 Generator Interconnection TOIF | GIP | 27908 | 27908-Thetford- | Install position RH29 to interconnect J1203 generator. | METC | M2 - Appendix A Approved | 0 | 2028-03-01 | Substation | Small miscellaneous substation equipment | Thetford |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24435 | J1226 Generator Interconnection TOIF | GIP | 27909 | 27909-Morocco- | Install position RH36 to interconnect J1226 generator. | METC | M2 - Appendix A Approved | 0 | 2028-04-03 | Substation | Small miscellaneous substation equipment | Morocco |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24456 | Marshall - Blackstone (Stable) - J1248 GIA (Bearcat) TOIF | GIP | 27910 | 27910-Bearcat- | Install position WM14 as TOIF for the J1248 generator to connect. | METC | M2 - Appendix A Approved | 1 | 2026-03-02 | Substation | Small miscellaneous substation equipment | Bearcat |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24436 | J1375 Generator Interconnection TOIF | GIP | 27911 | 27911-Lamos- | Install position WM8 to interconnect J1375 generator. | METC | M2 - Appendix A Approved | 0 | 2028-05-01 | Substation | Small miscellaneous substation equipment | Lamos |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24493 | Claremont - Cornell #2 - J1297 GIA (Hathon) TOIF | GIP | 27913 | 27913-Hathon- | Install position BM10 as TOIF for J1297 to connect. | METC | M2 - Appendix A Approved | 1 | 2028-12-29 | Substation | Small miscellaneous substation equipment | Hathon |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23957 | Amite South Reliability Project - Phase 2 | Other | 27914 | 27914-Willow Glen-Conway - Audubon | Construct new 230 kV lines from Willow Glen to Conway to Audubon | Entergy-LA | M2 - Appendix A Approved | 121000000 | 2028-06-30 | Line New | New Transmission line, new ROW - may include terminations | Willow Glen | Audubon |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23957 | Amite South Reliability Project - Phase 2 | Other | 27915 | 27915-Audubon | Construct Audubon 500 kV station, 4 breaker ring and two Autotransformer. Construct new control house. | Entergy-LA | M3 - Under Construction | 209000000 | 2026-12-30 | Substation | Substation (breakers only, no transformer) | Audubon |  |  | 500 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23957 | Amite South Reliability Project - Phase 2 | Other | 27916 | 27916-Audubon | Audubon 230 kV station to connect two Autotransformers and 5 230 kV lines | Entergy-LA | M3 - Under Construction | 1 | 2026-12-30 | Transformer | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Audubon |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23957 | Amite South Reliability Project - Phase 2 | Other | 27917 | 27917-Willow Glen- | Install 2 new breakers and 4 new switches, replace 1 breaker. Other station equipment required | Entergy-LA | M2 - Appendix A Approved | 1 | 2027-12-30 | Substation | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Willow Glen |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23959 | Amite South Reliability Project - Phase 3 | Other | 27918 | 27918-Adams Creek-Robert | Construct ~40 mile 230 kV line from Adams Creek to Robert. | Entergy-LA | M2 - Appendix A Approved | 260000000 | 2027-11-16 | Line New | New Transmission line, new ROW - may include terminations | Adams Creek | Robert |  | 230 |  | 40 |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23959 | Amite South Reliability Project - Phase 3 | Other | 27919 | 27919-Robert- | Install 1 new 230 kV breaker and associated equipment | Entergy-LA | M2 - Appendix A Approved | 1 | 2027-11-16 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Robert |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23959 | Amite South Reliability Project - Phase 3 | Other | 27920 | 27920-Adams Creek- | Install 3 new 230 kV breakers and associated equipment, Install new control house. | Entergy-LA | M2 - Appendix A Approved | 1 | 2027-11-16 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Adams Creek |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | METC | East | 24437 | Delhi-Thompkins #2 J1399 (Edgar) TOIF | GIP | 27922 | 27922-Edgar- | Install position BM14 to connect the J1399 generator | METC | M2 - Appendix A Approved | 0 | 2028-01-26 | Substation | Small miscellaneous substation equipment | Edgar |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | METC | East | 24459 | J1379 Generator Interconnection TOIF | GIP | 27929 | 27929-Hornet- | Install a 138 kV entrance structure and 177 disconnect switch at the J1379 PCO at J1379 Station position WM14. | METC | M2 - Appendix A Approved | 0 | 2027-04-06 | Substation | Small miscellaneous substation equipment | Hornet |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23952 | SETEX Area Reliability Project | BRP | 27941 | 27941-Babel- | Construct 500 kV Babel station on the Hartburg to Layfield 500 kV line. Install 500 kV reactors at station | Entergy-TX | M2 - Appendix A Approved | 1 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Babel |  |  | 500 |  |  |  | TX |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23952 | SETEX Area Reliability Project | BRP | 27942 | 27942-Running Bear-Lewis Creek | Construct 500-230kV Running Bear Station. Install 500-230 kV Autotransformer. Construct an ~ .6 mile 230 kV line to the Lewis Creek 230 kV Station. Install a 2nd Lewis Creek 230-138 kV Autotransformer. | Entergy-TX | M2 - Appendix A Approved | 1 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Running Bear |  |  | 500 | 138 |  |  | TX |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 23952 | SETEX Area Reliability Project | BRP | 27943 | 27943-Babel-Running Bear | Construct ~150 mile 500 kV line from Babel to Running Bear 500 kV station | Entergy-TX | M2 - Appendix A Approved | 1111000000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Babel | Running Bear |  | 500 |  |  |  | TX |  | Not Shared
MTEP23 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 25252 | Fairmont, MN Area 69kV Transmission Expansion | Other | 28345 | 28345-Fairmont Energy Station-West Industrial Park Substation | Approximately 2 miles of 69kV transmission line being built on preexisting ROW and on new ROW as applicable. | SMMPA | M2 - Appendix A Approved | 3520000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Fairmont Energy Station | West Industrial Park Substation | 1 | 69 | 13 | 2 |  | MN |  | Not Shared
MTEP23 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 25252 | Fairmont, MN Area 69kV Transmission Expansion | Other | 28346 | 28346-West Industrial Park Substation- | New 69/12.5kV distribution substation being built west of Fairmont, MN to meet new distribution needs. | SMMPA | M2 - Appendix A Approved | 800000 | 2026-09-01 | Substation | Distribution substation - may include trans high side | West Industrial Park Substation |  |  | 69 | 13 |  |  | MN |  | Not Shared
MTEP23 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 25252 | Fairmont, MN Area 69kV Transmission Expansion | Other | 28347 | 28347-West Industrial Park Substation-West Tap | New 0.5mi 69kV transmission line being built on new ROWs. | SMMPA | M2 - Appendix A Approved | 880000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | West Industrial Park Substation | West Tap |  | 69 |  | 0.5 |  | MN |  | Not Shared
MTEP23 | A | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | West | 25252 | Fairmont, MN Area 69kV Transmission Expansion | Other | 28348 | 28348-Fairmont Energy Station- | New 69/12.5kV breaker station. | SMMPA | M2 - Appendix A Approved | 3720000 | 2023-03-01 | Substation | Distribution substation - may include trans high side | Fairmont Energy Station |  |  | 69 | 13 |  |  | MN |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 25305 | OTP Load Addition Milbank, SD | Other | 28361 | 28361-Big Stone (620214)-New Milbank 115/12.5 kV substation | Construct a new approximate 12-mile 115 kV line from Big Stone 115 kV to a new Milbank 115/12.5 kV substation. The new 115 kV line will mainly be built on the existing 41.6 kV route with the elimination of the 41.6 kV line. | OTP | M4 - Project in Service | 6521822 | 2024-12-13 | Line New | New Transmission line, new ROW - may include terminations | Big Stone (620214) | New Milbank 115/12.5 kV substation | 1 | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 25305 | OTP Load Addition Milbank, SD | Other | 28362 | 28362-New Milbank 115/12.5 kV substation-New Switching Station on Big Stone - Marietta 115 kV line | Construct a new approximate 18.5-mile 115 kV line from Milbank 115/12.5 kV substation to a new breaker station on the Big Stone - Milbank 115 kV line. The new 115 kV line will utilize a portion of the existing 41.6 kV route where the 41.6 kV line will be removed. | OTP | M2 - Appendix A Approved | 14300000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | New Milbank 115/12.5 kV substation | New Switching Station on Big Stone - Marietta 115 kV line | 1 | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 25305 | OTP Load Addition Milbank, SD | Other | 28363 | 28363-Big Stone (620214)- | Expand the 115 kV bus to accommodate a new 115 kV line position. | OTP | M4 - Project in Service | 2102339 | 2024-11-06 | Substation | Substation (breakers only, no transformer) | Big Stone (620214) |  |  | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 25305 | OTP Load Addition Milbank, SD | Other | 28364 | 28364-Milbank 115/12.5 kV (new)- | Construct a new Milbank 115/12.5 kV substation. | OTP | M4 - Project in Service | 4307184 | 2024-12-20 | Substation | Substation (breakers only, no transformer) | Milbank 115/12.5 kV (new) |  |  | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 25305 | OTP Load Addition Milbank, SD | Other | 28365 | 28365-New 115 kV Breaker Station- | New 115 kV breaker station along the Big Stone - Marietta 115 kV line. | OTP | M3 - Under Construction | 5800000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | New 115 kV Breaker Station |  |  | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | OTTER TAIL POWER COMPANY | West | 25305 | OTP Load Addition Milbank, SD | Other | 28366 | 28366-New Milbank 115/12.5 kV substation-New Breaker Station on Big Stone - Marietta 115 kV line | A new tap to convert the Milbank South substation from the 41.6 kV system to the 115 kV system. This tap will occur on the new 115 kV line between the new Milbank 115/12.5 kV substaiton and the new breaker station on the Big Stone to Marietta 115 kV line | OTP | M2 - Appendix A Approved | 200000 | 2026-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | New Milbank 115/12.5 kV substation | New Breaker Station on Big Stone - Marietta 115 kV line | 1 | 115 |  |  |  | SD |  | Not Shared
MTEP23 | A | ENTERGY ARKANSAS, LLC | South | 12055 | Gum Springs 115kV: Build Breaker Station | Other | 22136 | 22136-Gum Springs- | Create a new substation by tapping the Arkadelphia North – Richwood 115kV and the Arkadelphia West – Dalark 115kV line sections. | Entergy-AR | M2 - Appendix A Approved | 14950800 | 2031-12-01 | Substation | Substation (breakers only, no transformer) | Gum Springs |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 12084 | Dixie Baker to Zachary 69 kV: Upgrade Line | Other | 22170 | 22170-Dixie Baker-Zachary | The ~3.3 mile long line should be upgraded to a minimum rating of 143 MVA. If any station equipment is rated lower than 143 MVA (1200 Amps), it should be upgraded as well. | Entergy-LA | M2 - Appendix A Approved | 18900000 | 2027-06-01 | Line Upgrade | Line reconductor | Dixie Baker | Zachary |  | 69 |  |  | 3.3 | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 12098 | Delmont to Hazel 230 kV: Upgrade Line | BRP | 22204 | 22204-Delmont-Hazel | Upgrade the Delmont to Hazel kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. | Entergy-LA | M2 - Appendix A Approved | 9500000 | 2026-06-01 | Line Upgrade | Line reconductor | Delmont | Hazel |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | ENTERGY SERVICES, LLC. | South | 12098 | Delmont to Hazel 230 kV: Upgrade Line | BRP | 22206 | 22206-Delmont-Hazel | Upgrade the Delmont to Hazel kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. | Entergy-LA | M2 - Appendix A Approved | 1 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Delmont | Hazel |  | 230 |  |  |  | LA |  | Not Shared
MTEP23 | A | PRAIRIE POWER, INC. | Central | 19948 | New Mason City-Middletown 69 kV Line | Other | 25631 | New Mason City-Middletown 69 kV Line | New Mason City-Middletown 69 kV Line with 556 ACSR | PPI | M2 - Appendix A Approved | 9197500 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Mason City | Middletown |  | 69 |  | 13 |  | IL |  | Not Shared
MTEP23 | A | AMERICAN TRANSMISSION COMPANY | West | 19963 | Kirkwood SS, Power Transformer and Breaker Asset Renewal | Other | 25648 | 25648-Kirkwood SS- | Asset Renewal | ATC | M2 - Appendix A Approved | 14100000 | 2029-12-13 | Substation | Substation (breakers only, no transformer) | Kirkwood SS |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23447 | W3441 Extension to W3510 | Other | 27208 | 27208-Birchwood-W3510 | Extend the line from Birchwood substation to the east to connect to Xcel line W3510 in the vicinity of the town of Wieger, a distance of about 13 miles. Install motor operated switches at Birchwood to sectionalize the line. Install manual switches at the connection to W3510. The line would initially be operated as a normally open second source to Birchwood. | XEL | M2 - Appendix A Approved | 9000000 | 2029-12-10 | Line New | New Transmission line, new ROW - may include terminations | Birchwood | W3510 | 1 | 69 |  | 13 |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23450 | STY Install TR3 & 115kV Bus Tie | Other | 27211 | 27211-Stockyards- | Install new 115kV bus tie and associated disconnect switches and bus work and re-terminate 0818/5529 at Rogers Lake Sub. | XEL | M2 - Appendix A Approved | 5300000 | 2026-03-15 | Substation | Substation bus upgrade | Stockyards |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23466 | W3351 88kv Rebuild STR 336 to Saxton Pump | Other | 27212 | 27212-Saxon Pump-Norrie | Rebuild W3551 with twisted pair 4/0 wire (477 eq.) and direct embedded steel structures from structure 336 to Saxton Pump. Design the 88kv circuit to be 115kv capable. Include provision for a 34.5 kv under build circuit to connect to W3628 north of Saxton Pump. | XEL | M2 - Appendix A Approved | 13000000 | 2026-03-16 | Line Upgrade | Line reconductor | Saxon Pump | Norrie | 1 | 88 |  |  | 9 | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23490 | Crystal Cave TR01 ELR | Other | 27227 | 27227-Crystal Cave- | Replace Crystal Cave 161/115 kV TR01. | XEL | M2 - Appendix A Approved | 11239747 | 2026-12-31 | Transformer | Transformer New | Crystal Cave |  |  | 161 | 115 |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23493 | Monticello TR06 & TR10 ELR | Other | 27230 | 27230-Monticello- | Replace Monticello 345/230 kV TR06. | XEL | M2 - Appendix A Approved | 3500000 | 2027-06-01 | Transformer | Transformer New | Monticello |  |  | 345 | 230 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23493 | Monticello TR06 & TR10 ELR | Other | 27231 | 27231-Monticello- | Replace Monticello 345/115 kV TR10. | XEL | M2 - Appendix A Approved | 5500000 | 2027-06-01 | Transformer | Transformer New | Monticello |  |  | 345 | 115 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23495 | Pipestone TR05 & TR06 ELR | Other | 27233 | 27233-Pipestone- | Replace Pipestone TR05 and TR06 115/69 kV transformers. | XEL | M2 - Appendix A Approved | 3000000 | 2026-01-30 | Transformer | Transformer New | Pipestone |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23496 | Inver Grove TR02 ELR | Other | 27234 | 27234-Inver Grove- | Replace Inver Grove 115/69 kV TR02. | XEL | M2 - Appendix A Approved | 2500000 | 2027-12-15 | Transformer | Transformer New | Inver Grove |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23455 | Parkers Lake TR09 ELR | Other | 27235 | 27235-Parkers Lake- | Replace Parkers Lake 345/115 kV TR09 (3 phases). | XEL | M2 - Appendix A Approved | 6000000 | 2026-05-29 | Transformer | Transformer New | Parkers Lake |  |  | 345 | 115 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23497 | Lake Pulaski TR05 ELR | Other | 27236 | 27236-Lake Pulaski- | Replace Lake Pulaski 115/69 kV TR05. | XEL | M2 - Appendix A Approved | 2500000 | 2026-12-31 | Transformer | Transformer New | Lake Pulaski |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23456 | Lake Yankton TR02 ELR | Other | 27237 | 27237-Lake Yankton- | Replace Lake Yankton 115/69 kV TR02. | XEL | M2 - Appendix A Approved | 1500000 | 2026-12-31 | Transformer | Transformer New | Lake Yankton |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23498 | Minnesota Valley TR11 ELR | Other | 27238 | 27238-Minnesota Valley- | Replace Minnesota Valley 115/69 kV TR11. | XEL | M2 - Appendix A Approved | 2500000 | 2027-12-31 | Transformer | Transformer New | Minnesota Valley |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23506 | Gingles TR05 ELR | Other | 27239 | 27239-Gingles- | Replace Gingles 115/69 kV TR05. | XEL | M2 - Appendix A Approved | 5000000 | 2026-12-15 | Transformer | Transformer New | Gingles |  |  | 115 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23457 | Hydro Lane TR05 ELR | Other | 27240 | 27240-Hydro Lane- | Replace Hydro Lane 115/69 kV TR05. | XEL | M2 - Appendix A Approved | 4604843 | 2027-12-12 | Transformer | Transformer New | Hydro Lane |  |  | 115 | 69 |  |  | WI |  | Not Shared
MTEP23 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23471 | Upgrade Roxana to Mittal 2 138 kV Line | BRP | 27244 | 27244-Roxana-MITTAL2 | Reconductor 2.2 miles of line. | NIPS | M2 - Appendix A Approved | 5648342 | 2026-05-31 | Line Upgrade | Line reconductor | Roxana | MITTAL2 | 1 | 138 |  |  |  | IN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23501 | Line 0840 Elliot Park Pumping Plants | Other | 27246 | 27246-Elliot Park-Hiawatha West | Upgrades to pumping station for HPFF. | XEL | M3 - Under Construction | 5000000 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Elliot Park | Hiawatha West | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23458 | Line 0893 NSS-BCK Rebuild | Other | 27247 | 27247-North Star Steel-Battle Creek | Rebuild 3.4 miles of 115 kV line between North Star Steel and Battle Creek substations. Portions of this line are double circuited with 0892, this project will separate the two circuits. | XEL | M2 - Appendix A Approved | 3437000 | 2026-03-30 | Line Upgrade | Line reconductor | North Star Steel | Battle Creek | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23473 | Line 0892 RRK-BCK Rebuild | Other | 27248 | 27248-Red Rock-Battle Creek | Rebuild 3.4 miles of 115 kV line between Red Rock and Battle Creek substations. Portions of this line are double circuited with 0893, this project will separate the two circuits. | XEL | M2 - Appendix A Approved | 6900000 | 2026-03-30 | Line Upgrade | Line reconductor | Red Rock | Battle Creek | 1 | 115 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23474 | Line 0736 Arden Hills - Lawrence Creek Rebuild | Other | 27251 | 27251-Arden Hills-Lawrence Creek | Rebuild 33 miles of line 0736 69 kV from Arden Hills - Lawrence Creek and add OPGW. | XEL | M2 - Appendix A Approved | 13987459 | 2030-06-15 | Line Upgrade | Line reconductor | Arden Hills | Lawrence Creek | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23475 | Line 0721 STR 71 to 476 Rebuild | Other | 27252 | 27252-Franklin-Winthrop | Rebuild 22 miles line 0721 69 kV from Structure 71 - Structure 476. | XEL | M2 - Appendix A Approved | 11000000 | 2028-11-15 | Line Upgrade | Line reconductor | Franklin | Winthrop |  | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23503 | Line 0719 Winthrop to STR 45 Rebuild | Other | 27253 | 27253-Winthrop-Lafayette | Rebuild 1.5 miles of line 0719 69 kV from Winthrop - Structure 45. | XEL | M2 - Appendix A Approved | 3267728 | 2027-12-31 | Line Upgrade | Line reconductor | Winthrop | Lafayette | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23461 | Line 0708 STR 78 to 476 Rebuild | Other | 27259 | 27259-Eagle Lake-Waterville | Rebuild 16 miles of line 0708 69 kV from Eagle Lake - Waterville and add OPGW. | XEL | M2 - Appendix A Approved | 9000000 | 2028-02-22 | Line Upgrade | Line reconductor | Eagle Lake | Waterville | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23477 | Line 0772 Prairie to MNPC Connection Rebuild | Other | 27261 | 27261-Prairie-Emerado | Rebuild 12 miles of line 0772 69 kV from Prairie - Emerado. | XEL | M2 - Appendix A Approved | 4523505 | 2026-11-30 | Line Upgrade | Line reconductor | Prairie | Emerado | 1 | 69 |  |  |  | ND |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23462 | Line 0718 Arlington - Winthrop Rebuild | Other | 27262 | 27262-Arlington-Winthrop | Rebuild 15 miles line 0718 69 kV from Arlington - Winthrop. | XEL | M2 - Appendix A Approved | 9252481 | 2026-04-15 | Line Upgrade | Line reconductor | Arlington | Winthrop | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP23 | A | NORTHERN STATES POWER COMPANY | West | 23508 | Line 5503 Cherry Creek - Great Plains - West Sioux Falls Rebuild | Other | 27263 | 27263-Cherry Creek-West Sioux Falls | Rebuild 2 miles 115 kV Cherry Creek - Great Plains. Rebuild 1 mile 115 kV Great Plains - West Sioux Falls (single circuit portion) as bifurcated double circuit. Rebuild 0.7 mile 115 kV Great Plains - West Sioux Falls (double circuit portion). | XEL | M2 - Appendix A Approved | 5000000 | 2029-12-01 | Line Upgrade | Line reconductor | Cherry Creek | West Sioux Falls | 1 | 115 |  |  |  | SD |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | West | 15649 | Texas 138 kV: New Distribution Station | Other | 23655 | 23655-Texas- | Construct a new 138 kV distribution station | Entergy-TX | M2 - Appendix A Approved | 19865079 | 2027-01-25 | Substation | Distribution substation - may include trans high side | Texas |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | West | 15649 | Texas 138 kV: New Distribution Station | Other | 23656 | 23656-Texas- | Construct a 138 kV station on the Lewis Creek to Goree kV line. | Entergy-TX | M2 - Appendix A Approved | 1 | 2027-01-25 | Substation | Distribution substation - may include trans high side | Texas |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 15649 | Texas 138 kV: New Distribution Station | Other | 23657 | 23657-Cut in-Texas | 230 kV cut in to the Texas Station | Entergy-TX | M2 - Appendix A Approved | 1 | 2027-01-25 | Line New | New Transmission line, new ROW - may include terminations | Cut in | Texas |  | 138 |  |  |  | TX |  | Not Shared
MTEP22 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 15652 | Rebuild Atlanta to Gaylord 138kV | Other | 23663 | 23663-Atlanta-Gaylord OCB | Rebuild of line section to 138kV design. | WPSC | M2 - Appendix A Approved | 16500000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Atlanta | Gaylord OCB | 1 | 138 |  | 22 |  | MI |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Other | 24925 | 24925-Arrowhead-Center (Block 1) | HVDC transmission line targeted structure replacements, Year 1 | MP | M2 - Appendix A Approved | 3000000 | 2023-12-31 | Misc. | High Voltage DC line or terminal | Arrowhead | Center (Block 1) |  | 250 |  |  |  | ND |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Other | 24926 | 24926-Arrowhead-Center (Block 2) | HVDC transmission line targeted structure replacements, Year 2 | MP | M2 - Appendix A Approved | 3000000 | 2024-12-31 | Misc. | High Voltage DC line or terminal | Arrowhead | Center (Block 2) |  | 250 |  |  |  | ND |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 25389 | 25389-Hilltop- | Hilltop 115 kV line entrance addition, 115 kV circuit breaker and panel replacements | MP | M2 - Appendix A Approved | 1300000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Hilltop |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 25390 | 25390-Hilltop-Haines Road | New 115 kV transmission line alongside existing transmission corridor, portion double circuit with existing line | MP | M2 - Appendix A Approved | 19000000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Hilltop | Haines Road |  | 115 |  | 6.8 | 3.3 | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 25391 | 25391-Haines Road- | Haines Road breaker addition and panel replacements | MP | M2 - Appendix A Approved | 400000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Haines Road |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 25392 | 25392-Arrowhead-Swan Lake | Uncross existing Arrowhead - Haines Road 115 kV & Arrowhead - Colbyville 115 kV. Merge reconfigured Arrowhead - Haines Road 115 kV & Haines Road - Swan Lake 115 kV Lines to create Arrowhead - Swan Lake 115 kV Line. Reconductor existing 115 kV line between Haines Road and Swan Lake. Rebuild significant portion of existing 115 kV line due to corridor constraints. | MP | M2 - Appendix A Approved | 10100000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Arrowhead | Swan Lake |  | 115 |  |  | 7.5 | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 25393 | 25393-Haines Road-Ridgeview | New 115 kV transmission line alongside existing transmission corridor | MP | M2 - Appendix A Approved | 4300000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Haines Road | Ridgeview |  | 115 |  | 4.2 |  | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 25395 | 25395-Ridgeview- | Expand Ridgeview to a 5 position ring bus, replace a 115/14 kV transformer | MP | M2 - Appendix A Approved | 9900000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Ridgeview |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21628 | Rockdale and Christiana SS - Control House and Relay Asset Renewal | Other | 26306 | 26306-Rockdale SS- | Control House & Relay Asset Renewal | ATC | M3 - Under Construction | 3400000 | 2026-06-05 | Substation | Substation (breakers only, no transformer) | Rockdale SS |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21628 | Rockdale and Christiana SS - Control House and Relay Asset Renewal | Other | 26307 | 26307-Christina SS- | Control House & Relay Asset Renewal | ATC | M3 - Under Construction | 3400000 | 2026-06-05 | Substation | Substation (breakers only, no transformer) | Christina SS |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21629 | Oak Creek, Racine SS and Remote Ends, Control Buildings and Relaying Asset Renewal | Other | 26308 | 26308-Oak Creek SS- | Control Building & Relay Asset Renewal | ATC | M3 - Under Construction | 13963283 | 2026-07-31 | Substation | Substation (breakers only, no transformer) | Oak Creek SS |  |  | 230 | 138 |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21629 | Oak Creek, Racine SS and Remote Ends, Control Buildings and Relaying Asset Renewal | Other | 26309 | 26309-Racine SS- | Control Building & Relay Asset Renewal | ATC | M3 - Under Construction | 17388751 | 2026-07-31 | Substation | Substation (breakers only, no transformer) | Racine SS |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP22 | A | ITC | East | 21726 | Warren 120kV Pos JJ Station Equipment Upgrade | BRP | 26336 | 26336-Warren- | Replace station equipment at Warren to meet or exceed 528 MVA (2540 Amps) | ITCT | M2 - Appendix A Approved | 160000 | 2027-05-14 | Substation | Small miscellaneous substation equipment | Warren |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP22 | A | ITC | East | 21745 | Cato - Waterman 120 kV Rebuild | BRP | 26337 | 26337-Cato-Waterman | Re-conductor approximately 4.43 miles utilizing 1600MM2 CU XLPE underground cable. | ITCT | M2 - Appendix A Approved | 106000000 | 2034-12-29 | Line Upgrade | Line rebuild on existing ROW | Cato | Waterman | 1 | 120 |  |  | 4.43 | MI |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21746 | New Bluff Hall-E. Hannibal 69 kV Line | Other | 26338 | New Bluff Hall-E. Hannibal 69 kV Line | New Bluff Hall-E. Hannibal 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 4184000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Bluff Hall | E. Hannibal |  | 69 |  |  |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21749 | Upgrade Bluff Hall 69 kV Breaker Station | Other | 26342 | Upgrade Bluff Hall 69 kV Breaker Station | Upgrade Bluff Hall 69 kV Breaker Station in AEC | PPI | M2 - Appendix A Approved | 2935000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Bluff Hall |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21750 | New Rock Creek 69 kV Substation | Other | 26343 | New Rock Creek 69 kV Breaker Station | New Rock Creek 69 kV Breaker Station near Ursa substation | PPI | M2 - Appendix A Approved | 2935000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Rock Creek |  |  | 69 | 69 |  |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21751 | New Paragon 138/69 kV Substation | Other | 26344 | New Paragon 138/69 kV substation | New Paragon 138/69 kV substation in SEC. | PPI | M2 - Appendix A Approved | 7675000 | 2028-03-01 | Substation | Substation (breakers only, no transformer) | Paragon |  | 1 | 138 | 69 |  |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21752 | New Paragon-Pana 69 kV line | Other | 26345 | New Paragon-Pana 69 kV line | New Paragon-Pana 69 kV Line with 336 ACSR. Includes a portion of rebuild from the current Pana Tap to the future Pana Tap-Lakewood. | PPI | M2 - Appendix A Approved | 4575500 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Paragon | Pana | 1 | 69 |  | 1.4 | 2.7 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21753 | New Pana Tap-Lakewood 69 kV Line | Other | 26346 | New Pana Tap-Lakewood 69 kV Line | New Pana Tap-Lakewood 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 7680000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Pana Tap | Lakewood |  | 69 |  | 12 |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21754 | New ISHI-Herrick 69 kV Line | Other | 26347 | New ISHI-Herrick 69 kV Line | New ISHI-Herrick 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 6973000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | ISHI | New Herrick Tap | 1 | 69 |  | 9.7 |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21755 | Rebuild Hadley Breaker-Barry 69 kV Line | Other | 26348 | Rebuild Hadley-Barry 69 kV Line | Rebuild Hadley Breaker-Old E. Hannibal Tap 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 350000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Hadley Breaker | Barry |  | 69 |  |  | 0.54 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21756 | Rebuild Hadley Breaker-Hadley 69 kV line | Other | 26349 | Rebuild Hadley Breaker-Hadley Distribution 69 kV line | Rebuild Hadley Breaker-Hadley Distribution 336 ACSR 69 kV line in IEC. | PPI | M2 - Appendix A Approved | 880000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Hadley Breaker | Hadley Distribution | 1 | 69 |  |  | 1.61 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21757 | Rebuild Barry-Liberty 69 kV line | Other | 26350 | Rebuild E. Hannibal Tap-Liberty 69 kV Line | Rebuild E. Hannibal Tap-Liberty 69 kV line | PPI | M2 - Appendix A Approved | 3375000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | E. Hannibal Tap | Liberty | 1 | 69 | 69 |  | 6.35 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21758 | Rebuild Kampsville-Kampsville River Crossing 69 kV line | Other | 26351 | Rebuild Kampsville-Kampsville River Crossing 69 kV line | Rebuild Kampsville-Kampsville River Crossing 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 650000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Pearl | Carrollton | 1 | 69 | 69 |  | 0.7 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21760 | New Rushville 69 kV Breaker Station | Other | 26353 | New Rushville 69 kV Breaker Station | New Rushville 69 kV Breaker Station in AEC. | PPI | M3 - Under Construction | 2950000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Rushville |  |  | 69 | 69 |  |  | IL |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 21766 | 126 Line Asset Renewal | Other | 26356 | 26356-Little Fork-International Falls | Asset renewal upgrades to 126 Line | MP | M3 - Under Construction | 750000 | 2025-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Little Fork | International Falls |  | 115 |  |  |  | MN |  | Not Shared
MTEP22 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21785 | Grawn Station Protection System Update | Other | 26361 | 26361-Grawn- | Protection system upgrade | WPSC | M2 - Appendix A Approved | 2000000 | 2026-08-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Grawn |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP22 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21787 | Westwood 138kV Interconnection | Other | 26363 | 26363-Westwood- | Reconfigure station and install transformer | WPSC | M2 - Appendix A Approved | 8000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Westwood |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21788 | Rebuild Andrew-Barclay 69 kV line | Other | 26364 | Rebuild Barclay-Andrew 69 kV line | Rebuild Barclay-Andrew 69 kV line with 556 ACSR | PPI | M2 - Appendix A Approved | 3755000 | 2026-06-30 | Line Upgrade | Line rebuild on existing ROW | Barclay | Andrew | 1 | 69 | 69 |  | 7.5 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21789 | Rebuild Lanesville-Barclay 69 kV Line | Other | 26365 | Rebuild Lanesville-Barclay 69 kV line | Rebuild Lanesville-Barclay 69 kV line with 556 ACSR | PPI | M2 - Appendix A Approved | 6045000 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Lanesville | Barclay | 1 | 69 | 69 |  | 11.5 | IL |  | Not Shared
MTEP22 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21787 | Westwood 138kV Interconnection | Other | 26366 | 26366-Westwood-Plum | Rebuild existing 69kV facility to 138kV WPSC standard and add circuit on existing METC double circuit structures to Plum station. | WPSC | M2 - Appendix A Approved | 12000000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Westwood | Plum | 1 | 138 |  | 3 | 9 | MI |  | Not Shared
MTEP22 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21787 | Westwood 138kV Interconnection | Other | 26368 | 26368-Alba- | Alba Station demolition. | WPSC | M2 - Appendix A Approved | 500000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Alba |  |  | 138 | 69 |  |  | MI |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21792 | Rebuild Fancy Creek-Andrew 69 kV line | Other | 26369 | Rebuild Fancy Creek-Andrew 69 kV line | Rebuild Fancy Creek-Andrew 69 kV line with 556 ACSR | PPI | M2 - Appendix A Approved | 2450000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Fancy Creek | Andrew |  | 69 |  |  | 4.5 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21793 | New Forest City-Bishop 69 kV line | Other | 26370 | New Forest City-Bishop 69 kV line | New Forest City-Bishop 556 ACSR 69 kV line | PPI | M2 - Appendix A Approved | 790600 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Forest City | Bishop | 1 | 69 |  | 2 |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21794 | New Forest City 138/69 kV Substation | BRP | 26371 | New Forest City 138/69 kV Substation | New Forest City 138/69 kV Substation in MEC. | PPI | M2 - Appendix A Approved | 7225000 | 2028-03-01 | Substation | Substation (breakers only, no transformer) | Forest City |  |  | 138 | 69 |  |  | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21795 | New Middletown 69 kV Breaker Station | Other | 26372 | New Middletown 69 kV Breaker Station | New Middletown 69 kV Breaker Station in MEC. | PPI | M2 - Appendix A Approved | 3200000 | 2028-12-31 | Substation | Switching station (breakers only, no transformer) | Middletown |  |  | 69 | 69 |  |  | IL |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 21811 | Richard 500-138 kV AT1 Relay Improvement SPOF | BRP | 26379 | 26379-Richard- | Ensure the Richard 500/138 kV auto #1 has redundant high-speed protection with independent CT and PT windings. | Entergy-LA | M2 - Appendix A Approved | 10270000 | 2028-11-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Richard |  |  | 500 | 138 |  |  | LA |  | Not Shared
MTEP22 | A | AMEREN ILLINOIS | Central | 21970 | Reconductor Kinmundy-Tanner 138 kV | Other | 26598 | 26598-Kinmundy-Tanner | Reconductor 27.4 miles Kinmundy-Tanner 138 kV line | AmerenIL | M2 - Appendix A Approved | 19800000 | 2029-06-01 | Line Upgrade | Line reconductor | Kinmundy | Tanner |  | 138 |  |  |  | IL |  | Not Shared
MTEP22 | A | AMEREN MISSOURI | Central | 21971 | Upgrade Callaway 345 kV Substation | BRP | 26599 | 26599-Callaway- | Add circuit breakers to high side of safeguard transformers A and B | AmerenMO | M2 - Appendix A Approved | 5700000 | 2028-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Callaway |  |  | 345 |  |  |  | MO |  | Not Shared
MTEP22 | A | Central Minnesota Municipal Power Agency | West | 21974 | Blue Earth West Sub 20-37.3 MVA Transformer Replacement | Other | 26602 | Blue Earth West Sub 20-37.3 MVA Transformer Replacement | Blue Earth West Sub 20-37.3 MVA, 69/12.47kV transformer replacement. | CMMPA | M2 - Appendix A Approved | 4000000 | 2027-12-31 | Transformer | Transformer New | West |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21976 | Jasper to Laurel 161kV Line Rebuild | Other | 26606 | 26606-Jasper-Laurel | ITC will rebuild approximately 10 miles of the Jasper to Laurel 161kV line. The 161kV line conductor will be capable of 1600A or greater. | ITCM | M2 - Appendix A Approved | 18420000 | 2028-12-30 | Line Upgrade | Line rebuild on existing ROW | Jasper | Laurel |  | 161 | 161 |  | 10 | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21976 | Jasper to Laurel 161kV Line Rebuild | Other | 26607 | 26607-Jasper County-Substation | Substation work to accommodate OPGW between Jasper County and Laurel | ITCM | M2 - Appendix A Approved | 180860 | 2028-12-30 | Substation | Small miscellaneous substation equipment | Jasper County | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21976 | Jasper to Laurel 161kV Line Rebuild | Other | 26608 | 26608-Laurel-Substation | Laurel Substation work to accommodate the addition of OPGW | ITCM | M2 - Appendix A Approved | 180860 | 2028-12-30 | Substation | Small miscellaneous substation equipment | Laurel | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 17868 | Duluth Loop 115 kV Project | BRP | 26611 | 26611-Swan Lake Road-Ridgeview | Rebuild and reconductor existing Swan Lake Road - Ridgeview 115 kV | MP | M2 - Appendix A Approved | 1900000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Swan Lake Road | Ridgeview |  | 115 |  |  | 2.9 | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Other | 26615 | 26615-Edval-Substation | ITC Midwest will construct a new three position 161kV Ring (convertable to Bkr and 1/2) with a new 161/69kV 150 MVA to a single 69kV line terminal initially to Bunker Hill and looping to Dubuque 8th Street. | ITCM | M2 - Appendix A Approved | 10741866 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Edval | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Other | 26616 | 26616-Salem-Julian | New 161kV line taps for the new 161/69kV substation. | ITCM | M2 - Appendix A Approved | 1035600 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Salem | Julian | 1 | 161 | 161 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Other | 26617 | 26617-Edval-Bunker Hill | New 69kv line from the new Edval Substation to Bunker Hill (~2.6 miles) | ITCM | M2 - Appendix A Approved | 4279200 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Edval | Bunker Hill | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Other | 26618 | 26618-Bunker Hill-Substation | Alliant will expand the Bunker Hill sub if necessary to allow for ITC to install 2 69kV line breakers and a 69kV bus tie breaker to allow for the 2nd Alliant 69/distribution transformer. | ITCM | M2 - Appendix A Approved | 3051600 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Bunker Hill | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Other | 26619 | 26619-Dubuque 8th Street-Substation | Upgrade 69kV terminal limits to above line conductor rating of T2-477 ACSR. | ITCM | M2 - Appendix A Approved | 198000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Dubuque 8th Street | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 16766 | Small Capital Project and Asset Renewal Program 2023 | Other | 26620 | 26620-Various Sites- | Small capital project and asset renewal. | ATC | M3 - Under Construction | 34925540 | 2027-12-01 | Substation | Small miscellaneous substation equipment | Various Sites |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 16769 | Physical Security Program 2023 | Other | 26623 | 26623-Various Sites- | Physical Security Program | ATC | M3 - Under Construction | 1859619 | 2026-08-24 | Substation | Small miscellaneous substation equipment | Various Sites |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 16770 | Load Interconnection Program 2023 | Other | 26624 | Load Interconnection Program 2023 | Load Interconnection Program 2023 | ATC | M3 - Under Construction | 18045914 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Various Sites |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP22 | A | METC | East | 21995 | 2025 METC Customer Interconnections | Other | 26643 | 26643-METC Facilities- | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. | METC | M2 - Appendix A Approved | 2000000 | 2025-12-31 | Substation | Small miscellaneous substation equipment | METC Facilities |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21996 | J1084 Generator Interconnection TOIF | GIP | 26645 | 26645-Rock Creek-Substation | TOIF includes facilities and equipment at the 345 kV substation dedicated to the 345 kV radial line and Generating Facility | ITCM | M2 - Appendix A Approved | 661704 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Rock Creek | Substation |  | 345 | 345 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21997 | J1084 Generator Interconnection Network Upgrades | GIP | 26646 | 26646-Rock Creek-Substation | Rock Creek 345 kV ring bus will be expanded with a 345 kV breaker and other necessary equipment to interconnect the new terminal for project J1084. | ITCM | M2 - Appendix A Approved | 1294462 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Rock Creek | Substation |  | 345 | 345 |  |  | IA |  | Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21926 | Harbor – Russell Terminal 138 kV (893K11), Rebuild | Other | 26648 | 26648-Norwich SS-Harbor SS | Norwich - Harbor 138kV, (893K11), underground line replacement | ATC | M2 - Appendix A Approved | 61200000 | 2029-11-01 | Line Upgrade | Line rebuild on existing ROW | Norwich SS | Harbor SS |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | ITC | East | 22016 | 2025 ITCT Customer Interconnections | Other | 26663 | 26663-ITCT Facilities- | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. | ITCT | M2 - Appendix A Approved | 2000000 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | ITCT Facilities |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22020 | Leoni – Parr Rd 138kV Rebuild | Other | 26668 | 26668-Leoni-Parr Road | Rebuild approximately 19 miles from Leoni to Parr Rd utilizing 1431 ACSR on standard 138 kV double circuit steel poles with OPGW. | METC | M4 - Project in Service | 41842000 | 2025-12-01 | Line Upgrade | Line rebuild on existing ROW | Leoni | Parr Road | 1 | 138 |  | 18.65 |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22021 | Chopin – Dupont – White Lake 138kV Rebuild | Other | 26669 | 26669-Chopin-White Lake | Rebuild section from Chopin to White Lake from the line to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate Cobb - White Lake (Benston) line to the other side of the new 138 kV standard structures utilizing 954 ACSR conductor. | METC | M4 - Project in Service | 28050000 | 2027-05-03 | Line Upgrade | Line rebuild on existing ROW | Chopin | White Lake | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22021 | Chopin – Dupont – White Lake 138kV Rebuild | Other | 26670 | 26670-White Lake- | Upgrade Terminal Equipment | METC | M2 - Appendix A Approved | 107000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | White Lake |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22021 | Chopin – Dupont – White Lake 138kV Rebuild | Other | 26672 | 26672-White Lake-Dupont | Rebuild section from White Lake to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate the line from Dupont back up to White Lake (to the east) to the other side of the new 138 kV structures utilizing 954 ACSR conductor. | METC | M2 - Appendix A Approved | 8475000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | White Lake | Dupont | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22021 | Chopin – Dupont – White Lake 138kV Rebuild | Other | 26673 | 26673-Cobb-Dupont | Remove the old structures on the Cobb-Dupont-White Lake and the Cobb-White (Benston) circuits | METC | M2 - Appendix A Approved | 2310000 | 2027-05-03 | Line Upgrade | Line rebuild on existing ROW | Cobb | Dupont | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21998 | J1164 Generator Interconnection TOIF | GIP | 26674 | 26674-Magnolia-Substation | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | ITCM | M2 - Appendix A Approved | 475538 | 2026-08-14 | Substation | Substation (breakers only, no transformer) | Magnolia | Substation |  | 161 | 161 |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21999 | J1164 Generator Interconnection Network Upgrades | GIP | 26675 | 26675-Magnolia-Substation | Rebuild of Magnolia 161 kV substation as a 4-terminal, 4 breaker, ring-bus substation | ITCM | M2 - Appendix A Approved | 6770308 | 2026-08-14 | Substation | Substation (breakers only, no transformer) | Magnolia | Substation |  | 161 | 161 |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21999 | J1164 Generator Interconnection Network Upgrades | GIP | 26676 | 26676-Sibley-Magnolia | The Sibley to Magnolia 69 kV line will be relocated to allow for expansion of facilities at Magnolia | ITCM | M2 - Appendix A Approved | 558000 | 2026-08-14 | Line New | New Transmission line, new ROW - may include terminations | Sibley | Magnolia | 1 | 69 | 69 |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21999 | J1164 Generator Interconnection Network Upgrades | GIP | 26677 | 26677-Elk-Magnolia | The Magnolia-Elk 161 kV line will be relocated to a new terminal at the reconstructed Magnolia 161 kV ring-bus | ITCM | M2 - Appendix A Approved | 775200 | 2026-08-14 | Line New | New Transmission line, new ROW - may include terminations | Elk | Magnolia | 1 | 161 | 161 |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21999 | J1164 Generator Interconnection Network Upgrades | GIP | 26678 | 26678-Rock County-Magnolia | The Magnolia - Rock County 161 kV line will be relocated to a new terminal at the reconstructed Magnolia 161 kV ring-bus | ITCM | M2 - Appendix A Approved | 730080 | 2026-08-14 | Line New | New Transmission line, new ROW - may include terminations | Rock County | Magnolia | 1 | 161 | 161 |  |  | MN |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21751 | New Paragon 138/69 kV Substation | Other | 26683 | New Ameren Pana-PPI Paragon 138 kV Line | New Ameren Pana-PPI Paragon 138 kV Line in SEC. | PPI | M2 - Appendix A Approved | 1320000 | 2028-03-01 | Line New | New Transmission line, new ROW - may include terminations | Ameren Pana N | PPI Paragon | 1 | 138 |  | 2.3 |  | IL |  | Not Shared
MTEP22 | A | GREAT RIVER ENERGY | West | 22026 | Deer River - Jessie Lake - Wirt Tap 69 kV Line Rebuild | Other | 26687 | 26687-Deer River-Wirt Tap | Rebuild the Deer River - Jessie Lake - Wirt Tap 69 kV line. | GRE | M2 - Appendix A Approved | 25354206 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Deer River | Wirt Tap | 1 | 69 |  |  | 26.52 | MN |  | Not Shared
MTEP22 | A | METC | East | 15910 | Marquette - Bingham 138 kV Rebuild | Other | 24018 | 24018-Marquette-Bingham | Rebuild 18.76 miles of the Marquette – Bingham circuit using 954 ACSR conductor with single circuit steel structures. | METC | M2 - Appendix A Approved | 27450000 | 2027-04-30 | Line Upgrade | Line rebuild on existing ROW | Marquette | Bingham | 1 | 138 |  |  | 18.76 | MI |  | Not Shared
MTEP22 | A | GREAT RIVER ENERGY | West | 22528 | Matter 69 kV Substation | Other | 26795 | 26795-Matter- | Install a manual load break 3-way load break 69kV/1200A switch on a steel pole and foundation on GRE’s DX (Crow River to Victor) line. Install adjacent grading structures if needed. Build HS DE to 115kV. | GRE | M2 - Appendix A Approved | 403343 | 2026-04-30 | Substation | Distribution substation - may include trans high side | Matter |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP22 | A | AMEREN MISSOURI | Central | 22529 | New Vanduser 161 kV Ring Bus for J1034 Ringer Solar | GIP | 26796 | 26796-Vanduser- | Construct a new 161 kV switching station in Stoddard County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Vanduser 161 kV J1034 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Morley – Stoddard 161 kV transmission line | AmerenMO | M2 - Appendix A Approved | 6730000 | 2027-12-01 | Substation | Switching station (breakers only, no transformer) | Vanduser |  |  | 161 |  |  |  | MO |  | Not Shared
MTEP22 | A | DAIRYLAND POWER COOPERATIVE | West | 22531 | Bell Center-Lancaster N6 Rebuild | Other | 26801 | 26801-Bell Center-Lancaster | 40.51 Mile Rebuild to 477 ACSR on existing ROW | DPC | M2 - Appendix A Approved | 23877825 | 2029-04-23 | Line Upgrade | Line rebuild on existing ROW | Bell Center | Lancaster |  | 69 |  | 0 | 40.51 | WI |  | Not Shared
MTEP22 | A | METC | East | 22586 | Buskirk - New CE Interconnection | Other | 26803 | Tulip - Construct New 138 kV Station | Construct a new 138 kV station (Tulip) with three 138 kV breakers in a ring bus configuration, expandable for a fourth line exit. The new station would be located near the existing Titus Lake bulk power substation. | METC | M3 - Under Construction | 7240000 | 2026-04-06 | Substation | Switching station (breakers only, no transformer) | Tulip |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22586 | Buskirk - New CE Interconnection | Other | 26804 | BUKCK-HZLWD_ OHL Cut-In | Cut the Buck Creek–Hazelwood (formerly Beals Road–Hazelwood) 138 kV line into the new 138 kV station (Tulip). The cut-in would be between structures #008Q158 and #008Q159ABSW, near Titus Lake bulk power substation. | METC | M3 - Under Construction | 2770000 | 2026-04-06 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Buck Creek | Hazelwood | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | COOPERATIVE ENERGY | South | 22345 | East Winstonville Delivery Point | Other | 26805 | 26805-East Winstonville- | Install communication equipment for metering and motor operated switching. | Entergy-MS | M2 - Appendix A Approved | 60000 | 2026-12-01 | Misc. | Communication equipment | East Winstonville |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 22989 | Columbus SS, DIC, Reconfiguration | Other | 26883 | Columbus SS, DIC, Reconfiguration | • ATC will acquire and rebuild 1.65 miles of CWL 69 kV capable T-Line assets. • ATC will construct 2.18 miles of new 69 kV T-Line. • ATC will rebuild 2.44 miles of line Y-21. • ATC will construct a new 69 kV loop through straight bus with disconnect switches at the CWL Maple Street Substation. • ATC will construct a new 69 kV loop through straight bus with disconnect switches and 2 line breakers at the CWL South Substation. • ATC will construct a new 69 kV 3-way GOAB for a new CWL Water Street Tap. • ATC will retire the ATC Columbus Substation and 1.75 miles of line Y-21 that run through neighborhoods northwest of the ATC Columbus Substation | ATC | M2 - Appendix A Approved | 26600000 | 2029-09-12 | Substation | Substation (breakers only, no transformer) | Columbus SS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 23008 | WisDOT I-94 Stadium Group of Projects | Other | 26894 | 26894-WisDOT Relocation (Reimbursable)- | WisDOT I-94 E/W Road Move: Conflict and relocation of ATC existing facilities | ATC | M2 - Appendix A Approved | 66700000 | 2028-12-31 | Misc. | Line relocation (road move) | WisDOT Relocation (Reimbursable) |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 23008 | WisDOT I-94 Stadium Group of Projects | Other | 26896 | 26896-Asset Renewal of Structures 4145-4149- | Rebuild lines adjacent and concurrent to WisDOT Road Move due to age and condition | ATC | M2 - Appendix A Approved | 11100000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Asset Renewal of Structures 4145-4149 |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 23008 | WisDOT I-94 Stadium Group of Projects | Other | 26897 | 26897-96th Street-Valley | Communication Infrastructure Improvement | ATC | M2 - Appendix A Approved | 6700000 | 2028-12-31 | Misc. | Communication equipment | 96th Street | Valley |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | METC | East | 22020 | Leoni – Parr Rd 138kV Rebuild | Other | 26945 | 26945-Leoni- | Upgrade Terminal Equipment at Leoni 138 kV substation. | METC | M4 - Project in Service | 427000 | 2025-05-16 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Leoni |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22020 | Leoni – Parr Rd 138kV Rebuild | Other | 26946 | 26946-Parr Road- | Upgrade Terminal Equipment at Parr Road 138 kV substation. | METC | M2 - Appendix A Approved | 225000 | 2026-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Parr Road |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 22020 | Leoni – Parr Rd 138kV Rebuild | Other | 26947 | 26947-Lark-Leoni | Utilize 1431 ACSR conductor and OPWG on the Northeast side of the double-circuit structures to relocate Lark – Washtenaw – Leoni 138 kV circuit to the same structures as the Leoni – Parr Road 138 kV circuit from Leoni until Parr Road. Decommission the existing 138 kV structures of the Lark – Washtenaw – Leoni 138 kV circuit from Leoni – Parr Road. | METC | M4 - Project in Service | 9726000 | 2025-12-01 | Line Upgrade | Line reconductor | Lark | Leoni | 1 | 138 |  |  | 18.65 | MI |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 23147 | J1219/J1257 115 kV station(Hickory) | GIP | 26971 | 26971-Amite-Chicken Farm | Construct 115 kV station for a solar interconnection customer between Amite and Chicken Farm 115 kV stations. | Entergy-LA | M2 - Appendix A Approved | 14390000 | 2027-10-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Amite | Chicken Farm |  | 115 |  |  |  | LA |  | Not Shared
MTEP22 | A | METC | East | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | GIP | 28652 | 28652-White Lake- | Replace 188 and 288 deadends | METC | M2 - Appendix A Approved | 2268354 | 2026-06-01 | Substation | Small miscellaneous substation equipment | White Lake |  |  | 138 |  |  |  | MI |  | Shared
MTEP22 | A | METC | East | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | GIP | 28653 | 28653-Donaldson Creek-White Lake | Rebuild approximately 3 spans (from existing structure# 100C2713 going into White Lake) using permeant design and construction standards. | METC | M2 - Appendix A Approved | 1118750 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Donaldson Creek | White Lake | 1 | 138 |  |  |  | MI |  | Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 19945 | New Topeka-Bishop 69 kV Line | Other | 25628 | New Topeka-Bishop 69 kV line | New Topeka-Bishop 336 ACSR 69 kV line in MEC. | PPI | M2 - Appendix A Approved | 5120000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Topeka | Bishop | 1 | 69 |  | 8 |  | IL |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 23518 | Tunica - Lula 115 kV Cut-in (J1440) | GIP | 27298 | 27298-Tunica-Lula | J1440 generator interconnection on the Tunica – Lula 115 kV transmission line. | Entergy-MS | M2 - Appendix A Approved | 13560000 | 2028-05-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Tunica | Lula |  | 115 |  |  |  | MS |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21929 | Forks Switching Station & Forks-Rost 161kV Circuit | BRP | 27301 | 27301-Dickinson Coutny-Lakefireld | Line taps for the new Forks 161kV Switch Station on the Dickinson County-Lakefield 161kV line. | ITCM | M2 - Appendix A Approved | 0 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Dickinson Coutny | Lakefireld | 1 | 161 | 161 |  |  | MN |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 23520 | Johnstown SS, DIC, New Substation | Other | 27305 | Johnstown SS, DIC, New Substation | New Substation | ATC | M3 - Under Construction | 6000000 | 2026-12-31 | Substation | Distribution substation - may include trans high side | Johnstown SS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP22 | A | METC | East | 22586 | Buskirk - New CE Interconnection | Other | 27709 | TULIP-Buskirk_ Construct 138kV Tie | METC to install a couple spans and supporting structure connecting CE’s transformer to METC bus. This tie is to be constructed using 954 ACSR conductor on single-circuit structure. | METC | M3 - Under Construction | 1420000 | 2026-05-04 | Line New | New Transmission line, new ROW - may include terminations | Tulip (METC) | Buskirk (CE) | 1 | 138 |  | 0.01 |  | MI |  | Not Shared
MTEP22 | A | MONTANA-DAKOTA UTILITIES CO. | West | 20946 | Poplar2 115/60 kV | Other | 27407 | 27407-Poplar- | Bay addition for new line to Poplar 2 | MDU | M2 - Appendix A Approved | 1792472 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Poplar |  |  | 115 | 60 |  |  | MT |  | Not Shared
MTEP22 | A | MONTANA-DAKOTA UTILITIES CO. | West | 20946 | Poplar2 115/60 kV | Other | 26118 | 26118-Poplar Trans-Poplar Oil Field | Build a new Poplar Trans-Poplar Oil Field 115 kV line | MDU | M2 - Appendix A Approved | 1668853 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Poplar Trans | Poplar Oil Field | 1 | 115 |  | 10 |  | MT |  | Not Shared
MTEP22 | A | MONTANA-DAKOTA UTILITIES CO. | West | 20946 | Poplar2 115/60 kV | Other | 26119 | 26119-Poplar Oil Field- | Build a new Poplar Oil Field 115/60 kV sub | MDU | M2 - Appendix A Approved | 7077174 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Poplar Oil Field |  |  | 115 | 60 |  |  | MT |  | Not Shared
MTEP22 | A | METC | East | 21145 | J996 Generator Interconnection | GIP | 26150 | 26150-Pixley- | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | METC | M2 - Appendix A Approved | 5697000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Pixley |  |  | 138 |  |  |  | MI |  | Shared
MTEP22 | A | METC | East | 21145 | J996 Generator Interconnection | GIP | 26151 | 26151-Beecher-Morocco | Loop the Beecher - Morocco 138kV circuit into the new METC Pixley 138kV station. | METC | M2 - Appendix A Approved | 843600 | 2026-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Beecher | Morocco |  | 138 |  |  |  | MI |  | Shared
MTEP22 | A | METC | East | 21145 | J996 Generator Interconnection | GIP | 26152 | 26152-Beecher- | Replace existing SCADA router at Beecher and update telecom. | METC | M2 - Appendix A Approved | 78132 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Beecher |  |  | 138 |  |  |  | MI |  | Shared
MTEP22 | A | ITC | East | 21166 | Maple - J1062 Generator Interconnection | GIP | 26160 | Maple - J1062 NU - Construct new 345kV station | Build the J1062 Interconnection station as a breaker and half station with three breakers in a ring bus configuration. | ITCT | M2 - Appendix A Approved | 10908064 | 2028-05-09 | Substation | Substation (breakers only, no transformer) | Maple (J1062) |  |  | 345 |  |  |  | MI |  | Shared
MTEP22 | A | ITC | East | 21166 | Maple - J1062 Generator Interconnection | GIP | 26161 | Lemoyne - Majestic_J1062 NU_Cut in J1062 | Extend the Lemoyne - Majestic 345kV line to loop in the station. | ITCT | M2 - Appendix A Approved | 1795000 | 2028-05-09 | Line Upgrade | Generic transmission line project (try not to use the generic) | Majestic | Lemoyne | 1 | 345 |  |  |  | MI |  | Shared
MTEP22 | A | ITC | East | 21166 | Maple - J1062 Generator Interconnection | GIP | 26162 | Majestic - J1062 NU - Remove Pos. AI Wave Trap | Remove Majestic pos. AI wave trap. | ITCT | M2 - Appendix A Approved | 252456 | 2026-08-14 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Majestic |  |  | 345 |  |  |  | MI |  | Shared
MTEP22 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 21167 | New Menges Ditch 138/69 kV Substation | Other | 26163 | 26163-E.Elkart (AEP)-Menges Ditch | 2 New 138kV Circuits from E.Elkhart to Menges Ditch. (3) 69kV lines | NIPS | M3 - Under Construction | 17544253 | 2026-06-30 | Line New | New Transmission line, new ROW - may include terminations | E.Elkart (AEP) | Menges Ditch | 1 | 138 |  | 18 |  | IN |  | Not Shared
MTEP22 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 21167 | New Menges Ditch 138/69 kV Substation | Other | 26164 | 26164-Menges Ditch- | New 138/69kV substation | NIPS | M2 - Appendix A Approved | 24824367 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Menges Ditch |  |  | 138 | 69 |  |  | IN |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 20063 | Choctaw - TVA French Camp 500 kV: Decommission Line | Other | 25766 | 25766-Choctaw-TVA French Camp | Decommission and demolish the existing Choctaw-TVA French Camp 500kV line that was recently acquired by Entergy in November of 2019 (~0.75mi). | Entergy-MS | M3 - Under Construction | 1100000 | 2026-12-15 | Line Upgrade | Generic transmission line project (try not to use the generic) | Choctaw | TVA French Camp |  | 500 |  |  |  | MS |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 20064 | Choctaw - Wolf Creek 500 kV: Build New Line | Other | 25767 | 25767-Choctaw-Wolf Creek | Utilize ~0.1mi of existing Choctaw-French Camp 500kV line to tie into Wolf Creek (Choctaw – French Camp 500 kV decommissioned with a separate project). Convert Wolf Creek 500kV switching yard to 4 breaker ring bus to accommodate 2nd line. | Entergy-MS | M3 - Under Construction | 8600000 | 2026-12-15 | Line New | New Transmission line, new ROW - may include terminations | Choctaw | Wolf Creek |  | 500 |  |  |  | MS |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 20077 | Hilltop 230 kV Reliability Project | BRP | 25783 | 25783-Arrowhead 230 kV-Hilltop 230 kV | Sectionalize existing Iron Range-Arrowhead-Hilltop 230 kV Line by extending the Hilltop Tap 0.7 Miles to a new line entrance at Arrowhead 230 kV. Upgrade Hilltop 230 kV Tap from 55C to 100C. Replace existing polymer insulators and OPGW. | MP | M2 - Appendix A Approved | 7000000 | 2025-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Arrowhead 230 kV | Hilltop 230 kV |  | 230 |  | 0.7 | 7 | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 20077 | Hilltop 230 kV Reliability Project | BRP | 25786 | 25786-Arrowhead 230 kV- | New 230 kV line entrance at Arrowhead 230 kV substation for extending Hilltop 230 kV Tap to Arrowhead | MP | M2 - Appendix A Approved | 1300000 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Arrowhead 230 kV |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 20077 | Hilltop 230 kV Reliability Project | BRP | 25789 | 25789-Hilltop 230 kV-Hilltop 115 kV | Replace existing 187 MVA 230/115 kV transformer at Hilltop with a 373 MVA base transformer. Add 230 kV circuit breaker to high side of Hilltop transformer and replace low side transformer breaker. Replace low side transformer switch and some jumpers due to increased transformation capacity | MP | M4 - Project in Service | 4800000 | 2024-12-31 | Transformer | Transformer New | Hilltop 230 kV | Hilltop 115 kV |  | 230 | 115 |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21828 | Agency Street New Control Enclosure & Relay Replacements | Other | 26414 | 26414-Agency Street-Substation | The relays at Agency Street are approaching their 20 year end of life. ITC will install a new control enclosure with all new relays to provide ITC a separate control enclosure from IPL and minimize required outages and outage times for the relay replacements. All necessary outages should be coordinated with IPL. Also coordinate with IPL on location of new control building as this is an IPL owned site. | ITCM | M2 - Appendix A Approved | 2090891 | 2027-05-28 | Misc. | Relaying, protection, RTU and SCADA equipment | Agency Street | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 21838 | Replace Southwest 138 kV Breake | Other | 26428 | 26428-Southwest-Substation | Replacement of five (5) 138 kV breakers #4, #5, #3, #26, #27. Update: Breakers 3, 5, and 26 completed. 4 and 27 pushed back. | IPL | M2 - Appendix A Approved | 4500000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Southwest |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 21843 | Neches River Crossing Structure Mitigation | Other | 26433 | 26433-Neches-Sabine | Replace coffers, de-water and excavate soils Perform structure foundation inspection(s), fortify/repair where possible Restore soils around structure foundations, fill coffers to grade | Entergy-TX | M2 - Appendix A Approved | 16300000 | 2027-10-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Neches | Sabine |  | 138 |  |  |  | TX |  | Not Shared
MTEP22 | A | NORTHERN STATES POWER COMPANY | West | 21845 | NSPM Metro Steel Pole Replacement | Other | 26435 | 26435-Riverside-Main Street | Approximately 4-mile of triple circuit structure(35-structures) to be either replaced, painted or a combination of replace/paint | XEL | M3 - Under Construction | 21000000 | 2027-06-15 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Riverside | Main Street |  | 115 |  |  |  | MN |  | Not Shared
MTEP22 | A | NORTHERN STATES POWER COMPANY | West | 21869 | BRI CHB 34.5kV Cap Bank Retirement | Other | 26450 | 26450-Buffalo Ridge- | Retire 34.5kV cap banks at Buffalo Ridge feeders BRI311 and BRI312. | XEL | M2 - Appendix A Approved | 750000 | 2027-03-25 | Voltage Device | Capacitor (switched capacitor) | Buffalo Ridge |  |  | 35 |  |  |  | MN |  | Not Shared
MTEP22 | A | NORTHERN STATES POWER COMPANY | West | 21869 | BRI CHB 34.5kV Cap Bank Retirement | Other | 26451 | 26451-Chanarambe- | Retire 34.5kV cap bank at Chanarambe feeder CHB341. | XEL | M2 - Appendix A Approved | 750000 | 2027-03-25 | Voltage Device | Capacitor (switched capacitor) | Chanarambe |  |  | 35 |  |  |  | MN |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21871 | Sub E East Moline 69 kV Upgrades | Other | 26452 | 26452-Sub E East Moline-69 kV Upgrades | Replace aged equipment at Sub E East Moline. Project includes installing a new control building, replacing 69 kV oil circuit breakers, and replacing 69 kV cap-and-pin switches and insulators. | MEC | M2 - Appendix A Approved | 10000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Sub E East Moline |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21872 | Sub E East Moline-Sub 37 69 kV OPGW Installation | Other | 26453 | 26453-Sub E East Moline-Sub 37 69 kV OPGW | Install OPGW on the Sub E East Moline-Sub 37 69 kV Line | MEC | M2 - Appendix A Approved | 1500000 | 2028-12-31 | Misc. | Communication equipment | Sub E East Moline | Sub 37 |  | 69 |  |  |  | IL |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21873 | Sub 39-Sub 28 161 kV OPGW Installation | Other | 26454 | 26454-Sub 39-Sub 31 Tap | Install OPGW on the Sub 39-Sub 31 Tap 161 kV line | MEC | M4 - Project in Service | 70000 | 2022-12-11 | Misc. | Communication equipment | Sub 39 | Sub 31 Tap |  | 161 |  |  |  | IL |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21873 | Sub 39-Sub 28 161 kV OPGW Installation | Other | 26455 | 26455-Sub 31 Tap-Sub 28 OPGW | Install OPGW on the Sub 31 Tap-Sub 28 161 kV line | MEC | M2 - Appendix A Approved | 200000 | 2029-12-31 | Misc. | Communication equipment | Sub 31 Tap | Sub 28 |  | 161 |  |  |  | IL |  | Not Shared
MTEP22 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 21875 | Rebuild Lagrange 69 kV line-Circuit 6980 | Other | 26462 | 26462-Lagrange-Angola | Partial rebuild of line | NIPS | M2 - Appendix A Approved | 6000000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Lagrange | Angola |  | 69 |  |  | 6 | IN |  | Not Shared
MTEP22 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 21885 | Upgrade Transmission Substation - 2026 Program | Other | 26472 | 26472-Various- | 69kv and up Substation replacements/upgrades based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | NIPS | M2 - Appendix A Approved | 54852316 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Various |  |  | 345 | 34 |  |  | IN |  | Not Shared
MTEP22 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 21886 | Upgrade transmission lines - 2026 program | Other | 26473 | 26473-Various- | 69kv and up line rebuilds/upgrades based on age and condition, including structures, conductor, switches and communication upgrades(fiber) | NIPS | M2 - Appendix A Approved | 68286845 | 2026-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Various |  |  | 345 | 34 |  |  | IN |  | Not Shared
MTEP22 | A | MONTANA-DAKOTA UTILITIES CO. | West | 21889 | Hettinger 115/69/41.6 | Other | 26475 | 26475-Hettinger- | Age and condition to replace existing 115/69/41.6 kV facilities | MDU | M2 - Appendix A Approved | 10100000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Hettinger |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP22 | A | METC | East | 21890 | Gallagher - Ogemaw 138 kV Sag Remediation | BRP | 26476 | 26476-Gallagher-Ogemaw | Remediate sag on the 336 ACSR conductor on the Gallagher to Ogemaw 138 kV circuit up to at least 60 MVA summer emergency rating. | METC | M2 - Appendix A Approved | 660000 | 2026-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gallagher | Ogemaw | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | NORTHERN STATES POWER COMPANY | West | 21891 | Line 0726 Rebuild | Other | 26478 | 26478-Pipestone-Tracy Switching Station | NSM 0726-69kV Line Major line rebuild from Pipestone to Tracy Switching Station. | XEL | M3 - Under Construction | 12469273 | 2026-09-11 | Line Upgrade | Line rebuild on existing ROW | Pipestone | Tracy Switching Station |  | 69 |  |  |  | MN |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21897 | Crosswinds 161-13.2 kV Substation | Other | 26487 | 26487-Crosswinds | Construct new 161-13.2 kV substation | MEC | M2 - Appendix A Approved | 6000000 | 2028-02-01 | Substation | Substation (breakers only, no transformer) | Crosswinds |  |  | 161 | 13 |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21897 | Crosswinds 161-13.2 kV Substation | Other | 26488 | 26488-Delaware-34th Ave NW | Construct 161 kV line taps | MEC | M2 - Appendix A Approved | 4600000 | 2028-02-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Delaware | 34th Ave NW |  | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21898 | Increase Bus Withstand Capabiities | Other | 26491 | 26491-CBEC- | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities | MEC | M3 - Under Construction | 1600000 | 2026-12-01 | Substation | Substation bus upgrade | CBEC |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21898 | Increase Bus Withstand Capabiities | Other | 26492 | 26492-Raun- | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities | MEC | M3 - Under Construction | 1500000 | 2026-12-01 | Substation | Substation bus upgrade | Raun |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21898 | Increase Bus Withstand Capabiities | Other | 26493 | 26493-Neal North- | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities. | MEC | M2 - Appendix A Approved | 1000000 | 2026-12-01 | Substation | Substation bus upgrade | Neal North |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21898 | Increase Bus Withstand Capabiities | Other | 26494 | 26494-Sycamore- | Replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities. | MEC | M2 - Appendix A Approved | 4500000 | 2028-12-04 | Substation | Substation bus upgrade | Sycamore |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | METC | East | 15910 | Marquette - Bingham 138 kV Rebuild | Other | 26989 | 26989-Bingham- | Complete all work necessary to connect OPGW at position WM8 at Bingham 138 kV station. | METC | M2 - Appendix A Approved | 80000 | 2026-10-02 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Bingham |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21908 | Carroll County-Auburn-Sherwood 69 kV Line Rebuild & Terminal Upgrades | Other | 26996 | 26996-Auburn-Sherwood | Rebuild Auburn to Sherwood 69 kV line. | MEC | M3 - Under Construction | 8500000 | 2026-09-01 | Line Upgrade | Line rebuild on existing ROW | Auburn | Sherwood | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | ENTERGY ARKANSAS, LLC | South | 23154 | Keo 500kV: Expansion for J1258 & J1415 | GIP | 26997 | 26997-Keo 500kV- | New interconnection for J1258 and J1415 at Keo 500kV | Entergy-AR | M2 - Appendix A Approved | 8888000 | 2027-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Keo 500kV |  |  | 500 |  |  |  | AR |  | Shared
MTEP22 | A | HOOSIER ENERGY | Central | 23266 | New HE_AboutBit 115 MVA Load | Other | 27000 | 27000-Merom 69kV-AboutBit (new customer-owned) | Extend a new 69kV transmission line from an available bay position at Merom transmission station (Bus # 248774) to the new customer. The 69kV line will split at about 0.3 miles from Merom station, extending to two separate substations. | HE | M2 - Appendix A Approved | 1200000 | 2027-01-01 | Line New | New Transmission line, new ROW - may include terminations | Merom 69kV | AboutBit (new customer-owned) |  | 69 |  | 0.8 |  | IN |  | Not Shared
MTEP22 | A | ENTERGY ARKANSAS, LLC | South | 23326 | Tindall 230kV: J1215 New Switching Station Cut-In | GIP | 27015 | 27015-Tindall | New 230kV switching station for J1215 interconnection | Entergy-AR | M2 - Appendix A Approved | 16375000 | 2027-02-17 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Tindall |  |  | 230 |  |  |  | AR |  | Not Shared
MTEP22 | A | ENTERGY ARKANSAS, LLC | South | 23267 | Fountain Hill 115kV: J1281 Cut In Switching Station | GIP | 27022 | 27022-Fountain Hill 115kV- | New cut-in for a 115kV substation to interconnect J1281. | Entergy-AR | M2 - Appendix A Approved | 3796000 | 2027-09-15 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Fountain Hill 115kV |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 23330 | Rilla 115 kV: Expand Station (J1239) | GIP | 27023 | 27023-Rilla- | Interconnection at Rilla switching station for J1239 generation interconnection. | Entergy-LA | M3 - Under Construction | 7233000 | 2026-06-26 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Rilla |  |  | 115 |  |  |  | LA |  | Not Shared
MTEP22 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 23346 | Hutchinson Substation | Other | 27025 | 27025-658279- | This project will add a second 115/69 kV transformer to the existing City of Hutchinson MN, Hutchinson Substation. The project will also rebuild the Hutchinson 115 kV into a four position ring bus. | MRES | M2 - Appendix A Approved | 15200000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | 658279 |  |  | 115 | 69 |  |  | MN |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 23387 | Gerald Andrus - Tinnin 230 kV Cut-in and Line Upgrade (J1458) | GIP | 27031 | 27031-336858-337040 | POI on Gerald Andrus - Tinnin 230 kV line | Entergy-MS | M2 - Appendix A Approved | 4516000 | 2026-06-30 | Substation | Points of Interconnection for generators (User TAP for dist subs) | 336858 | 337040 | 1 | 230 |  |  |  | MS |  | Not Shared
MTEP22 | A | ENTERGY SERVICES, LLC. | South | 23387 | Gerald Andrus - Tinnin 230 kV Cut-in and Line Upgrade (J1458) | GIP | 27032 | 27032-337044-337045 | Network Upgrade Line Rebuild on Greenville - SE Greenville 115 kV line | Entergy-MS | M2 - Appendix A Approved | 5909000 | 2026-06-30 | Line Upgrade | Line rebuild on existing ROW | 337044 | 337045 | 1 | 115 |  |  |  | MS |  | Not Shared
MTEP22 | A | ITC | East | 20185 | Warren 120kV 55 MVAR Reactor | Other | 25947 | 25947-Warren- | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Warren 120kV bus. | ITCT | M2 - Appendix A Approved | 3300000 | 2027-05-14 | Voltage Device | Reactor or Inductor | Warren |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP22 | A | ITC | East | 20186 | Mack 120kV 55 MVAR Reactor | Other | 25948 | 25948-Mack- | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Mack 120kV bus. | ITCT | M2 - Appendix A Approved | 3231000 | 2026-04-01 | Voltage Device | Reactor or Inductor | Mack |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 19966 | Munising Area Reactive Power Project | BRP | 25971 | 25971-Munising Area- | Reactive Power Project | ATC | M3 - Under Construction | 14400000 | 2027-05-01 | Voltage Device | Reactor or Inductor | Munising Area |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | OTTER TAIL POWER COMPANY | West | 20385 | OTP Buffalo to Alice 115 kV Rebuild | Other | 26009 | 26009-Buffalo 115kV-Alice 115kV | Rebuild 7 miles of 115 kV line due to poor performance. | OTP | M2 - Appendix A Approved | 2000000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Buffalo 115kV | Alice 115kV |  | 115 |  |  | 7 | ND |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21345 | National - Presque Isle SW YD 138 kV (446), Re-insulate & OPGW | Other | 26237 | 26237-National SS-Presque Isle SW YD | PR08836: Reinsulate ~50% of structures on the line with like for like porcelain bells. Replacement of structures (~15% based on ground inspection) for woodpecker damage. Install OPGW. PR09237: This fiber addition is also being done in a similar location and is being combined with this project to terminate UG fiber from structure 156 into the North Lake SS. PR09232: Rerate of line 446. This portion of the project was formerly in the Line Clearance Mitigation program and has been now combined with this project to create efficiencies for work being done on the same line. | ATC | M3 - Under Construction | 18000000 | 2026-07-22 | Line Upgrade | Line rebuild on existing ROW | National SS | Presque Isle SW YD | 446 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21348 | Tower Dr - Pulliam 69 kV (P-16/R-70), Partial Rebuild | Other | 26240 | Tower Dr - Pulliam 69 kV (P-16/R-70), Partial Rebuild | Rebuild and reroute ~1 mile of double circuit 69kV lines P-16/R-70. This would get structures out of the high-water area where they are susceptible to ice damage and would replace the aging river crossing conductor. | ATC | M2 - Appendix A Approved | 23900000 | 2029-01-31 | Line Upgrade | Line rebuild on existing ROW | Tower Dr | Pulliam | P-16/R-70 | 69 |  |  | 1 | WI |  | Not Shared
MTEP22 | A | AMEREN ILLINOIS | Central | 21406 | Rebuild Sparta Tap 138 kV radial line | Other | 26253 | 26253-Sparta-Tibbs | Repair issues found during inspections | AmerenIL | M2 - Appendix A Approved | 4300000 | 2029-12-01 | Line Upgrade | Line rebuild on existing ROW | Sparta | Tibbs |  | 138 |  |  |  | IL |  | Not Shared
MTEP22 | A | METC | East | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | GIP | 26271 | 26271-Donaldson Creek-White Lake | Rebuild approximately 18.43 miles of the 336 ACSR conductor utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW. | METC | M4 - Project in Service | 29581200 | 2024-04-09 | Line Upgrade | Line rebuild on existing ROW | Donaldson Creek | White Lake |  | 138 |  |  | 18.43 | MI |  | Shared
MTEP22 | A | METC | East | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | GIP | 26272 | 26272-Donaldson Creek- | Replace BM11 Line Drop, Install OPGW | METC | M4 - Project in Service | 113970 | 2024-04-09 | Substation | Small miscellaneous substation equipment | Donaldson Creek |  |  | 138 |  |  |  | MI |  | Shared
MTEP22 | A | METC | East | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | GIP | 26273 | 26273-White Lake- | Replace 188 Line Drop and Bus, Install OPGW | METC | M4 - Project in Service | 446857 | 2024-04-09 | Substation | Small miscellaneous substation equipment | White Lake |  |  | 138 |  |  |  | MI |  | Shared
MTEP22 | A | METC | East | 21485 | Lawndale - Murphy 138kV Sag Remediation | BRP | 26281 | 26281-Lawndale-Murphy | Remove the sag limit on the Lawndale to Murphy 138 kV line to conductor limit | METC | M2 - Appendix A Approved | 931000 | 2027-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Lawndale | Murphy | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 21505 | Houghton Lake Interconnection | Other | 26282 | 26282-New Station - Name TBD- | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | METC | M3 - Under Construction | 4427067 | 2026-10-15 | Substation | Switching station (breakers only, no transformer) | New Station - Name TBD |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 21505 | Houghton Lake Interconnection | Other | 26283 | 26283-Bard-Higgins | Loop the Bard Rd - Higgins 138kV circuit into the new METC 138kV switching station. | METC | M3 - Under Construction | 4045025 | 2026-10-15 | Line New | New Transmission line, new ROW - may include terminations | Bard | Higgins |  | 138 |  | 0.2 |  | MI |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 19950 | New St. David-Wee-Ma-Tuk-Canton 69 kV line | Other | 26288 | New Canton-Wee-Ma-Tuk 69 kV line | New Canton-Wee-Ma-Tuk 336 ACSR 69 kV line in SREC. | PPI | M3 - Under Construction | 2400000 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Canton | Wee-Ma-Tuk | 1 | 69 |  | 4 |  | IL |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Other | 26296 | 26296-Arrowhead-Center (Block 3) | HVDC transmission line targeted structure replacements, Year 3 | MP | M2 - Appendix A Approved | 3000000 | 2025-12-31 | Misc. | High Voltage DC line or terminal | Arrowhead | Center (Block 3) |  | 250 |  |  |  | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Other | 26297 | 26297-Arrowhead-Center (Block 4) | HVDC transmission line targeted structure replacements, Year 1 | MP | M2 - Appendix A Approved | 3000000 | 2026-12-31 | Misc. | High Voltage DC line or terminal | Arrowhead | Center (Block 4) |  | 250 |  |  |  | MN |  | Not Shared
MTEP22 | A | MINNESOTA POWER INC. | West | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Other | 26298 | 26298-Arrowhead-Ground Electrode | Replace existing ground electrode from Arrowhead converter station | MP | M2 - Appendix A Approved | 2000000 | 2027-12-31 | Misc. | High Voltage DC line or terminal | Arrowhead | Ground Electrode |  | 250 |  |  |  | MN |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 2125 | Upgrade Centerton 138/69kV Bk 1 | Other | 2910 | 2910-Centerton-transformer | Upgrade/replace existing 75MVA 138/69kV bank with 150MVA bank | DEI | M2 - Appendix A Approved | 7969251 | 2027-02-26 | Transformer | Transformer New | Centerton | transformer | 1 | 138 | 69 |  |  | IN |  | Not Shared
MTEP22 | A | ITC | Central | 15875 | Kentucky - Luzon 120 kV Sag Remediation | BRP | 23968 | 23968-Kentucky-Luzon | Completely remove the sag limit on the Kentucky – Luzon 120 kV line. | ITCT | M2 - Appendix A Approved | 500000 | 2026-10-23 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Kentucky | Luzon | 1 | 120 |  |  |  | MI |  | Not Shared
MTEP22 | A | ITC | East | 17999 | Corktown - Waterman 120 kV UG Rebuild | BRP | 24771 | 24771-Corktown-Waterman | The proposed solution is to re-conductor approximately 3.7 miles utilizing 3200 Kcmil underground cable. | ITCT | M2 - Appendix A Approved | 80000000 | 2034-12-29 | Line Upgrade | Line rebuild on existing ROW | Corktown | Waterman | 1 | 120 |  |  | 3.7 | MI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 18046 | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | Other | 24826 | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | Line Rebuild | ATC | M2 - Appendix A Approved | 29800000 | 2027-03-10 | Line Upgrade | Line rebuild on existing ROW | Darlington | Rock Branch | Y-109 | 69 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 18047 | South Beaver Dam - Hubbard, (Y-134), 69kV Rebuild & OPGW | Other | 24827 | 24827-South Beaver Dam-Horicon | Line Rebuild | ATC | M3 - Under Construction | 26000000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | South Beaver Dam | Horicon | Y-134 | 69 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMEREN MISSOURI | Central | 18063 | New Saunders 345 kV substation (fka Mt. Pleasant) | Other | 24847 | 24847-Maywood-Sub T | Placeholder | AmerenMO | M2 - Appendix A Approved | 2600000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Maywood | Sub T |  | 345 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21902 | Anthon Substation | Other | 26497 | 26497-Anthon- | Install 69 kV line taps into new substation to serve customer load or to improve system reliability. | MEC | M2 - Appendix A Approved | 1500000 | 2028-12-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Anthon |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21908 | Carroll County-Auburn-Sherwood 69 kV Line Rebuild & Terminal Upgrades | Other | 26505 | 26505-Carroll County-Auburn | Rebuild the Carroll County-Auburn 69 kV line | MEC | M2 - Appendix A Approved | 13000000 | 2027-02-01 | Line Upgrade | Line rebuild on existing ROW | Carroll County | Auburn |  | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21908 | Carroll County-Auburn-Sherwood 69 kV Line Rebuild & Terminal Upgrades | Other | 26507 | 26507-Auburn- | Replace limiting terminal equipment (jumpers and switches) at Auburn Substation | MEC | M2 - Appendix A Approved | 0 | 2026-09-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Auburn |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21909 | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | BRP | 26508 | 26508-Sac City- | Construct a new switching station to interconnect two MidAmerican 69 kV lines and one Corn Belt 69 kV line | MEC | M2 - Appendix A Approved | 15000000 | 2028-06-01 | Substation | Switching station (breakers only, no transformer) | Sac City |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21909 | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | BRP | 26509 | 26509-Sac City- | Construct line taps into Sac City Switching Station | MEC | M2 - Appendix A Approved | 6000000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sac City |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21909 | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | BRP | 26510 | 26510-Sac County-Schaller | Rebuild and reconductor the Sac County-Schaller 69 kV line | MEC | M2 - Appendix A Approved | 4700000 | 2028-09-30 | Line Upgrade | Line rebuild on existing ROW | Sac County | Schaller | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21909 | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | BRP | 26512 | 26512-Schaller-Odebolt | Rebuild and reconductor the Schaller-Odebolt 69 kV line | MEC | M2 - Appendix A Approved | 17000000 | 2028-02-28 | Line Upgrade | Line rebuild on existing ROW | Schaller | Odebolt | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21912 | Substation J 161 kV Capacitor Bank Replacement | Other | 26519 | 26519-Substation J Iowa City- | Replace 161 kV capacitor at Sub J Iowa City | MEC | M3 - Under Construction | 1700000 | 2026-05-31 | Voltage Device | Capacitor (switched capacitor) | Substation J Iowa City |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21913 | Northgate Substation: Ring bus expansion and 161 kV tie line to ITCM’s Rose Hollow Substation | Other | 26520 | 26520-Northgate-Rose Hollow | Construct 161 kV line from Northgate to Rose Hollow | MEC | M2 - Appendix A Approved | 3500000 | 2027-10-31 | Line New | New Transmission line, new ROW - may include terminations | Northgate | Rose Hollow | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | MIDAMERICAN ENERGY CO. | West | 21913 | Northgate Substation: Ring bus expansion and 161 kV tie line to ITCM’s Rose Hollow Substation | Other | 26521 | 26521-Northgate- | Expand existing Northgate bus to a ring bus to accommodate new line terminal | MEC | M2 - Appendix A Approved | 4100000 | 2027-10-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Northgate |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21915 | Fitzgerald SS – Transformer and Breaker Asset Renewal | Other | 26523 | 26523-Fitzgerald SS- | Transformer Replacement | ATC | M3 - Under Construction | 3200000 | 2026-11-20 | Substation | Substation (breakers only, no transformer) | Fitzgerald SS |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21918 | Pine River - Mich Limestone Loading Dock 69 kV (ESE_6906), Rebuild | Other | 26526 | 26526-Pine River SS-Mich Limestone Load Dock | Pine River - Mich Limestone Loading Dock 69 kV (ESE_6906), Rebuild | ATC | M2 - Appendix A Approved | 42000000 | 2028-03-20 | Line Upgrade | Line rebuild on existing ROW | Pine River SS | Mich Limestone Load Dock | 6906 | 69 |  |  |  | MI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21923 | Everett GIS Asset Renewal | Other | 26531 | 26531-Everett GIS SS- | Everett GIS Asset Renewal | ATC | M2 - Appendix A Approved | 22645727 | 2027-04-30 | Substation | Substation (breakers only, no transformer) | Everett GIS SS |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | AMERICAN TRANSMISSION COMPANY | West | 21925 | Plymouth Reliability Project | Other | 26533 | Plymouth Reliability Project | New 138-kV/12.47-kV interconnection substation to be named the Plymouth 5 Substation. New double-circuit 138-kV transmission line approximately 8.0 miles in length from the Saukville-Elkhart Lake 138-kV line (8241) to loop in and out of the new Plymouth 5 Substation. Plymouth Utilities will install two distribution transformers with this project. | ATC | M3 - Under Construction | 33529000 | 2026-05-30 | Substation | Substation (breakers only, no transformer) | Plymouth #5 SS |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21929 | Forks Switching Station & Forks-Rost 161kV Circuit | BRP | 26535 | 26535-Forks-Switch Station | ITC Midwest will construct a three position 161kV ring bus substation named Forks on the Dickinson County – Lakefield Junction circuit. | ITCM | M2 - Appendix A Approved | 5353800 | 2025-09-30 | Substation | Substation (breakers only, no transformer) | Forks | Switch Station |  | 161 | 161 |  |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21929 | Forks Switching Station & Forks-Rost 161kV Circuit | BRP | 26536 | 26536-Forks-Rost | ITC Midwest will construct a ~6.5mi 161kV circuit between the new Forks – Rost substations using T2-636 ACSR. | ITCM | M2 - Appendix A Approved | 8102400 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Forks | Rost | 1 | 161 | 161 | 6.5 |  | MN |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21936 | Centerville Cooper Creek 69kV Interconnection | Other | 26550 | 26550-Centerville Cooper Creek-Substation | Construct new Centerville Cooper Creek Substation | ITCM | M2 - Appendix A Approved | 2884631 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Centerville Cooper Creek | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21936 | Centerville Cooper Creek 69kV Interconnection | Other | 26551 | 26551-Centerville North-Bridgeport North | Terminate Bridgeport - Centerville North Line into new Cooper Creek Substation | ITCM | M2 - Appendix A Approved | 134400 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | Centerville North | Bridgeport North | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21936 | Centerville Cooper Creek 69kV Interconnection | Other | 26552 | 26552-Centerville North-Centerville South | Terminate Centerville North - Centerville South Line into new Cooper Creek Substation | ITCM | M2 - Appendix A Approved | 156000 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | Centerville North | Centerville South | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21936 | Centerville Cooper Creek 69kV Interconnection | Other | 26553 | 26553-Centerville North-Substation | Retire Centerville North substation | ITCM | M2 - Appendix A Approved | 533243 | 2026-06-30 | Substation | Substation (breakers only, no transformer) | Centerville North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21937 | Chariton North 69kV Substation Interconnection | Other | 26554 | 26554-Chariton North-Substation | New 69 kV Substation Chariton North. | ITCM | M2 - Appendix A Approved | 4128417 | 2027-07-02 | Substation | Substation (breakers only, no transformer) | Chariton North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21937 | Chariton North 69kV Substation Interconnection | Other | 26555 | 26555-Court-Lucas County | New Double Circuit line tapping the Lucas County to Court 69 kV line to the new Chariton North Substation. | ITCM | M2 - Appendix A Approved | 2226000 | 2027-07-02 | Line New | New Transmission line, new ROW - may include terminations | Court | Lucas County | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21937 | Chariton North 69kV Substation Interconnection | Other | 26556 | 26556-Lucas County-Woodburn Jct | New 69 kV line taps tapping the Lucas County to Woodburn Junction 69 kV line to the new Chariton North Substation | ITCM | M2 - Appendix A Approved | 482400 | 2027-07-02 | Line New | New Transmission line, new ROW - may include terminations | Lucas County | Woodburn Jct | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21939 | Cedar Rapids Hunter Field Substation Expansion | Other | 26557 | 26557-Cedar Rapids Hunter Field-Substation | IPL has notified ITC that it will be adding a 3rd 161x69/24.9 kV transformer at the Hunter Field Substation. ITC will need to add an additional breaker and bus to connect the new IPL transformer at Hunter Field. All new ITC equipment to be designed to 161 kV specs to allow future conversion of the substation to 161 kV operation. Substation will initially be operated at 69 kV. | ITCM | M2 - Appendix A Approved | 1284996 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Cedar Rapids Hunter Field | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21940 | Turkey River to Guttenburg 69kV Rebuiild | Other | 26558 | 26558-Turkey River-Guttenburg | The 9.04 mile Turkey River – Guttenberg 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Turkey River and Monona. | ITCM | M2 - Appendix A Approved | 10376400 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Turkey River | Guttenburg | 1 | 69 | 69 |  | 9.04 | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21941 | Guttenburg to Garnavillo 69kV Rebuild | Other | 26559 | 26559-Guttenburg-Garnavillo | The 11.23 mile Guttenberg - Garnavillo 69 kV line along with the 0.18 mile tap to Garnavillo are at the end of their useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Guttenberg and Monona. | ITCM | M2 - Appendix A Approved | 14391600 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Guttenburg | Garnavillo | 1 | 69 | 69 |  | 11.23 | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21942 | Garnavillo to Elkader 69kV Rebuild | Other | 26560 | 26560-Garnavillo-Elkader | The 7.63 mile Garnavillo - Elkader 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Garnavillo and Elkader. | ITCM | M2 - Appendix A Approved | 10012800 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Garnavillo | Elkader | 1 | 69 | 69 |  | 7.63 | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21943 | Rose Hollow Add 161kV Terminal for North Gate line | Other | 26562 | 26562-Rose Hollow-Substation | MidAmerican has notified ITC that they will be building a new 161 kV line from their exiting North Gate substation to the ITC Rose Hollow substation. Per the terms of the agreement with MidAmerican, ITC will need to install a new 161 kV terminal at Rose Hollow for the new line to North Gate. | ITCM | M2 - Appendix A Approved | 984000 | 2026-07-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Rose Hollow | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP22 | A | METC | East | 21945 | Parr Road-Whiting 138kV Rebuild | Other | 26563 | 26563-PARRR-TNGNT_Rbld with OPGW | Rebuild approximately 12 miles from Parr Rd - Tangent (J875 Generator Interconnection) on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW. | METC | M2 - Appendix A Approved | 18655313 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Parr Road | Tangent |  | 138 |  |  | 12 | MI |  | Not Shared
MTEP22 | A | METC | East | 21945 | Parr Road-Whiting 138kV Rebuild | Other | 26564 | 26564-TNGNT-WHTNG_Rbld with OPGW | Rebuild approximately 28.6 miles from Raisin Tap - Whiting section of the Tangent - Whiting 138kV line on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW. | METC | M2 - Appendix A Approved | 41136216 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Raisin Tap | Whiting |  | 138 |  |  | 28.6 | MI |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21946 | Pelican-Triboji 69kV Rebuild | Other | 26565 | 26565-Pelican-West Okoboji | Rebuild the line between Pelican and structure 162 (~1.04 miles). | ITCM | M2 - Appendix A Approved | 1422000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Pelican | West Okoboji | 1 | 69 | 69 |  | 1.04 | IA |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21946 | Pelican-Triboji 69kV Rebuild | Other | 26566 | 26566-Tirboji-West Okoboji | Rebuild the line between Triboji and structure 72 (~4.45 miles). | ITCM | M2 - Appendix A Approved | 5040000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Tirboji | West Okoboji | 1 | 69 | 69 |  | 4.45 | IA |  | Not Shared
MTEP22 | A | WABASH VALLEY POWER ASSOCIATION, INC. | Central | 21955 | Upgrade Fair Oaks 2nd bank 138/69/12 kV transformer | Other | 26574 | 26574-Fair Oaks- | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area | NIPS | M2 - Appendix A Approved | 4176754 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Fair Oaks |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP22 | A | GREAT RIVER ENERGY | West | 22030 | Rost 161/69 kV Substation and Lorain - Rost 69 kV Line | BRP | 26691 | 26691-Rost- | Build the Rost 161/69 kV substation | GRE | M2 - Appendix A Approved | 13268173 | 2026-10-30 | Substation | Substation (breakers only, no transformer) | Rost |  |  | 161 | 69 |  |  | MN |  | Not Shared
MTEP22 | A | GREAT RIVER ENERGY | West | 22030 | Rost 161/69 kV Substation and Lorain - Rost 69 kV Line | BRP | 26692 | 26692-Lorain-Rost | Construct a new 69 kV line from Lorain substation to the Rost substation. | GRE | M2 - Appendix A Approved | 7839109 | 2025-10-03 | Line New | New Transmission line, new ROW - may include terminations | Lorain | Rost | 1 | 69 |  | 9 |  | MN |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21794 | New Forest City 138/69 kV Substation | BRP | 26709 | New Forest City 69kV Capacitor Bank | New Forest City 69kV Capacitor Bank 4.8 MVAR | PPI | M2 - Appendix A Approved | 300000 | 2028-03-01 | Voltage Device | Capacitor (switched capacitor) | Forest City |  |  | 69 |  |  |  | IL |  | Not Shared
MTEP22 | A | ITC MIDWEST | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | Other | 26743 | 26743-Dubuque 8th Street-Bunker Hill | Line tap modifications for Bunker Hills expansion. | ITCM | M2 - Appendix A Approved | 158750 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Dubuque 8th Street | Bunker Hill | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP22 | A | METC | East | 21945 | Parr Road-Whiting 138kV Rebuild | Other | 26744 | 26744-Parr Road - Connect OPGW | Equipment Connection | METC | M2 - Appendix A Approved | 213366 | 2026-06-01 | Substation | Small miscellaneous substation equipment | Parr Road |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 21945 | Parr Road-Whiting 138kV Rebuild | Other | 26745 | 26745-Tangent - Connect OPGW | Equipment Connection | METC | M2 - Appendix A Approved | 178994 | 2026-12-01 | Substation | Small miscellaneous substation equipment | Tangent |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | METC | East | 21945 | Parr Road-Whiting 138kV Rebuild | Other | 26746 | 26746-Whiting- | Equipment Connection | METC | M2 - Appendix A Approved | 154704 | 2028-12-01 | Substation | Small miscellaneous substation equipment | Whiting |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 22245 | Improve 23008 Tipton W-Cammack Rd Line | Other | 26747 | 26747-Tipton West-Cammack Rd SS | 23008 Tipton W-Cammack Rd: Insulator Replacement and anti-gallop line conductor modifications | DEI | M2 - Appendix A Approved | 4716099 | 2028-03-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Tipton West | Cammack Rd SS |  | 230 |  |  |  | IN |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 22206 | Replace Dresser 138kV Breaker | BRP | 26748 | 26748-Dresser- | Replace (5) Dresser CBs: 13869-9, 13869-10, 138B3-1, 138B3-2, 138138 were identified in the 2021 short circuit study as being over-dutied during certain fault conditions. This is a NERC TPL 001-4 compliance requirement to replace the following breakers with higher interruption capacity (63 KIAC rating). | DEI | M3 - Under Construction | 3816851 | 2028-06-06 | Substation | Circuit Breaker (replacement at existing substation) | Dresser |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 22226 | New Bolton 345kV-230kV Substation | BRP | 26750 | 26750-Bolton 345 lines | Bolton 345 in/out lines: cut the 34513 Cayuga - Sugar Crk line; loop through Bolton sub - 3.7 miles of new line on each side to be built on separate structures, common ROW; line cut to be located approximately 6 miles from Sugar Creek. | DEI | M2 - Appendix A Approved | 25900000 | 2028-08-21 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Bolton 345 |  |  | 345 |  | 7.4 |  | IN |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 22226 | New Bolton 345kV-230kV Substation | BRP | 26751 | 26751-Bolton 345/230 sub | Bolton 345kV-230kV Substation: new sub with 2-450MVA 345/230kV xfmrs; both 345kV and 230kV will have 4-CBs with ultimate breaker and 1/2 layout | DEI | M2 - Appendix A Approved | 44400000 | 2028-08-21 | Transformer | Transformer New | Bolton 345/230 sub |  |  | 345 | 230 |  |  | IN |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 22226 | New Bolton 345kV-230kV Substation | BRP | 26752 | 26752-Bolton 230 lines | (2) Bolton to Wabash River 230kV lines: high capacity lines - (2)954ACSR @ 1006MVA/1160MVA min.; 1.7 miles of new line for each ckt to be built on separate structures, common ROW | DEI | M2 - Appendix A Approved | 16500000 | 2028-08-21 | Line New | New Transmission line, new ROW - may include terminations | Bolton 345/230 sub | Wabash River Gen Station |  | 230 |  | 3.4 |  | IN |  | Not Shared
MTEP22 | A | DUKE ENERGY INDIANA, LLC | Central | 22209 | Upgrade Columbus 13830 Line Terminal | BRP | 26755 | 26755-Columbus-Seymour | Columbus 13830 line terminal: upgrade 300CU bus to 954AL to increase facility rating to 178MVA (line conductor rating) | DEI | M2 - Appendix A Approved | 1232000 | 2027-06-05 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Columbus | Seymour | 1 | 138 |  |  |  | IN |  | Not Shared
MTEP22 | A | COOPERATIVE ENERGY | South | 22345 | East Winstonville Delivery Point | Other | 26774 | 26774-East Winstonville- | Tap the Energy owned Delta SES - Shelby 115kV line with switching station. | Entergy-MS | M2 - Appendix A Approved | 925000 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | East Winstonville |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP22 | A | COOPERATIVE ENERGY | South | 22345 | East Winstonville Delivery Point | Other | 26775 | 26775-East Winstonville- | Tap the Energy owned Delta SES - Shelby 115kV line with switching station and build a 115kV line to the new member East Winstonville delivery point. | Entergy-MS | M2 - Appendix A Approved | 877800 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | East Winstonville |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP22 | A | AMEREN ILLINOIS | Central | 22385 | New Dion 345 kV Ring Bus for J1115 Greenswitch Wind | GIP | 26778 | 26778-Dion- | The Dion switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Latham-Oreana 345 kV transmission line will be cut. | AmerenIL | M2 - Appendix A Approved | 9500000 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | Dion |  |  | 345 |  |  |  | IL |  | Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 19950 | New St. David-Wee-Ma-Tuk-Canton 69 kV line | Other | 25633 | New St. David-Canton 69 kV line | New St. David-Canton 336 ACSR 69 kV line in SREC. | PPI | M3 - Under Construction | 3196000 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | St David | Canton | 1 | 69 |  | 4.5 | 1 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 19952 | Rebuild Walkerville-Eldred 69 kV line | Other | 25635 | Rebuild Walkerville-Eldred 69 kV line | Rebuild Walkerville-Eldred 69 kV line with 336 ACSR | PPI | M3 - Under Construction | 3942000 | 2026-05-01 | Line Upgrade | Line rebuild on existing ROW | Walkerville | Eldred |  | 69 |  |  | 7.3 | IL |  | Not Shared
MTEP22 | A | PRAIRIE POWER, INC. | Central | 21794 | New Forest City 138/69 kV Substation | BRP | 51442 | New Ameren Winnabago-Forest City 138 kV Line | New Ameren Winnabago-Forest City 138 kV Line with 795 ACSR |  | M2 - Appendix A Approved | 200000 | 2028-03-01 | Line New | New Transmission line, new ROW - may include terminations | Winnabago | Forest City |  | 138 |  | 0.1 | 0 | IL |  | Not Shared
MTEP22 | A | ITC | East | 21166 | Maple - J1062 Generator Interconnection | GIP | 51646 | Maple-Majestic - J1062 NU - Install OPGW | Install OPGW on the Maple-Majestic 345 kV line |  | M2 - Appendix A Approved | 4000000 | 2026-07-22 | Line Upgrade | Line rebuild on existing ROW | Maple | Majestic |  | 345 |  |  |  | MI |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 18066 | Badoura 115kV Substation Modernization | Other | 24901 | 24901-Badoura- | Replace existing circuit breaker & associated equipment | MP | M2 - Appendix A Approved | 0 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Badoura |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 18066 | Badoura 115kV Substation Modernization | Other | 24903 | 24903-Badoura- | Add two breakers in existing ring bus to accommodate relocated lines. Also includes new relay panels. | MP | M2 - Appendix A Approved | 750000 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Badoura |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 18889 | Rebuild Hickok-North LaSalle 138 kV line (1659) | BRP | 25339 | 25339-Hickok-North LaSalle | Rebuild to 2000A | AmerenIL | M2 - Appendix A Approved | 6500000 | 2029-06-01 | Line Upgrade | Line rebuild on existing ROW | Hickok | North LaSalle | 1659 | 138 |  |  |  | IL |  | Not Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 19025 | New J815 Hickory Point Wind Generator Interconnection (Yvonne 138 kV switching Station) | GIP | 25370 | 25370-Yvonne- | New station for Hickory Point Wind Generator J815 | AmerenIL | M2 - Appendix A Approved | 6600000 | 2026-06-01 | Substation | Switching station (breakers only, no transformer) | Yvonne |  |  | 138 |  |  |  | IL |  | Not Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 19026 | New J912 Christian County Solar Generator Interconnection (Pana 138 kV switching station) | GIP | 25371 | 25371-Pana- | New position for J912 | AmerenIL | M2 - Appendix A Approved | 900000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Pana |  |  | 138 |  |  |  | IL |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 19165 | Fieldon Retirement | Other | 25413 | 25413-Fieldon- | Removes the existing Fieldon substation and series capacitor. | XEL | M2 - Appendix A Approved | 1000000 | 2026-02-27 | Substation | Substation (breakers only, no transformer) | Fieldon |  |  | 345 |  |  |  | MN |  | Not Shared
MTEP21 | A | ITC | East | 20132 | Pontiac 303 Transformer Replacement | Other | 25838 | 25838-Pontiac- | Replace Pontiac 303 345/120kV Transformer. | ITCT | M2 - Appendix A Approved | 4800000 | 2026-12-31 | Transformer | Transformer New | Pontiac |  |  | 345 | 120 |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 20133 | Hines 201 Transformer Replacement | Other | 25839 | 25839-Hines- | Replace the Hines 201 230/120kV transformer | ITCT | M2 - Appendix A Approved | 5870000 | 2026-06-03 | Transformer | Transformer New | Hines |  |  | 230 | 120 |  |  | MI |  | Not Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 20135 | Panther - Big Swan Rebuild | Other | 25841 | 25841-Adams Wind Tap- | Convert Adams Wind Tap to a breaker station with 2 breakers and 1 MOD | XEL | M2 - Appendix A Approved | 2700000 | 2029-09-16 | Substation | Switching station (breakers only, no transformer) | Adams Wind Tap |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 20135 | Panther - Big Swan Rebuild | Other | 25845 | 25845-Panther-Big Swan | Rebuild Line to 477ACSR for age and condition and to support Adams wind upgrade | XEL | M2 - Appendix A Approved | 31200000 | 2029-09-16 | Line Upgrade | Line rebuild on existing ROW | Panther | Big Swan | 1 | 69 |  |  |  | MN |  | Not Shared
MTEP21 | A | METC | East | 20144 | Argenta 2 Transformer Replacement | Other | 25848 | 25848-Argenta- | Replace the Argenta #2 345/138kV transformer. | METC | M3 - Under Construction | 7994000 | 2026-07-15 | Transformer | Transformer New | Argenta |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20145 | Tallmadge 2 Transformer Replacement | Other | 25849 | 25849-Tallmadge- | Replace the Tallmadge #2 345/138kV transformer. | METC | M2 - Appendix A Approved | 6100000 | 2027-09-10 | Transformer | Transformer New | Tallmadge |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 20148 | Appleton - Benson (AG-AB) 115 kV Line | Other | 25853 | 25853-Appleton-Benson | Construct about 27 miles of 115 kV transmission line from Appleton to GRE’s AG-BK line and about 1.75-mile 115 kV transmission line from AG-BK line to Benson Muni substation with associated tap switch, distribution sub, and retirement projects. | GRE | M2 - Appendix A Approved | 32574591 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Appleton | Benson | 1 | 115 |  | 26 |  | MN |  | Not Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 20148 | Appleton - Benson (AG-AB) 115 kV Line | Other | 25854 | 25854-Benson-Benson Muni | Build 2 miles of new 115 kV transmission line from end of GRE ownership of Appleton to Benson to Benson Muni and two new 115 kV breakers. | MRES | M2 - Appendix A Approved | 9284688 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Benson | Benson Muni | 1 | 115 |  | 2 |  | MN |  | Not Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 20148 | Appleton - Benson (AG-AB) 115 kV Line | Other | 25856 | 25856-Appleton- | Rebuild Appleton Substation from line breaker to a 4 position ring bus with 25 MVAR cap bank on the Appleton to Benson 115 kV line. | MRES | M2 - Appendix A Approved | 12750000 | 2029-12-31 | Substation | Switching station (breakers only, no transformer) | Appleton |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 25861 | 25861-Denver-Waverly | Rebuild 69 kV Denver to Waverly Junction line due to condition and to improve reliability. | MEC | M4 - Project in Service | 7200000 | 2021-12-31 | Line Upgrade | Line rebuild on existing ROW | Denver | Waverly | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 25862 | 25862-Sub G-GRS Tap 69 kV Line Rebuild | Rebuild 69 kV lines due to condition an to improve reliability. | MEC | M2 - Appendix A Approved | 2100000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Sub G | GRS Tap | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 25863 | 25863-Otley-West Pella | Rebuild 69 kV Monroe - Otley - W. Pella REC 69 kV line | MEC | M4 - Project in Service | 3900000 | 2024-04-20 | Line Upgrade | Line rebuild on existing ROW | Otley | West Pella |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Other | 25864 | 25864-Humboldt East/Humboldt Central- | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | MEC | M2 - Appendix A Approved | 1000000 | 2029-12-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Humboldt East/Humboldt Central |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Other | 25865 | 25865-Sub Fort Dodge M- | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | MEC | M4 - Project in Service | 800000 | 2023-04-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sub Fort Dodge M |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Other | 25868 | 25868-Raun- | New control cable entrance and cable trench replacement. | MEC | M2 - Appendix A Approved | 5000000 | 2028-12-31 | Substation | Small miscellaneous substation equipment | Raun |  |  | 345 | 161 |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Other | 25869 | 25869-Council Bluffs- | Replace 9T1 differential relaying | MEC | M4 - Project in Service | 800000 | 2023-01-04 | Misc. | Relaying, protection, RTU and SCADA equipment | Council Bluffs |  |  | 345 | 161 |  |  | IA |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25885 | 25885-Claremont- | rebuild Claremont 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | METC | M2 - Appendix A Approved | 17500000 | 2028-12-29 | Substation | Switching station (breakers only, no transformer) | Claremont |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25886 | 25886-Grey Iron-Claremont | Redirect Grey Iron - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 530000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Grey Iron | Claremont |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25887 | 25887-Holland Road-Claremont | Redirect Holland Road - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 530000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Holland Road | Claremont | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25888 | 25888-Manning #1-Claremont | Redirect Manning #1 - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 530000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Manning #1 | Claremont | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25889 | 25889-Manning #2-Claremont | Redirect Manning #2 - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 535000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Manning #2 | Claremont | 2 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25890 | 25890-Cornell #1-Claremont | Redirect Cornell #1 - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 440000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Cornell #1 | Claremont | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25891 | 25891-Cornell #2-Claremont | Redirect Cornell #2 - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 444000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Cornell #2 | Claremont | 2 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25892 | 25892-Lawndale-Claremont | Redirect Lawndale - Claremont 138 kV line from Claremont into the new station | METC | M2 - Appendix A Approved | 448000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Lawndale | Claremont |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25893 | 25893-Claremont (CE TB#1)-New Station | Redirect Claremont TB1 from Claremont into the new station | METC | M2 - Appendix A Approved | 495000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Claremont (CE TB#1) | New Station | TB1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 25894 | 25894-Claremont (CE TB#3)-New Station | Redirect Claremont TB3 from Claremont into the new station | METC | M2 - Appendix A Approved | 475000 | 2028-12-29 | Line New | New Transmission line, new ROW - may include terminations | Claremont (CE TB#3) | New Station | TB3 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 25895 | 25895-Sub Fort Dodge M- | 161 kV breaker replacements to increase reliability and operational flexibility. | MEC | M4 - Project in Service | 4000000 | 2023-04-01 | Substation | Circuit Breaker (replacement at existing substation) | Sub Fort Dodge M |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 25896 | 25896-Lehigh- | Replace Lehigh 345 kV breaker to increase reliability and operational flexibility. | MEC | M4 - Project in Service | 300000 | 2021-06-09 | Substation | Circuit Breaker (replacement at existing substation) | Lehigh |  |  | 345 |  |  |  | IA |  | Not Shared
MTEP21 | A | ITC | East | 20167 | Cato – Corktown 120 kV | Other | 25898 | 25898-Cato-Corktown | Build approximately 0.85 miles of 120kV 1600mm² underground cable from Cato to Corktown. Include underground direct fiber through conduit | ITCT | M2 - Appendix A Approved | 17000000 | 2027-10-01 | Line New | New Transmission line, new ROW - may include terminations | Cato | Corktown | 1 | 120 |  | 0.85 |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 20167 | Cato – Corktown 120 kV | Other | 25900 | 25900-Corktown- | Install bus 104, standard 3000A breakers JC and HT, and associated disconnects and line switch. All breakers at Corktown to have interrupting capability of at least 50kA | ITCT | M2 - Appendix A Approved | 8200000 | 2027-06-01 | Substation | Switching station (breakers only, no transformer) | Corktown |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 20167 | Cato – Corktown 120 kV | Other | 25901 | 25901-Cato- | Upgrade Cato to a 4 breaker ring bus to accommodate a third line termination. Install 3 standard 3000A breakers, associated disconnect switches and line switches. All breakers at Cato to have interrupting capability of at least 50kA | ITCT | M2 - Appendix A Approved | 14800000 | 2029-05-30 | Substation | Switching station (breakers only, no transformer) | Cato |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | Central Minnesota Municipal Power Agency | West | 20168 | Delano_Municipal_Utilities_Substation_B_Transformer_Upgrade | Other | 25902 | 25902-Delano 8- | Delano is planning to replace substation B transformer with new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. This solution also includes a new fire wall between the new transformers and additional distribution feeders for load transfer. | CMMPA | M3 - Under Construction | 638500 | 2025-11-15 | Transformer | Transformer New | Delano 8 |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP21 | A | Central Minnesota Municipal Power Agency | West | 20169 | Delano_Municipal_Utilities_New_69_kV_Industrial_Park_Substation | Other | 25903 | 25903-DELANO 8- | Delano is planning to build a new 69kV substation to serve expected residential and future industrial park load growth on the NW side of the city. | CMMPA | M3 - Under Construction | 4100000 | 2026-07-01 | Substation | Substation (breakers only, no transformer) | DELANO 8 |  |  | 69 |  |  |  | MN |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25905 | 25905-Wealthy Street- | Rebuild Wealthy Street 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | METC | M2 - Appendix A Approved | 17000000 | 2028-04-24 | Substation | Switching station (breakers only, no transformer) | Wealthy Street |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25906 | 25906-Beals Road-New Station | Redirect Beals Road - Wealthy Street 138 kV line from Wealthy Street into the new station | METC | M2 - Appendix A Approved | 1100000 | 2028-04-24 | Line New | New Transmission line, new ROW - may include terminations | Beals Road | New Station | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25907 | 25907-Tallmadge-New Station | Redirect Tallmadge - Wealthy Street #1 138 kV line from Wealthy Street into the new station | METC | M2 - Appendix A Approved | 495000 | 2028-04-24 | Line New | New Transmission line, new ROW - may include terminations | Tallmadge | New Station | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25908 | 25908-Tallmadge-New Station | Redirect Tallmadge - Wealthy Street #2 138 kV line from Wealthy Street into the new station | METC | M2 - Appendix A Approved | 495000 | 2028-04-24 | Line New | New Transmission line, new ROW - may include terminations | Tallmadge | New Station | 2 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25909 | 25909-Northridge-New Station | Redirect Four Mile (Northridge) - Wealthy Street #1 138 kV line from Wealthy Street into the new station | METC | M2 - Appendix A Approved | 1250000 | 2028-04-24 | Line New | New Transmission line, new ROW - may include terminations | Northridge | New Station | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25910 | 25910-Wealthy Street CE TB#6-New Station | Wealthy Street TB6 from Wealthy Street into the new station | METC | M2 - Appendix A Approved | 830000 | 2028-04-24 | Line New | New Transmission line, new ROW - may include terminations | Wealthy Street CE TB#6 | New Station | TB6 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 25911 | 25911-Wealthy Street CE TB#7-New Station | Wealthy Street TB7 from Wealthy Street into the new station | METC | M2 - Appendix A Approved | 830000 | 2028-04-24 | Line New | New Transmission line, new ROW - may include terminations | Wealthy Street CE TB#7 | New Station | TB7 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 26037 | 26037-Raisin Tap-Raisin | Install approximately 7.3 miles of OPGW on the Raisin Tap - Raisin Substation line segment. | METC | M4 - Project in Service | 1445000 | 2023-05-19 | Misc. | Communication equipment | Raisin Tap | Raisin |  | 138 |  |  | 7.3 | MI |  | Shared
MTEP21 | A | ENTERGY SERVICES, LLC. | South | 20628 | J1158 Generator Interconnection at Vacherie 230 kV | GIP | 26061 | 26061-Vacherie 230 kV- | This construction at the existing Vacherie 230 kV substation is to accommodate the interconnection of a solar facility (J1158) | Entergy-LA | M2 - Appendix A Approved | 40000 | 2026-12-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Vacherie 230 kV |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 20136 | Pine Lake to Dunn Ethanol N4 Rebuild | Other | 26085 | 26085-Pine Lake-Dunn Ethanol | This project is a mix of a rebuild of DPC’s existing 69 kV line in the area and construction on new right-of-way. The recommended plan in this area is to construct new transmission line with 477 ACSR conductor, a mix of replacement of existing line and new right-way from XEL’s Pine Lake transmission substation to the east towards the Dunn Ethanol distribution substation. The recommended plan will address the age and condition issues, constructing the line with new poles and 477 ACSR conductor. The plan will also address the longer tap lines to distribution substations with individual taps to all five distribution substations served from this line. Finally, building to the Dunn Ethanol distribution substation will provide backup service. | DPC | M3 - Under Construction | 13051780 | 2027-02-15 | Line Upgrade | Line rebuild on existing ROW | Pine Lake | Dunn Ethanol | 1 | 69 |  | 0.58 | 22.15 | WI |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | Other | 26087 | 26087-Monona-Postville | Monona-Postville line work | ITCM | M2 - Appendix A Approved | 709827 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | Monona | Postville | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | Other | 26088 | 26088-Monona-Lansing | Monona-Lansing line work | ITCM | M2 - Appendix A Approved | 823827 | 2025-09-30 | Line New | New Transmission line, new ROW - may include terminations | Monona | Lansing | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | Other | 26089 | 26089-Monona-Turkey River | Monona-Turkey River line work | ITCM | M2 - Appendix A Approved | 805827 | 2025-09-30 | Line New | New Transmission line, new ROW - may include terminations | Monona | Turkey River | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | Other | 26090 | 26090-Monona-Ckt 432 | Monona Circuit 432 line work | ITCM | M2 - Appendix A Approved | 739827 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | Monona | Ckt 432 | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | Other | 26091 | 26091-Monona-IPL dist customer | Radial line to IPL distribution customer. | ITCM | M2 - Appendix A Approved | 541827 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | Monona | IPL dist customer | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 18066 | Badoura 115kV Substation Modernization | Other | 26107 | 26107-Badoura-Dog Lake | Relocate 40 Line to ring bus in new substation (deadend outside substation) | MP | M2 - Appendix A Approved | 580000 | 2025-12-31 | Misc. | Line relocation (road move) | Badoura | Dog Lake |  | 115 |  | 0.1 | 0 | MN |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 18066 | Badoura 115kV Substation Modernization | Other | 26108 | 26108-Badoura-Hubbard | Relocate existing 48 Line into ring bus in new yard (deadend outside yard). NOTE: winter ratings increased. | MP | M2 - Appendix A Approved | 490000 | 2025-12-31 | Misc. | Line relocation (road move) | Badoura | Hubbard |  | 115 |  | 0.1 | 0 | MN |  | Not Shared
MTEP21 | A | METC | East | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Other | 26854 | Thetford_New Relay Panels | Remove existing wave trap and tuner on line. Add new relay panel. | METC | M3 - Under Construction | 223000 | 2027-05-14 | Misc. | Relaying, protection, RTU and SCADA equipment | Thetford |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Other | 26855 | Hampton_Add fiber jumpers | Install jumpers between Atlanta and Thetford for Atlanta-Thetford line relaying. | METC | M3 - Under Construction | 92000 | 2027-05-14 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Hampton |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Other | 26856 | Karn_New Relay Panels | Remove existing wave trap and tuner on line. Add new relay panel. | METC | M3 - Under Construction | 294000 | 2027-05-14 | Misc. | Relaying, protection, RTU and SCADA equipment | Karn |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 20107 | Atlanta-Karn-Thetford Split & Station Reconfiguration (ITCT) | Other | 26857 | Bauer_Add fiber jumpers | Install jumpers between Atlanta and Thetford for Atlanta-Thetford line relaying. Install additional fiber and 10G SFP to connect Bauer Nokia to Atlanta | ITCT | M3 - Under Construction | 115000 | 2027-05-14 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Bauer |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 26940 | 26940-Monroe-Otley | 69 kV rebuild | MEC | M4 - Project in Service | 7500000 | 2024-02-16 | Line Upgrade | Line rebuild on existing ROW | Monroe | Otley |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 3439 | New Ensor 161/69 kV Substation | BRP | 6342 | 6342-Ensor 161 kV-Ensor 69 kV | new substation | BREC | M2 - Appendix A Approved | 5400000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Ensor 161 kV | Ensor 69 kV |  | 161 | 69 |  |  | KY |  | Not Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 25531 | 25531-Tangent- | Install a new 138 kV station with 3-138kV 40KAIC breakers and associated disconnects in a ring bus configuration. | METC | M4 - Project in Service | 6358229 | 2023-12-21 | Substation | Substation (breakers only, no transformer) | Tangent |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 25532 | 25532-Parr Road-Whiting | Loop the Parr Road - Whiting 138kV circuit into the new METC 138kV Tangent station. | METC | M4 - Project in Service | 801901 | 2023-12-21 | Line Upgrade | Generic transmission line project (try not to use the generic) | Parr Road | Whiting |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 25533 | 25533-Parr Road- | Install required relay upgrades at Parr Rd to interconnect J875 | METC | M3 - Under Construction | 1115000 | 2027-05-14 | Substation | Small miscellaneous substation equipment | Parr Road |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 25534 | 25534-Whiting- | Install required relay upgrades at Whiting to interconnect J875 | METC | M4 - Project in Service | 355386 | 2023-12-21 | Substation | Small miscellaneous substation equipment | Whiting |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 25535 | 25535-Leoni- | Install required relay upgrades at Leoni to interconnect J875 | METC | M4 - Project in Service | 642000 | 2024-02-16 | Substation | Small miscellaneous substation equipment | Leoni |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 25536 | 25536-Leoni-Parr Road, Tangent, and Whiting | Install approximately 12.5 miles of underground fiber optic for the Parr Road - Tangent 138kV circuit. Install approximately 30 miles of underground fiber optic for the Tangent - Whiting 138kV circuit. Install approximately 18.5 miles of underground fiber optic for the Leoni - Parr Road 138kV circuit. | METC | M4 - Project in Service | 3865459 | 2023-12-21 | Misc. | Communication equipment | Leoni | Parr Road, Tangent, and Whiting |  | 138 |  |  | 61 | MI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25549 | 25549-Superior SS- | Network Upgrades | ATC | M2 - Appendix A Approved | 15621555 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Superior SS |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25550 | 25550-Arrowhead SS-Stone Lake SS | Line 651/W25 Loop into Superior SS | ATC | M2 - Appendix A Approved | 1796413 | 2029-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Arrowhead SS | Stone Lake SS | 651 | 345 |  |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25551 | 25551-Stone Lake SS- | Stone Lake SS Relay Upgrades | ATC | M2 - Appendix A Approved | 423319 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Stone Lake SS |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25552 | 25552-Arrowhead SS- | Arrowhead SS Relay Upgrades | ATC | M2 - Appendix A Approved | 535063 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Arrowhead SS |  |  | 345 | 230 |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25553 | 25553-Stone Lake SS- | Grounding Improvements | ATC | M2 - Appendix A Approved | 419936 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Stone Lake SS |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25554 | 25554-Arrowhead SS- | Grounding Improvements | ATC | M2 - Appendix A Approved | 1291386 | 2029-12-31 | Substation | Small miscellaneous substation equipment | Arrowhead SS |  |  | 345 | 230 |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | GIP | 25555 | 25555-Superior SS- | Interconnection Facilities | ATC | M2 - Appendix A Approved | 1157933 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Superior SS |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP21 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 3439 | New Ensor 161/69 kV Substation | BRP | 25559 | 25559-Ensor- | add capacitor at proposed substation | BREC | M2 - Appendix A Approved | 400000 | 2029-12-31 | Voltage Device | Capacitor (switched capacitor) | Ensor |  |  | 69 |  |  |  | KY |  | Not Shared
MTEP21 | A | GRIDLIANCE HEARTLAND LLC | Central | 19746 | Rebuild Joppa-Shawnee 161 kV line Ckt 2 | Other | 25560 | 25560-Joppa-Shawnee | Rebuild 6.4 miles of 161 kV line Joppa- Shawnee ckt 2. | GLH | M2 - Appendix A Approved | 11000000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Joppa | Shawnee | 2 | 161 |  |  | 6.4 | IL | KY | Not Shared
MTEP21 | A | CITY OF COLUMBIA, MISSOURI (WATER AND LIGHT DEPT.) | Central | 19805 | New UMC 69 kV Substation | Other | 25566 | 25566-Grindstone 69 kV-UMC 69 kV | Build a new substation with a 69/13.8 kV transformer at UMC. Build a new 69 kV ringbus at UMC. Disconnect Grindstone-Hinkson Creek (HC) 69 kV line at HC and connect it to new UMC ringbus. | CWLD | M2 - Appendix A Approved | 26000000 | 2029-09-01 | Line New | New Transmission line, new ROW - may include terminations | Grindstone 69 kV | UMC 69 kV | 1 | 69 | 14 |  |  | MO |  | Not Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 19806 | Bonnie Road SS, DIC, New Substation | Other | 25567 | 25567-Bonnie Road SS- | New substation DIC | ATC | M2 - Appendix A Approved | 3500000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Bonnie Road SS |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19847 | New Golden 138/69 kV Substation | Other | 25576 | New Golden 138/69 kV Substation | New Golden 138/69 kV Substation near Golden, IL | PPI | M2 - Appendix A Approved | 6625000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Golden |  | 1 | 138 | 69 |  |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19848 | New Camden-Rushville 69 kV Line | Other | 25577 | New Camden-Rushville 69 kV Line | New Camden-Rushville 69 kV Line in AEC | PPI | M3 - Under Construction | 7680000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Camden | Rushville | 1 | 69 | 69 | 12 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19849 | New Rushville-Sugar Grove 69 kV Line | Other | 25578 | New Rushville-Sugar Grove 69 kV Line | New Rushville-Sugar Grove 69 kV Line in AEC | PPI | M3 - Under Construction | 8448000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Rushville | Sugar Grove | 1 | 69 | 69 | 13 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19850 | New Sugar Grove - Mt. Sterling 69 kV Line | Other | 25579 | New Sugar Grove-Mt. Sterling 69 kV line | New Sugar Grove-Mt. Sterling 69 kV line with 556 ACSR in AEC | PPI | M2 - Appendix A Approved | 5548800 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Sugar Grove | Mt. Sterling | 1 | 69 |  | 8.5 |  | IL |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19925 | Albia-Melrose 69kV Rebuild | Other | 25607 | 25607-Albia-Melrose | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. The line between the Albia and Melrose substations (~17.25 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | ITCM | M2 - Appendix A Approved | 16293244 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Albia | Melrose | 1 | 69 | 69 |  | 17.25 | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19926 | Osceola North-Woodburn Jct 69kV Rebuild | Other | 25608 | 25608-Osceola North-Osceola REC | Osceola N-Woodburn Jct 69kV Rebuild | ITCM | M2 - Appendix A Approved | 4248000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Osceola North | Osceola REC | 1 | 69 | 69 |  | 3.99 | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19926 | Osceola North-Woodburn Jct 69kV Rebuild | Other | 25609 | 25609-Osceola REC-Woodburn Jct | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. The line between the Osceola North, Osceola Rec, and Woodburn Jct. substations (~9.57 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | ITCM | M2 - Appendix A Approved | 4716000 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Osceola REC | Woodburn Jct | 1 | 69 | 69 |  | 5.58 | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19928 | Marion-Old Settlers 115kV Ckt#2 | Other | 25611 | 25611-Old Settlers-115kV Bus K1 | ITC will install an additional 115kV breaker on Bus K1 at Old Settlers. All new terminal equipment will be capable of 2000A minimum. | ITCM | M2 - Appendix A Approved | 878438 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Old Settlers | 115kV Bus K1 |  | 115 | 115 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19928 | Marion-Old Settlers 115kV Ckt#2 | Other | 25612 | 25612-Marion-115kV Bus K2 | ITC will install an additional 115kV breaker on Bus K2 at Marion. All new terminal equipment will be capable of 2000A minimum. | ITCM | M2 - Appendix A Approved | 1128140 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Marion | 115kV Bus K2 |  | 115 | 115 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19928 | Marion-Old Settlers 115kV Ckt#2 | Other | 25615 | 25615-Marion-Old Settlers | ITC will rebuild the existing ~0.5 mi tap into Old Settlers double circuit with T2-477. These circuits will be terminated into the new positions at Marion and Old Settlers using T2-477. | ITCM | M2 - Appendix A Approved | 1890000 | 2027-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Marion | Old Settlers |  | 115 | 115 |  | 0.5 | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19928 | Marion-Old Settlers 115kV Ckt#2 | Other | 25616 | 25616-Dry Creek-Old Settlers | Reterminate Dry Creek - Old Settlers 115kV circuit into new position at Old Settlers using T2-477 | ITCM | M2 - Appendix A Approved | 336000 | 2027-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Dry Creek | Old Settlers |  | 115 | 115 |  |  | IA |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19851 | New Mt. Sterling - Kellerville 69 kV Line | Other | 25618 | New Mt. Sterling-Kellerville 69 kV line | New Mt. Sterling-Kellerville 69 kV line with 556 ACSR in AEC | PPI | M2 - Appendix A Approved | 13585000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Mt. Sterling | Kellerville |  | 69 |  | 21 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19932 | New Disco-Lomax 69 kV Line | Other | 25619 | New Disco-Lomax 69 kV Line | New Disco-Lomax 69 kV Line in WIEC | PPI | M2 - Appendix A Approved | 9862500 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Disco | Lomax | 1 | 69 | 69 | 15 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19933 | New Disco-Powellton 69 kV Line | Other | 25620 | New Disco-Powellton 69 kV Line | New Disco-Powellton 69 kV Line in WIEC | PPI | M2 - Appendix A Approved | 8000000 | 2026-06-30 | Line New | New Transmission line, new ROW - may include terminations | Disco | Powellton | 1 | 69 | 69 | 12.5 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19934 | Add Elvaston 69 kV Breakers | Other | 25621 | Add 2 Elvaston 69kV Breakers | Add breakers on the Elvaston-Powellton line and the Elvaston - Sutter line | PPI | M2 - Appendix A Approved | 350000 | 2026-12-01 | Substation | Small miscellaneous substation equipment | Elvaston |  | 1 | 69 |  |  |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19935 | New Sutter - Ursa 69 kV Line | Other | 25622 | New Sutter-Ursa 69 kV line | New Sutter-Ursa 69 kV line between WIEC and AEC | PPI | M2 - Appendix A Approved | 13312000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Sutter | Ursa | 1 | 69 |  | 21 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19937 | New Wolf Run 69 kV Breaker Station | Other | 25624 | New Wolf Run 69 kV Breaker Station | New Wolf Run 69 kV Breaker Station | PPI | M3 - Under Construction | 2844450 | 2026-06-01 | Substation | Switching station (breakers only, no transformer) | Wolf Run |  | 1 | 69 | 69 |  |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19940 | Upgrade Grand Island 138/69 kV Transformer | Other | 25627 | Upgrade Grand Island 138/69 kV Transformer | Upgrade Grand Island Delta-Wye 138/69 kV Transformer with Wye-Wye | PPI | M2 - Appendix A Approved | 1500000 | 2027-12-01 | Transformer | Transformer Replacement | Grand Island |  | 1 | 138 | 69 |  |  | IL |  | Not Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 28033 | 28033-345kV deadend structure-161kV structure outside Alma Substation | Replace existing DPC single circuit 69kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 69kV. Replace existing 69kV conductor, insulators, and hardware. | DPC | M2 - Appendix A Approved | 4000000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | 345kV deadend structure | 161kV structure outside Alma Substation |  | 345 | 69 |  | 1 | WI |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 28034 | 28034-345kV deadend structure-161kV structure outside Alma Substation | Install new 345kV conductor, insulators, and hardware on replaced transmission line structures. | DAIRYLAND POWER COOPERATIVE | M2 - Appendix A Approved | 414242 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | 345kV deadend structure | 161kV structure outside Alma Substation |  | 345 | 69 |  | 1 | WI |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 28035 | 28035-161kV structure outside Alma Substation-Tremval | Replace existing DPC single circuit 161kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 161kV. Replace existing 161kV conductor, insulators, and hardware. | DPC | M2 - Appendix A Approved | 156000000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | 161kV structure outside Alma Substation | Tremval |  | 345 | 161 |  | 34 | WI |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 28036 | 28036-161kV structure outside Alma Substation-Tremval | Install new 345kV conductor, insulators, and hardware on replaced transmission line structures. | DAIRYLAND POWER COOPRATIVE | M2 - Appendix A Approved | 7946316 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | 161kV structure outside Alma Substation | Tremval |  | 345 | 161 |  | 34 | WI |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23415 | LRTP-13: Coddington – Ipava | MVP | 28037 | 28037-IA/IL State Border -Mississippi River-Ipava | Replace existing ITCM 69/161kV structures with triple circuit structures with 1 circuit operated at 345kV, 1 circuit operated at 161kV, and 1 circuit operated at 69kV for approximately 2 miles. Replace existing 69kV and 161kV conductor, insulators, and hardware on replaced ITCM structures. Replace existing Ameren-IL 138kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 138 kV for approximately 67 miles. Replace existing 138kV conductor, insulators, and hardware on replaced AmerenIL structures. | AmerenIL, ITCM | M2 - Appendix A Approved | 281600000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | IA/IL State Border -Mississippi River | Ipava |  | 345 | 69 |  | 69 | IL |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23415 | LRTP-13: Coddington – Ipava | MVP | 28038 | 28038-IA/IL State Border -Mississippi River-Ipava | Install new 345kV conductor, insulators, and hardware on replaced transmission line structures. | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 19814315 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | IA/IL State Border -Mississippi River | Ipava |  | 345 | 138 |  | 69 | IL |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 28039 | 28039-Columbia- | Bus-connected 345kV, 80MVAr reactor | ATC | M2 - Appendix A Approved | 13000000 | 2030-12-31 | Voltage Device | Reactor or Inductor | Columbia |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 24604 | 24604-Magee Road SS-Olive Oil | Add OPGW to L576 (Magee Road SS - Olive Oil) | Entergy-MS | M2 - Appendix A Approved | 301000 | 2027-03-01 | Misc. | Communication equipment | Magee Road SS | Olive Oil |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15848 | Jayess Loop Project | Other | 25217 | 25217-Norfield- | Entergy - Transmission line adjustments for Norfield and Jayess switching stations. | Entergy-MS | M2 - Appendix A Approved | 3300000 | 2027-03-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Norfield |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 25218 | 25218-Arlington- | Entergy - Transmission line adjustments for Arlington switching station. | Entergy-MS | M2 - Appendix A Approved | 1700000 | 2027-03-01 | Line Upgrade | Generic transmission line project (try not to use the generic) | Arlington |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 18605 | New Hardinsburg 161kV Substation (J753) for solar Interconnection | GIP | 25232 | 25232-Hardinsburg- | 100 MW solar per J753 | BREC | M2 - Appendix A Approved | 0 | 2026-06-01 | Misc. | Generator | Hardinsburg |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP21 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 18605 | New Hardinsburg 161kV Substation (J753) for solar Interconnection | GIP | 25233 | 25233-Hardinsburg- | Terminal equipment necessary to connect 100 MW solar facility J753 | BREC | M2 - Appendix A Approved | 200000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Hardinsburg |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 20925 | Lancaster Transformer Replacement & Substation Rebuild | Other | 26116 | Lancaster Transformer Replacement & Substation Rebuild | Lancaster Transformer Replacement & Substation Rebuild | ATC | M3 - Under Construction | 6200000 | 2026-02-28 | Substation | Substation (breakers only, no transformer) | Lancaster SS |  |  | 138 | 69 |  |  | WI |  | Not Shared
MTEP21 | A | ITC | East | 21105 | Apollo Interconnection | Other | 26138 | 26138-Hunters Creek-Lapeer | Cut in the ITCT Hunters Creek-Lapeer line to the new in-and-out station. | ITCT | M2 - Appendix A Approved | 12446400 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Hunters Creek | Lapeer |  | 120 |  | 4 |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21105 | Apollo Interconnection | Other | 26139 | 26139-Lapeer- | Upgrade remote end protection and control at Lapeer. | ITCT | M2 - Appendix A Approved | 301538 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Lapeer |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21105 | Apollo Interconnection | Other | 26140 | 26140-Hunters Creek- | Upgrade remote end protection and control at Lapeer. | ITCT | M2 - Appendix A Approved | 330632 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Hunters Creek |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21105 | Apollo Interconnection | Other | 26141 | 26141-Apollo- | Construct a new in-and-out station. Install one 120 kV tie breaker, two 120 kV line breakers, buswork, and associated disconnects. | ITCT | M2 - Appendix A Approved | 4068682 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | Apollo |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26168 | 26168-Shrine- | Construct a new 120kV station with two 40kA line breakers and one 40kA section breaker. | ITCT | M3 - Under Construction | 5795921 | 2027-03-31 | Substation | Substation (breakers only, no transformer) | Shrine |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26169 | 26169-Lenox-Stephens | Extend the Lenox - Stephens 120kV line by adding about 1 mile of 954 ACSR DCT to loop in the new station. | ITCT | M3 - Under Construction | 6943463 | 2027-03-31 | Line New | New Transmission line, new ROW - may include terminations | Lenox | Stephens |  | 120 |  | 2 |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26170 | 26170-Lenox- | Upgrade Lenox position HS relaying. | ITCT | M3 - Under Construction | 356535 | 2027-03-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Lenox |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26171 | 26171-Stephens- | Upgrade Stephens position HS relaying | ITCT | M3 - Under Construction | 777494 | 2027-03-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Stephens |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26172 | 26172-Bismarck- | Install Fiber patch Panels | ITCT | M3 - Under Construction | 159922 | 2027-03-31 | Substation | Small miscellaneous substation equipment | Bismarck |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26173 | 26173-Jewell- | Install fiber patch panels | ITCT | M3 - Under Construction | 20068 | 2027-03-31 | Substation | Small miscellaneous substation equipment | Jewell |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Other | 26175 | 26175-Bismarck-Golf | install fiber from the new station to Bismarck along the Bismarck - Golf line | ITCT | M3 - Under Construction | 3631436 | 2027-03-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Bismarck | Golf |  | 120 |  |  | 4.5 | MI |  | Not Shared
MTEP21 | A | CLECO POWER LLC | South | 21207 | Slidell Airport Line Move | Other | 26185 | 26185-North Slidell-Tailsheek | Move transmission line for Airport Expansion | CLECO | M2 - Appendix A Approved | 5300000 | 2026-06-01 | Misc. | Line relocation (road move) | North Slidell | Tailsheek | 1 | 230 |  |  |  | LA |  | Not Shared
MTEP21 | A | CLECO POWER LLC | South | 21207 | Slidell Airport Line Move | Other | 26186 | 26186-North Slidell-Cane Bayou | Line move for Airport Expansion | CLECO | M2 - Appendix A Approved | 4500000 | 2026-06-01 | Misc. | Line relocation (road move) | North Slidell | Cane Bayou | 1 | 230 |  |  |  | LA |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26187 | 26187-Clinton Tap-Eaton Rapids | Rebuild line from Clinton Tap to Eaton Rapids | WPSC | M2 - Appendix A Approved | 10450000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Clinton Tap | Eaton Rapids |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26188 | 26188-Eaton Rapids- | Eaton Rapids 128kV BUS | WPSC | M2 - Appendix A Approved | 200000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Eaton Rapids |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26189 | 26189-Vermontville- | 138kV BUS at Vermontville Additional line mods required in conjunction with the planned relocation of the Vermontville distribution station, redesign and install new line exits | WPSC | M2 - Appendix A Approved | 2200000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Vermontville |  |  | 138 |  | 0.5 |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26190 | 26190-Hastings- | Hastings 139kV BUS | WPSC | M2 - Appendix A Approved | 200000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Hastings |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26191 | 26191-Otsego- | Otsego 138kV BUS Additional line mods required in conjunction with the planned relocation of the Otsego distribution station, redesign and install new line exits | WPSC | M2 - Appendix A Approved | 2200000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Otsego |  |  | 138 |  | 0.5 |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26192 | 26192-Clinton- | Clinton Line Modifications | WPSC | M2 - Appendix A Approved | 1250000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Clinton |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26193 | 26193-Clinton-Clinton Tap | Clinton to Clinton Tap reconductor | WPSC | M2 - Appendix A Approved | 3000000 | 2026-12-31 | Line Upgrade | Line reconductor | Clinton | Clinton Tap |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 21205 | Clinton Area Alternative | Other | 26194 | 26194-Clinton- | Transformer Rotation | WPSC | M2 - Appendix A Approved | 1500000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Clinton |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 21208 | Clinton Station Cut-in | Other | 26195 | 26195-Island Rd-Delhi | Cut into the Island Rd – Delhi 138 kV line at the Clinton Junction with a new double tap structure and install pole top switches at the Packard and Eaton Rapids taps. | METC | M2 - Appendix A Approved | 3300000 | 2026-12-31 | Line Upgrade | Generic transmission line project (try not to use the generic) | Island Rd | Delhi | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Other | 26197 | 26197-Council Bluffs-Glenwood | 69 kV line relay replacement | MEC | M4 - Project in Service | 2100000 | 2023-10-25 | Misc. | Relaying, protection, RTU and SCADA equipment | Council Bluffs | Glenwood | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 26199 | 26199-Sub A-Sub E 69 kV Reconductor | Sub A to Sub E double circuit 69 kV reconductor due to age and to increase reliability | MEC | M4 - Project in Service | 4000000 | 2024-03-29 | Line Upgrade | Line rebuild on existing ROW | Sub A | Sub E |  | 69 |  |  |  | IA | IL | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 26202 | 26202-Macedonia-Hastings | Rebuild Macedonia to Hastings 69 kV line. | MEC | M4 - Project in Service | 2658650 | 2022-04-08 | Line Upgrade | Line rebuild on existing ROW | Macedonia | Hastings | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Other | 26203 | 26203-Humboldt East-Goldfield | Humboldt East - Dakota City - Thor - Eagle Grove 69 kV line | MEC | M4 - Project in Service | 7000000 | 2023-06-30 | Line Upgrade | Line rebuild on existing ROW | Humboldt East | Goldfield | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Other | 26204 | 26204-Dakota City- | Dakota City line work | MEC | M4 - Project in Service | 400000 | 2024-03-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Dakota City |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Other | 26205 | 26205-Charles City North- | Install 69 kV line taps into new or existing substations to serve customer load or to improve system reliability. | MEC | M2 - Appendix A Approved | 600000 | 2027-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Charles City North |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 26208 | 26208-Hampton East- | Substation upgrade. | MEC | M4 - Project in Service | 450000 | 2023-04-01 | Substation | Substation (breakers only, no transformer) | Hampton East |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 26209 | 26209-CBEC- | Replace 161 kV breakers 807, 810, 811, and 812 | MEC | M3 - Under Construction | 1600000 | 2026-12-01 | Substation | Circuit Breaker (replacement at existing substation) | CBEC |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25724 | 25724-Lenox-Lenox Muni | ITC will be installing a 2-way switch outside IPL’s Lenox substation, building a new 69kV line (about 2.6 miles), and connecting it into CIPCO’s substation “Lenox Muni”. | ITCM | M2 - Appendix A Approved | 4161967 | 2027-05-01 | Line New | New Transmission line, new ROW - may include terminations | Lenox | Lenox Muni | 1 | 69 | 69 | 2.6 |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25726 | 25726-Albia-Court | ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. | ITCM | M2 - Appendix A Approved | 726017 | 2027-05-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Albia | Court | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25727 | 25727-Bridgeport North-Centerville North | ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. | ITCM | M2 - Appendix A Approved | 726017 | 2027-05-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Bridgeport North | Centerville North | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25728 | 25728-Creston-Mount Ayr | ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. | ITCM | M2 - Appendix A Approved | 734622 | 2027-05-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Creston | Mount Ayr | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25730 | 25730-Lenox-Lenox Tap | ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. | ITCM | M2 - Appendix A Approved | 600706 | 2027-05-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Lenox | Lenox Tap | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20037 | Carbide-Viele 161kV Rebuild | Other | 25736 | 25736-Carbide-Viele | ITC Midwest has entered into an agreement with Northeast Missouri Electric Cooperative to rebuild approximately 12.3 miles of the ITC Carbide – Viele 161 kV line to double circuit to allow Northeast to connect a new 161 kV line from their Franklin Substation in Lee County, Iowa to their Winchester Substation in Clarke County, Missouri. Per the terms of the agreement, Northeast will be responsible for design and construction for this project. ITC will contribute a fixed amount of $6,120,00 for the project as a credit for planned maintenance ITC needs to perform on this line. The ITC portion of the rebuild will be constructed with T2-795 ACSR conductor and OPGW. ITC will own the double circuit poles, conductor, insulators, and 1 OPGW static wire. | ITCM | M2 - Appendix A Approved | 6200000 | 2026-11-30 | Line Upgrade | Line rebuild on existing ROW | Carbide | Viele | 1 | 161 | 161 |  | 12.3 | IA |  | Not Shared
MTEP21 | A | METC | East | 20049 | Rebuild and Sag Remediate Gallagher - Twining 138kV | BRP | 25748 | 25748-Gallagher-Twining | The proposed solution is to Raise the sag limit on the 336 ACSR between Gallagher and Withey Lake Jct. and replace the 1/0 Copper on the Withey Lake Jct. - Twinning 138kV line with 477 ACSR utilizing standard 138 kV double circuit structures | METC | M2 - Appendix A Approved | 4679000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gallagher | Twining | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20054 | Warren 138 kV 377 Equipment Upgrades | BRP | 25756 | Warren - Upgrade 377 Breaker, Bus, CTs, & Relay | Upgrade terminal station equipment, including a 138 kV breaker, at Warren position 377 to meet or exceed the rating of a 954 ACSR conductor. | METC | M3 - Under Construction | 1050000 | 2027-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Warren |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20075 | Forbes 230 kV Modernization | Other | 25776 | 25776-Forbes 230- | Replace aging 230 kV capacitor bank | MP | M2 - Appendix A Approved | 1100000 | 2027-12-31 | Voltage Device | Capacitor (switched capacitor) | Forbes 230 |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20075 | Forbes 230 kV Modernization | Other | 25777 | 25777-Forbes 230- | Replace a 230 kV oil circuit breaker and a older 230 kV SF6 oil circuit breaker at Forbes | MP | M2 - Appendix A Approved | 1400000 | 2027-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Forbes 230 |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20081 | Stinson Asset Renewal Project | Other | 25790 | 25790-Stinson 115- | Replace existing problematic capacitor bank with a 28 MVAR bank. | MP | M3 - Under Construction | 970000 | 2025-12-31 | Voltage Device | Capacitor (switched capacitor) | Stinson 115 |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20081 | Stinson Asset Renewal Project | Other | 25791 | 25791-Stinson 115- | Replace switches, panels, arresters, PT's, and jumper. | MP | M3 - Under Construction | 360000 | 2025-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Stinson 115 |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20081 | Stinson Asset Renewal Project | Other | 25792 | 25792-Stinson 115- | Replace 115W Breaker | MP | M3 - Under Construction | 200000 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Stinson 115 |  |  | 115 |  |  |  | WI |  | Not Shared
MTEP21 | A | ITC | East | 20107 | Atlanta-Karn-Thetford Split & Station Reconfiguration (ITCT) | Other | 25807 | Atlanta_Add HG, GB,GF brkrs and Upgrade equipment | Add HG, GB,GF brkrs and switches | ITCT | M3 - Under Construction | 4430000 | 2027-05-14 | Substation | Substation (breakers only, no transformer) | Atlanta |  |  | 138 | 120 |  |  | MI |  | Not Shared
MTEP21 | A | ITC | East | 20107 | Atlanta-Karn-Thetford Split & Station Reconfiguration (ITCT) | Other | 25808 | ATLAN-KARN-THETF_138 kV Rebuild | Rebuild 0.75 miles utilizing 1431 ACSR on standard double circuit structures | ITCT | M3 - Under Construction | 1340000 | 2027-05-14 | Line Upgrade | Line rebuild on existing ROW | Atlanta | Karn/Thetford | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Other | 25809 | ATLAN-KARN-THTFD Split | Split Atlanta-Karn-Thetford into two line | METC | M3 - Under Construction | 322000 | 2027-05-05 | Line New | New Transmission line, new ROW - may include terminations | Atlanta |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | OTTER TAIL POWER COMPANY | West | 23368 | LRTP-01: Jamestown – Ellendale | MVP | 27039 | 27039-Jamestown 345 kV- | Add 1-345kV line position (replace existing 345kV ring bus with breaker-and-a-half bus) Add 1-345kV 50MVAr line reactor (for outgoing transmission line to Ellendale) | OTP | M2 - Appendix A Approved | 15600000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Jamestown 345 kV |  |  | 345 |  |  |  | ND |  | Shared
MTEP21 | A | OTTER TAIL POWER COMPANY | West | 23368 | LRTP-01: Jamestown – Ellendale | MVP | 27040 | 27040-Jamestown 345 kV-Ellendale 345 | Construct new 345kV single circuit transmission line (constructed with double circuit capable 345kV structures) | MDU, OTP | M2 - Appendix A Approved | 379600000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Jamestown 345 kV | Ellendale 345 |  | 345 |  | 95 |  | ND |  | Shared
MTEP21 | A | MONTANA-DAKOTA UTILITIES CO. | West | 23368 | LRTP-01: Jamestown – Ellendale | MVP | 27041 | 27041-Ellendale 345- | Add 1-345kV line position (replace existing 345kV ring bus with breaker-and-a-half bus) Add 1-345kV 50MVAr line reactor (for outgoing transmission line to Jamestown) | MDU | M2 - Appendix A Approved | 9808747 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Ellendale 345 |  |  | 345 |  |  |  | ND |  | Shared
MTEP21 | A | OTTER TAIL POWER COMPANY | West | 23368 | LRTP-01: Jamestown – Ellendale | MVP | 27042 | 27042-Maple River 345 kV- | Replace two existing 230/345kV, 336MVA transformers with two new 230/345kV 500MVA transformers | OTP | M2 - Appendix A Approved | 22000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Maple River 345 kV |  |  | 345 | 230 |  |  | ND |  | Shared
MTEP21 | A | OTTER TAIL POWER COMPANY | West | 23368 | LRTP-01: Jamestown – Ellendale | MVP | 27043 | 27043-Twin Brooks 345 kV- | Add 2-345kV 25MVAr shunt connected reactors in substation | MDU, OTP | M2 - Appendix A Approved | 12000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Twin Brooks 345 kV |  |  | 345 |  |  |  | ND |  | Shared
MTEP21 | A | OTTER TAIL POWER COMPANY | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27044 | 27044-Big Stone South 345 kV- | Add 1-345kV line position (replace existing ring bus with breaker-and-a-half bus) Add 1-345kV 50MVAr line reactor (for outgoing transmission line to Alexandria 345kV) | GRE, MP, OTP, WMMPA, XEL | M2 - Appendix A Approved | 12000000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Big Stone South 345 kV |  |  | 345 |  |  |  | SD |  | Shared
MTEP21 | A | OTTER TAIL POWER COMPANY | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27045 | 27045-Big Stone South 345 kV-Alexandria 345kV | Construct new 345kV single circuit transmission line (constructed with double circuit capable 345kV structures) | MRES, OTP, WMMPA | M2 - Appendix A Approved | 441200000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Big Stone South 345 kV | Alexandria 345kV |  | 345 |  | 128 |  | SD | MN | Shared
MTEP21 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27046 | 27046-Alexandria 345kV- | Add 2-345kV breaker-and-a-half positions (replace existing 345kV ring bus with breaker-and-a-half bus) Add 2 345kV 50MVAr line reactors (for outgoing transmission line to Big Stone South and outgoing transmission line to Big Oaks (Cassie’s Crossing)) | GRE, MP, OTP, WMMPA, XEL | M2 - Appendix A Approved | 16700000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Alexandria 345kV |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27047 | 27047-Alexandria 345kV-Outside Monticello Substation | Install second 345kV circuit on open spare position on existing structures on Alexandria - Monticello 345kV line. | GRE, MP, OTP, WMMPA, XEL | M2 - Appendix A Approved | 135820000 | 2027-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Alexandria 345kV | Outside Monticello Substation |  | 345 |  |  | 106 | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27048 | 27048-Outside Monticello Substation-Big Oaks (Cassie’s Crossing) | Replace existing GRE single circuit 230kV transmission line with double circuit capable 345kV transmission line, one circuit initially strung, Mississippi river crossing will include second circuit. Strung circuit will carry Alexandria-Big Oaks (Cassie’s Crossing) circuit. | GRE, MP, OTP, WMMPA, XEL | M2 - Appendix A Approved | 0 | 2027-06-01 | Line New | New Transmission line, new ROW - may include terminations | Outside Monticello Substation | Big Oaks (Cassie’s Crossing) |  | 345 |  | 1.5 | 1.5 | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27049 | 27049-Big Oaks (Cassie’s Crossing)- | Modify existing 345kV transmission lines to connect into Big Oaks Substation (Cassie’s Crossing). | GRE, MP, OTP, WMMPA, XEL | M2 - Appendix A Approved | 18515000 | 2027-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Big Oaks (Cassie’s Crossing) |  |  | 345 |  |  | 2 | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | MVP | 27050 | 27050-Big Oaks (Cassie’s Crossing)- | Construct new 11-position, 345kV breaker-and-a-half bus substation | GRE, MP, OTP, WMMPA, XEL | M2 - Appendix A Approved | 54532670 | 2027-06-01 | Substation | Substation (breakers only, no transformer) | Big Oaks (Cassie’s Crossing) |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27051 | 27051-Big Oaks Substation (Cassie’s Crossing)-Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W | Replace existing GRE single circuit 230kV transmission line with double circuit 345kV transmission line. Both lines will tie to Benton County. | GRE, MP | M2 - Appendix A Approved | 0 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Big Oaks Substation (Cassie’s Crossing) | Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W |  | 345 |  | 12.5 |  | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27052 | 27052-Sherco-Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W | Replace the existing Benton County-Sherco line to accommodate a rating greater than 3000 Amps. Including south deadend structure for new conductor. This line will tie to Benton County. | GRE, MP | M2 - Appendix A Approved | 0 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sherco | Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W |  | 345 |  |  | 7.3 | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27053 | 27053-Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W-Benton County | Replace existing GRE single circuit 230kV transmission line with double circuit 345kV transmission line. One line will tie to Sherco and other to Big Oaks Substation (Cassie’s Crossing). | GRE, MP | M2 - Appendix A Approved | 139871000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W | Benton County |  | 345 |  | 12.5 |  | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27054 | 27054-Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W-Benton County | Replace the existing Benton County-Sherco line to accommodate a rating greater than 3000 Amps. Including north deadend structure for new conductor. This line will tie to Big Oaks Substation (Cassie’s Crossing). | GRE, MP | M2 - Appendix A Approved | 106013000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Structure(s) at estimated GPS Coordinates: 45°27'37.5"N 93°53'32.5"W | Benton County |  | 345 |  |  | 14.1 | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27055 | 27055-Benton County- | Add 345kV 7-position breaker-and-a-half bus with 2 transformer positions and 5 line positions (one an existing modification), with two line connected 70MVAr shunt reactors on Iron Range lines, and modify 230kV position for one 230/345kV transformer | GRE, MP | M2 - Appendix A Approved | 45152000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Benton County |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27056 | 27056-Benton County-Riverton 230/115kV | Construct new 345kV double circuit transmission line | GRE, MP | M2 - Appendix A Approved | 458932000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Benton County | Riverton 230/115kV |  | 345 |  | 78 |  | MN |  | Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27057 | 27057-Riverton 230/115kV- | Add 4-345kV series capacitor bank groups (2 in series for each circuit) with protective bypass equipment. Impedance of series capacitor bank will be approximately 60% compensation of line | GRE, MP | M2 - Appendix A Approved | 116436000 | 2030-06-01 | Voltage Device | Series compensation of Series capacitor | Riverton 230/115kV |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27058 | 27058-Riverton 230/115kV-Iron Range 500/230kV | Construct new 345kV double circuit transmission line | GRE, MP | M2 - Appendix A Approved | 407612000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Riverton 230/115kV | Iron Range 500/230kV |  | 345 |  | 78 |  | MN |  | Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27059 | 27059-Iron Range 500/230kV- | Add 4-position 345kV ring bus (expandable to breaker-and-a-half bus) for 2-345/500kV transformer positions and 2 line positions (includes 2-345 kV shunt reactors on lines to Benton, est. 50 MVAR each) | GRE, MP | M2 - Appendix A Approved | 115879000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Iron Range 500/230kV |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27060 | 27060-Iron Range 500/230kV- | Add 2-345/500kV 1200MVA transformers (with 1 single phase spare on-site) | GRE, MP | M2 - Appendix A Approved | 0 | 2030-06-01 | Transformer | Transformer New | Iron Range 500/230kV |  |  | 500 | 345 |  |  | MN |  | Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | MVP | 27061 | 27061-Iron Range 500/230kV- | Add 5-position 500 kV ring bus (line to Dorsey, 500-230 TX, 500-345 TX, Cap Bank, 500-345 TX) | GRE, MP | M2 - Appendix A Approved | 0 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Iron Range 500/230kV |  |  | 500 |  |  |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27062 | 27062-Crandall-Last double circuit structure from Wilmarth (44.032, -94.293) | Increase load capability of existing transmission line | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 69200000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Crandall | Last double circuit structure from Wilmarth (44.032, -94.293) |  | 345 |  |  | 30 | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27063 | 27063-Chub Lake- | Add 1-345kV transformer position (replace existing ring bus with breaker-and-a-half bus) | GRE | M2 - Appendix A Approved | 0 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Chub Lake |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27064 | 27064-Chub Lake- | Add 1-115/345kV 448MVA transformer | GRE | M2 - Appendix A Approved | 13721558 | 2027-07-13 | Transformer | Transformer New | Chub Lake |  |  | 345 | 115 |  |  | MN |  | Shared
MTEP21 | A | GREAT RIVER ENERGY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27065 | 27065-Chub Lake- | Add 1-115kV transformer position (replace existing ring bus with breaker-and-a-half bus) | GRE | M2 - Appendix A Approved | 0 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Chub Lake |  |  | 115 |  |  |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27066 | 27066-Wilmarth- | Add 1-345kV line position (breaker-and-a-half bus) | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 11584482 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Wilmarth |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27067 | 27067-Wilmarth-North Rochester | Replace existing XEL Wilmarth - Faribault Energy Park single circuit 115kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 115kV. Construct new 345kV single circuit transmission line from Faribault Energy Park - North Rochester | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 373000000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Wilmarth | North Rochester |  | 345 | 115 | 42 | 44 | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27068 | 27068-North Rochester- | Add 2-345kV line positions (breaker-and-a-half bus) | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 13057135 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | North Rochester |  |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 16490 | Granville SS, Control House and Relay Replacement and Asset Renewal | Other | 24316 | 24316-Granville- | Granville SS Asset Renewal | ATC | M3 - Under Construction | 48408902 | 2026-06-15 | Substation | Substation (breakers only, no transformer) | Granville |  |  | 345 | 138 |  |  | WI |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19949 | New ISHI Shelbyville 69 kV Loop | Other | 25920 | New ISHI Dist-Airport 69 kV Line | New ISHI Dist-Airport 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 6032000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | ISHI Dist | Airport |  | 69 |  | 1.7 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19949 | New ISHI Shelbyville 69 kV Loop | Other | 25926 | New Airport-Johnston 69 kV Line | New Airport-Johnston 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 650000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Airport | Johnston |  | 69 |  | 1.3 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19949 | New ISHI Shelbyville 69 kV Loop | Other | 25927 | New Johnston-Crest 69 kV Line | New Johnston-Crest 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 128000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Johnston | Crest |  | 69 |  | 0.2 |  | IL |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19949 | New ISHI Shelbyville 69 kV Loop | Other | 25928 | New Ishi-Crest 69 kV Line | New Ishi-Crest 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 981500 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Crest | Ishi |  | 69 |  | 3.15 |  | IL |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | Other | 25931 | 25931-Quick-Sub. 701 | Construct a new Quick-Sub 701 161 kV line | MEC | M2 - Appendix A Approved | 20100000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Quick | Sub. 701 | 1 | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | Other | 25934 | 25934-Quick- | New 161 kV Line Terminal at Quick Substation | MEC | M4 - Project in Service | 4750000 | 2024-04-26 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Quick |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | Other | 25939 | 25939-Sub 701- | New 161 kV Line Terminal at Sub 701 | MEC | M2 - Appendix A Approved | 2500000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Sub 701 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 20187 | Upgrade Chesterville 138 kV Substation | Other | 25949 | 25949-Chesterville- | Add 2 line breakers | AmerenIL | M2 - Appendix A Approved | 3100000 | 2029-12-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Chesterville |  |  | 138 | 69 |  |  | IL |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20189 | Washburn: 161 kV Bus A Improvement | Other | 25952 | 25952-Washburn- | Washburn Bus A: Same upgrades needed on Bus A as are being completed on Bus B under T91PK. The 161 kV circuit switcher on 161-69 kV transformer does not interrupt faults | MEC | M2 - Appendix A Approved | 3000000 | 2028-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Washburn |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | DUKE ENERGY INDIANA, LLC | Central | 20196 | New Rosston 69/12 kV substation | Other | 25965 | 25965-Rosston 69/12kV sub- | new sub to be fed from the 69182 ckt and will replace existing Whitestown 69/12kV sub in the 6983 ckt. | DEI | M2 - Appendix A Approved | 1337000 | 2027-09-30 | Substation | Distribution substation - may include trans high side | Rosston 69/12kV sub |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP21 | A | DUKE ENERGY INDIANA, LLC | Central | 20206 | Rebuild Huntington 138 kV to Meridian Rd Jct 69 kV | Other | 25974 | 25974-Huntington 138-Meridian Rd Jct | 6923 Part 2 rebuild with 954acsr; replace switches at Erie Stone jct | DEI | M2 - Appendix A Approved | 3540000 | 2027-06-15 | Line Upgrade | Line rebuild on existing ROW | Huntington 138 | Meridian Rd Jct |  | 69 |  |  | 1.4 | IN |  | Not Shared
MTEP21 | A | DUKE ENERGY INDIANA, LLC | Central | 20225 | Rebuild McKay Rd Jct. to H.E. Lewis Creek Jct. 69 kV line | Other | 25977 | 25977-McKay Rd. Jct.-HE Lewis Crk. Jct. | Rebuild transmission line 6975 from McKay Rd Junction (pole #807-3096) to H.E. Lewis Creek Junction (pole #807-3168) using light duty steel poles, 477 ACSR conductor and OPGW. - 5.9 miles ; Replace two switches at McKay Rd Junction 2000A | DEI | M2 - Appendix A Approved | 7244000 | 2027-10-29 | Line Upgrade | Line rebuild on existing ROW | McKay Rd. Jct. | HE Lewis Crk. Jct. |  | 69 |  |  | 5.9 | IN |  | Not Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 20229 | J732 Stone Lake XFMR Upgrade | GIP | 25982 | 25982-Stone Lake- | Transformer upgrade for J732 in Aug 17 ATC DPP cycle | XEL | M2 - Appendix A Approved | 5800000 | 2026-07-31 | Transformer | Transformer New | Stone Lake |  |  | 345 | 161 |  |  | WI |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19847 | New Golden 138/69 kV Substation | Other | 25994 | New Ameren Whitetail-Golden 138 kV Line | New Ameren Whitetail-Golden 138 kV Line in AEC | PPI | M2 - Appendix A Approved | 800000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Ameren Whitetail | Golden | 1 | 138 | 138 | 0.8 |  | IL |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Other | 26210 | 26210-Various- | Substation relay and communication upgrades at various locations | MEC | M2 - Appendix A Approved | 14000000 | 2024-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Various |  |  | 345 | 161 |  |  | IA | IL | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Other | 26211 | 26211-DPS- | Relay replacement at DPS substation | MEC | M2 - Appendix A Approved | 1479000 | 2026-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | DPS |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 21265 | Sub A Riverside 69 kV Upgrades | Other | 26212 | 26212-Sub A-69 kV Upgrades | Replace 69 kV breakers and protective relaying. Also replace 161-69 kV transformer bank 8T1 and 8T2 with a new 161-69 kV 125 MVA transformer. | MEC | M3 - Under Construction | 10000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Sub. A |  |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | METC | East | 20164 | Wealthy Street 138 kV Station Rebuild | Other | 26216 | 26216-Wealthy- | Remove equipment at Wealthy | METC | M2 - Appendix A Approved | 2000000 | 2028-12-29 | Substation | Small miscellaneous substation equipment | Wealthy |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20075 | Forbes 230 kV Modernization | Other | 26227 | 26227-Forbes 230- | Replace or upgrade 230 kV disconnect switches, wave traps, ccvt's, and control panels; improve substation grounding | MP | M2 - Appendix A Approved | 1800000 | 2027-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Forbes 230 |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP21 | A | MINNESOTA POWER INC. | West | 20075 | Forbes 230 kV Modernization | Other | 26228 | 26228-Forbes 230- | Replace Forbes 3TR 230/115 kV 373 MVA Transformer and foundation | MP | M2 - Appendix A Approved | 3050000 | 2027-12-31 | Transformer | Transformer New | Forbes 230 |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP21 | A | METC | East | 20162 | Claremont 138 kV Station Rebuild | Other | 26230 | 26230-Claremont- | Remove transmission equipment at Claremont | METC | M2 - Appendix A Approved | 2300000 | 2028-12-29 | Substation | Small miscellaneous substation equipment | Claremont |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 26244 | 26244-Beecher-METC Structure 017E9231 | Install overhead fiber from Beecher to Structure #017E9231 | METC | M4 - Project in Service | 1286022 | 2023-04-05 | Misc. | Communication equipment | Beecher | METC Structure 017E9231 |  | 138 |  |  | 1.7 | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 26246 | 26246-Tangent-Raisin Tap | Install overhead fiber from Tangent to Raisin Tap and connect to the OPGW on the Raisin Tap. Install 2nd OPGW bundle from Tangent to approximately Structure #084A4759 to connect underground fiber to Parr Rd. | METC | M4 - Project in Service | 5397618 | 2023-05-19 | Misc. | Communication equipment | Tangent | Raisin Tap |  | 138 |  |  | 2.5 | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 26247 | 26247-Beecher- | Install fiber optic patch cables. Create communication path from Tangent to Whiting. | METC | M4 - Project in Service | 172363 | 2023-12-21 | Substation | Small miscellaneous substation equipment | Beecher |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 26248 | 26248-Morocco- | Install fiber optic patch cables. Create communication path from Tangent to Whiting. | METC | M4 - Project in Service | 18818 | 2023-12-21 | Substation | Small miscellaneous substation equipment | Morocco |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 21387 | Hancock County Capacitor Bank Addition | BRP | 26251 | 26251-Hancock County- | 35 MVar capacitor bank addition to the existing Hancock County substation. | BREC | M2 - Appendix A Approved | 500000 | 2029-12-01 | Voltage Device | Capacitor (switched capacitor) | Hancock County |  |  | 69 |  |  |  | KY |  | Not Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27085 | 27085-North Rochester-161kV structure along line to Chester (44.173, -92.390) | Construct new 161kV single circuit transmission line | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 52000000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | North Rochester | 161kV structure along line to Chester (44.173, -92.390) |  | 161 |  | 17 |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27086 | 27086-North Rochester-161kV structure along line to Chester (44.173, -92.390) | Re-energize existing (currently operated at 161kV) conductors to 345kV | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 0 | 2028-06-01 | Line Upgrade | Line conversion to higher voltage | North Rochester | 161kV structure along line to Chester (44.173, -92.390) |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27087 | 27087-161kV structure along line to Chester (44.173, -92.390)-161kV structure along line Wabaco (44.1937, -92.0859) | Install second 345kV circuit on existing spare position | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 25000000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | 161kV structure along line to Chester (44.173, -92.390) | 161kV structure along line Wabaco (44.1937, -92.0859) |  | 345 |  |  | 17 | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27088 | 27088-161kV structure along line Wabaco (44.1937, -92.0859)-Kellogg | Construct new 161kV single circuit transmission line | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 18800000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | 161kV structure along line Wabaco (44.1937, -92.0859) | Kellogg |  | 161 |  | 11 |  | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27089 | 27089-Kellogg- | Construct transmission structures to cut-in existing Wabaco - Alma 161kV transmission line into Kellogg Substation | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 1500000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Kellogg |  |  | 161 |  |  | 1 | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27090 | 27090-Kellogg- | Construct new 3-position 161kV ring bus in the Kellogg Substation 1. Cut-in to existing Wabaco - Alma 161kV transmission line 2. Cut-in to existing Wabaco - Alma 161kV transmission line 3. 69/161kV, 112MVA transformer | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 6700000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Kellogg |  |  | 161 |  |  |  | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27091 | 27091-Kellogg- | Add 1-69/161kV, 112MVA transformer | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 740000 | 2028-06-01 | Transformer | Transformer New | Kellogg |  |  | 161 | 69 |  |  | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27092 | 27092-Kellogg- | Construct new 2-position 69kV straight bus in the Kellogg Substation and cut-in existing Alma-Utica 69 kV transmission line. | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 1900000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Kellogg |  |  | 69 |  |  |  | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27093 | 27093-Kellogg- | Construct transmission structures to cut-in existing Alma-Utica 69kV transmission line into Kellogg Substation | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 1300000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Kellogg |  |  | 69 |  |  | 1 | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27094 | 27094-Kellogg-Alma | Install OPGW across Mississippi River to provide communications protection of new Alma-Kellogg 161 kV line | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 200000 | 2028-06-01 | Misc. | Communication equipment | Kellogg | Alma |  | 161 |  |  |  | MN |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27095 | 27095-Alma- | Protection Upgrade at Alma to accommodate new Alma-Kellogg 161 kV line protection Requirements | DPC | M2 - Appendix A Approved | 300000 | 2028-06-01 | Misc. | Relaying, protection, RTU and SCADA equipment | Alma |  |  | 161 |  |  |  | WI |  | Shared
MTEP21 | A | DAIRYLAND POWER COOPERATIVE | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27096 | 27096-161kV structure along line Wabaco (44.1937, -92.0859)-345kV deadend structure | Re-energize existing (currently operated at 161kV) conductors to 345kV | City of Rochester, DPC, SMMPA, XEL | M2 - Appendix A Approved | 0 | 2028-06-01 | Line Upgrade | Line conversion to higher voltage | 161kV structure along line Wabaco (44.1937, -92.0859) | 345kV deadend structure |  | 345 |  |  |  | MN |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27099 | 27099-Tremval- | Modify existing Briggs Road - North Madison single circuit 345 kV transmission line to construct transmission structures to cut-in existing Briggs Road - North Madison 345kV transmission line into Tremval Substation | ATC, DPC, SMPA, WPPI, XEL | M2 - Appendix A Approved | 4600000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Tremval |  |  | 345 |  |  | 1 | WI |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | MVP | 27100 | 27100-Tremval- | Add 6-345kV line positions (breaker-and-a-half bus). 1. New transmission line from near Alma 2. New transmission line to Eau Claire 3. Cut-in to existing Briggs Road-North Madison 345kV line 4. Cut-in to existing Briggs Road-North Madison 345kV line 5. New transmission line to Rocky Run Substation 6. Bus connected 345kV, 80MVAr reactor | Local TO(s) | M2 - Appendix A Approved | 23700000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Tremval |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23372 | LRTP-05: Tremval – Eau Claire – Jump River | MVP | 27101 | 27101-Tremval-Eau Claire | Replace existing Xcel single circuit 161kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 161kV. | Local TO(s), XEL | M2 - Appendix A Approved | 185227000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Tremval | Eau Claire |  | 345 | 161 |  | 46 | WI |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23372 | LRTP-05: Tremval – Eau Claire – Jump River | MVP | 27102 | 27102-Eau Claire- | Add 2-345kV line positions (ring bus). 1. New transmission line to Tremval 2. New transmission line to Jump River | XEL | M2 - Appendix A Approved | 85720000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Eau Claire |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | NORTHERN STATES POWER COMPANY | West | 23372 | LRTP-05: Tremval – Eau Claire – Jump River | MVP | 27103 | 27103-Eau Claire-Jump River | Replace existing Xcel single circuit 161kV and 115kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 161kV or 115kV. | ATC, XEL | M2 - Appendix A Approved | 167053000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Eau Claire | Jump River |  | 345 | 115 |  | 51 | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23372 | LRTP-05: Tremval – Eau Claire – Jump River | MVP | 27104 | 27104-Jump River (45.3, -90.95)- | Modify existing Stone Lake -- Gardner Park 345 kV single-circuit transmission line to construct transmission structures to cut-in existing Stone Lake - Gardner Park 345kV transmission line into Jump River Substation. Remote station upgrades. | ATC | M2 - Appendix A Approved | 5745000 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Jump River (45.3, -90.95) |  |  | 345 |  |  | 1 | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23372 | LRTP-05: Tremval – Eau Claire – Jump River | MVP | 27105 | 27105-Jump River (45.3, -90.95)- | Construct new 4-position, 345kV ring bus substation. 1). New transmission line from Eau Claire 2). Cut-in to existing Stone Lake to Gardner Park 3). Cut-in to existing Stone Lake to Gardner Park 4). Bus-connected 345kV, 80MVAr reactor | ATC | M2 - Appendix A Approved | 39755000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Jump River (45.3, -90.95) |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 27106 | 27106-Tremval-Rocky Run | Replace existing Xcel single circuit 69 kV structures with double circuit structures, with 1 circuit operated at 345kV and 1 circuit operated at 69kV for approximately 21 miles. Construct new 345kV single circuit transmission line for approximately 47 miles. Replace existing ATC single and double circuit 69kV, 138kV and 345kV structures with double circuit structures, with 1 circuit operated at 345kV and 1 circuit operated at 69kV, 138kV or 345kV for approximately 31 miles. | Local TO(s) | M2 - Appendix A Approved | 282991110 | 2030-12-31 | Line New | New Transmission line, new ROW - may include terminations | Tremval | Rocky Run |  | 345 |  | 47 | 52 | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 27107 | 27107-Rocky Run- | Modify existing transmission lines to connect to Rocky Run substation | ATC | M2 - Appendix A Approved | 0 | 2030-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Rocky Run |  |  | 345 |  |  | 3 | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 27108 | 27108-Rocky Run- | Replace existing 6-position 345kV ring bus, with 9-position 345kV breaker-and-a-half bus. Replaced bus will terminate all existing 6-positions, and 3 new bus positions - 1). New transmission line from Tremval 2). New transmission line to Columbia 3). Bus-connected 345kV, 80MVAr reactor | ATC | M2 - Appendix A Approved | 59593492 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | Rocky Run |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 27109 | 27109-Rocky Run-Columbia | Replace existing single circuit 69kV, 115kV, 138kV, and 345kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 69kV, 115kV, 138kV or 345kV. | ATC | M2 - Appendix A Approved | 906970649 | 2030-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Rocky Run | Columbia |  | 345 | 69 |  | 114 | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 27110 | 27110-345 kV Structure (43.477439, -89.284950)-Columbia | Replace existing double circuit 345 kV structures with new double circuit 345 kV structures, both 345 kV circuits rated for 3000Amps | ATC | M2 - Appendix A Approved | 72872008 | 2030-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | 345 kV Structure (43.477439, -89.284950) | Columbia |  | 345 |  |  | 9 | WI |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | MVP | 27111 | 27111-Columbia- | Add 2-345kV line positions (breaker-and-a-half bus). 1). New transmission line to Rocky Run 2). | ATC | M2 - Appendix A Approved | 24321128 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | Columbia |  |  | 345 |  |  |  | WI |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27112 | 27112-Webster- | Add 1-345kV line position (ring bus) | CFU, MEC | M2 - Appendix A Approved | 3800000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Webster |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27113 | 27113-Webster-North Franklin | Replace existing MEC single circuit 161kV structures with double circuit structures capable of supporting 1 circuit operated at 345kV and 1 circuit operated at 161kV. | CFU, MEC | M2 - Appendix A Approved | 135000000 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Webster | North Franklin |  | 345 | 161 | 1 | 42 | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27114 | 27114-North Franklin- | Construct new 4-345kV line position (breaker-and-a-half bus) substation. 1. New transmission line from Webster 2. New transmission line to Marshalltown 3. Cut-in to existing Quinn-Black Hawk 345kV line 4. Cut-in to existing Quinn-Black Hawk 345kV line Add 2-345kV 50MVAr line reactors for outgoing transmission lines to Webster and to Marshalltown | MEC | M2 - Appendix A Approved | 44300000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | North Franklin |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27115 | 27115-North Franklin-Marshalltown | Construct new 345kV single circuit transmission line (constructed with double circuit capable 345kV structures) | ITCM, MEC | M2 - Appendix A Approved | 310500000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | North Franklin | Marshalltown |  | 345 |  | 69 |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27116 | 27116-Marshalltown- | Add 3-345kV positions (ring bus, expandable to breaker-and-a-half bus). 1. New transmission line to North Franklin 2. New transmission line to Morgan Valley 3. 1-161/345kV 560MVA transformer Add 1-345kV 55MVAr line reactor for outgoing transmission line to Morgan Valley | ITCM | M2 - Appendix A Approved | 21000000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Marshalltown |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27117 | 27117-Marshalltown- | Add 1-161/345kV 560MVA transformer | ITCM | M2 - Appendix A Approved | 7500000 | 2027-12-31 | Transformer | Transformer New | Marshalltown |  |  | 345 | 161 |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27118 | 27118-Marshalltown- | Add 1-115/161kV 250MVA transformer | ITCM | M2 - Appendix A Approved | 3000000 | 2027-12-31 | Transformer | Transformer New | Marshalltown |  |  | 161 | 115 |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27119 | 27119-Marshalltown- | Add 1-161kV transformer position (breaker-and-a-half bus) for the 161/345kV transformer Utilize existing spare 161 kV position for 115/161kV transformer | ITCM | M2 - Appendix A Approved | 2300000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Marshalltown |  |  | 161 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27120 | 27120-Marshalltown- | Add 1-115kV transformer position | ITCM | M2 - Appendix A Approved | 1500000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Marshalltown |  |  | 115 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27121 | 27121-Marshalltown-Morgan Valley | Replace existing 115kV transmission line with new 345kV single circuit transmission line | ITCM | M2 - Appendix A Approved | 221000000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Marshalltown | Morgan Valley |  | 345 |  | 65 |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | MVP | 27122 | 27122-Morgan Valley- | Add 1-345kV line position (breaker-and-a-half bus) | ITCM | M2 - Appendix A Approved | 5100000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Morgan Valley |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23410 | LRTP-08: Beverly – Sub 92 | MVP | 27125 | 27125-Beverly- | Add 1-345kV line position (replace existing bus with ring bus) Add 1-345kV 55MVAr line reactor for outgoing transmission line to Sub 92 | ITCM | M2 - Appendix A Approved | 9000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Beverly |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23410 | LRTP-08: Beverly – Sub 92 | MVP | 27126 | 27126-Beverly-Sub 92 | Construct new 345kV single circuit transmission line and replace existing 115kV transmission line with new 345kV single circuit transmission line for a portion of the route | ITCM, MEC | M2 - Appendix A Approved | 203000000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Beverly | Sub 92 |  | 345 |  | 58 |  | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23410 | LRTP-08: Beverly – Sub 92 | MVP | 27127 | 27127-Sub 92- | Add 1-345kV line position (replace existing bus with ring bus) | MEC | M2 - Appendix A Approved | 19000000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Sub 92 |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23411 | LRTP-09: Orient – Denny - Fairport | MVP | 27128 | 27128-Orient- | Add 1-345kV line position (breaker-and-a-half bus) Add 1-345kV 50 MVAr line reactor (for outgoing line to Denny) | MEC | M2 - Appendix A Approved | 10000000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Orient |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23411 | LRTP-09: Orient – Denny - Fairport | MVP | 27129 | 27129-Orient-IA/MO State Border | Construct new 345kV single circuit transmission line. | MEC | M2 - Appendix A Approved | 208000000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Orient | IA/MO State Border |  | 345 |  | 44 | 8 | IA |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23411 | LRTP-09: Orient – Denny - Fairport | MVP | 27130 | 27130-IA/MO State Border-Denny | Construct new 345kV single circuit transmission line. | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 88770369 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | IA/MO State Border | Denny |  | 345 |  | 50 |  | MO |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23411 | LRTP-09: Orient – Denny - Fairport | MVP | 27131 | 27131-Denny- | Construct new 4-position 345kV ring bus substation. 1. New transmission line to Orient. 2. New transmission line to Fairport. 3. New transmission line to Zachary. 4. Add 1-345kV bus 50 MVAr reactor | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 0 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Denny |  |  | 345 |  |  |  | MO |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23411 | LRTP-09: Orient – Denny - Fairport | MVP | 27132 | 27132-Denny-Fairport | Construct new 345kV single circuit transmission line | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 0 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denny | Fairport |  | 345 |  | 2 |  | MO |  | Shared
MTEP21 | A | Midcontinent Independent System Operator, Inc. | Central | 23411 | LRTP-09: Orient – Denny - Fairport | MVP | 27133 | 27133-Fairport- | Add 1-345kV line position (replace existing bus with ring bus) | AECI | M2 - Appendix A Approved | 11300000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Fairport |  |  | 345 |  |  |  | MO |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27134 | 27134-Denny-Zachary | Construct new 345kV single circuit transmission line. | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 345393372 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Denny | Zachary |  | 345 |  | 135 |  | MO |  | Shared
MTEP21 | A | AMEREN MISSOURI | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27135 | 27135-Zachary- | Add 3-345kV positions (replace existing ring bus with breaker-and-a-half bus). 1. New transmission line to Denny 2. New transmission line to Thomas Hill 3. New transmission line to Maywood | AmerenMO | M2 - Appendix A Approved | 16900000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Zachary |  |  | 345 |  |  |  | MO |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27136 | 27136-Zachary-Maywood | Construct new 345kV single circuit transmission line. | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 0 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Zachary | Maywood |  | 345 |  | 60 |  | MO |  | Shared
MTEP21 | A | AMEREN MISSOURI | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27137 | 27137-Zachary-Thomas Hill | Replace existing Ameren single circuit 161kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 161kV. Replace existing 161kV conductor, insulators, and hardware. | AmerenMO | M2 - Appendix A Approved | 154120801 | 2030-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Zachary | Thomas Hill |  | 345 | 161 |  | 44 | MO |  | Shared
MTEP21 | A | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27138 | 27138-Zachary-Thomas Hill | Install new 345kV conductor, insulators, and hardware on replaced transmission line structures. | AMEREN TRANSMISSION COMPANY OF ILLINOIS | M2 - Appendix A Approved | 0 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Zachary | Thomas Hill |  | 345 | 161 |  | 44 | MO |  | Shared
MTEP21 | A | Midcontinent Independent System Operator, Inc. | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27139 | 27139-Thomas Hill- | Add 1-345kV line position | To Be Determined | M2 - Appendix A Approved | 4200000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Thomas Hill |  |  | 345 |  |  |  | MO |  | Shared
MTEP21 | A | AMEREN MISSOURI | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | MVP | 27140 | 27140-Maywood- | Add 2-345kV line positions (breaker-and-a-half bus) | AmerenMO | M2 - Appendix A Approved | 8600000 | 2030-06-01 | Substation | Substation (breakers only, no transformer) | Maywood |  |  | 345 |  |  |  | MO |  | Shared
MTEP21 | A | AMEREN MISSOURI | Central | 23413 | LRTP-11: Maywood – Meredosia | MVP | 27141 | 27141-Maywood-Meredosia | Replace existing Ameren 161kV single circuit transmission line with double circuit structures capable of support 1 circuit at 345kV and 1 circuit at 161kV for approximately 6 miles. Replace existing Ameren 138kV single circuit transmission line with double circuit structures capable of support 1 circuit at 345kV and 1 circuit at 138kV for approximately 56 miles. Construct new 345kV single circuit transmission line for approximately 2.5 miles | AmerenIL, AmerenMO | M2 - Appendix A Approved | 286100000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Maywood | Meredosia |  | 345 | 138 | 2.5 | 62 | MO | IL | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23413 | LRTP-11: Maywood – Meredosia | MVP | 27142 | 27142-Meredosia- | Add 1-345kV line position (breaker-and-a-half bus) | AmerenIL | M2 - Appendix A Approved | 7100000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Meredosia |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | MVP | 27143 | 27143-Madison County- | Add 1-345kV line position (ring bus) Add 1-345kV, 50MVAr line reactor (for outgoing line to Ottumwa) | MEC | M2 - Appendix A Approved | 10300000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Madison County |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | MVP | 27144 | 27144-Madison County-Ottumwa Generation | Construct new 345kV single circuit transmission line (a portion of the route assumed to be double circuit with existing ITCM single circuit 161kV structures between Lucas County - Ottumwa). The portion that uses the existing 161kV line route will utilize double circuit structures 1 circuit operated at 345kV and 1 circuit operated at 161kV. | ITCM, MEC | M2 - Appendix A Approved | 378500000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Madison County | Ottumwa Generation |  | 345 | 161 | 53 | 42 | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | MVP | 27145 | 27145-Ottumwa Generation- | Add 3-345kV line positions (replace existing bus with breaker-and-a-half bus). 1. New transmission line to Madison County 2. New transmission line to Skunk River 3. Bus-connected 345kV, 55MVAr reactor | ITCM, MEC | M2 - Appendix A Approved | 11900000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Ottumwa Generation |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | MVP | 27146 | 27146-Ottumwa Generation-Coddington | Construct new 345kV single circuit transmission line (a portion of the route assumed to be double circuit with existing ITCM single circuit 161kV structures between Ottumwa - Woody - Jefferson County - Henry County). The portion that uses the existing 161kV line route will utilize double circuit structures 1 circuit operated at 345kV and 1 circuit operated at 161kV. | ITCM, MEC | M2 - Appendix A Approved | 248000000 | 2026-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Ottumwa Generation | Skunk River |  | 345 | 161 | 2 | 60 | IA |  | Shared
MTEP21 | A | AMEREN ILLINOIS | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | MVP | 27147 | 27147-Coddington (40.973, -91.634)- | Modify existing Sub T - Maywood 345 kV single-circuit transmission line to construct transmission structures to cut-in existing Sub T - Maywood 345kV transmission line into Skunk River Substation | Local TO(s) | M2 - Appendix A Approved | 0 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Skunk River (40.973, -91.634) |  |  | 345 |  |  | 1 | IA |  | Shared
MTEP21 | A | AMEREN ILLINOIS | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | MVP | 27148 | 27148-Coddington (40.973, -91.634)- | Construct new 5-position 345kV breaker-and-a-half bus substation 1. New transmission line to Ottumwa 2. New transmission line to Denmark 3. Cut-in to existing Sub T - Maywood transmission line 4. Cut-in to existing Sub T - Maywood 5. Bus-connected 345kV, 50MVAr reactor | Local TO(s) | M2 - Appendix A Approved | 41300000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Skunk River (40.973, -91.634) |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23415 | LRTP-13: Coddington – Ipava | MVP | 27149 | 27149-Coddington-Denmark | Construct new 345kV single circuit transmission line (a portion of the route assumed to be double circuit with existing ITCM single circuit 161kV structures between Jefferson County - Henry County - Denmark). The portion that uses the existing 161 kV line route will utilize double circuit structures 1 circuit operated at 345kV and 1 circuit operated at 161kV. | ITCM | M2 - Appendix A Approved | 102500000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Skunk River | Denmark |  | 345 | 161 | 25 |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23415 | LRTP-13: Coddington – Ipava | MVP | 27150 | 27150-Denmark- | Add 1-161kV transformer position (replace existing bus to breaker-and-a-half bus) | ITCM | M4 - Project in Service | 18500000 | 2025-04-08 | Substation | Substation (breakers only, no transformer) | Denmark |  |  | 161 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23415 | LRTP-13: Coddington – Ipava | MVP | 27151 | 27151-Denmark- | Add 161/345kV 560 MVA transformer | ITCM | M2 - Appendix A Approved | 7500000 | 2029-12-31 | Transformer | Transformer New | Denmark |  |  | 345 | 161 |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23415 | LRTP-13: Coddington – Ipava | MVP | 27152 | 27152-Denmark- | Add 3-345kV positions (ring bus) 1. New Transmission line to Skunk River 2. New transmission line to Ipava 3. New 161/345kV 560MVA transformer Add 1-345kV, 55MVAr line reactor (for outgoing transmission line to Ipava) | ITCM | M2 - Appendix A Approved | 15600000 | 2029-12-31 | Substation | Substation (breakers only, no transformer) | Denmark |  |  | 345 |  |  |  | IA |  | Shared
MTEP21 | A | ITC MIDWEST | West | 23415 | LRTP-13: Coddington – Ipava | MVP | 27153 | 27153-Denmark-IA/IL State Border -Mississippi River | Construct new 345kV single circuit transmission line (a portion of the route assumed to be double circuit with existing ITCM single circuit 161kV structures between Denmark - Burlington). The portion that uses the existing 161 kV line route will utilize double circuit structures 1 circuit operated at 345kV and 1 circuit operated at 161kV. | ITCM | M2 - Appendix A Approved | 123000000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Denmark | IA/IL State Border -Mississippi River |  | 345 |  | 30 |  | IA |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23415 | LRTP-13: Coddington – Ipava | MVP | 27155 | 27155-Ipava- | Add 2-345kV line positions (breaker-and-a-half bus) | AmerenIL | M2 - Appendix A Approved | 10700000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Ipava |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27156 | 27156-Ipava-Maple Ridge | Replace existing transmission line, and install second 345kV on spare position. Replaced transmission line structures will be capable of supporting 2-345kV circuits. Replaced segment: 21 miles of Ameren-IL single circuit 345kV structures from Ipava, to a structure outside Duck Creek (40.4598, -89.9851). Replace existing 345kV conductor with new conductor. Second circuit on spare position: 21 miles from a structure outside Duck Creek (40.4598, -89.9851) to Maple Ridge | AmerenIL | M2 - Appendix A Approved | 106300000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Ipava | Maple Ridge |  | 345 |  |  | 42 | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27157 | 27157-Maple Ridge- | Add 2-345kV line positions (replace existing bus with breaker-and-a-half bus) | AmerenIL | M2 - Appendix A Approved | 16200000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Maple Ridge |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27158 | 27158-Maple Ridge-Tazewell | Construct new and re-energize existing conductors to a higher voltage (currently operated at 69kV from Maple Ridge to Edwards & at 138kV from Edwards to Tazewell) to 345kV. Construct new 69kV single circuit transmission line for approximately 5.5 miles from a structure outside Maple Ridge (40.595, -89.759) to Edwards Construct new 138kV single circuit transmission line from Edwards to Tazewell for approximately 9 miles. | AmerenIL | M2 - Appendix A Approved | 66000000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Maple Ridge | Tazewell |  | 345 | 69 | 14.5 |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27159 | 27159-Tazewell- | Add 2-345kV line positions (breaker-and-a-half bus) | AmerenIL | M2 - Appendix A Approved | 5200000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Tazewell |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27160 | 27160-Tazewell-Brokaw | Replace existing Ameren single circuit 138kV structures (Havanna - Old Danvers) with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 138kV for approximately 25 miles. Construct new 345kV single circuit transmission line for approximately 20 miles. | AmerenIL | M2 - Appendix A Approved | 180100000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Tazewell | Brokaw |  | 345 | 138 | 20 | 25 | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27161 | 27161-Brokaw- | Add 6-position 345kV breaker-and-a-half bus 1. Re-terminate Brokaw-South Bloomington into added bus 2. Re-terminate Brokaw-Clinton into added bus 3. New transmission line to Tazewell 4. New transmission line to Paxton East 5. Tie to existing Brokaw ring bus 6. Tie to existing Brokaw ring bus | AmerenIL | M2 - Appendix A Approved | 32100000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Brokaw |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27162 | 27162-Brokaw-Paxton East | Replace existing Ameren single circuit 138kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 138kV. | AmerenIL | M2 - Appendix A Approved | 160100000 | 2028-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Brokaw | Paxton East |  | 345 | 138 |  | 45 | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27163 | 27163-Paxton East- | Add 5-position 345kV breaker-and-a-half bus 1. New transmission line to Brokaw 2. New transmission line to Gilman South 3. New transmission line Sidney 4. 1-138/345kV 700MVA transformer 5. Bus-connected, 345kV, 50MVAr reactor | AmerenIL | M2 - Appendix A Approved | 59900000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Paxton East |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27164 | 27164-Paxton East- | Add 1-138/345kV 700MVA transformer | AmerenIL | M2 - Appendix A Approved | 0 | 2028-06-01 | Transformer | Transformer New | Paxton East |  |  | 345 | 138 |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | MVP | 27165 | 27165-Paxton East- | Replace 6-position 138kV breaker-and-a-half bus 1. Re-terminate Paxton-Paxton East into replaced bus 2. Re-terminate Paxton East-Gilman South into replaced bus 3. Re-terminate Paxton East-Sidney into replaced bus 4. Re-terminate Paxton East-Hoopeston into replaced bus 5. Re-terminate Paxton East-Pioneer Wind into replaced bus 6. New 138/345kV 700MVA transformer | AmerenIL | M2 - Appendix A Approved | 0 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Paxton East |  |  | 138 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27166 | 27166-Sidney- | Add 1-345kV line position (breaker-and-a-half bus) | AmerenIL | M2 - Appendix A Approved | 2600000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Sidney |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27167 | 27167-Sidney-Paxton East | Replace existing Ameren single circuit 138kV structures with double circuit structures with 1 circuit operated at 345kV and 1 circuit operated at 138kV. | AmerenIL | M2 - Appendix A Approved | 112500000 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Sidney | Paxton East |  | 345 | 138 |  | 31 | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27168 | 27168-Paxton East-Gilman South | Replace existing Ameren single circuit 138kV structures with double circuit structures, with 1 circuit operated at 345kV and 1 circuit operated at 138kV for approximately 21 miles. Construct new 345kV single circuit transmission line for approximately 2.5 miles | AmerenIL | M2 - Appendix A Approved | 89400000 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Paxton East | Gilman South |  | 345 | 138 | 2.5 | 21 | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27169 | 27169-Gilman South- | Add 3-position 345kV ring bus (expandable to breaker-and-a-half bus) 1. New transmission line to Paxton East 2. New transmission line to Morrison Ditch 3. 1-138/345kV 700MVA transformer | AmerenIL | M2 - Appendix A Approved | 24600000 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Gilman South |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27170 | 27170-Gilman South- | Add 1-138/345kV 700MVA transformer | AmerenIL | M2 - Appendix A Approved | 0 | 2029-06-01 | Transformer | Transformer New | Gilman South |  |  | 345 | 138 |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27171 | 27171-Gilman South- | Add 1-138kV line position (replace existing bus with ring bus) | AmerenIL | M2 - Appendix A Approved | 0 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Gilman South |  |  | 138 |  |  |  | IL |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27173 | 27173-Morrison Ditch- | Add 3-345kV positions ring bus (expandable to breaker-and-a-half bus) 1. New Transmission line from Gilman South 2. New Transmission line to Reynolds 3. New 138/345kV 560MVA transformer | NIPS | M2 - Appendix A Approved | 27279491 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Morrison Ditch |  |  | 345 |  |  |  | IL |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27174 | 27174-Morrison Ditch- | Add 1-138/345kV 560MVA transformer | NIPS | M2 - Appendix A Approved | 7118920 | 2029-06-01 | Transformer | Transformer New | Morrison Ditch |  |  | 345 | 138 |  |  | IL |  | Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 14964 | Small Capital Project and Asset Renewal Program 2022 | Other | 23465 | 23465-NA- | Small Capital Project and Asset Renewal 2022 | ATC | M3 - Under Construction | 52320773 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | NA |  |  | 345 | 69 |  |  | WI | MI | Not Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 14968 | Load Interconnection Program 2022 | Other | 23479 | 23479-NA- | Distribution Interconnection 2022 | ATC | M3 - Under Construction | 27586994 | 2032-02-04 | Substation | Substation (breakers only, no transformer) | NA |  |  | 138 | 69 |  |  | WI | MI | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | West | 15848 | Jayess Loop Project | Other | 23917 | 23917-Norfield switching station-Little Creek | Rebuild L523 (Norfield SS to Little Creek). | Entergy-MS | M2 - Appendix A Approved | 2070000 | 2027-03-01 | Line Upgrade | Line rebuild on existing ROW | Norfield switching station | Little Creek |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | West | 15848 | Jayess Loop Project | Other | 23918 | 23918-Jayess GOAB- | Tap L549 (Jayess SS to Jayess) with a 115kV GOAB. | Entergy-MS | M2 - Appendix A Approved | 260000 | 2027-03-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Jayess GOAB |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | West | 15848 | Jayess Loop Project | Other | 23919 | 23919-Little Creek GOAB- | Tap L523 (Norfield SS to Little Creek) with a 115kV GOAB. | Entergy-MS | M2 - Appendix A Approved | 260000 | 2027-03-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Little Creek GOAB |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | West | 15848 | Jayess Loop Project | Other | 23920 | 23920-Jayess GOAB-Little Creek GOAB | Build a new 115kV transmission line from Jayess GOAB to Little Creek GOAB. | Entergy-MS | M2 - Appendix A Approved | 4680000 | 2027-03-01 | Line New | New Transmission line, new ROW - may include terminations | Jayess GOAB | Little Creek GOAB |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | West | 15848 | Jayess Loop Project | Other | 23921 | 23921-Jayess switching station- | Build a new 115kV breaker switching station at Jayess. | Entergy-MS | M2 - Appendix A Approved | 1800000 | 2027-03-01 | Substation | Switching station (breakers only, no transformer) | Jayess switching station |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | Central | 15848 | Jayess Loop Project | Other | 23922 | 23922-Norfield switching station- | Build a new 115kV breaker switching station at Norfield. | Entergy-MS | M2 - Appendix A Approved | 2290000 | 2027-03-01 | Substation | Switching station (breakers only, no transformer) | Norfield switching station |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 23926 | 23926-Pisgah GOAB-Magee Road switching station | Rebuild L546 (Pisgah GOAB to Magee Road SS). | Entergy-MS | M2 - Appendix A Approved | 1207500 | 2027-03-01 | Line Upgrade | Line rebuild on existing ROW | Pisgah GOAB | Magee Road switching station |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 23927 | 23927-Arlington GOAB-Arlington | Rebuild L547 (Arlington GOAB to Arlington). | Entergy-MS | M2 - Appendix A Approved | 1897500 | 2027-03-01 | Line Upgrade | Line rebuild on existing ROW | Arlington GOAB | Arlington |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 23928 | 23928-Arlington Sub GOAB- | Tap L547 (Arlington GOAB to Arlington) with a 115kV GOAB. | Entergy-MS | M2 - Appendix A Approved | 260000 | 2027-03-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Arlington Sub GOAB |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 23929 | 23929-Olive Oil GOAB- | Tap L576 (Magee Road SS to Olive Oil) with a 115kV GOAB. | Entergy-MS | M2 - Appendix A Approved | 260000 | 2027-03-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Olive Oil GOAB |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 23930 | 23930-Arlington Sub GOAB-Olive Oil GOAB | Build a new 115kV transmission line from Arlington Sub GOAB to Olive Oil GOAB. | Entergy-MS | M2 - Appendix A Approved | 4680000 | 2027-03-01 | Line New | New Transmission line, new ROW - may include terminations | Arlington Sub GOAB | Olive Oil GOAB |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15850 | Olive Oil Loop Project | Other | 23931 | 23931-Arlington- | Build a new 115kV breaker switching station at Arlington. | Entergy-MS | M2 - Appendix A Approved | 1800000 | 2027-03-01 | Substation | Switching station (breakers only, no transformer) | Arlington |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | AMERICAN TRANSMISSION COMPANY | West | 18048 | Lincoln - 43rd Street Terminal 138 kV (5053), Replace with double circuit duct bank and XLPE cable | Other | 24828 | Lincoln - 43rd Street Terminal 138 kV (5053), Replace with double circuit duct bank and XLPE cable | Line Rebuild - Underground | ATC | M3 - Under Construction | 74300000 | 2027-07-01 | Line Upgrade | Line rebuild on existing ROW | Lincoln | Bluemound | 5053 | 138 |  |  |  | WI |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 26591 | 26591-Avoca- | Replace 161 kV breaker at Avoca | MEC | M2 - Appendix A Approved | 450000 | 2030-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Avoca |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 26707 | 26707-Wright- | Wright 161 kV sub work | MEC | M4 - Project in Service | 900000 | 2023-01-01 | Substation | Circuit Breaker (replacement at existing substation) | Wright |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | METC | East | 19546 | J875 Generator Interconnection | GIP | 26738 | 26738-Blackstone- | Install Sar-8 at Blackstone substation. Create communication path between Leoni-Parr, and Parr-Tangent. | METC | M4 - Project in Service | 328271 | 2023-09-01 | Substation | Small miscellaneous substation equipment | Blackstone |  |  | 138 |  |  |  | MI |  | Shared
MTEP21 | A | COOPERATIVE ENERGY | South | 15848 | Jayess Loop Project | Other | 27925 | 27925-Jayess Switching Station-Jayess | Rebuild L549 Jayess Switching Station to Jayess | Entergy-MS | M2 - Appendix A Approved | 5184000 | 2027-03-01 | Line Upgrade | Line rebuild on existing ROW | Jayess Switching Station | Jayess |  | 115 |  |  |  | MS |  | Not Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 28341 | 28341-Gilman South-Illinois/Indiana State Border | Replace existing Ameren single circuit 138kV structures with double circuit structures capable of supporting 1 circuit operated at 345kV and 1 circuit operated at 138kV for approximately 28 miles. Construct new 345kV single circuit transmission line for approximately 2 miles. | AmerenIL | M2 - Appendix A Approved | 97400000 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Gilman South | Illinois/Indiana State Border |  | 345 | 138 | 2 | 28 | IL |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 28342 | 28342-Illinois/Indiana State Border-Morrison Ditch | Replace existing NIPSCO single circuit 138kV structures with double circuit structures capable of supporting 1 circuit operated at 345kV and 1 circuit operated at 138kV for approximately 2 miles. | NIPS | M2 - Appendix A Approved | 37580596 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Illinois/Indiana State Border | Morrison Ditch |  | 345 | 138 |  | 2 | IN |  | Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 28380 | 28380-Lehigh Substation- | Lehigh Substation | MEC | M2 - Appendix A Approved | 3000000 | 2029-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Lehigh Substation |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | PRAIRIE POWER, INC. | Central | 19951 | Rebuild Pisgah - Berlin 69 kV Line | Other | 25634 | Rebuild Pisgah-Berlin 69 kV line | Rebuild Pisgah-Berlin 69 kV line with 336 ACSR | PPI | M2 - Appendix A Approved | 7880000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Pisgah | Berlin |  | 69 |  |  | 15.76 | IL |  | Not Shared
MTEP21 | A | AMEREN MISSOURI | Central | 19969 | New Belleau 138 kV Capacitor Bank | BRP | 25652 | 25652-Belleau- | Belleau 345/138 kV Substation - Install 138 kV capacitor bank | AmerenMO | M2 - Appendix A Approved | 22400000 | 2027-06-01 | Voltage Device | Capacitor (switched capacitor) | Belleau |  |  | 345 | 138 |  |  | MO |  | Not Shared
MTEP21 | A | METC | East | 19970 | Rebuild Alma - Vestaburg 138 kV 477 ACSR | BRP | 25653 | 25653-Alma-Vestaburg | Rebuild approximately 0.43 mile of the Alma - Vestaburg 138kV circuit using 954 ACSR on double circuit structures constructed at 138kV Standards with OPGW. | METC | M2 - Appendix A Approved | 3350000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Alma | Vestaburg | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | METC | East | 19970 | Rebuild Alma - Vestaburg 138 kV 477 ACSR | BRP | 25654 | 25654-Alma- | Replace terminal equipment at Alma | METC | M2 - Appendix A Approved | 84000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Alma |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | ENTERGY SERVICES, LLC. | South | 19987 | Nelson 230/138 kV Relay Improvement SPOF | BRP | 25659 | 25659-Nelson- | Ensure dual battery installations or monitoring sufficient to FERC 754 guidelines at Nelson 230 kV and 138 kV. | Entergy-LA | M4 - Project in Service | 7700000 | 2025-07-10 | Misc. | Substation battery replacement | Nelson |  |  | 230 | 138 |  |  | LA |  | Not Shared
MTEP21 | A | ENTERGY SERVICES, LLC. | South | 19987 | Nelson 230/138 kV Relay Improvement SPOF | BRP | 25660 | 25660-Nelson- | Ensure coordination with PowerGen on GSU high speed dual primary protection for all generation at Nelson | Entergy-LA | M3 - Under Construction | 9500000 | 2027-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Nelson |  |  | 230 | 138 |  |  | LA |  | Not Shared
MTEP21 | A | EAST TEXAS ELECTRIC COOPERATIVE, INC. | South | 19954 | Newton 138 kV Station | Other | 25663 | 25663-Jasper Newton 69 kV- | Route Entergy 138 kV line #420 in and out of adjacent JNEC Newton 69 kV substation. At JNEC Newton, install 138/69 kV transformer and 138 kV line breakers and relaying. | Entergy-TX | M2 - Appendix A Approved | 3800000 | 2027-05-01 | Substation | Substation (breakers only, no transformer) | Jasper Newton 69 kV |  |  | 138 | 69 |  |  | TX |  | Not Shared
MTEP21 | A | EAST TEXAS ELECTRIC COOPERATIVE, INC. | South | 19954 | Newton 138 kV Station | Other | 25664 | 25664-Jasper Newton 69 kV- | At JNEC Newton, install 138 kV bus. | Entergy-TX | M2 - Appendix A Approved | 1500000 | 2027-05-01 | Substation | Substation bus upgrade | Jasper Newton 69 kV |  |  | 138 | 69 |  |  | TX |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | Other | 25671 | 25671-Monona-Substation | ITC rebuild the Monona 69kV substation and install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor at a new Monona Substation adjacent to the existing site. All substation equipment should have a minimum rating of 1200A. | ITCM | M2 - Appendix A Approved | 6275558 | 2026-09-30 | Substation | Substation (breakers only, no transformer) | Monona | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Other | 25673 | 25673-Sub. Fort Dodge M- | Add 161 kV circuit breaker at Sub Fort Dodge M to increase reliability and operational flexibility. | MEC | M4 - Project in Service | 250000 | 2023-04-01 | Substation | Circuit Breaker (replacement at existing substation) | Sub. Fort Dodge M |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19998 | NW 2nd Street Substation | Other | 25674 | 25674-NW 2nd Street- | New 69 kV distribution substation | MEC | M3 - Under Construction | 7500000 | 2027-07-31 | Substation | Substation (breakers only, no transformer) | NW 2nd Street |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 19998 | NW 2nd Street Substation | Other | 25675 | 25675-NW 2nd Street- | New 69 kV Line Work | MEC | M3 - Under Construction | 2500000 | 2027-07-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | NW 2nd Street |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | GRIDLIANCE HEARTLAND LLC | Central | 20001 | Rebuild Joppa-Shawnee 161 kV Ckt 3 | Other | 25678 | 25678-Joppa-Shawnee | Rebuild Joppa-Shawnee 161 kV Ckt 3 | GLH | M2 - Appendix A Approved | 11700000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Joppa | Shawnee | 3 | 161 |  |  | 8 | IL | KY | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20002 | Waukee: Add 69 kV Capacitor Bank | Other | 25679 | 25679-Waukee- | Install 69 kV capacitor bank and 69 kV breakers | MEC | M2 - Appendix A Approved | 6000000 | 2028-08-31 | Voltage Device | Capacitor (switched capacitor) | Waukee |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | GRIDLIANCE HEARTLAND LLC | Central | 20004 | Rebuild Joppa-Shawnee 161 kV Ckt 4 | Other | 25680 | 25680-Joppa-Shawnee | Rebuild 8 miles of Joppa-Shawnee 161 kV Ckt 4 | GLH | M2 - Appendix A Approved | 11700000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Joppa | Shawnee | 4 | 161 |  |  | 8 | IL | KY | Not Shared
MTEP21 | A | GRIDLIANCE HEARTLAND LLC | Central | 20005 | Rebuild Joppa-Shawnee 161 kV Ckt 1 | Other | 25681 | 25681-Joppa-Shawnee | Rebuild Joppa - Shawnee 161 kV ckt 1 | GLH | M2 - Appendix A Approved | 14700000 | 2031-12-31 | Line Upgrade | Line rebuild on existing ROW | Joppa | Shawnee | 1 | 161 |  |  | 10 | KY | IL | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20003 | Highway 6 161/13.2 kV Substation | Other | 25682 | 25682-Highway 6- | New 161/13.2 kV substation | MEC | M2 - Appendix A Approved | 3100000 | 2027-07-31 | Substation | Substation (breakers only, no transformer) | Highway 6 |  |  | 161 | 13 |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20003 | Highway 6 161/13.2 kV Substation | Other | 25683 | 25683-Highway 6- | 161 kV Line Work | MEC | M2 - Appendix A Approved | 2900000 | 2027-07-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Highway 6 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20007 | Clarion: Add 69 kV Breakers | Other | 25685 | 25685-Clarion- | Substation bus expansion | MEC | M2 - Appendix A Approved | 2000000 | 2028-12-31 | Substation | Substation bus upgrade | Clarion |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20011 | Sub 84: 69 kV Line Taps and Line Upgrades | Other | 25688 | 25688-Sub 84-69 kV Line Taps | 69 kV line tap work to support converting Sub 84 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. | MEC | M3 - Under Construction | 500000 | 2026-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Sub. 84 |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20011 | Sub 84: 69 kV Line Taps and Line Upgrades | Other | 25689 | 25689-Valley Drive-Sub 84 69 kV Reconductor and OPGW | Install OPGW from Valley Drive to Sub 84 for communications and replace structures and conductor on sections of line subject to galloping. | MEC | M4 - Project in Service | 6400000 | 2024-11-15 | Line Upgrade | Line rebuild on existing ROW | Valley Drive | Sub. 84 | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | MIDAMERICAN ENERGY CO. | West | 20011 | Sub 84: 69 kV Line Taps and Line Upgrades | Other | 25690 | 25690-Sub 84-Sub 55 69 kV Reconductor and OPGW | Install OPGW from Sub 84 to Sub 55 for communications and replace structures and conductor on sections of line subject to galloping. | MEC | M4 - Project in Service | 6300000 | 2024-07-27 | Line Upgrade | Line rebuild on existing ROW | Sub. 84 | Sub. 55 | 1 | 69 |  |  |  | IA |  | Not Shared
MTEP21 | A | METC | East | 20018 | Rebuild Bullock - Shale 138 kV | BRP | 25701 | 25701-Bullock-Shale | Rebuild the Bullock to Structure 006A6682 (approximately 5 miles) utilizing 954 ACSR conductor with 230 kV double circuit structure standards with OPGW. Rebuild from Structure 006A6682 to the future Shale Substation (approximately 15 miles) utilizing 954 ACSR conductor with 138 kV double circuit structures standards with OPGW | METC | M2 - Appendix A Approved | 37330539 | 2028-02-04 | Line Upgrade | Line rebuild on existing ROW | Bullock | Shale | 1 | 138 |  |  | 20 | MI |  | Not Shared
MTEP21 | A | METC | East | 20018 | Rebuild Bullock - Shale 138 kV | BRP | 25702 | 25702-Bullock- | Upgrade terminal station equipment | METC | M2 - Appendix A Approved | 64846 | 2027-06-03 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Bullock |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20026 | Osage Jct-Rice 69kV Rebuild | Other | 25715 | 25715-Osage Jct-Douglas Tap | Phase 1: The line between Osage JCT and Douglas Tap (~13.9 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | ITCM | M2 - Appendix A Approved | 12660000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Osage Jct | Douglas Tap | 1 | 69 | 69 |  | 13.9 | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20026 | Osage Jct-Rice 69kV Rebuild | Other | 25716 | 25716-Riceville-Rice | Phase 2: The line between Riceville and Rice (~9.8 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | ITCM | M2 - Appendix A Approved | 10320000 | 2029-12-31 | Line Upgrade | Line rebuild on existing ROW | Riceville | Rice | 1 | 69 | 69 |  | 9.8 | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25720 | 25720-Winterset Jct-Tiberius | ITC will be building about 29 miles of 161kV line from CIPCO’s Winterset Jct. to Osceola’s new substation. All new lines should be T2 636 ACSR and rated at 2000A or higher minimum summer normal rating. | ITCM | M2 - Appendix A Approved | 49920538 | 2027-05-01 | Line New | New Transmission line, new ROW - may include terminations | Winterset Jct | Tiberius | 1 | 161 | 161 | 29 |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25721 | 25721-Tiberius-Substation | ITC will construct a new Tiberius 161/69kV, 150 MVA transformer will be needed in the Osceola area to provide a new 69kV source for the area. | ITCM | M2 - Appendix A Approved | 8584794 | 2029-05-07 | Substation | Substation (breakers only, no transformer) | Tiberius | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25722 | 25722-Raysh-Substation | New 69kV switch station in the Albia area. | ITCM | M2 - Appendix A Approved | 4642593 | 2027-05-01 | Substation | Switching station (breakers only, no transformer) | Raysh | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | ITC MIDWEST | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | Other | 25723 | 25723-Golem-Substation | New 69kV breaker station in the Lenox area. | ITCM | M2 - Appendix A Approved | 3568525 | 2027-05-01 | Substation | Switching station (breakers only, no transformer) | Golem | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27175 | 27175-Morrison Ditch- | Add 1-138kV transformer position (ring bus) Replace substation bus for 3000A | NIPS | M2 - Appendix A Approved | 6788927 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Morrison Ditch |  |  | 138 |  |  |  | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27176 | 27176-Hoopeston West-Rossville | Replace 138kV conductor to achieve 2000A | AmerenIL | M2 - Appendix A Approved | 6000000 | 2029-06-01 | Line Upgrade | Line reconductor | Hoopeston West | Rossville |  | 138 |  |  | 5.5 | IL |  | Shared
MTEP21 | A | AMEREN ILLINOIS | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | MVP | 27177 | 27177-Hoopeston West- | Replace substation bus to achieve 2000A | AmerenIL | M2 - Appendix A Approved | 0 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Hoopeston West |  |  | 138 |  |  |  | IL |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27178 | 27178-Morrison Ditch-Reynolds | Replace existing NIPSCO single circuit 138kV structures with double circuit structures capable of supporting 1 circuit operated at 345kV and 1 circuit operated at 138kV for approximately 34 miles. Construct new 345kV single circuit transmission line for approximately 7 miles. | NIPS | M2 - Appendix A Approved | 181549224 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Morrison Ditch | Reynolds |  | 345 | 138 | 7 | 34 | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27179 | 27179-Goodland- | Replace terminal equipment to achieve 3000A | NIPS | M2 - Appendix A Approved | 6430077 | 2029-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Goodland |  |  | 138 |  |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27180 | 27180-Reynolds- | Add 3-345kV line positions (breaker-and-a-half bus) 1. New transmission line to Morrison Ditch 2. New transmission line to Burr Oak 3. New 138/345kV 560MVA transformer | NIPS | M2 - Appendix A Approved | 26911928 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Reynolds |  |  | 345 |  |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27181 | 27181-Reynolds- | Add 1-138/345kV 560 MVA transformer Replace 1-138/345kV 350 MVA transformer with a 138/345kV 560MVA transformer | NIPS | M2 - Appendix A Approved | 13535966 | 2029-06-01 | Transformer | Transformer New | Reynolds |  |  | 345 | 138 |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27182 | 27182-Reynolds- | Add 1-138kV transformer position Replace existing straight bus with a ring (expandable to breaker-and-a-half) bus | NIPS | M2 - Appendix A Approved | 7479670 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Reynolds |  |  | 138 |  |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27183 | 27183-Reynolds-Monticello | Replace 138kV conductor from ACSR conductor to ACSS conductor of same size and replace fiber optic cable | NIPS | M2 - Appendix A Approved | 19770832 | 2029-06-01 | Line Upgrade | Line reconductor | Reynolds | Monticello |  | 138 |  |  | 7 | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27184 | 27184-Monticello- | Replace terminal equipment to achieve 3000A | NIPS | M2 - Appendix A Approved | 2868121 | 2029-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Monticello |  |  | 138 |  |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27185 | 27185-Reynolds-Burr Oak | Install second 345kV circuit on open spare position on existing structures on existing Reynolds - Burr Oak 345kV transmission line | NIPS | M2 - Appendix A Approved | 60679572 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Reynolds | Burr Oak |  | 345 |  |  | 48 | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27186 | 27186-Burr Oak- | Add 2-345kV line positions (breaker-and-a-half bus) | NIPS | M2 - Appendix A Approved | 9827655 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Burr Oak |  |  | 345 |  |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27187 | 27187-Burr Oak-Leesburg | Install second 345kV circuit on open spare position on existing structures on existing Burr Oak - Leesburg 345kV line | NIPS | M2 - Appendix A Approved | 54075433 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Burr Oak | Leesburg |  | 345 |  |  | 29 | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27188 | 27188-Leesburg- | Add 2-345kV line positions (replace existing bus with breaker-and-a-half bus) | NIPS | M2 - Appendix A Approved | 28969797 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Leesburg |  |  | 345 |  |  |  | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27189 | 27189-Leesburg-Hiple, F G | Add 345kV circuit to spare position on existing transmission line structure | NIPS | M2 - Appendix A Approved | 41615974 | 2029-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Leesburg | Hiple, F G |  | 345 |  |  | 23 | IN |  | Shared
MTEP21 | A | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | MVP | 27190 | 27190-Hiple, F G- | Add 3-345kV line positions (breaker-and-a-half bus) 1. New transmission line to Leesburg 2. New transmission line to Duck Lake 3. New transmission line to Duck Lake | NIPS | M2 - Appendix A Approved | 24085750 | 2029-06-01 | Substation | Substation (breakers only, no transformer) | Hiple, F G |  |  | 345 |  |  |  | IN |  | Shared
MTEP21 | A | REPUBLIC TRANSMISSION, LLC | East | 23419 | LRTP-17: Hiple – Duck Lake | MVP | 27191 | 27191-Hiple, F G-IN/MI State Border | Construct new 345kV double circuit transmission line | REPUBLIC TRANSMISSION, LLC | M2 - Appendix A Approved | 77300898 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | Hiple, F G | IN/MI State Border |  | 345 |  | 55 |  | IN |  | Shared
MTEP21 | A | METC | East | 23419 | LRTP-17: Hiple – Duck Lake | MVP | 27192 | 27192-IN/MI State Border-Duck Lake | Construct new 345kV double circuit transmission line | METC | M2 - Appendix A Approved | 406700000 | 2030-06-01 | Line New | New Transmission line, new ROW - may include terminations | IN/MI State Border | Duck Lake |  | 345 |  | 72 |  | MI |  | Shared
MTEP21 | A | METC | East | 23419 | LRTP-17: Hiple – Duck Lake | MVP | 27193 | 27193-Duck Lake (42.41, -84.792)- | Construct new 8-position 345kV breaker-and-a-half bus substation. Loop in Argenta-Tompkins, Battle Creek-Oneida, and Oneida-Majestic 345 kV lines into Duck Lake. | METC | M2 - Appendix A Approved | 35800000 | 2026-12-29 | Substation | Substation (breakers only, no transformer) | Duck Lake (42.41, -84.792) |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27194 | 27194-Oneida- | Add 2-345kV line positions (replace existing bus with breaker-and-a-half bus) | METC | M2 - Appendix A Approved | 8900000 | 2029-12-29 | Substation | Substation (breakers only, no transformer) | Oneida |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27195 | 27195-Oneida-Nelson Road | Construct new 345kV double circuit transmission line | METC | M2 - Appendix A Approved | 181900000 | 2029-12-29 | Line New | New Transmission line, new ROW - may include terminations | Oneida | Nelson Road |  | 345 |  | 38.5 |  | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27196 | 27196-Nelson Road- | Add 2-345kV line positions (breaker-and-a-half bus) | METC | M2 - Appendix A Approved | 5500000 | 2029-12-29 | Substation | Substation (breakers only, no transformer) | Nelson Road |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27197 | 27197-Duck Lake (42.41, -84.792)-Tompkins | Replace double circuit 345kV transmission line (one circuit) | METC | M2 - Appendix A Approved | 20600000 | 2026-12-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Duck Lake (42.41, -84.792) | Tompkins |  | 345 |  |  | 16 | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27198 | 27198-Tompkins-Majestic | Replace double circuit 345kV transmission line (one circuit) | ITCT, METC | M2 - Appendix A Approved | 36000000 | 2027-12-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Tompkins | Majestic |  | 345 |  |  | 28 | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27199 | 27199-Tompkins- | Replace terminal equipment to achieve 3000A | METC | M4 - Project in Service |  | 2024-01-18 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Tompkins |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | ITC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27200 | 27200-Majestic- | Replace terminal equipment to achieve 3000A | ITCT | M3 - Under Construction | 1500000 | 2028-12-29 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Majestic |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | ITC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27201 | 27201-Majestic-Wayne | Replace conductor to achieve 3000A | ITCT | M4 - Project in Service | 55900000 | 2025-03-28 | Line Upgrade | Line reconductor | Majestic | Wayne |  | 345 |  |  | 31 | MI |  | Shared
MTEP21 | A | ITC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27202 | 27202-Wayne- | Replace terminal equipment to achieve 3000A | ITCT | M4 - Project in Service | 5500000 | 2024-11-27 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Wayne |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | ITC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27203 | 27203-Majestic-Coventry | Replace conductor to achieve 3000A | ITCT | M4 - Project in Service | 26500000 | 2025-03-28 | Line Upgrade | Line reconductor | Majestic | Coventry |  | 345 |  |  | 20 | MI |  | Shared
MTEP21 | A | ITC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27204 | 27204-Coventry- | Replace terminal equipment to achieve 3000A | ITCT | M4 - Project in Service | 1100000 | 2024-02-02 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Coventry |  |  | 345 |  |  |  | MI |  | Shared
MTEP21 | A | METC | East | 23420 | LRTP-18: Oneida – Nelson Rd. | MVP | 27205 | 27205-Duck Lake (42.41, -84.792)-Majestic | Replace double circuit 345kV transmission line (one circuit) | ITCT, METC | M2 - Appendix A Approved | 57800000 | 2027-12-29 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Duck Lake (42.41, -84.792) | Majestic |  | 345 |  |  | 43.5 | MI |  | Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 15598 | Badoura Transformer Replacement | BRP | 23630 | 23630-Badoura 230-Badoura 115 | Move existing Hilltop 1TR to Badoura. This transformer does not have LTCs. | MP | M2 - Appendix A Approved | 400000 | 2026-12-31 | Transformer | Transformer New | Badoura 230 | Badoura 115 |  | 230 | 115 | 0 | 0 | MN |  | Not Shared
MTEP20 | A | COOPERATIVE ENERGY | South | 17086 | Brandon Area Loop Project | Other | 24482 | 24482-South Brandon-East Brandon | Build a new 115kV line from South Brandon to East Brandon | Entergy-MS | M2 - Appendix A Approved | 3510000 | 2026-09-01 | Line New | New Transmission line, new ROW - may include terminations | South Brandon | East Brandon |  | 115 |  |  |  | MS |  | Not Shared
MTEP20 | A | COOPERATIVE ENERGY | South | 17086 | Brandon Area Loop Project | Other | 24483 | 24483-South Brandon- | Tap L540A(East Whitfield - South Brandon) | Entergy-MS | M2 - Appendix A Approved | 260000 | 2026-09-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | South Brandon |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 18078 | Upgrade Carbondale NW 138 kV substation | Other | 24863 | 24863-Carbondale NW-Substation | Replace 138 kV breaker CDNW-138KV LINE 1744 at Carbondale NW Substation. | AmerenIL | M2 - Appendix A Approved | 10700000 | 2027-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Carbondale NW | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 18081 | Upgrade Newton 138 kV substation | Other | 24868 | 24868-Newton-Switchyard | Replace 138 kV breakers NWTY-138KV LT 1869 and NWTY-138KV LT 1868 at the Newton switchyard. | AmerenIL | M3 - Under Construction | 4200000 | 2026-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Newton | Switchyard |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | ENTERGY ARKANSAS, LLC | South | 18101 | Blakehill 115kV: Construct new substation | Other | 24887 | Blakehill 115kV substation | Build a new substation with a single 40 MVA 115/13.8 kV LTC transformer. | Entergy-AR | M3 - Under Construction | 4261552 | 2026-12-31 | Substation | Distribution substation - may include trans high side | Blakehill |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 18107 | Upgrade Tilton Energy Center 138 kV substation | Other | 24895 | 24895-Tilton Energy Center-Switchyard | Replace breaker TEC-138KV LINE TIE BKR 1320 at Tilton Energy Center. | AmerenIL | M3 - Under Construction | 4300000 | 2026-06-01 | Substation | Circuit Breaker (replacement at existing substation) | Tilton Energy Center | Switchyard |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18116 | New Kilbourne-Saidora 69 kV Line | Other | 24924 | New Kilbourne-Saidora 69 kV Line | New Kilbourne-Saidora 69 kV Line in MEC | PPI | M2 - Appendix A Approved | 6195200 | 2026-07-01 | Line New | New Transmission line, new ROW - may include terminations | Saidora | Kilbourne | 1 | 69 |  | 8.67 |  | IL |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17870 | National Taconite Breaker Replacements | Other | 24930 | 24930-National Tac 78L- | Replace circuit breaker & associated equipment | MP | M2 - Appendix A Approved | 385000 | 2021-12-31 | Substation | Circuit Breaker (replacement at existing substation) | National Tac 78L |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17870 | National Taconite Breaker Replacements | Other | 24931 | 24931-National Tac 14L- | Replace circuit breaker & associated equipment | MP | M2 - Appendix A Approved | 385000 | 2021-12-31 | Substation | Circuit Breaker (replacement at existing substation) | National Tac 14L |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17870 | National Taconite Breaker Replacements | Other | 24933 | 24933-National Tac 1H- | Replace circuit breaker & associated equipment | MP | M2 - Appendix A Approved | 270000 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | National Tac 1H |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17870 | National Taconite Breaker Replacements | Other | 24934 | 24934-National Tac 2H- | Replace circuit breaker & associated equipment | MP | M2 - Appendix A Approved | 270000 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | National Tac 2H |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17870 | National Taconite Breaker Replacements | Other | 24935 | 24935-National Tac 3H- | Replace circuit breaker & associated equipment | MP | M2 - Appendix A Approved | 270000 | 2025-12-31 | Substation | Circuit Breaker (replacement at existing substation) | National Tac 3H |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 9100 | Burlington-4th St-Agency 69kV Rebuild | Other | 24948 | 24948-Burlington-Burlington South | Upgrade the terminal equipment on the Burlington terminal 6994 so the line is conductor limited (132MVA minimum). | ITCM | M2 - Appendix A Approved | 26160 | 2028-05-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Burlington | Burlington South | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | ITC | East | 15883 | Bismarck-Stephens #2 120 kV Rebuild | BRP | 28040 | 28040-Stephens- | Upgrade Station Equipment at Pos. GK | ITCT | M2 - Appendix A Approved | 300000 | 2028-04-21 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Stephens |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 15883 | Bismarck-Stephens #2 120 kV Rebuild | BRP | 28041 | 28041-Bismarck- | Upgrade Station Equipment at Pos. JL | ITCT | M2 - Appendix A Approved | 200000 | 2028-04-21 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Bismarck |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 15900 | Rebuild Wayne - Newburgh #1 120 kV | BRP | 24005 | 24005-Wayne-Newburgh | Rebuild approximately 2.7 miles of 795 ACSS conductor to 2156 ACSS on the Wayne – Newburgh #1 120 kV circuit. | ITCT | M2 - Appendix A Approved | 6810000 | 2027-04-02 | Line Upgrade | Line rebuild on existing ROW | Wayne | Newburgh | 1 | 120 |  |  | 2.7 | MI |  | Not Shared
MTEP20 | A | ITC | East | 15900 | Rebuild Wayne - Newburgh #1 120 kV | BRP | 24006 | 24006-Wayne | Terminate OPGW at WAYNE substation | ITCT | M2 - Appendix A Approved | 690000 | 2027-04-02 | Substation | Small miscellaneous substation equipment | Wayne |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 15900 | Rebuild Wayne - Newburgh #1 120 kV | BRP | 24007 | 24007-Newburgh- | Terminate OPGW at Newburgh Station. | ITCT | M2 - Appendix A Approved | 220000 | 2027-04-02 | Substation | Small miscellaneous substation equipment | Newburgh |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 15987 | Berry Plastics Dist. XFMR Repl. | Other | 24118 | 24118-Berry Plastics- | Replace one of the 69 kV distribution transformers serving Berry Plastics | SIGE | M2 - Appendix A Approved | 1100000 | 2029-12-31 | Transformer | Transformer New | Berry Plastics |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP20 | A | METC | East | 15939 | Leoni - Beecher 138 kV Sixed Wire | BRP | 24052 | 24052-Leoni-Beecher | Sixed wire 0.21 miles of the Mercer – Cement City Jct. section of the Leoni – Beecher circuit using existing 477 ACSR conductor. Also remediate sag limit on the 6-wired conductor section to increase its summer emergency rating to a minimum of 1196 Amps (286 MVA). | METC | M2 - Appendix A Approved | 8300000 | 2027-04-30 | Line Upgrade | Line rebuild on existing ROW | Leoni | Beecher | 1 | 138 |  |  | 0.21 | MI |  | Not Shared
MTEP20 | A | ITC | East | 16015 | Sunset - Quaker 120 kV Rebuild | BRP | 24151 | 24151-Sunset-Quaker | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | ITCT | M2 - Appendix A Approved | 2000000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Sunset | Quaker | 1 | 120 |  |  | 0.26 | MI |  | Not Shared
MTEP20 | A | ITC | South | 16015 | Sunset - Quaker 120 kV Rebuild | BRP | 24152 | 24152-Sunset- | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | ITCT | M2 - Appendix A Approved | 130000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Sunset |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 16015 | Sunset - Quaker 120 kV Rebuild | BRP | 24153 | 24153-Quaker- | The proposed solution is to rebuild 0.259 mile of the Sunset – Quaker 120kV circuit using 2156 ACSR conductor with single circuit steel structures and replace terminal equipment and station equipment at Quaker Pos HD and Sunset Pos HN. | ITCT | M2 - Appendix A Approved | 130000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Quaker |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | DUKE ENERGY INDIANA, LLC | Central | 2864 | Reconductor Centerton to Martinsville 69kV - 69163 ckt. | Other | 5017 | 5017-Centeron-Martinsville | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | DEI | M2 - Appendix A Approved | 6477000 | 2027-12-15 | Line Upgrade | Line reconductor | Centeron | Martinsville | 1 | 69 |  |  | 3.7 | IN |  | Not Shared
MTEP20 | A | COOPERATIVE ENERGY | South | 17086 | Brandon Area Loop Project | Other | 25469 | 25469-Whitfield- | Entergy - Install substation breakers at Whitfield 115kV substation | Entergy-MS | M2 - Appendix A Approved | 6182989 | 2026-09-01 | Substation | Circuit Breaker (replacement at existing substation) | Whitfield |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP20 | A | CITY OF ALEXANDRIA, LA | South | 19408 | Sterkx – Willow Glen 138 kV Reconductor | Other | 25477 | 25477-Sterkx-Willow Glen | Reconductor. | AXLA | M2 - Appendix A Approved | 940000 | 2027-05-31 | Line Upgrade | Line reconductor | Sterkx | Willow Glen | 1 | 138 |  |  |  | LA |  | Not Shared
MTEP20 | A | ITC | East | 19565 | Trenton Channel 120 kV - Upgrade HH Station Equipment | BRP | 25511 | 25511-Trenton Channel- | Upgrade station equipment at Trenton Channel 120 kV position HH. | ITCT | M2 - Appendix A Approved | 335000 | 2029-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Trenton Channel |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 19607 | Brownstown - Navarre #2 230 kV Sag Remediation | BRP | 25520 | 25520-Navarre- | Upgrade station equipment at Navarre 230 kV | ITCT | M2 - Appendix A Approved | 85000 | 2027-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Navarre |  |  | 230 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 19607 | Brownstown - Navarre #2 230 kV Sag Remediation | BRP | 25521 | 25521-Brownstown-Navarre | Remediate the sag on the Brownstown - Navarre #2 230 kV circuit up to the conductor limit. | ITCT | M2 - Appendix A Approved | 985000 | 2027-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Brownstown | Navarre | 2 | 230 |  |  |  | MI |  | Not Shared
MTEP20 | A | EAST TEXAS ELECTRIC COOPERATIVE, INC. | South | 19665 | Deer to Indian 138 kV line | BRP | 25527 | 25527-Deer-Indian (or to the new switching station) | Build ~16 miles of new 138 kV transmission line from Deer substation to Indian substation (or to the new switching station). The final length of the line is contingent on the solution to construct. | Entergy-TX | M2 - Appendix A Approved | 28860000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Deer | Indian (or to the new switching station) |  | 138 |  |  |  | TX |  | Not Shared
MTEP20 | A | EAST TEXAS ELECTRIC COOPERATIVE, INC. | South | 19665 | Deer to Indian 138 kV line | BRP | 25528 | 25528-Indian- | Build a new 3 breaker ring bus switching station (cut into existing Indian to Gulf Livingston transmission line) approximately 1 mile to the west of Indian Substation. | Entergy-TX | M2 - Appendix A Approved | 3660000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | Indian |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP20 | A | EAST TEXAS ELECTRIC COOPERATIVE, INC. | South | 19665 | Deer to Indian 138 kV line | BRP | 25529 | 25529-Deer- | Install transmission upgrades at Deer substation - Install a new 138kV breaker, CCVT, and 138kV Disconnect switches. | Entergy-TX | M2 - Appendix A Approved | 500000 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Deer |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP20 | A | EAST TEXAS ELECTRIC COOPERATIVE, INC. | South | 19665 | Deer to Indian 138 kV line | BRP | 25530 | 25530-Gulf Livingston- | Install transmission upgrades at Gulf Livingston substation - install a new CCVT, transmission relay panel, and conduit/cable. | Entergy-TX | M2 - Appendix A Approved | 320000 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Gulf Livingston |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP20 | A | METC | East | 18728 | Cobb (Chopin) - Sternberg 138kV Line Rebuild | BRP | 25556 | 25556-Sternberg- | Upgrade line entrance at Sternberg | METC | M4 - Project in Service | 200000 | 2024-03-08 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Sternberg |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP20 | A | METC | East | 18728 | Cobb (Chopin) - Sternberg 138kV Line Rebuild | BRP | 25564 | 25564-CHOPIN- | Terminate fiber in station | METC | M2 - Appendix A Approved | 50000 | 2027-10-29 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | CHOPIN |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18166 | New Virginia - Saidora 69 kV Line | Other | 51688 | New Virginia-Drake BKR 69 kV Line | New Virginia-Drake 69 kV Line with 556 ACSR | PPI | M2 - Appendix A Approved | 1450000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Virginia | Drake |  | 69 |  | 2.25 |  | IL |  | Not Shared
MTEP20 | A | METC | West | 15809 | Four Mile (Northridge) - North Belding 138 kV Rebuild | BRP | 23841 | 23841-Four Mile (Northridge)-North Belding | The proposed solution is to rebuild 8.38 miles Alpine Jct. – Rogue River Jct. and Rogue River Jct. – Cannon Jct. sections of the Four Mile – North Belding 138kV line using 954 ACSR conductor. | METC | M2 - Appendix A Approved | 11700000 | 2025-12-31 | Line Upgrade | Line rebuild on existing ROW | Four Mile (Northridge) | North Belding | 1 | 138 |  |  | 8.38 | MI |  | Not Shared
MTEP20 | A | NORTHERN STATES POWER COMPANY | West | 18131 | Orienta Tap - Iron River 34.5kV Rebuild | Other | 24952 | 24952-Iron River-Port Wing | Rebuild 9 miles of 34.5kV line from Iron River to Port Wing to remediate aging condition issues. | XEL | M2 - Appendix A Approved | 5000000 | 2026-12-15 | Line Upgrade | Line rebuild on existing ROW | Iron River | Port Wing | 1 | 35 |  |  |  | WI |  | Not Shared
MTEP20 | A | METC | East | 18133 | Station Eq. Upgrades Pere Marquette 138 kV 5M9 & 7W8 | BRP | 24954 | 24954-Pere Marquette- | Upgrade two breakers (at positions 5M9 and 7W8) and other overloaded station equipment at the Pere Marquette 138 kV station. | METC | M2 - Appendix A Approved | 970000 | 2028-05-15 | Substation | Substation (breakers only, no transformer) | Pere Marquette |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18157 | New Indian Creek 138/69 kV Substation | Other | 24976 | New Ameren Duff-PPI Indian Creek 138 kV line | New Ameren Duff - PPI Indian Creek 138 kV line in IEC | PPI | M3 - Under Construction | 1425000 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Ameren Duff | Indian Creek |  | 138 |  | 1 |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18157 | New Indian Creek 138/69 kV Substation | Other | 24979 | New Indian Creek 138/69 kV Substation | New Indian Creek 138/69 kV Substation with 56 MVA XFMR | PPI | M3 - Under Construction | 6000000 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Indian Creek |  |  | 138 | 69 |  |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18160 | New Arenzville - Bluff Springs 69 kV Line | Other | 24981 | New Arenzville-Bluff Springs 69 kV line | New Arenzville - Bluff Springs 69 kV line tying IEC to MEC | PPI | M2 - Appendix A Approved | 7459000 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Arenzville | Bluff Springs | 1 | 69 | 69 | 10.5 |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18161 | New Bluff Springs - Virginia 69 kV Line | Other | 24982 | New Bluff Springs-Virginia 69 kV Line | New Bluff Springs-Virginia 69 kV Line in MPC | PPI | M2 - Appendix A Approved | 8000000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Bluff Springs | Virginia |  | 69 | 69 | 13.9 |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18162 | New Ellisville-Kington 69 kV Line | Other | 24983 | New Ellisville-Kington 69 kV Line | New Ellisville-Kington 69 kV Line tying MPC to SREC | PPI | M3 - Under Construction | 11925000 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Ellisville | Kington | 1 | 69 | 69 | 18 |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18165 | New Drake 69 kV Breaker Station | Other | 24986 | New Drake 69 kV Breaker Station | New Drake 69 kV Breaker Station | PPI | M2 - Appendix A Approved | 3954825 | 2026-12-01 | Substation | Switching station (breakers only, no transformer) | Drake |  |  | 69 | 69 |  |  | IL |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18166 | New Virginia - Saidora 69 kV Line | Other | 24987 | New Drake BKR-Saidora 69 kV Line | New Drake-Saidora 69 kV Line with 556 ACSR | PPI | M2 - Appendix A Approved | 9490000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Drake BKR | Saidora | 1 | 69 |  | 14.6 |  | IL |  | Not Shared
MTEP20 | A | ITC | East | 18168 | Reconductor of Bismarck - Red Run 230 kV | BRP | 24990 | 24990-Bismarck-Red Run | Reconductor approximately 2 miles utilizing 1431 ACSR and upgrade terminal station equipment at Bismarck and Red Run. | ITCT | M2 - Appendix A Approved | 2250000 | 2028-05-11 | Line Upgrade | Line reconductor | Bismarck | Red Run | 1 | 230 |  |  | 2 | MI |  | Not Shared
MTEP20 | A | ITC | East | 18168 | Reconductor of Bismarck - Red Run 230 kV | BRP | 24991 | 24991-Bismarck- | Upgrade terminal equipment at Bismarck 230 kV station. | ITCT | M2 - Appendix A Approved | 47000 | 2028-05-11 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Bismarck |  |  | 230 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 18168 | Reconductor of Bismarck - Red Run 230 kV | BRP | 24992 | 24992-Red Run- | Upgrade terminal equipment at Red Run 230 kV station. | ITCT | M2 - Appendix A Approved | 47000 | 2028-05-11 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Red Run |  |  | 230 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 18178 | Rebuild of Hancock – Lily 120 kV | BRP | 25003 | 25003-Hancock-Lily | Rebuild approximately 2 miles of 3/0 Cu X2 utilizing 954 ACSR on 230kV, double-circuit structures. | ITCT | M2 - Appendix A Approved | 4400000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Hancock | Lily | 1 | 120 |  |  | 2 | MI |  | Not Shared
MTEP20 | A | ITC | East | 18179 | Rebuild of Hood – Lily 120 kV | BRP | 25005 | 25005-Hood-Lily | Rebuild approximately 2.6 miles of 3/0 Cu X2 utilizing 954 ACSR on 230kV, double circuit structures. | ITCT | M2 - Appendix A Approved | 5730000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Hood | Lily | 1 | 120 |  |  | 2.6 | MI |  | Not Shared
MTEP20 | A | ITC | East | 18184 | Rebuild Red Run – Logan 2 – Sloan 120 kV | BRP | 25007 | 25007-Red Run-Sloan | Rebuild approximately 2.8 miles utilizing 954 ACSR on double circuit structures. | ITCT | M2 - Appendix A Approved | 7010000 | 2028-05-03 | Line Upgrade | Line rebuild on existing ROW | Red Run | Sloan | 1 | 120 |  |  | 2.8 | MI |  | Not Shared
MTEP20 | A | ITC | East | 18184 | Rebuild Red Run – Logan 2 – Sloan 120 kV | BRP | 25008 | 25008-Sloan- | Upgrade terminal equipment at Sloan 120 kV station. | ITCT | M2 - Appendix A Approved | 85000 | 2027-02-19 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Sloan |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 18205 | Upgrade Red Run 120 kV Station Equipment | BRP | 25045 | 25045-Red Run- | Upgrade the station equipment at Red Run 120 kV station. | ITCT | M2 - Appendix A Approved | 1100000 | 2026-12-15 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Red Run |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | INDIANAPOLIS POWER & LIGHT COMPANY | Central | 17886 | Replace Southeast #8 Breaker | BRP | 24700 | 24700-Southeast- | 138 kV breaker | IPL | M2 - Appendix A Approved | 900000 | 2026-12-31 | Substation | Circuit Breaker (replacement at existing substation) | Southeast |  |  | 138 |  |  |  | IN |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 17904 | New Highland-Aviston 138 kV line | Other | 24703 | 24703-Highland Area-Substation | Install new Highland area ring bus. | AmerenIL | M2 - Appendix A Approved | 13000000 | 2028-12-01 | Substation | Switching station (breakers only, no transformer) | Highland Area | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 17904 | New Highland-Aviston 138 kV line | Other | 24704 | 24704-Aviston-Substation | Re-configure Aviston Substation to a ring bus. | AmerenIL | M2 - Appendix A Approved | 8700000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Aviston | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 17904 | New Highland-Aviston 138 kV line | Other | 24705 | 24705-Highland Area-Aviston | Install new 16.5 mile 138 kV line between Highland and Aviston. | AmerenIL | M2 - Appendix A Approved | 32200000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Highland Area | Aviston |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 17908 | Rebuild Bland-Franks 345 kV line | Other | 24717 | 24717-Bland-Franks | Rebuild approximately 44 miles 345kV line to 3000A. | AmerenMO | M3 - Under Construction | 74000000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Bland | Franks | 3 | 345 |  |  |  | MO |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 17686 | New Dougherty Ferry 138/12 kV substation | Other | 24622 | 24622-Dougherty Ferry-Substation | Tap the Mason-Meramec-1 & 2 lines to provided a main-tie-main configuration for the installation of a new 138-12 kV substation. Name is Caboose | AmerenMO | M2 - Appendix A Approved | 19400000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Dougherty Ferry | Substation |  | 138 | 12 |  |  | MO |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 17945 | New Highway M 138/12 kV substation | Other | 24724 | 24724-Hwy M-Substation | Install 2 unit 138-12.47 kV substation on a site adjacent to the Dardenne Substation. | AmerenMO | M2 - Appendix A Approved | 20000000 | 2028-12-01 | Substation | Substation (breakers only, no transformer) | Hwy M | Substation |  | 138 | 12 |  |  | MO |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 17947 | New Fountain Lakes 138/12 kV transformer No. 2 | Other | 24728 | 24728-Fountain Lakes-Substation | Add 2nd 138-12 kV unit at Fountain Lakes | AmerenMO | M2 - Appendix A Approved | 9300000 | 2027-12-01 | Substation | Substation (breakers only, no transformer) | Fountain Lakes | Substation |  | 138 | 12 |  |  | MO |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 9100 | Burlington-4th St-Agency 69kV Rebuild | Other | 24729 | 24729-Burlington 4th Street-South Burlington | Rebuild a small section of 69kV line to T2-477 ACSR. | ITCM | M2 - Appendix A Approved | 1 | 2028-05-31 | Line Upgrade | Line rebuild on existing ROW | Burlington 4th Street | South Burlington | 1 | 69 | 69 |  | 0.05 | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17724 | Sixth Street 115kV Substation Retirement | Other | 24631 | 24631-Sixth Street-Substation | Once the remaining 34.5 kV lines at the Sixth St Substation are converted to 69 kV, the remaining substation equipment should be retired, including any control enclosures and fence, etc. The communications currently routed through Sixth Street will also need to be moved/removed before the retirement can be completed. | ITCM | M2 - Appendix A Approved | 366540 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Sixth Street | Substation |  | 115 | 34 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17724 | Sixth Street 115kV Substation Retirement | Other | 24632 | 24632-Stoney Point-Saints Run | Reroute the 115kV lines to bypass the Sixth Street substation. | ITCM | M4 - Project in Service | 1140000 | 2021-12-17 | Line New | New Transmission line, new ROW - may include terminations | Stoney Point | Saints Run | 1 | 115 | 115 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17967 | Bowen Substation 69kV Conversion | Other | 24734 | 24734-Bowen-Substation | ITC will be converting the Bowen Substation to 69kV. All network path 69kV equipment will be capable of 600A or greater. | ITCM | M2 - Appendix A Approved | 2754375 | 2029-12-30 | Substation | Substation (breakers only, no transformer) | Bowen | Substation |  | 69 | 69 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17725 | Savanna 161kV Substation Expansion | Other | 24633 | 24633-Savanna-Substation | TC will be expanding the Savanna Substation to a Ring Bus capable of 6-positions. The new 161kV equipment will be capable of 2000A. There will be several phases for the 161kV. | ITCM | M3 - Under Construction | 10593113 | 2028-07-18 | Substation | Substation (breakers only, no transformer) | Savanna | Substation |  | 161 | 161 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17725 | Savanna 161kV Substation Expansion | Other | 24634 | 24634-Savanna-York | Line tap work required for the Savanna 161kV sub expansion. | ITCM | M2 - Appendix A Approved | 723000 | 2028-02-08 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Savanna | York | 1 | 161 | 161 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17725 | Savanna 161kV Substation Expansion | Other | 24635 | 24635-Savanna-Galena | Line tap work required for the Savanna 161kV sub expansion. | ITCM | M2 - Appendix A Approved | 723000 | 2027-12-20 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Savanna | Galena | 1 | 161 | 161 |  |  | IL |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 17969 | Replace Mason 345/138 kV Transformer | BRP | 24738 | 24738-Mason-Substation | Replace 345/138 kV, 560 MVA Transformer #2 with a 700 MVA unit | AmerenMO | M3 - Under Construction | 13100000 | 2026-06-01 | Transformer | Transformer New | Mason | Substation |  | 345 | 138 |  |  | MO |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17729 | Savanna-Argo Fay-York Area Rebuilds | Other | 24642 | 24642-Argo Fay-York | ITC will build a new 69kV line approximately 6 miles from the York Substation to the Argo Fay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | ITCM | M2 - Appendix A Approved | 8986800 | 2026-12-30 | Line New | New Transmission line, new ROW - may include terminations | Argo Fay | York | 1 | 69 | 69 | 6 |  | IL |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 17974 | New Crab Orchard 345/138 kV transformer (Stilleys) | Other | 24744 | 24744-Crab Orchard-Substation | Tap the Shawnee-West Frankfort east-4564 line and install 345kV ring bus to make the connection. | AmerenIL | M3 - Under Construction | 43600000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Crab Orchard | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17729 | Savanna-Argo Fay-York Area Rebuilds | Other | 24643 | 24643-Chadwick-Clay | ITC will build a new 69kV line approximately 6.5 miles from the Clay Substation to the Chadwick Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | ITCM | M2 - Appendix A Approved | 7375200 | 2026-12-30 | Line New | New Transmission line, new ROW - may include terminations | Chadwick | Clay | 1 | 69 | 69 | 6.5 |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17729 | Savanna-Argo Fay-York Area Rebuilds | Other | 24644 | 24644-Argo Fay-Chadwick | ITC will rebuild approximately 6.5 miles of the Argo Fay Substation to the Chadwick Substation 34.5kV line to 69kV Standards. The overhead conductor will have an ampacity of 600A or higher. | ITCM | M2 - Appendix A Approved | 5088000 | 2026-12-30 | Line Upgrade | Line rebuild on existing ROW | Argo Fay | Chadwick | 1 | 69 | 69 |  | 6.5 | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17729 | Savanna-Argo Fay-York Area Rebuilds | Other | 24645 | 24645-Argo Fay-Clay | ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Clay substation. | ITCM | M2 - Appendix A Approved | 360000 | 2026-12-30 | Line New | New Transmission line, new ROW - may include terminations | Argo Fay | Clay | 1 | 34 | 34 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17729 | Savanna-Argo Fay-York Area Rebuilds | Other | 24646 | 24646-Argo Fay-Savanna | ITC will retire approximately 6 miles of 34.5kV line between Argo Fay and the Savanna substation | ITCM | M2 - Appendix A Approved | 540000 | 2026-12-30 | Line New | New Transmission line, new ROW - may include terminations | Argo Fay | Savanna | 1 | 34 | 34 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17731 | Savanna City Loop 34kV to 69kV Rebuild | Other | 24647 | 24647-Savanna-Eaton | ITC will rebuild approximately 1.66 miles of the Savanna – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | ITCM | M2 - Appendix A Approved | 2537746 | 2027-12-30 | Line Upgrade | Line rebuild on existing ROW | Savanna | Eaton | 1 | 69 | 69 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17731 | Savanna City Loop 34kV to 69kV Rebuild | Other | 24648 | 24648-Bowen-Eaton | ITC will rebuild approximately 0.85 miles of the Bowen – Eaton 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | ITCM | M2 - Appendix A Approved | 2164800 | 2027-12-30 | Line Upgrade | Line rebuild on existing ROW | Bowen | Eaton | 1 | 69 | 69 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17731 | Savanna City Loop 34kV to 69kV Rebuild | Other | 24649 | 24649-Bowen-Savanna | ITC will rebuild approximately 3.80 miles of the Bowen – Savanna 34.5kV line to 69kV standards. The overhead conductor will have an ampacity of 600A or higher. | ITCM | M2 - Appendix A Approved | 5775600 | 2027-12-30 | Line Upgrade | Line rebuild on existing ROW | Bowen | Savanna | 1 | 69 | 69 |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17730 | Savanna-Clay 34kV to 69kV Rebuild | Other | 24650 | 24650-Savanna-Clay | ITC will rebuild approximately 7.75 miles of 34.5kV to 69kV standards from Savanna Substation to Clay Substation. The overhead conductor will have an ampacity of 600A or higher. A route study may be needed to determine the best route. | ITCM | M2 - Appendix A Approved | 8262000 | 2026-06-20 | Line Upgrade | Line rebuild on existing ROW | Savanna | Clay | 1 | 69 | 69 |  | 7.75 | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | Other | 24651 | 24651-EIC-Substation | In order to mitigate an N-1-1 issue at the Cargill Eddyville plant, ITC will expand the Eddyville Industrial Complex 161kV substation to the North. ITC will construct a five position 161kV ring bus North of the existing Eddyville Industrial Complex substation. All new terminal equipment will be capable of 2000A minimum. | ITCM | M2 - Appendix A Approved | 5488862 | 2026-12-30 | Substation | Substation (breakers only, no transformer) | EIC | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | Other | 24652 | 24652-Beacon-Tri County | ITC will install one 90 deg. double dead end structure and terminate the 161kV circuits into two Western most breaker positions at the EIC substation using the standard 1600A conductor. | ITCM | M2 - Appendix A Approved | 1036800 | 2026-12-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Beacon | Tri County | 1 | 161 | 161 |  | 0.1 | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | Other | 24653 | 24653-EIC-Tri County | Using the existing structures, ITC will terminate the 161kV circuit to the Eastern most breaker of the EIC expansion using the standard 1600A conductor. | ITCM | M2 - Appendix A Approved | 720000 | 2026-12-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | EIC | Tri County | 1 | 161 | 161 |  | 0.1 | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | Other | 24654 | 24654-Tri County-Substation | ITC will need to update the relay settings at Tri County | ITCM | M2 - Appendix A Approved | 278376 | 2026-12-30 | Substation | Small miscellaneous substation equipment | Tri County | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17736 | Waukon Ironmine 69kV Substation Interconnection | Other | 24660 | 24660-Waukon Ironmine-Substation | IPL will be constructing the Waukon Ironmine 2 transformer 69/25kV substation the replace the nearby Waukon substation. ITC will install 2 box structures, 2 line breakers and 1 tie breaker. The cap bank and cap bank breaker at the existing Waukon substation should be moved to the Decorah side of the Waukon Ironmine substation if possible or a new cap bank and breaker of equivalent effective rating should be installed. All substation equipment should have a minimum rating of 1200A. | ITCM | M2 - Appendix A Approved | 2248847 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Waukon Snakeskin | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17736 | Waukon Ironmine 69kV Substation Interconnection | Other | 24661 | 24661-Decorah-Lansing | Line taps for the new Waukon Snakeskin sub. Tap the line between the Ludlow sub and the existing Waukon sub. | ITCM | M2 - Appendix A Approved | 258600 | 2026-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Decorah | Lansing | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17738 | Thompson MacTavish 69kV Substation Interconnection | Other | 24663 | 24663-Thompson MacTavish-Line taps | New in and out line taps for the new Thompson MacTavish substation. | ITCM | M2 - Appendix A Approved | 346800 | 2030-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Thompson MacTavish | Line taps |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17739 | Calmar Prairie Farmer 69kV Substation Interconnection | Other | 24664 | 24664-Calmar Prairie Farmer-Line taps | ITC will install an ~0.02 mile tap line to IPL’s new Calmar Prairie Farmer 69/24.9kV Distribution Substation. The transformer will have a high side breaker installed by IPL. This substation will be located near the existing Calmar substation. IPL has provided four proposed locations. | ITCM | M2 - Appendix A Approved | 205200 | 2030-12-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Calmar Prairie Farmer | Line taps |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | DUKE ENERGY INDIANA, LLC | Central | 18307 | New Noblesville West 69/12 kV substation | Other | 25150 | 25150-Noblesville West-new dist sub | Noblesville West (previously Westfield East): new sub - 69/12kv - 22.4 MVA xfmr bank, single phase regulators SCADA/IVVC, 2 breakers, and space for second bank. Normal feed from 6917 ckt, alternate from 69142. | DEI | M2 - Appendix A Approved | 5376105 | 2028-06-30 | Substation | Distribution substation - may include trans high side | Noblesville West | new dist sub |  | 69 | 12 | 3.6 |  | IN |  | Not Shared
MTEP20 | A | DUKE ENERGY INDIANA, LLC | Central | 18308 | New Hunts Creek 138/12 kV substation | Other | 25151 | 25151-Hunts Creek-new dist sub | Hunts Creek 138/12kV substation: new sub to be located in the 13855 ckt between LGE Ghent and DEI Fairview | DEI | M2 - Appendix A Approved | 3313000 | 2031-07-01 | Substation | Distribution substation - may include trans high side | Hunts Creek | new dist sub |  | 138 | 12 | 4 |  | IN |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 18315 | New Galesburg Wind (J844) interconnection | GIP | 25157 | 25157-Sandburg-Substation | Add 1 BAAH 138 kV leg to the Sandburg Substation and add 1 breaker postion to interconnect J844. | AmerenIL | M2 - Appendix A Approved | 2700000 | 2026-06-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Sandburg | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | AMEREN ILLINOIS | Central | 18322 | New City of Roses Wind (J848) interconnection | GIP | 25165 | 25165-Pana-Substation | Add terminal facilities at the Pana Substation to make the inteconnection for J848. | AmerenIL | M2 - Appendix A Approved | 1100000 | 2026-12-01 | Substation | Points of Interconnection for generators (User TAP for dist subs) | Pana | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 9100 | Burlington-4th St-Agency 69kV Rebuild | Other | 20813 | 20813-Burlington-Burlington 4th Street | Rebuid 0.77 miles of 69kV line and upgrade terminal equipment above the conductor rating of 132 MVA. | ITCM | M2 - Appendix A Approved | 1363309 | 2028-05-31 | Line Upgrade | Line rebuild on existing ROW | Burlington | Burlington 4th Street | 1 | 69 | 69 |  | 0.77 | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 9100 | Burlington-4th St-Agency 69kV Rebuild | Other | 20814 | 20814-Burlington 4th Street-Agency | Rebuild the 4th Street-Agency 69kV line to T2-477. | ITCM | M2 - Appendix A Approved | 3549948 | 2028-05-31 | Line Upgrade | Line rebuild on existing ROW | Burlington 4th Street | Agency | 1 | 69 | 69 |  | 2.51 | IA |  | Not Shared
MTEP20 | A | PRAIRIE POWER, INC. | Central | 18152 | Rebuild Andrew - Amos 69 kV Line | Other | 25056 | Rebuild Andrew-Amos 69 kV Line | Rebuild Andrew-Amos 69 kV Line from 336 ACSR to 795 ACSR | PPI | M2 - Appendix A Approved | 6765000 | 2026-12-01 | Line Upgrade | Line rebuild on existing ROW | Andrew | Amos | 1 | 69 | 69 |  | 8.9 | IL |  | Not Shared
MTEP20 | A | ITC | East | 18240 | Install Capacitor at Boyne 120 kV | BRP | 25066 | 25066-Boyne - Install Capacitors | Install 51 MVAR capacitor (18 & 33 MVAR banks) at Boyne 120 kV station to maintain acceptable voltage levels within this region of the Oakland area. | ITCT | M2 - Appendix A Approved | 4287000 | 2026-06-01 | Voltage Device | Capacitor (switched capacitor) | Boyne |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | METC | East | 18244 | Gallagher Transformer #2 Replacement | Other | 25070 | 25070-Gallagher- | Replace Gallagher Transformer #2 with a new Transformer | METC | M2 - Appendix A Approved | 6200000 | 2026-05-15 | Transformer | Transformer New | Gallagher |  |  | 345 | 138 |  |  | MI |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 18267 | New Scarlet 345 kV substation | BRP | 25102 | 25102-Labadie-Montgomery | Tap the Ameren Missouri Labadie-Montgomery 345kV line via a new 3-breaker, 345kV ring bus near the intersection of the line and the AECI (Central Electric Power Coop) 161kV line west of Charrette. | AmerenMO | M4 - Project in Service | 41500000 | 2026-04-02 | Substation | Switching station (breakers only, no transformer) | Labadie | Montgomery | 4 | 345 |  |  |  | MO |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 18267 | New Scarlet 345 kV substation | BRP | 25103 | 25103-Ameren Wright City Area Sub-AECI Wright City Sub | Rebuild the existing 161kV line between the tap point and the AECI Wright City Substation as double-circuit 345/161kV. | AmerenMO | M3 - Under Construction | 32100000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Ameren Wright City Area Sub | AECI Wright City Sub |  | 345 | 161 |  |  | MO |  | Not Shared
MTEP20 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 18268 | New Grandview Substation Generation Interconnection | GIP | 25112 | 25112-Grandview 69 kV- | Complete ring bus and add terminal for GI project J783 | SIGE | M2 - Appendix A Approved | 885456 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Grandview 69 kV |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP20 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 18268 | New Grandview Substation Generation Interconnection | GIP | 25115 | 25115-Grandview 69 kV- | Replace two 600 amp 69 kV bus switches at Grandview with 1200 amp switches for GI project J783 | SIGE | M2 - Appendix A Approved | 71418 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Grandview 69 kV |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP20 | A | SOUTHERN INDIANA GAS & ELECTRIC COMPANY D/B/A CENTERPOINT ENERGY INDIANA SOUTH | Central | 18268 | New Grandview Substation Generation Interconnection | GIP | 25117 | 25117-Rockport 69 kV- | Replace three 600 amp 69 kV switches with 1200 amp switches for GI project J783 | SIGE | M2 - Appendix A Approved | 60622 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Rockport 69 kV |  |  | 69 |  |  |  | IN |  | Not Shared
MTEP20 | A | ITC | East | 18178 | Rebuild of Hancock – Lily 120 kV | BRP | 25259 | 25259-Hancock- | Replace terminal equipment at Hancock. | ITCT | M2 - Appendix A Approved | 140000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Hancock |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 18178 | Rebuild of Hancock – Lily 120 kV | BRP | 25260 | 25260-Lily- | Replace terminal equipment at Lily 120kV station. | ITCT | M2 - Appendix A Approved | 140000 | 2026-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Lily |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 18179 | Rebuild of Hood – Lily 120 kV | BRP | 25261 | 25261-Lily- | Replace terminal equipment at Lily 120kV station. | ITCT | M2 - Appendix A Approved | 50000 | 2027-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Lily |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | ITC | East | 18184 | Rebuild Red Run – Logan 2 – Sloan 120 kV | BRP | 25262 | 25262-Red Run- | Replace terminal equipment at Red Run 120kV. | ITCT | M2 - Appendix A Approved | 115000 | 2027-03-23 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Red Run |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17869 | Superior Transmission Line Relocations | Other | 25265 | 25265-Stinson-Gary | Relocate existing Stinson - Gary 115 kV Line (will become Enbridge East - Enbridge South after completion of Nemadji 115 kV Project) | MP | M2 - Appendix A Approved | 2000000 | 2025-12-31 | Misc. | Line relocation (road move) | Stinson | Gary |  | 115 |  | 0.5 |  | WI |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17869 | Superior Transmission Line Relocations | Other | 25266 | 25266-Stinson-Bayfront | Relocate existing Stinson - Bayfront 115 kV Line (double circuit with Stinson - Gordon 161 kV) | MP | M2 - Appendix A Approved | 900000 | 2025-12-31 | Misc. | Line relocation (road move) | Stinson | Bayfront |  | 115 |  | 0.75 |  | WI |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 17869 | Superior Transmission Line Relocations | Other | 25267 | 25267-Stinson-Gordon | Relocate existing Stinson - Gordon 161 kV Line (double circuit with Stinson - Bayfront 115 kV) | MP | M2 - Appendix A Approved | 2000000 | 2025-12-31 | Misc. | Line relocation (road move) | Stinson | Gordon |  | 161 |  | 0.75 |  | WI |  | Not Shared
MTEP20 | A | METC | East | 18728 | Cobb (Chopin) - Sternberg 138kV Line Rebuild | BRP | 25284 | 25284-Cobb-Sternberg | Rebuild approximately 8 miles of the Cobb - Sternberg 138kV circuit using 954 ACSR conductor with single circuit steel structures. | METC | M2 - Appendix A Approved | 10200000 | 2027-05-03 | Line Upgrade | Line rebuild on existing ROW | Cobb | Sternberg | 1 | 138 |  |  | 8 | MI |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 17732 | Eddyville Industrial Complex 161kV Substation Expansion | Other | 25288 | 25288-Bridgeport North-EIC | ITCM will terminate the circuit into the southwestern most position using the standard 1600A conductor | ITCM | M2 - Appendix A Approved | 432000 | 2026-12-30 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Bridgeport North | EIC | 1 | 161 | 161 |  | 0.1 | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 18846 | Creston Roundhouse 69kV Substation Interconnection | Other | 25308 | 25308-Creston Roundhouse-Substation | Per Alliant’s request, ITC will construct a 3-terminal straight bus with tie breaker at the proposed Creston Roundhouse substation. All ITC terminal equipment will be capable of 2000A minimum and Alliant will own the land and joint use assets. In addition, ITC line equipment will use T2-4/0. Ringgold Telecom Upgrades required for Creston Roundhouse Interconnection | ITCM | M2 - Appendix A Approved | 4961275 | 2025-11-14 | Substation | Substation (breakers only, no transformer) | Creston Roundhouse | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 18846 | Creston Roundhouse 69kV Substation Interconnection | Other | 25309 | 25309-Creston East-Creston D.O.E. | Retrofit with OPGW and terminate the circuit into Creston Roundhouse using T2-4/0. Upgrade relays at Creston DOE | ITCM | M2 - Appendix A Approved | 1132129 | 2026-07-17 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Creston East | Creston D.O.E. | 1 | 69 | 69 |  | 4.77 | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 18846 | Creston Roundhouse 69kV Substation Interconnection | Other | 25310 | 25310-Creston-Mount Ayr | ITC will terminate the 69kV circuit into Creston Roundhouse using T2-4/0 | ITCM | M2 - Appendix A Approved | 1233331 | 2026-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Creston | Mount Ayr | 1 | 69 | 69 | 0.33 |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 18846 | Creston Roundhouse 69kV Substation Interconnection | Other | 25311 | 25311-Creston East-Creston | ITC will tie the existing Creston- Summit Lake and Creston – Creston East 69kV circuits together using T2- 4/0 creating a Creston Roundhouse- Summit Lake Circuit. It would be ideal to tie the circuits together near the existing Creston Substation. This circuit will be terminated into the Creston Roundhouse substation using T2-4/0. | ITCM | M2 - Appendix A Approved | 456931 | 2025-04-25 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Creston East | Creston | 1 | 69 | 69 | 0.1 |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 18846 | Creston Roundhouse 69kV Substation Interconnection | Other | 25312 | 25312-Creston-Creston East | Retire ITC assets at Creston and Creston East | ITCM | M2 - Appendix A Approved | 1567483 | 2028-05-29 | Substation | Substation (breakers only, no transformer) | Creston | Creston East |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP20 | A | ITC MIDWEST | West | 18846 | Creston Roundhouse 69kV Substation Interconnection | Other | 25313 | 25313-Creston East-CKT 4220 | ITC will terminate the circuit into Creston Roundhouse using T2-4/0. | ITCM | M4 - Project in Service | 456931 | 2024-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Creston East | CKT 4220 | 1 | 69 | 69 | 0.1 |  | IA |  | Not Shared
MTEP20 | A | MINNESOTA POWER INC. | West | 15598 | Badoura Transformer Replacement | BRP | 25762 | 25762-Badoura 230- | New EEE building and expand 230 kV bus to a 3-position ring bus with 3 new 230 kV breakers | MP | M2 - Appendix A Approved | 3600000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Badoura 230 |  |  | 230 |  |  |  | MN |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 16504 | Reconfigure Viburnum 161/34 kV Substation | Other | 24322 | 24322-Viburnum-Substation | Install 2 161 kV line breakers and 1 161 kV circuit switcher on the transformer to split the CLK-CMCO-2 line and create 2 circuits into Viburnum Substation. | AmerenMO | M2 - Appendix A Approved | 13500000 | 2027-06-01 | Substation | Small miscellaneous substation equipment | Viburnum | Substation |  | 161 | 34 |  |  | MO |  | Not Shared
MTEP20 | A | AMERICAN TRANSMISSION COMPANY | West | 10590 | Academy - Columbus, 69kV (Y-21), rebuild & OPGW | Other | 21620 | Rebuild Academy - Columbus 69kV | Rebuild Academy - Columbus 69kV. | ATC | M2 - Appendix A Approved | 3263000 | 2028-12-20 | Line Upgrade | Line rebuild on existing ROW | Academy | Columbus | 1 | 69 |  |  | 1 | WI |  | Not Shared
MTEP20 | A | ENTERGY SERVICES, LLC. | South | 13943 | Southern Point 138 kV: New Substation | Other | 23030 | 23030-Southern Point- | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | Entergy-TX | M2 - Appendix A Approved | 7486185 | 2028-04-01 | Substation | Distribution substation - may include trans high side | Southern Point |  |  | 138 |  |  |  | TX |  | Not Shared
MTEP20 | A | AMERICAN TRANSMISSION COMPANY | Central | 14907 | Load Interconnection Program 2021 | Other | 23478 | 23478-NA- | Distribution Interconnection 2021 | ATC | M3 - Under Construction | 20124594 | 2027-04-30 | Substation | Substation (breakers only, no transformer) | NA |  |  | 138 | 69 |  |  | WI | MI | Not Shared
MTEP20 | A | ITC | Central | 15883 | Bismarck-Stephens #2 120 kV Rebuild | BRP | 23980 | 23980-Bismarck-Stephens | Rebuild approximately 3.61 miles of 795 ACSS and 954 ACSR conductors to 2156 ACSR on the Bismarck – Stephens #2 120 kV line. | ITCT | M2 - Appendix A Approved | 9750000 | 2028-04-21 | Line Upgrade | Line rebuild on existing ROW | Bismarck | Stephens | 2 | 120 |  |  | 3.6 | MI |  | Not Shared
MTEP20 | A | METC | East | 17992 | Rebuild Hodenpyl Line | Other | 24763 | 24763-Hodenpyl-Hodenpyl Jct | Rebuild the Hodenpyl 138 kV Line, approximately 0.6 miles, utilizing 138 kV single circuit construction | METC | M2 - Appendix A Approved | 3002551 | 2026-11-13 | Line Upgrade | Line rebuild on existing ROW | Hodenpyl | Hodenpyl Jct | 1 | 138 |  |  | 0.6 | MI |  | Not Shared
MTEP20 | A | METC | East | 17993 | Muskegon #2 Line Rebuild | Other | 24764 | 24764-Muskegon Heights-Cobb | Rebuild a portion of the Muskegon #2 138 kV Line, approximately 2.1 miles, utilizing 138 kV single circuit construction | METC | M3 - Under Construction | 4707598 | 2028-12-29 | Line Upgrade | Line rebuild on existing ROW | Muskegon Heights | Cobb | 2 | 138 |  |  | 2.1 | MI |  | Not Shared
MTEP20 | A | AMEREN MISSOURI | Central | 18013 | New Montgomery 345 kV shunt reactor | Other | 24787 | 24787-Montgomery-Substation | Install 50 Mvar reactor at Montgomery Substation | AmerenMO | M3 - Under Construction | 5200000 | 2026-06-01 | Voltage Device | Reactor or Inductor | Montgomery | Substation |  | 345 |  |  |  | MO |  | Not Shared
MTEP20 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 18012 | Hardinsburg Upgrade | Other | 24788 | 24788-Hardinsburg- | Add 161 kV breaker and upgrade protection equipment | BREC | M2 - Appendix A Approved | 980000 | 2028-06-01 | Substation | Substation (breakers only, no transformer) | Hardinsburg |  |  | 161 |  |  |  | KY |  | Not Shared
MTEP20 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 18011 | Rebuild Atlanta to Airport 138kV | Other | 24791 | 24791-Atlanta-Airport | Rebuild and upgrade 31.5 miles of 138 kV with double circuit steel poles, 795ACSS conductor, and OPGW. | WPSC | M3 - Under Construction | 19000000 | 2026-08-01 | Line Upgrade | Line rebuild on existing ROW | Atlanta | Airport | 1 | 138 |  | 15.5 |  | MI |  | Not Shared
MTEP20 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 18022 | Westwood 69kV BUS replacement | Other | 24803 | 24803-Westwood- | 69kV BUS replacement | WPSC | M2 - Appendix A Approved | 870000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Westwood |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP20 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 18023 | Eaton Rapids 69kV BUS replacement | Other | 24804 | 24804-Eaton Rapids- | Rebuild the existing 69kV BUS to accommodate distribution equipment replacement. | WPSC | M2 - Appendix A Approved | 170000 | 2026-09-01 | Substation | Small miscellaneous substation equipment | Eaton Rapids |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP20 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 18024 | Atlanta 69kV BUS replacement | Other | 24805 | 24805-Atlanta- | 69kV BUS replacement. | WPSC | M2 - Appendix A Approved | 170000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Atlanta |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP20 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 18026 | Hawks 69kV BUS replacement and Line modifications | Other | 24806 | 24806-Hawks- | BUS replacement | WPSC | M2 - Appendix A Approved | 1170000 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Hawks |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP20 | A | METC | East | 18043 | Sag Remediation Scott Lake - Argenta 138kV | BRP | 24824 | 24824-Scott Lake-Argenta | Remediate sag limit on the Scott Lake - Trowbridge 138kV section to increase its summer emergency rating to a minimum of 219 MVA (917 Amps) and also remediate sag limit on the Trowbridge - Argenta 138kV section to increase its summer emergency rating to a minimum of 235 MVA (985 Amps). | METC | M2 - Appendix A Approved | 830000 | 2027-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Scott Lake | Argenta | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP20 | A | MIDAMERICAN ENERGY CO. | West | 18050 | Sub 77: Add 161 kV Circuit Breaker | Other | 24830 | 24830-Sub 77-161 kV Breaker on Sub 91 Line Terminal | New 161 kV circuit breaker and associated equipment on line terminal to Sub 91 to separate the 161 kV line from the 161-13.2 kV distribution transformer. | MEC | M2 - Appendix A Approved | 1500000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Sub 77 |  |  | 161 |  |  |  | IA |  | Not Shared
MTEP19 | A | ENTERGY SERVICES, LLC. | East | 15586 | Ninemile S2015: Close Normally Open Breaker | Other | 23613 | 23613-Ninemile- | Return breaker to normally closed. | Entergy-LA | M2 - Appendix A Approved | 0 | 2027-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Ninemile |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP19 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 15646 | Atlanta to Lewiston Rebuild | Other | 23650 | 23650-Atlanta-Lewiston | Rebuild 12 miles to Wolverine 138kV standard | WPSC | M2 - Appendix A Approved | 10200000 | 2026-06-30 | Line Upgrade | Line rebuild on existing ROW | Atlanta | Lewiston | 1 | 69 |  |  |  | MI |  | Not Shared
MTEP19 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 15651 | Clinton to Wayland Rebuild | Other | 23659 | 23659-Clinton-Vermontville | Rebuild line section to Wolverine 138kV standard | WPSC | M2 - Appendix A Approved | 8500000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Clinton | Vermontville | 1 | 69 |  | 11 |  | MI |  | Not Shared
MTEP19 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 15651 | Clinton to Wayland Rebuild | Other | 23660 | 23660-Hastings-Vermontville | Rebuild line section to Wolverine 138kV standard | WPSC | M2 - Appendix A Approved | 20500000 | 2025-12-31 | Line Upgrade | Line rebuild on existing ROW | Hastings | Vermontville | 1 | 69 |  | 24 |  | MI |  | Not Shared
MTEP19 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 15651 | Clinton to Wayland Rebuild | Other | 23661 | 23661-Hastings-Wayland | Rebuild line section to Wolverine 138kV standard | WPSC | M2 - Appendix A Approved | 8250000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Hastings | Wayland | 1 | 69 |  | 11 |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 16023 | Lincoln-Northeast-Northwest 120 kV Rebuild | BRP | 24493 | 24493-Northeast-Northwest | Rebuild approximately 3.3 miles of underground cable on the Lincoln – Northeast – Northwest 120 kV circuit to 3500KCMIL, rebuild about 7.1 miles of overhead conductor to 1431 ACSR, and upgrade station equipment at Northeast and Northwest. | ITCT | M3 - Under Construction | 49642000 | 2026-05-15 | Line Upgrade | Line reconductor | Northeast | Northwest | 1 | 120 |  |  | 3.3 | MI |  | Not Shared
MTEP19 | A | AMERICAN TRANSMISSION COMPANY | West | 15947 | Waupaca Area Energy Storage Project | Other | 24556 | 24556-Harrison North- | 6 Mvar, 138 kV capacitor installed at Harrison North | ATC | M3 - Under Construction | 2500000 | 2026-06-01 | Voltage Device | Capacitor (switched capacitor) | Harrison North |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 23392 | 23392-Shale- | Acquire new property ~1.5 miles to the west of the existing Saginaw River 138 kV site. Construct a new switchyard in a 4-row breaker-and-a-half scheme configuration and install (12) 138 kV, 3000 A breakers w/ at least 40 kA interrupting capability (should auto-trip/block-close on low-low SF6 gas pressure). The summer emergency rating of all new equipment should be no less than 800 MVA/3347 Amps (similar to recently constructed 138 kV stations). | METC | M4 - Project in Service | 27000000 | 2025-04-28 | Substation | Switching station (breakers only, no transformer) | Shale |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 23393 | 23393-Saginaw River- | At Saginaw River 138 kV station: Remove all METC equipment except for what is necessary to connect the high-side of CE’s 138/46 kV Transformer #1 to the 138 kV. Utilize new 954 ACSR conductor as necessary. | METC | M2 - Appendix A Approved | 1505000 | 2026-03-31 | Substation | Switching station (breakers only, no transformer) | Saginaw River |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 23394 | 23394-Monitor-Shale | Rebuild a portion of the Monitor - Saginaw River 138 kV line to double-circuit. Also, reroute the Saginaw River - Twining 138 kV line on the other side of the Monitor - Saginaw River 138 kV line and bring both into the new Shale 138 kV station using 954 ACSR conductor. | METC | M4 - Project in Service | 3245000 | 2025-04-28 | Line Upgrade | Line rebuild on existing ROW | Monitor | Shale | 1 | 138 |  |  | 3.8 | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 23395 | 23395-Grey Iron-Shale | Rebuild a section of the Lawndale - Saginaw River 138 kV double-circuit line to create the Grey Iron - Shale 138 kV and Karn - Shale 138 kV lines utilizing 954 and 1431 ACSR conductor, respectively. The Lawndale 138 kV end will reterminate at Shale 138 kV station, while the new double-circuit rebuild portion will connect with the existing Karn 138 kV and Grey Iron 138 kV lines near the Saginaw River station. | METC | M2 - Appendix A Approved | 2905000 | 2026-01-30 | Line Upgrade | Line rebuild on existing ROW | Grey Iron | Shale | 1 | 138 |  |  | 2.5 | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 23396 | 23396-Saginaw River-Shale | Cut the existing Bullock - Saginaw River 138 kV and Monitor - Saginaw River 138 kV lines into Shale 138 kV station. Reconductor the new Saginaw River - Shale 138 kV line utilizing 954 ACSR conductor and add fiber from Shale to Saginaw River. For the Shale - Weadock 138 kV line, connect the Shale 138 kV and Weadock 138 kV ends around the Saginaw River 138 kV station. | METC | M4 - Project in Service | 1387000 | 2025-07-11 | Line Upgrade | Line rebuild on existing ROW | Saginaw River | Shale | 1 | 138 |  |  | 1.5 | MI |  | Not Shared
MTEP19 | A | ITC | East | 15888 | Scottsdale - Willow Run 120 kV Rebuild | BRP | 23988 | 23988-Scottsdale-Willow Run | Rebuild approximately 0.4 mile of 120 kV line from Scottsdale to Willow Run using 954 ACSR conductor. | ITCT | M2 - Appendix A Approved | 3000000 | 2028-12-29 | Line Upgrade | Line rebuild on existing ROW | Scottsdale | Willow Run | 1 | 120 |  |  | 0.4 | MI |  | Not Shared
MTEP19 | A | ITC | East | 15888 | Scottsdale - Willow Run 120 kV Rebuild | BRP | 23989 | 23989-Scottsdale- | Upgrade station equipment at Scottsdale. | ITCT | M2 - Appendix A Approved | 221000 | 2028-12-29 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Scottsdale |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 15888 | Scottsdale - Willow Run 120 kV Rebuild | BRP | 23990 | 23990-Willow Run- | Upgrade station equipment at Willow Run. | ITCT | M2 - Appendix A Approved | 194000 | 2028-10-13 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Willow Run |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | Central | 15905 | Willow Run - Zebra 120 kV Rebuild | BRP | 24012 | 24012-Willow Run-Zebra | Rebuild approximately 4.6 miles of 120 kV line from Willow Run to Zebra using 1431 ACSR conductor. | ITCT | M2 - Appendix A Approved | 6072000 | 2028-08-02 | Line Upgrade | Line rebuild on existing ROW | Willow Run | Zebra | 1 | 120 |  |  | 4.6 | MI |  | Not Shared
MTEP19 | A | ITC | East | 15905 | Willow Run - Zebra 120 kV Rebuild | BRP | 24013 | 24013-Willow Run- | Upgrade station equipment at Willow Run. | ITCT | M2 - Appendix A Approved | 140000 | 2028-08-02 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Willow Run |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 15905 | Willow Run - Zebra 120 kV Rebuild | BRP | 24014 | 24014-Zebra- | Upgrade station equipment at Zebra. | ITCT | M2 - Appendix A Approved | 186000 | 2027-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Zebra |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 15908 | Newburgh 120 kV 33.3 MVAR Capacitor | BRP | 24016 | 24016-Newburgh- | Install a 33.3 MVAR capacitor at Newburgh 120 kV on bus 101. | ITCT | M2 - Appendix A Approved | 1710000 | 2026-12-31 | Voltage Device | Capacitor (switched capacitor) | Newburgh |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | NORTHWESTERN WISCONSIN ELECTRIC CO. | West | 15915 | Frederic-Falun 69KV Old 35 from 350th to 330th | Other | 24023 | 24023-Frederic-Falun | Rebuild 69KV line Old 35 from 350th to 330th with 477 ACSR | NWEC | M2 - Appendix A Approved | 350000 | 2030-12-01 | Line Upgrade | Line rebuild on existing ROW | Frederic | Falun | 1 | 69 |  |  | 2 | WI |  | Not Shared
MTEP19 | A | NORTHWESTERN WISCONSIN ELECTRIC CO. | West | 15916 | Frederic-Falun 69KV Old 35 from Elbow Lake Road to 350th | Other | 24024 | 24024-Frederic-Falun | Rebuild 69KV line Old 35 from Elbow Lake Road to 350th with 477 ACSR | NWEC | M2 - Appendix A Approved | 420000 | 2031-01-01 | Line Upgrade | Line rebuild on existing ROW | Frederic | Falun | 1 | 69 |  |  | 2 | WI |  | Not Shared
MTEP19 | A | NORTHWESTERN WISCONSIN ELECTRIC CO. | West | 15920 | Lake 26-Tower Road 69KV CCC Road | Other | 24029 | 24029-Lake 26-Tower Road | Rebuild 69KV line CCC Road with 477 ASCR and horizontal post construction. | NWEC | M2 - Appendix A Approved | 437500 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Lake 26 | Tower Road | 1 | 69 |  |  | 2.5 | WI |  | Not Shared
MTEP19 | A | NORTHWESTERN WISCONSIN ELECTRIC CO. | West | 15921 | Lake 26-Tower Road 69KV Lake 26 Road | Other | 24031 | 24031-Lake 26-Tower Road | Rebuild 69KV line Lake 26 Road with 477 ASCR and horizontal post construction. | NWEC | M2 - Appendix A Approved | 262500 | 2028-12-01 | Line Upgrade | Line rebuild on existing ROW | Lake 26 | Tower Road | 1 | 69 |  |  | 1.5 | WI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 24056 | 24056-New 138kV Station (Chopin)- | Rebuild Cobb 138 kV station at a new site approximately 3.9 miles to the east (Chopin) utilizing new equipment in a six-row, breaker-and-a-half scheme configuration. This solution is to avoid tripping many 138kV circuits for a fault on the 500 bus – tie circuit breaker. Acquire new property as necessary and install (17) 138 kV, 3000 A breakers with at least 40 kA (upgradable to 63kA) interrupting capability in a six-row, breaker-and-a-half scheme configuration for this new station. | METC | M2 - Appendix A Approved | 18600000 | 2028-05-15 | Substation | Substation (breakers only, no transformer) | New 138kV Station (Pine Creek) |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | AMERICAN TRANSMISSION COMPANY | West | 15947 | Waupaca Area Energy Storage Project | Other | 24062 | 24062-Arnott- | 8 MVAR capacitor and associated equipment to be installed at Arnott substation | ATC | M4 - Project in Service | 912000 | 2022-11-22 | Voltage Device | Capacitor (switched capacitor) | Arnott |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP19 | A | AMERICAN TRANSMISSION COMPANY | West | 15947 | Waupaca Area Energy Storage Project | Other | 24063 | 24063-Harrison North- | Batteries and associated equipment to be upgraded and installed at Harrison North substation. Batteries to connect to tertiary winding of 69/138 kV transformer at 13.8 kV. | ATC | M3 - Under Construction | 10445000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Harrison North |  |  | 138 | 14 |  |  | WI |  | Not Shared
MTEP19 | A | ITC | East | 16023 | Lincoln-Northeast-Northwest 120 kV Rebuild | BRP | 24170 | 24170-Northeast-Northwest | Rebuild approximately 3.3 miles of underground cable on the Lincoln – Northeast – Northwest 120 kV circuit to 3500KCMIL, rebuild about 7.1 miles of overhead conductor to 1431 ACSR, and upgrade station equipment at Northeast and Northwest. | ITCT | M3 - Under Construction | 27090000 | 2026-08-31 | Line Upgrade | Line rebuild on existing ROW | Northeast | Northwest | 1 | 120 |  |  | 7 | MI |  | Not Shared
MTEP19 | A | ITC | Central | 16023 | Lincoln-Northeast-Northwest 120 kV Rebuild | BRP | 24172 | 24172-Northwest- | Rebuild approximately 3.3 miles of underground cable on the Lincoln – Northeast – Northwest 120 kV circuit to 3500KCMIL, rebuild about 7.1 miles of overhead conductor to 1431 ACSR, and upgrade station equipment at Northeast and Northwest. | ITCT | M2 - Appendix A Approved | 255000 | 2026-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Northwest |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 16029 | Caniff 120 kV – Upgrade KU & LBX Station Equipment | BRP | 24178 | 24178-Caniff- | Upgrade the station equipment at Caniff 120 kV positions “KU” and “LBX”. | ITCT | M2 - Appendix A Approved | 360000 | 2029-05-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Caniff |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 26024 | 26024-Chopin-Cobb (CE TB#7) | Connect Cobb CE TB#7 to Chopin utilizing line initially from Felch Road, 954 ACSR on DCT | METC | M2 - Appendix A Approved | 441500 | 2028-01-14 | Line New | New Transmission line, new ROW - may include terminations | Chopin | Cobb (CE TB#7) | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 26025 | 26025-Chopin-Cobb (CE TB#8) | Connect Cobb CE TB#8 to Chopin utilizing line initially from Muskegon 1, 954 ACSR on DCT | METC | M2 - Appendix A Approved | 1300000 | 2028-01-14 | Line New | New Transmission line, new ROW - may include terminations | Chopin | Cobb (CE TB#8) | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 26026 | 26026-Chopin-Muskegon Heights 1 (CE TB#4) | Connect Muskegon Heights CE TB#4 to Chopin utilizing additional 0.5 mile DCT and also utilizing line initially from Muskegon 1, 954 ACSR on DCT | METC | M2 - Appendix A Approved | 343000 | 2028-01-14 | Line New | New Transmission line, new ROW - may include terminations | Chopin | Muskegon Heights 1 (CE TB#4) | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 26027 | 26027-Chopin-Muskegon Heights 2 (CE TB#7) | Connect Muskegon Heights CE TB#7 to Chopin utilizing line initially from Muskegon 2, Utilizing the DCT construction of the Cobb - Sternberg 138kV line rebuilt to string ~2.5 miles section to Chopin station, 477 ACSR conductor on DCT | METC | M2 - Appendix A Approved | 158400 | 2028-01-14 | Line New | New Transmission line, new ROW - may include terminations | Chopin | Muskegon Heights 2 (CE TB#7) |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 26093 | 26093-Karn-Shale | Project #14824 (Shale 138 kV Station) needs additional facility entries due to real estate complications that changed the expected station location. | METC | M4 - Project in Service | 2135000 | 2025-11-05 | Misc. | Line relocation (road move) | Karn | Shale | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 26094 | 26094-Lawndale-Shale | Project #14824 (Shale 138 kV Station) needs additional facility entries due to real estate complications that changed the expected station location. | METC | M4 - Project in Service | 1419000 | 2025-07-11 | Misc. | Line relocation (road move) | Lawndale | Shale | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 26095 | 26095-Twining-Shale | Project #14824 (Shale 138 kV Station) needs additional facility entries due to real estate complications that changed the expected station location. | METC | M4 - Project in Service | 1965000 | 2025-04-28 | Misc. | Line relocation (road move) | Twining | Shale | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 26096 | 26096-Weadock-Shale | Project #14824 (Shale 138 kV Station) needs additional facility entries due to real estate complications that changed the expected station location. | METC | M2 - Appendix A Approved | 3750000 | 2026-01-30 | Misc. | Line relocation (road move) | Weadock | Shale | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 14824 | Shale 138 kV Station | Other | 26097 | 26097-Saginaw River-Shale | Construct new 138 kV line from the New Shale Substation to CE's Saginaw River 138/46kV Transformer | METC | M4 - Project in Service | 1390064 | 2025-11-07 | Line New | New Transmission line, new ROW - may include terminations | Saginaw River | Shale | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 15866 | Newburgh – Peru 120 kV Rebuild | BRP | 26943 | 26943-Newburgh-Peru | Replace HO line entrance | ITCT | M2 - Appendix A Approved | 40000 | 2027-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Newburgh | Peru |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15803 | Gaines - Meadowbrooke 138 kV Rebuild | BRP | 24201 | 24201-Gaines- | Replace terminal equipment at Gaines | METC | M2 - Appendix A Approved | 31000 | 2027-03-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Gaines |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 16104 | Altona to Pierson Rebuild | Other | 24210 | 24210-Altona-Pierson | Rebuild and upgrade 14 miles of 69 kV line to 138 kV design, 795ACSS conductor and OPGW. | WPSC | M2 - Appendix A Approved | 13200000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Altona | Pierson | 1 | 138 |  |  | 14 | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 24241 | 24241-Cobb- | Demolish un-used METC’s equipment at existing Cobb station. Remove buses, breakers 588, 988, 688, 888, 500, 148, 377, 488, and 788 and associated equipment at Cobb. | METC | M2 - Appendix A Approved | 2319000 | 2028-03-31 | Substation | Substation (breakers only, no transformer) | Cobb |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | South | 15942 | Rebuild Station Cobb 138 kV | BRP | 24252 | 24252-Cobb-Four Mile | COBB-FOUMI PINCK 138 kV Line Cut-In | METC | M2 - Appendix A Approved | 306000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Cobb | Four Mile |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | South | 15942 | Rebuild Station Cobb 138 kV | BRP | 24253 | 24253-Cobb-Tallmadge 1 | COBB- TALMG #1 PINCK 138 kV Line Cut-In | METC | M2 - Appendix A Approved | 306000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Cobb | Tallmadge 1 | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | South | 15942 | Rebuild Station Cobb 138 kV | BRP | 24254 | 24254-Cobb-Tallmadge 2 | COBB- TALMG #2 PINCK 138 kV Line Cut-In | METC | M2 - Appendix A Approved | 304000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Cobb | Tallmadge 2 | 2 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 24255 | 24255-Cobb-Felch Road (N-14) | COBB- FELCH PINCK 138 kV Line Cut-In | METC | M2 - Appendix A Approved | 304000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Cobb | Felch Road (N-14) |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 24256 | 24256-Cobb-Sternberg | COBB- STNBG PINCK 138 kV Line Cut-In | METC | M2 - Appendix A Approved | 357000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Cobb | Sternberg |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 24257 | 24257-White Lake-Chopin New 138kV Line | Tie Cobb-White Lake to Cobb-Tallmadge #1. Utilize existing 3.91 miles of the existing Cobb-Tallmadge #1 and loop this line into Chopin station. | METC | M2 - Appendix A Approved | 312000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | White Lake | Pine Creek New 138kV Line |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15942 | Rebuild Station Cobb 138 kV | BRP | 24258 | 24258-Dupont-Chopin | DUPONT-CHOPN 138 kV New Line | METC | M2 - Appendix A Approved | 317000 | 2028-01-14 | Line Upgrade | Generic transmission line project (try not to use the generic) | Dupont | Pine Creek |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15791 | Rebuild Hemphill – Sabine 138 kV | BRP | 24262 | 24262-Hemphill-Sabine | Remediate the sag limit on ~1.3 miles of 477 ACSR conductor to at least the planned target summer normal/summer emergency rating of 199 MVA/832 Amps. | METC | M2 - Appendix A Approved | 210000 | 2027-06-01 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hemphill | Sabine | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 12220 | Portland to Clinton line rebuild | BRP | 22348 | 22348-Portland-Clinton | Rebuild line to 138kV design with 795ACSS conductor | WPSC | M2 - Appendix A Approved | 12750000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Portland | Clinton |  | 69 |  | 15 |  | MI |  | Not Shared
MTEP19 | A | AMEREN ILLINOIS | Central | 13707 | New Merlot 138 kV substation ring bus | Other | 22775 | 22775-Merlot-138 kV ring bus | Install 3000A 138 kV Ring bus at Campbell Hill Junction location. Add breaker at Steelville on 1636 line. | AmerenIL | M2 - Appendix A Approved | 20000000 | 2029-06-01 | Substation | Switching station (breakers only, no transformer) | Merlot | 138 kV ring bus |  | 138 |  |  |  | IL |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15446 | Toledo Central 69kV Substation Interconnection | Other | 23536 | 23536-Toledo Central-Substation | Two (2) 69kV breakers will be installed at the Toledo Central Substation. All the substation equipment will be rated for 1200A or greater. IPL will purchase the land for the Toledo Central Substation. IPL will install one 69-34.5/25kV 33MVA transformer at the substation. | ITCM | M2 - Appendix A Approved | 1057487 | 2029-12-30 | Substation | Substation (breakers only, no transformer) | Toledo Central | Substation |  | 69 | 25 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15446 | Toledo Central 69kV Substation Interconnection | Other | 23537 | 23537-Fletcher-Tama East | Tap the Fletcher to Tama East line for the new Toledo Central substation. | ITCM | M2 - Appendix A Approved | 317833 | 2029-12-30 | Line New | New Transmission line, new ROW - may include terminations | Fletcher | Tama East | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15447 | Belle Plaine North 69kV Substation Interconnection | Other | 23538 | 23538-Belle Plaine North-Substation | The Belle Plaine North 69kV Substation will be a (3) three breaker In-and-Out 69kV Substation. All 69kV equipment will be capable of 2000A or greater. IPL will purchase the property. IPL will be installing (2) two 69x34.5/25kV 20 MVA distribution transformers at Belle Plaine North Substation. Belle Plaine North will be a PD Substation. | ITCM | M2 - Appendix A Approved | 2112481 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Belle Plaine North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15447 | Belle Plaine North 69kV Substation Interconnection | Other | 23539 | 23539-Belle Plaine North-Line Taps | Line taps for the new Belle Plaine North distribution substation. | ITCM | M2 - Appendix A Approved | 578434 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Belle Plaine North | Line Taps |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15447 | Belle Plaine North 69kV Substation Interconnection | Other | 23540 | 23540-Belle Plaine Jct-Belle Plaine North | Install fiber on the Belle Plaine Jct to Belle Plaine North line. | ITCM | M2 - Appendix A Approved | 1069200 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Belle Plaine Jct | Belle Plaine North | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15447 | Belle Plaine North 69kV Substation Interconnection | Other | 23541 | 23541-Belle Plaine North-River Valley | Install fiber on the Belle Plaine North to River Valley line. | ITCM | M2 - Appendix A Approved | 129600 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Belle Plaine North | River Valley | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15449 | Ottumwa Heights 161kV Substation Interconnection | Other | 23544 | 23544-Ottumwa Heights-Substation | As part of a long term plan to shift the load in Ottumwa off the 69kV and onto the 161kV system, IPL and ITC will be building a 161:26.2/13.1kV substation near Rutledge substation. IPL will purchase the land and own the joint use assets. ITCMW will construct a 4-position ring bus. All terminal equipment should be capable of 2000A minimum. ITC will build two independent taps from Ottumwa Generation – Woody #1 to the Ottumwa Heights substation. | ITCM | M2 - Appendix A Approved | 4218134 | 2029-06-15 | Substation | Substation (breakers only, no transformer) | Ottumwa Heights | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15449 | Ottumwa Heights 161kV Substation Interconnection | Other | 23545 | 23545-Ottumwa Generation-Ottumwa Heights | Tap the Ottumwa Generation to Woody #1 161kV circuit and route new 161kV line into the new Ottumwa Heights substation. | ITCM | M2 - Appendix A Approved | 2916000 | 2029-06-26 | Line New | New Transmission line, new ROW - may include terminations | Ottumwa Generation | Ottumwa Heights | 1 | 161 | 161 | 1.25 |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15449 | Ottumwa Heights 161kV Substation Interconnection | Other | 23546 | 23546-Ottumwa Heights-Woody | Tap the Ottumwa Generation to Woody #1 161kV circuit and route new 161kV line into the new Ottumwa Heights substation. | ITCM | M2 - Appendix A Approved | 2640000 | 2029-05-30 | Line New | New Transmission line, new ROW - may include terminations | Ottumwa Heights | Woody | 1 | 161 | 161 | 1.75 |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15450 | Beaver Rock 69kV Terminal Addition | Other | 23547 | 23547-Beaver Rock-Switch Station | Construct a new line terminal at the Beaver Rock substation. CIPCO will construct a new 69kV line (~13.5 miles) from the Buffalo Bill REC substation to the Beaver Rock substation (potentially using existing lines/ structures). This will create a second networked line between Beaver Rock and Grand Mound. MEC may also need to retire a portion(s) of the line between Sub 55, Sub 73, and Beaver Rock. | ITCM | M2 - Appendix A Approved | 279755 | 2029-11-30 | Substation | Switching station (breakers only, no transformer) | Beaver Rock | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15451 | Mt Vernon 161-69kV Transformer Addition | Other | 23548 | 23548-Mt Vernon-Substation | At Mount Vernon substation a 100 MVA 161/69 kV transformer will be installed. Also two 161 kV line breakers will be installed. The 161/34.5 kV transformer will remain until after all of the 34.5 kV loads are converted to 69 kV. | ITCM | M3 - Under Construction | 6747636 | 2026-06-01 | Substation | Substation (breakers only, no transformer) | Mt Vernon | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15454 | Walford Terry 69kV Substation Interconnection | Other | 23552 | 23552-Walford Terry-Substation | The Walford Terry Substation will be a new substation with three (3) 69kV terminals capable of 1200A or greater. One (1) future capacitor position will be needed. Staging and size of the capacitor bank will be finalized in a future EI Sketch. IPL will be installing a 69-34.5/25kV 12.5MVA transformer at the substation. | ITCM | M2 - Appendix A Approved | 2206140 | 2027-12-30 | Substation | Substation (breakers only, no transformer) | Walford Terry | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15454 | Walford Terry 69kV Substation Interconnection | Other | 23553 | 23553-Walford Terry-Line Taps | Construct the 69kV line taps for the new Walford Terry substation. | ITCM | M2 - Appendix A Approved | 514808 | 2027-12-30 | Line New | New Transmission line, new ROW - may include terminations | Walford Terry | Line Taps |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15456 | Brooklyn-Malcom 69kV line & Grinnell 69kV Terminal | Other | 23555 | 23555-Brooklyn-Malcom | ITC will construct a NEW 69kV line from Brooklyn to the Malcom Tap. The new 69kV line will be approximately 9.0 miles long. T2-4/0 or a similar conductor and construction type will be used. A 3-way or 3 1-way 69kV 1200A Switch/s will be needed at the Malcom Substation. | ITCM | M2 - Appendix A Approved | 8018086 | 2031-01-15 | Line New | New Transmission line, new ROW - may include terminations | Brooklyn | Malcom | 1 | 69 | 69 | 9 |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15456 | Brooklyn-Malcom 69kV line & Grinnell 69kV Terminal | Other | 23556 | 23556-Malcom Tap-Grinnell | ITC will rebuild approximately 1 mile of line to from the Malcom Tap to the Grinnell Substation to double circuit T2-4/0 ACSR 69kV or a similar conductor. | ITCM | M2 - Appendix A Approved | 2322020 | 2031-01-15 | Line Upgrade | Line rebuild on existing ROW | Malcom Tap | Grinnell | 1 | 69 | 69 |  | 1 | IA |  | Not Shared
MTEP19 | A | MIDAMERICAN ENERGY CO. | West | 15683 | Merrill North Substation Transformer and Line | Other | 23702 | 23702-Merrill North- | Expand Merrill North Substation 69 kV bus to install a second 69-12.47 kV transformer and a second 69 kV line terminal. Install two new 69 kV circuit breakers. Retire the existing Merrill 69-12.47 kV Substation. | MEC | M2 - Appendix A Approved | 0 | 2028-12-01 | Substation | Circuit Breaker (replacement at existing substation) | Merrill North |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP19 | A | MIDAMERICAN ENERGY CO. | West | 15683 | Merrill North Substation Transformer and Line | Other | 23703 | 23703-Merrill-Merrill North | Construct a new 69 kV line from Merrill Substation to Merrill North Substation. | MEC | M2 - Appendix A Approved | 1100000 | 2028-12-01 | Line New | New Transmission line, new ROW - may include terminations | Merrill | Merrill North | 69 | 69 |  | 0.7 |  | IA |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | East | 15746 | Beulah-Mandan 115 Rebuild | Other | 23759 | 23759-Beulah-Mandan | Rebuild Beulah-Mandan 115 kV line and add new 115 line segment to Coyote | MDU | M2 - Appendix A Approved | 25900000 | 2030-12-31 | Line Upgrade | Line rebuild on existing ROW | Beulah | Mandan | 1 | 115 |  | 5 | 44.4 | ND |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | West | 15747 | Merricourt 230/41.6 | Other | 23760 | 23760-Merricourt- | Add 230 kV breaker, 230/41.6 transformer and 41.6 kV ring bus | MDU | M2 - Appendix A Approved | 5300000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | Merricourt |  |  | 230 | 42 |  |  | ND |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | West | 15747 | Merricourt 230/41.6 | Other | 23761 | 23761-Merricourt-Ashley | Merricourt-Ashley 41.6 kV line | MDU | M2 - Appendix A Approved | 2200000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Merricourt | Ashley | 1 | 42 |  | 6 |  | ND |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | West | 15747 | Merricourt 230/41.6 | Other | 23762 | 23762-Merricourt-Fredonia | Merricourt-Fredonia 41.6 kV line | MDU | M2 - Appendix A Approved | 5500000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Merricourt | Fredonia |  | 42 |  | 15 |  | ND |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | West | 15746 | Beulah-Mandan 115 Rebuild | Other | 23763 | 23763-Coyote- | Add 115 kV breaker and switches from new 115 kV line terminal | MDU | M2 - Appendix A Approved | 1000000 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | Coyote |  |  | 115 |  |  |  | ND |  | Not Shared
MTEP19 | A | METC | East | 15754 | Mio Dam - Plywood Tap 138 kV Sag Remediation | BRP | 23769 | 23769-Mio Dam-Plywood Tap | The proposed solution is to remediate the sag limit on the Mio Dam – Lewiston Tap 138 kV section of the Gaylord – Mio Dam 138 kV line to increase its summer emergency rating to a minimum of 147 MVA/615 Amps and remediate the sag limit on the Lewiston Tap – Plywood Tap 138 kV section of the Gaylord – Mio Dam 138 kV line to increase its summer emergency rating to a minimum of 147 MVA/615 Amps. | METC | M2 - Appendix A Approved | 875000 | 2027-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Mio Dam | Plywood Tap |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | East | 15771 | Plentywood Loop | Other | 23785 | 23785-Plentywood Sub-Plentywood | 60 kV loop line around the city of Plentywood | MDU | M2 - Appendix A Approved | 5232000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Plentywood Sub | Plentywood |  | 60 |  | 8 |  | MT |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | West | 15780 | Lignite-Kincaid 60 kV | Other | 23791 | 23791-Lignite-Kincaid | new Lignite-Kincaid 60 kV line | MDU | M2 - Appendix A Approved | 5590164 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Lignite | Kincaid |  | 60 |  | 15 |  | ND |  | Not Shared
MTEP19 | A | MONTANA-DAKOTA UTILITIES CO. | West | 15780 | Lignite-Kincaid 60 kV | Other | 23792 | 23792-Lignite- | Add 60 kV breaker for new line | MDU | M2 - Appendix A Approved | 609836 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Lignite |  |  | 60 |  |  |  | ND |  | Not Shared
MTEP19 | A | ITC | West | 15776 | Juliet | Other | 23800 | 23800-Juliet- | Build new two bus straight bus Juliet 120kV Station with two circuit breakers. | ITCT | M2 - Appendix A Approved | 3431000 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | Juliet |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | West | 15776 | Juliet | Other | 23801 | 23801-Adams-Fitz | Loop in the Adams – Fitz 120kV circuit into the new substation. Install 1.5 miles of OPGW fiber between Adams and Juliet stations. | ITCT | M2 - Appendix A Approved | 734000 | 2030-12-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Adams | Fitz |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | PRAIRIE POWER, INC. | Central | 15774 | New Pleasant View 138/69 kV Substation and Lines | Other | 23810 | New Dempsey to Pleasant View 138 kV line | New AMIL Dempsey to Pleasant View 138 kV line | PPI | M2 - Appendix A Approved | 1200000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Dempsey | Pleasant View |  | 138 |  | 2 |  | IL |  | Not Shared
MTEP19 | A | PRAIRIE POWER, INC. | Central | 15774 | New Pleasant View 138/69 kV Substation and Lines | Other | 23811 | New Pleasant View 138/69 kV Substation | New Pleasant View 138/69 kV Substation | PPI | M2 - Appendix A Approved | 5900000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Pleasant View |  |  | 138 | 69 |  |  | IL |  | Not Shared
MTEP19 | A | METC | East | 15790 | Sag Remediation Hemphill - Thetford 138 kV | BRP | 23817 | 23817-Hemphill-Thetford | Remediate the sag limit on ~12.6 miles of 1431 ACSR conductor and ~3.5 miles of 795 ACSR conductor of the Hemphill – Thetford 138 kV line to achieve at least the planned target summer normal/summer emergency rating of 306 MVA/1280 Amps. | METC | M2 - Appendix A Approved | 386000 | 2028-12-31 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hemphill | Thetford | 1 | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | East | 15791 | Rebuild Hemphill – Sabine 138 kV | BRP | 23818 | 23818-Hemphill-Sabine | The proposed solution is to rebuild ~2.8 miles of the Hemphill – Sabine 138 kV line that is comprised of 336 ACSR conductor only utilizing 954 ACSR conductor. | METC | M2 - Appendix A Approved | 4600000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Hemphill | Sabine | 1 | 138 |  |  | 2.8 | MI |  | Not Shared
MTEP19 | A | METC | West | 15792 | Rebuild Halsey - Sabine 138 kV | BRP | 23819 | 23819-Halsey-Sabine | The proposed solution is to rebuild the entire ~5.3 mile-long Halsey – Sabine 138 kV line that is comprised of 336 ACSR conductor utilizing 954 ACSR conductor and upgrade the 336 ACSR line entrance at Halsey. | METC | M2 - Appendix A Approved | 6600000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Halsey | Sabine | 1 | 138 |  |  | 5.3 | MI |  | Not Shared
MTEP19 | A | METC | South | 15792 | Rebuild Halsey - Sabine 138 kV | BRP | 23820 | 23820-Halsey- | The proposed solution is to rebuild the entire ~5.3 mile-long Halsey – Sabine 138 kV line that is comprised of 336 ACSR conductor utilizing 954 ACSR conductor and upgrade the 336 ACSR line entrance at Halsey. | METC | M2 - Appendix A Approved | 130000 | 2027-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Halsey |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | METC | West | 15793 | Rebuild Gaylord - Livingston 138 kV | BRP | 23821 | 23821-Gaylord-Livingston | Rebuild ~1.3 miles of the Gaylord – Livingston 138 kV line that is comprised of 266 ACSR conductor only utilizing 954 ACSR conductor on 230 kV double-circuit structures. | METC | M2 - Appendix A Approved | 3500000 | 2027-05-14 | Line Upgrade | Line rebuild on existing ROW | Gaylord | Livingston | 1 | 138 |  |  | 1.3 | MI |  | Not Shared
MTEP19 | A | METC | Central | 15802 | Rebuild Beals Road - Wealthy 138 kV | BRP | 23832 | 23832-Beals Road-Wealthy | The proposed solution is to rebuild 3.15 miles, 6-wire 336 ACSR section of the Wealthy-Beals Road 138kV circuit using 1431 ACSR conductor with single circuit steel structures. | METC | M2 - Appendix A Approved | 4000000 | 2026-12-23 | Line Upgrade | Line rebuild on existing ROW | Beals Road | Wealthy | 1 | 138 |  |  | 3.15 | MI |  | Not Shared
MTEP19 | A | METC | Central | 15803 | Gaines - Meadowbrooke 138 kV Rebuild | BRP | 23833 | 23833-Gaines-Meadowbrooke | The proposed solution is to rebuild 0.09 mile Gaines – Meadowbrooke section of the Gaines – Plaster Creek 138kV circuit using 2156 ACSR with steel structures. | METC | M2 - Appendix A Approved | 455000 | 2027-04-01 | Line Upgrade | Line rebuild on existing ROW | Gaines | Meadowbrooke | 1 | 138 |  |  | 0.09 | MI |  | Not Shared
MTEP19 | A | METC | Central | 15804 | Rebuild Gaines - Stamping Plant 138kV | BRP | 23834 | 23834-Gaines-Stamping Plant | The proposed solution is to rebuild 10.98 miles of the Gaines – Stamping Plant 138kV circuit using 954 ACSR conductor with single steel structures. | METC | M2 - Appendix A Approved | 16000000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Gaines | Stamping Plant | 1 | 138 |  |  | 10.98 | MI |  | Not Shared
MTEP19 | A | METC | East | 15805 | Rebuild Spaulding - Vergennes 138 kV | BRP | 23835 | 23835-Spaulding-Vergennes | The proposed solution is to rebuild 7.17 miles the Vergennes – Spaulding circuit using 1431 ACSR conductor with single circuit steel structures. Also replace terminal equipment at Spaulding and Vergennes. | METC | M2 - Appendix A Approved | 6169000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Spaulding | Vergennes | 1 | 138 |  |  | 7.17 | MI |  | Not Shared
MTEP19 | A | METC | West | 15806 | Chopin-Arthur Jct. 138kV Sag Remediation | BRP | 23836 | 23836-Chopin-Arthur Jct | The Chopin – Arthur Jct. 138kV section of the Chopin – Tallmadge 138kV line is projected to overload under various contingency scenarios, the worst involving category P6 contingencies. The identified overloaded equipment on this circuit is the sag limit on the Chopin – Arthur Jct. 138kV section. The thermal violations are only found on peak cases. The proposed solution is to completely remediate sag on the Chopin – Arthur Jct. section to conductor limit of 908 Amps (217 MVA). | METC | M2 - Appendix A Approved | 3230000 | 2027-06-01 | Line Upgrade | Line rebuild on existing ROW | Chopin | Arthur Jct | 1 | 138 |  |  | 5.74 | MI |  | Not Shared
MTEP19 | A | METC | West | 15805 | Rebuild Spaulding - Vergennes 138 kV | BRP | 23837 | 23837-Spaulding- | Replace terminal equipment at Spaulding. | METC | M2 - Appendix A Approved | 31000 | 2028-06-01 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Spaulding |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 15456 | Brooklyn-Malcom 69kV line & Grinnell 69kV Terminal | Other | 23851 | 23851-Grinnell-Substation | Add a 69kV terminal at the Grinnell substation. | ITCM | M2 - Appendix A Approved | 346616 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Grinnell | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | Central | 15456 | Brooklyn-Malcom 69kV line & Grinnell 69kV Terminal | Other | 23852 | 23852-Grinnell-Line Taps | Construct the 69kV line taps for the new 69kV terminal at the Grinnell substation. | ITCM | M2 - Appendix A Approved | 0 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Grinnell | Line Taps |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | PRAIRIE POWER, INC. | Central | 15815 | New Fancy Creek-Middletown 69 kV Line | Other | 23858 | New Fancy Creek-Middletown 69 kV Line | New Fancy Creek-Middletown 69 kV Line with 556 ACSR | PPI | M2 - Appendix A Approved | 9141500 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Fancy Creek | Middletown | 1 | 69 | 69 | 15.1 |  | IL |  | Not Shared
MTEP19 | A | ITC | West | 15776 | Juliet | Other | 23873 | 23873-Adams-Juliet | Install OPGW between Adams and Juliet stations. | ITCT | M2 - Appendix A Approved | 1 | 2030-12-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Adams | Juliet |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | PRAIRIE POWER, INC. | Central | 15825 | New Mechanicsburg-Taylorville 69 kV Line | Other | 23875 | New Mechanicsburg-Taylorville 69 kV Line | New Mechanicsburg-Taylorville 69 kV Line with 336 ACSR | PPI | M2 - Appendix A Approved | 7050000 | 2026-12-01 | Line New | New Transmission line, new ROW - may include terminations | Mechanicsburg | Taylorville | 1 | 69 | 69 | 14.1 |  | IL |  | Not Shared
MTEP19 | A | METC | East | 15833 | Rebuild Bagley Tap - Gaylord 138 kV | BRP | 23882 | 23882-Bagley Tap-Gaylord | Rebuild the entire ~1.2 mile-long Bagley Tap – Gaylord 138 kV section of the ~40.4 mile-long Gaylord – Mio Dam 138 kV line. Pre-build it to 230 kV construction to facilitate potential future 230 kV expansion in northern Michigan. Replace the existing assets (all structures, 266 ACSR conductor, and the 266 ACSR line entrance at Gaylord) with new double-circuit structures that are designed for 954 ACSR conductor on each side and install this conductor along with OPGW for the existing line only. | METC | M2 - Appendix A Approved | 3950000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Bagley Tap | Gaylord | 1 | 138 |  |  | 1.2 | MI |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16686 | Garner Galls Creek 161kV Interconnection | Other | 24377 | 24377-Garner Galls Creek-Substation | New Garner Galls Creek 161kV/distribution substation. | ITCM | M2 - Appendix A Approved | 4276370 | 2030-03-12 | Substation | Substation (breakers only, no transformer) | Garner Galls Creek | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16686 | Garner Galls Creek 161kV Interconnection | Other | 24378 | 24378-Garner Galls Creek-Line Taps | Line tap work to connect the new Garner Galls Creek 161kV/distribution substation. | ITCM | M2 - Appendix A Approved | 376800 | 2030-02-27 | Line New | New Transmission line, new ROW - may include terminations | Garner Galls Creek | Line Taps |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16686 | Garner Galls Creek 161kV Interconnection | Other | 24379 | 24379-Hancock-Substation | Upgrade relaying to accomodate the new Garner Galls Creek substation. | ITCM | M2 - Appendix A Approved | 127200 | 2024-08-30 | Substation | Small miscellaneous substation equipment | Hancock | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16686 | Garner Galls Creek 161kV Interconnection | Other | 24380 | 24380-Hancock-Garner Galls Creek | Add OPGW on the circuit from Hancock to the new Garner Galls Creek substation. | ITCM | M2 - Appendix A Approved | 2483933 | 2024-08-30 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | Hancock | Garner Galls Creek | 1 | 161 | 161 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16687 | Clinton 2nd Ave-Clinton North 6 mile 69kV Rebuild | Other | 24381 | 24381-Clinton 2nd Avenue-Clinton North | Rebuild the ~6 mile 69kV circuit from the Clinton 2nd Ave tap to the Clinton North substation. | ITCM | M2 - Appendix A Approved | 5411800 | 2040-12-31 | Line Upgrade | Line rebuild on existing ROW | Clinton 2nd Avenue | Clinton North | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16687 | Clinton 2nd Ave-Clinton North 6 mile 69kV Rebuild | Other | 24382 | 24382-Beaver Channel-Substation | Upgrade relaying at Beaver Channel terminal 134. | ITCM | M2 - Appendix A Approved | 0 | 2028-05-31 | Substation | Small miscellaneous substation equipment | Beaver Channel | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16687 | Clinton 2nd Ave-Clinton North 6 mile 69kV Rebuild | Other | 24383 | 24383-Clinton North-Substation | Upgrade relaying at Clinton North. | ITCM | M2 - Appendix A Approved | 0 | 2028-05-31 | Substation | Small miscellaneous substation equipment | Clinton North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC MIDWEST | West | 16687 | Clinton 2nd Ave-Clinton North 6 mile 69kV Rebuild | Other | 24435 | 24435-Clinton 2nd Street-Clinton South | Retire the 69kV line from the Clinton 2nd Street Sub to the Clinton South sub. | ITCM | M2 - Appendix A Approved | 0 | 2028-05-31 | Line New | New Transmission line, new ROW - may include terminations | Clinton 2nd Street | Clinton South | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP19 | A | ITC | East | 17630 | 120 kV Cable Reactors | BRP | 24613 | 24613-Caniff- | Install 1% reactors on the Caniff – Cortland, Caniff – Bristol, and Caniff – Cyril 120 kV lines | ITCT | M3 - Under Construction | 13125000 | 2026-12-01 | Substation | Small miscellaneous substation equipment | Caniff |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 17630 | 120 kV Cable Reactors | BRP | 24614 | 24614-Bristol- | Install 1% reactors on the Caniff – Cortland, Caniff – Bristol, and Caniff – Cyril 120 kV lines | ITCT | M4 - Project in Service | 1261000 | 2024-07-17 | Substation | Substation (breakers only, no transformer) | Bristol |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 16023 | Lincoln-Northeast-Northwest 120 kV Rebuild | BRP | 25271 | 25271-L-N-NW-CTL2 | Rebuild the overhead span from L-N-NW tap to where the underground cable starts (CTL2) with 1431 ACSR conductor. | ITCT | M4 - Project in Service | 49850 | 2021-06-01 | Line Upgrade | Line rebuild on existing ROW | L-N-NW | CTL2 | 1 | 120 |  |  | 0.01 | MI |  | Not Shared
MTEP19 | A | AMERICAN TRANSMISSION COMPANY | West | 15947 | Waupaca Area Energy Storage Project | Other | 24325 | 24325-Wautoma- | Wautoma 69 kV Bus Upgrade | ATC | M3 - Under Construction | 0 | 2026-06-01 | Substation | Substation bus upgrade | Wautoma |  |  | 69 |  |  |  | WI |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15625 | East Brandon 115kV Delivery Point | Other | 24334 | 24334-East Brandon- | Install a 115kV GOAB at the East Brandon delivery point. | Entergy-MS | M2 - Appendix A Approved | 260000 | 2026-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | East Brandon |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15845 | Woodville Loop Project | Other | 24335 | 24335-Crosby Switching Station- | Entergy - Install 115kV line bay with breaker at Crosby switching station. Transmission line adjustments for Woodville - Centreville tap | Entergy-MS | M2 - Appendix A Approved | 3069000 | 2027-03-01 | Substation | Switching station (breakers only, no transformer) | Crosby Switching Station |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | South | 15847 | Utica JC Loop Project | Other | 24336 | 24336-HWY 547 switching station- | Entergy - Install a new 115kV line bay and breaker at HWY 547 switching station | Entergy-MS | M2 - Appendix A Approved | 2860000 | 2028-06-01 | Substation | Switching station (breakers only, no transformer) | HWY 547 switching station |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | DUKE ENERGY INDIANA, LLC | West | 15840 | Tetersburg 69/12kV Sub | Other | 23895 | 23895-Tetersburg 69-new sub | Tetersburg 69/12kV Sub: install new sub in the 69191 ckt | DEI | M2 - Appendix A Approved | 1040000 | 2027-06-01 | Substation | Distribution substation - may include trans high side | Tetersburg 69 | new sub |  | 69 | 12 | 0.25 |  | IN |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15625 | East Brandon 115kV Delivery Point | Other | 23902 | 23902-Rankin- | Entergy - Add new 115 kV line bay w/ breaker to Rankin substation | Entergy-MS | M2 - Appendix A Approved | 3403728 | 2026-06-01 | Substation | Switching station (breakers only, no transformer) | Rankin |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15625 | East Brandon 115kV Delivery Point | Other | 23903 | 23903-Rankin-East Brandon | Build a new 115 kV transmission line from the Rankin substation to East Brandon delivery point GOAB. | Entergy-MS | M2 - Appendix A Approved | 3510000 | 2026-06-01 | Line New | New Transmission line, new ROW - may include terminations | Rankin | East Brandon |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15845 | Woodville Loop Project | Other | 23911 | 23911-Woodville switching station- | Tap the EMI owned Centreville to Woodville 115kV line with new switching station. | Entergy-MS | M2 - Appendix A Approved | 600000 | 2027-03-01 | Substation | Switching station (breakers only, no transformer) | Woodville switching station |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15845 | Woodville Loop Project | Other | 23912 | 23912-Woodville switching station-Crosby switching station | Build a new 115kV transmission line from Woodville switching station to EMI Crosby switching station. | Entergy-MS | M2 - Appendix A Approved | 10400000 | 2027-03-01 | Line New | New Transmission line, new ROW - may include terminations | Woodville switching station | Crosby switching station |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15847 | Utica JC Loop Project | Other | 23914 | 23914-Utica-Utica JC | Rebuild L516 (Utica to Utica JC). | Entergy-MS | M2 - Appendix A Approved | 2415000 | 2028-06-01 | Line Upgrade | Line rebuild on existing ROW | Utica | Utica JC |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15847 | Utica JC Loop Project | Other | 23915 | 23915-Utica JC GOAB- | Tap L516 (Utica to Utica JC) with a 115kV GOAB. | Entergy-MS | M2 - Appendix A Approved | 260000 | 2028-06-01 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Utica JC GOAB |  |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | COOPERATIVE ENERGY | West | 15847 | Utica JC Loop Project | Other | 23916 | 23916-Utica JC GOAB-HW 547 Switching Station | Build a 115kV transmission line from Utica JC GOAB to Port Gibson substation. | Entergy-MS | M2 - Appendix A Approved | 5184000 | 2028-06-01 | Line New | New Transmission line, new ROW - may include terminations | Utica JC GOAB | HW 547 Switching Station |  | 115 |  |  |  | MS |  | Not Shared
MTEP19 | A | ITC | East | 15863 | Rebuild of Arizona – Dayton 120 kV | BRP | 23945 | 23945-Arizona-Dayton | Rebuild approximately 4.3 miles of 120 kV line from Arizona to Dayton using 954 ACSR conductor. Also upgrade station equipment at Arizona. | ITCT | M2 - Appendix A Approved | 6970000 | 2027-10-29 | Line Upgrade | Line rebuild on existing ROW | Arizona | Dayton | 1 | 120 |  |  | 2.7 | MI |  | Not Shared
MTEP19 | A | ITC | East | 15863 | Rebuild of Arizona – Dayton 120 kV | BRP | 23949 | 23949-Arizona- | Rebuild approximately 4.3 miles of 120 kV line from Arizona to Dayton using 954 ACSR conductor. Also upgrade station equipment at Arizona. | ITCT | M2 - Appendix A Approved | 30000 | 2027-10-29 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Arizona |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 15865 | Rebuild of Navarre – A-I-N – Ironton 120 kV | BRP | 23950 | 23950-Navarre-Ironton | Rebuild approximately 7.7 miles from Navarre to Adelaide-Ironton-Navarre junction to Ironton with 1431 ACSR conductor. Also upgrade station equipment at both ends. | ITCT | M3 - Under Construction | 11000000 | 2028-05-01 | Line Upgrade | Line rebuild on existing ROW | Navarre | Ironton | 1 | 120 |  |  | 7.7 | MI |  | Not Shared
MTEP19 | A | ITC | West | 15865 | Rebuild of Navarre – A-I-N – Ironton 120 kV | BRP | 23951 | 23951-Navarre- | Rebuild approximately 7.7 miles from Navarre to Adelaide-Ironton-Navarre junction to Ironton with 1431 ACSR conductor. Also upgrade station equipment at both ends. | ITCT | M3 - Under Construction | 150086 | 2027-04-30 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Navarre |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | East | 15865 | Rebuild of Navarre – A-I-N – Ironton 120 kV | BRP | 23952 | 23952-Ironton- | Rebuild approximately 7.7 miles from Navarre to Adelaide-Ironton-Navarre junction to Ironton with 1431 ACSR conductor. Also upgrade station equipment at both ends. | ITCT | M3 - Under Construction | 130400 | 2028-04-28 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Ironton |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP19 | A | ITC | Central | 15866 | Newburgh – Peru 120 kV Rebuild | BRP | 23953 | 23953-Newburgh-Peru | Rebuild approximately 2.2 miles of 477 ACSR conductor to 1431 ACSR on the Newburgh – Sport 2 120 kV section to match with the rest of the circuit. | ITCT | M2 - Appendix A Approved | 5680000 | 2027-12-31 | Line Upgrade | Line rebuild on existing ROW | Newburgh | Peru | 1 | 120 |  |  | 2.2 | MI |  | Not Shared
MTEP19 | A | ITC | East | 15879 | Monroe - Lulu 345 kV Station Equipment Upgrade | BRP | 23971 | 23971-Monroe- | Upgrade the station equipment at Monroe 345 kV positions “MF” and “MM”. | ITCT | M3 - Under Construction | 1259810 | 2026-11-03 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Monroe |  |  | 345 |  |  |  | MI |  | Not Shared
MTEP19 | A | AMEREN ILLINOIS | Central | 11971 | Reconfigure Jenkins (Formerly Grand Tower) 138 kV substation to BAAH | Other | 21941 | 21941-Jenkins-Substation | Establish a breaker-and-a-half 138 kV bus arrangement | AmerenIL | M2 - Appendix A Approved | 22000000 | 2028-12-01 | Substation | Substation bus upgrade | Jenkins | Substation |  | 138 |  |  |  | IL |  | Not Shared
MTEP19 | A | ENTERGY ARKANSAS, LLC | South | 12050 | Amity Tap 115kV: Add Transmission Breakers | Other | 22131 | 22131-Amity- | Add a 115kV breaker station at the Amity 115kV Tap. | Entergy-AR | M2 - Appendix A Approved | 16400000 | 2032-06-01 | Substation | Substation (breakers only, no transformer) | Amity |  |  | 115 |  |  |  | AR |  | Not Shared
MTEP19 | A | ENTERGY ARKANSAS, LLC | South | 13612 | Little Rock Enhanced Reliability Project Phase 2 | Other | 22700 | 22700-LR 8th and Woodrow-LR Palm Street | Rebuild this line to a minimum of 1950 Amps. | Entergy-AR | M2 - Appendix A Approved | 10966000 | 2030-06-01 | Line Upgrade | Line rebuild on existing ROW | LR 8th and Woodrow | LR Palm Street |  | 115 |  |  | 3.8 | AR |  | Not Shared
MTEP19 | A | ENTERGY ARKANSAS, LLC | South | 13612 | Little Rock Enhanced Reliability Project Phase 2 | Other | 22701 | 22701-LR Palm Street-LR West | Rebuild this line to a minimum of 1950 Amps | Entergy-AR | M2 - Appendix A Approved | 12000000 | 2030-06-01 | Line Upgrade | Line rebuild on existing ROW | LR Palm Street | LR West |  | 115 |  |  |  | AR |  | Not Shared
MTEP18 | A | METC | East | 13327 | METC Beecher Control Relocation Project | Other | 22605 | 22605-Beecher- | Relocate the existing Saginaw River control center and its contents to the Beecher station following the retirement of Saginaw River | METC | M2 - Appendix A Approved | 1020000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Beecher |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP18 | A | AMERICAN TRANSMISSION COMPANY | West | 12137 | Hwy V - Structure 123 69 kV (Z-26), Rebuild | Other | 22260 | Hwy V - Structure 123 69 kV (Z-26), Rebuild | The new proposed scope is to rebuild 5.5 miles of Z-26 from structure 123 to Hwy V. The rebuilt line will be monopole structures with conductor OPGW using the standard enhanced 69 kV design. If required in the future, this portion of the line could be converted to 138 kV with minimal upgrades. We will need new easements for approximately half of the line rebuild, and these easements will allow us to convert to 138kV in the future. The existing line from Oak St to structure 123 will remain in place. This section is a mix of wood and steel structures with 4/0 ACSR conductor with a range of age and conditions that we would maintain and monitor the condition of for the next 10-15 years. | ATC | M3 - Under Construction | 18200000 | 2026-07-06 | Line Upgrade | Line rebuild on existing ROW | Hwy V | Structure 123 | Z-26 | 69 |  |  | 5.5 | WI |  | Not Shared
MTEP18 | A | METC | East | 13687 | Equipment Upgrade Morrow 138kV – Station | BRP | 22760 | 22760-Morrow- | The proposed solution is to upgrade the relay equipment at Morrow position “500” to meet or exceed 338 MVA/1413 Amps (summer emergency). | METC | M2 - Appendix A Approved | 0 | 2026-03-31 | Misc. | Relaying, protection, RTU and SCADA equipment | Morrow |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP18 | A | METC | East | 13687 | Equipment Upgrade Morrow 138kV – Station | BRP | 22761 | 22761-Morrow- | The proposed solution is to upgrade the terminal equipment at Morrow position “500” to meet or exceed 338 MVA/1413 Amps (summer emergency). | METC | M2 - Appendix A Approved | 31000 | 2026-03-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Morrow |  |  | 138 |  |  |  | MI |  | Not Shared
MTEP18 | A | ITC | East | 14007 | Enrico Fermi-Shoal 120kV Rebuild | Other | 23292 | 23292-Toll Road-Shoal | Rebuild 3.7 miles wood pole section of the Toll Road - Shoal 120kV circuit utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on the circuit. | ITCT | M4 - Project in Service | 5747000 | 2024-12-31 | Line Upgrade | Line rebuild on existing ROW | Toll Road | Shoal |  | 120 |  |  | 3.7 | MI |  | Not Shared
MTEP18 | A | ITC | Central | 14007 | Enrico Fermi-Shoal 120kV Rebuild | Other | 23306 | 23306-Enrico Fermi- | Replace line entrance at Enrico Fermi | ITCT | M4 - Project in Service | 50500 | 2024-12-31 | Line Upgrade | Terminal equipment (bus, wavetrap, CT, switches, jumpers, trainers, risers) | Enrico Fermi |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP18 | A | ENTERGY ARKANSAS, LLC | South | 12663 | Jumpers Corner 161kV: Construct new substation | Other | 22461 | 22461-Jumpers Corner 161kV- | New 161/13.8kV Substation with a single 40 MVA transformer and three feeder breaker bays. | Entergy-AR | M2 - Appendix A Approved | 19400000 | 2028-05-17 | Substation | Substation (breakers only, no transformer) | Palestine 161kV |  |  | 161 | 14 |  |  | AR |  | Not Shared
MTEP18 | A | ENTERGY ARKANSAS, LLC | South | 12664 | Beryl 161kV: Construct new substation | Other | 22462 | 22462-Beryl 161kV- | Construct a new substation with a new 40 MVA 161/13.8kV LTC and four feeder breaker bays. | Entergy-AR | M2 - Appendix A Approved | 7433784 | 2029-12-01 | Substation | Distribution substation - may include trans high side | Ranchette 161kV |  | 1 | 161 | 14 |  |  | AR |  | Not Shared
MTEP18 | A | AMERICAN TRANSMISSION COMPANY | West | 13756 | Edgewater SS, 345 kV Asset Renewal and Bus Reconfiguration | Other | 22824 | 22824-Edgewater- | Edgewater 345kV Breaker replacement, Breaker retirement and Bus reconfiguration | ATC | M3 - Under Construction | 14200000 | 2026-12-01 | Substation | Substation (breakers only, no transformer) | Edgewater |  |  | 345 |  |  |  | WI |  | Not Shared
MTEP18 | A | DUKE ENERGY INDIANA, LLC | Central | 13765 | Metea to Lucerne 69kV Rebuild | Other | 22833 | 22833-Metea 69-Lucerne 69 | Metea to Lucerne 6926 (Part 1) 69kV Rebuild w/ 477ACSR | DEI | M2 - Appendix A Approved | 11861000 | 2028-05-12 | Line Upgrade | Line rebuild on existing ROW | Metea 69 | Lucerne 69 | 1 | 69 |  |  | 7.1 | IN |  | Not Shared
MTEP18 | A | DUKE ENERGY INDIANA, LLC | Central | 13820 | Galveston New 69-12kV Sub | Other | 22891 | 22891-Galveston- | Galveston New 69-12kV Sub: loop 69173 ckt thru with (3) 1200A switches and 954AAC bus; 22.4MVA NLTC xfmr | DEI | M2 - Appendix A Approved | 1767000 | 2027-06-01 | Substation | Distribution substation - may include trans high side | Galveston |  |  | 69 | 12 |  |  | IN |  | Not Shared
MTEP18 | A | ITC | East | 14007 | Enrico Fermi-Shoal 120kV Rebuild | Other | 23123 | 23123-Enrico Fermi-Toll Road | Rebuild 1.3 miles wood pole circuit from Enrico Fermi to Toll Road 120kV utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on the circuit. | ITCT | M3 - Under Construction | 3481000 | 2030-04-01 | Line Upgrade | Line rebuild on existing ROW | Enrico Fermi | Toll Road | 1 | 120 |  |  | 1.3 | MI |  | Not Shared
MTEP18 | A | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | West | 13647 | Detroit Lakes Jet Substation | Other | 23136 | 23136-DL Jet 115 kV- | Construct a new line-breaker substation adjacent to the existing Detroit Lakes Industrial Substation in order to relocate the existing distribution transformer at Detroit Lakes Industrial Substation. Also, allow for a second distribution transformer later on. | MRES | M2 - Appendix A Approved | 5000000 | 2026-12-30 | Substation | Switching station (breakers only, no transformer) | DL Industrial 115 kV |  |  | 115 |  |  |  | MN |  | Not Shared
MTEP18 | A | OTTER TAIL POWER COMPANY | West | 14056 | Parkers Prairie 115/12.5 kV Tap | Other | 23181 | 23181-Parkers Prairie 115 kV- | Parkers Prairie existing 41.6 kV load will be moved to a Parkers Prairie 115/12.5 kV Tap | OTP | M2 - Appendix A Approved | 950000 | 2030-08-31 | Line New | Install tap (typically a pole a switch or in-and-out loop) | Parkers Prairie 115 kV |  |  | 115 | 13 |  |  | MN |  | Not Shared
MTEP18 | A | MONTANA-DAKOTA UTILITIES CO. | West | 13869 | Stanley Substation | Other | 22936 | 22936-Stanley- | 115 kV three breaker ring bus and 115/69 kV transformer | MDU | M2 - Appendix A Approved | 4720000 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Stanley |  |  | 115 | 69 |  |  | ND |  | Not Shared
MTEP18 | A | ENTERGY SERVICES, LLC. | South | 13902 | Mossville to Lockmoor 69 kV: Rebuild/Reconductor line | BRP | 22972 | 22972-Mossville-Lockmoor | Rebuild or re-conductor the approximately 2.10 mile long Mossville to Lockmoor 69 kV transmission circuit to a minimum of 1200 A, 143 MVA. | Entergy-LA | M3 - Under Construction | 13000000 | 2026-08-31 | Line Upgrade | Line rebuild on existing ROW | Mossville | Lockmoor |  | 69 |  |  | 2.1 | LA |  | Not Shared
MTEP18 | A | AMERICAN TRANSMISSION COMPANY | West | 15126 | Edgewater SS, DIC, replace transformer and substation rebuild | Other | 23449 | 23449-Edgewater SS- | Loop through the 138 kV line X-37 with line breakers | ATC | M2 - Appendix A Approved | 5100000 | 2030-12-31 | Substation | Distribution substation - may include trans high side | Edgewater SS |  |  | 138 |  |  |  | WI |  | Not Shared
MTEP18 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 13577 | Rebuild Atlanta to Hillman | Other | 22679 | 22679-Atlanta-Hillman | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | WPSC | M3 - Under Construction | 13500000 | 2026-08-01 | Line Upgrade | Line rebuild on existing ROW | Atlanta | Hillman |  | 69 |  |  | 22 | MI |  | Not Shared
MTEP18 | A | WOLVERINE POWER SUPPLY COOPERATIVE, INC | East | 13579 | South Boardman Station Rebuild | Other | 22681 | 22681-South Boardman- | The control house and controls will be upgraded to include Wolverine’s standard protection and control system. The existing 69 kV switches limit facility ratings to sub-standard capacity and will be replaced. Additionally, the existing bus configuration will be upgraded to a ring bus and will be built to 138 kV design. | WPSC | M2 - Appendix A Approved | 10000000 | 2027-12-31 | Substation | Switching station (breakers only, no transformer) | South Boardman |  |  | 69 |  |  |  | MI |  | Not Shared
MTEP18 | A | ENTERGY ARKANSAS, LLC | South | 13622 | Southland - Mt. Home 161kV: Rebuild line | BRP | 22712 | 22712-Southland-Mt. Home | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amps. | Entergy-AR | M3 - Under Construction | 2260000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Southland | Mt. Home |  | 161 |  |  | 1.4 | AR |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22566 | 22566-Kalona Koe-Substation | Convert the new Kalona Koe substation to 69kV operation. | ITCM | M2 - Appendix A Approved | 114065 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Kalona Koe | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22567 | 22567-Iowa Junction-Substation | Retire the 34kV equipment at Iowa Jct. | ITCM | M2 - Appendix A Approved | 329790 | 2026-12-31 | Substation | Substation (breakers only, no transformer) | Iowa Junction | Substation |  | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22568 | 22568-Wellman-Wellamn Tap | Retire the 8.9 mile Wellman tap after the load is served from Kalona Koe. | ITCM | M2 - Appendix A Approved | 485394 | 2024-12-31 | Line New | New Transmission line, new ROW - may include terminations | Wellman | Wellamn Tap | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ENTERGY SERVICES, LLC. | South | 9781 | Jennings to Lawtag 69 kV L-13/L-19 and L-14: Rebuild lines | BRP | 22591 | 22591-Jennings-Lawtag | rebuild line | Entergy-LA | M3 - Under Construction | 19400000 | 2026-06-30 | Line Upgrade | Line rebuild on existing ROW | Jennings | Lawtag | 2 | 69 |  |  | 4.7 | LA |  | Not Shared
MTEP17 | A | DUKE ENERGY INDIANA, LLC | Central | 11957 | Wabash River Station new industrial load | Other | 21918 | 21918-Wabash River Station- | Wabash River Station new industrial load @ 50MW on the 230kV bus section #2 or #3 | DEI | M2 - Appendix A Approved | 5954443 | 2028-05-18 | Substation | Distribution substation - may include trans high side | Wabash River Station |  |  | 230 |  |  |  | IN |  | Not Shared
MTEP17 | A | ENTERGY SERVICES, LLC. | South | 12136 | Cullichia 230 kV: New substation | Other | 22258 | 22258-Cullichia- | Construct new station, station name changed to Cullichia | Entergy-LA | M3 - Under Construction | 22738800 | 2027-05-31 | Substation | Substation (breakers only, no transformer) | Cullichia |  |  | 230 |  |  |  | LA |  | Not Shared
MTEP17 | A | DUKE ENERGY INDIANA, LLC | Central | 1900 | Avon Industrial Park 138-12kV new dist sub | Other | 3796 | 3796-Avon Industrial Park-new dist sub | Avon Industrial Park - Construct 138-12kV - 22.4 MVA sub in the All Points Industrial Park and 2.5 miles of 138kV line | DEI | M2 - Appendix A Approved | 3571000 | 2027-01-21 | Substation | Distribution substation - may include trans high side | Avon Industrial Park | new dist sub | 1 | 138 | 12 | 2.5 |  | IN |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22391 | 22391-Frytown-Substation | New Frytown 69kv/distribution substation. | ITCM | M4 - Project in Service | 3290609 | 2023-08-01 | Substation | Substation (breakers only, no transformer) | Frytown | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22392 | 22392-Frytown-Parnell REC | Build a new circuit, approximately ~12 miles of T2-4/0 to be operated at 69kV | ITCM | M2 - Appendix A Approved | 15637512 | 2024-09-01 | Line New | New Transmission line, new ROW - may include terminations | Frytown | Parnell REC | 1 | 69 | 69 | 12 |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22393 | 22393-Frytown-Hills (IPL) | Convert this line section to 69kV operation | ITCM | M2 - Appendix A Approved | 674927 | 2026-12-31 | Line Upgrade | Line conversion to higher voltage | Frytown | Hills (IPL) |  | 69 | 69 |  | 11.68 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22395 | 22395-Hills (IPL)-New Hills Area Sub | Build a new circuit, approximately ~0.5 miles of T2-4/0 to be operated at 69kV | ITCM | M2 - Appendix A Approved | 1207219 | 2026-07-31 | Line New | New Transmission line, new ROW - may include terminations | Hills (IPL) | New Hills Area Sub | 1 | 69 | 69 | 1 |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22396 | 22396-Kalona Koe-Substation | New Kalona Koe 69kV/distribution substation. Operate at 34kV until conversion. | ITCM | M4 - Project in Service | 2119466 | 2018-12-19 | Substation | Substation (breakers only, no transformer) | Kalona Koe | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22397 | 22397-Kalona Koe-Riverside Voyager | Convert this line section to 69kV operation | ITCM | M2 - Appendix A Approved | 0 | 2026-12-31 | Line Upgrade | Line conversion to higher voltage | Kalona Koe | Riverside Voyager | 1 | 69 | 69 |  | 7.14 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22398 | 22398-Riverside Voyager-Iowa Junction | Convert this line section to 69kV operation | ITCM | M2 - Appendix A Approved | 201445 | 2026-12-31 | Line Upgrade | Line conversion to higher voltage | Riverside Voyager | Iowa Junction | 1 | 69 | 69 |  | 2.39 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22399 | 22399-Hills (MEC)-Iowa Junction | Re-terminate the existing Hills - Washington 69kV line to Iowa Junction and then continue to Washington | ITCM | M2 - Appendix A Approved | 0 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Hills (MEC) | Iowa Junction | 1 | 69 | 69 | 0.1 |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Other | 22400 | 22400-Iowa Junction-Kalona REC Tap | Re-terminate the existing Hills - Washington 69kV line to Iowa Junction and then continue to Washington | ITCM | M2 - Appendix A Approved | 201457 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Iowa Junction | Kalona REC Tap | 1 | 69 | 69 |  | 9.53 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22415 | 22415-Wyomiing-Substation | Add five 69kV breaker terminals at the Wyoming sub. | ITCM | M2 - Appendix A Approved | 1 | 2019-12-31 | Substation | Substation (breakers only, no transformer) | Wyomiing | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22416 | 22416-Wyoming-Monticello Industrial | Convert this line section to 69kV operation. Includes the conversion of Scotch Grove REC and Lovell REC distribution subs. | ITCM | M4 - Project in Service | 490266 | 2018-12-31 | Line Upgrade | Line conversion to higher voltage | Wyoming | Monticello Industrial | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22417 | 22417-Wyoming-Bennett | Convert this line section to 69kV operation. Includes the conversion of Olin, Rome REC, Clarence South, and Clarence REC distribution subs. | ITCM | M2 - Appendix A Approved | 17864047 | 2025-12-25 | Line Upgrade | Line conversion to higher voltage | Wyoming | Bennett | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22418 | 22418-Wyoming-Maquoketa | Convert this line section to 69kV operation. Includes the conversion of Monmouth REC and Monmouth distribution subs. | ITCM | M2 - Appendix A Approved | 103200 | 2022-06-30 | Line Upgrade | Line conversion to higher voltage | Wyoming | Maquoketa | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22420 | 22420-Wyoming-Dixon | Convert this line section to 69kV operation. Includes the conversion of Wyoming South, Massillon, Lowden, and Wheatland distribution subs. | ITCM | M2 - Appendix A Approved | 5311982 | 2026-12-31 | Line Upgrade | Line conversion to higher voltage | Wyoming | Dixon | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22422 | 22422-Sand Springs-Substation | Terminal work to connect the Coggon to Sand Springs 69 kV line at Sand Springs. | ITCM | M4 - Project in Service | 19902 | 2018-06-04 | Substation | Substation (breakers only, no transformer) | Sand Springs | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ENTERGY SERVICES, LLC. | South | 9781 | Jennings to Lawtag 69 kV L-13/L-19 and L-14: Rebuild lines | BRP | 21155 | 21155-Jennings-Lawtag | Upgrade Line | Entergy-LA | M3 - Under Construction | 1 | 2026-06-30 | Line Upgrade | Line rebuild on existing ROW | Jennings | Lawtag | 1 | 69 |  |  | 4.83 | LA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22031 | 22031-Albion REC Tap-Fletcher | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Albion REC Tap | Fletcher | 1 | 69 | 69 |  | 13.18 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22032 | 22032-Albion REC-Albion REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Albion REC | Albion REC Tap | 1 | 69 | 69 |  | 0.27 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22033 | 22033-Albion REC Tap-St Anthony REC | Convert this line section to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Albion REC Tap | St Anthony REC | 1 | 69 | 69 |  | 11.6 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22034 | 22034-McCallsburg-St Anthony REC | Convert this line section to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | McCallsburg | St Anthony REC | 1 | 69 | 69 |  | 11.7 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22035 | 22035-McCallsburg-Substation | New McCallsburg 69kV/distribution sub. | ITCM | M2 - Appendix A Approved | 2471678 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | McCallsburg | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22037 | 22037-McCallsburg-Story City 1 | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | McCallsburg | Story City 1 | 1 | 69 | 69 |  | 11.16 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22038 | 22038-Story City 1-Story City Muni Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Story City 1 | Story City Muni Tap | 1 | 69 | 69 |  | 2.86 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22040 | 22040-Story City Muni Tap-Story City 2 | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Story City Muni Tap | Story City 2 | 1 | 69 | 69 |  | 1.54 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22041 | 22041-Story City Muni Tap-Ames | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 505200 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Story City Muni Tap | Ames | 1 | 69 | 69 |  | 7.5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22043 | 22043-Ames-Substation | Add a 69kV breaker | ITCM | M4 - Project in Service | 260987 | 2017-12-21 | Substation | Small miscellaneous substation equipment | Ames | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22045 | 22045-East Nevada St-Timber Creek | Convert this line to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 342000 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | East Nevada St | Timber Creek | 1 | 69 | 69 |  | 4.2 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22046 | 22046-Grand Junction North-Substation | Add a 69kV breaker | ITCM | M2 - Appendix A Approved | 295774 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Grand Junction North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22047 | 22047-Grand Junction-Grand Junction Muni | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 303078 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Grand Junction | Grand Junction Muni | 1 | 69 | 69 |  | 1.78 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22049 | 22049-Grand Junction Muni-Grand Junction North | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Grand Junction Muni | Grand Junction North | 1 | 69 | 69 |  | 1.85 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22050 | 22050-Grand Junction North-Iron Man REC | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Grand Junction North | Iron Man REC | 1 | 69 | 69 |  | 7.93 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22051 | 22051-Iron Man REC-Harcourt | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Iron Man REC | Harcourt | 1 | 69 | 69 |  | 11.55 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22052 | 22052-Harcourt-Substation | Construct a new 4 breaker station with 3 line terminals and a capacitor bank. The site would ideally be located near the Gowrie tap point on Grand Jct N Ckt 2030. The capacitor bank should be sized for a single stage of 10.8 (9.18 effective) MVAR, set up to add an additional 10.8 (9.18 effective) MVAR stage. | ITCM | M2 - Appendix A Approved | 3052551 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Harcourt | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22053 | 22053-Harcourt-Gowrie Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Harcourt | Gowrie Tap | 1 | 69 | 69 |  | 4.43 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22054 | 22054-Gowrie Tap-Gowrie REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Gowrie Tap | Gowrie REC | 1 | 69 | 69 |  | 1 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22055 | 22055-Gowrie Tap-Gowrie Muni | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Gowrie Tap | Gowrie Muni | 1 | 69 | 69 |  | 1.51 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22056 | 22056-Harcourt-Wevster REC Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 1176000 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Harcourt | Wevster REC Tap | 1 | 69 | 69 |  | 5.55 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22057 | 22057-Webster REC Tap-Webster REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Webster REC Tap | Webster REC | 1 | 69 | 69 |  | 3.93 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22058 | 22058-Webster REC Tap-Hardin REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Webster REC Tap | Hardin REC | 1 | 69 | 69 |  | 3.08 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22059 | 22059-Hardin REC-Boxholme | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Hardin REC | Boxholme | 1 | 69 | 69 |  | 5.96 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22060 | 22060-Boxholme-Fraser REC Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Boxholme | Fraser REC Tap | 1 | 69 | 69 |  | 4.26 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22061 | 22061-Fraser REC Tap-Fraser REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Fraser REC Tap | Fraser REC | 1 | 69 | 69 |  | 0.75 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22062 | 22062-Fraser REC Tap-Doud | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Fraser REC Tap | Doud | 1 | 69 | 69 |  | 14.88 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22063 | 22063-Boone Quartz-Substation | Add a 69kV breaker | ITCM | M2 - Appendix A Approved | 228210 | 2022-12-31 | Substation | Small miscellaneous substation equipment | Boone Quartz | Substation | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22064 | 22064-Boone Quartz-Boone South | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 264428 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Boone Quartz | Boone South | 1 | 69 | 69 |  | 4.75 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22065 | 22065-Boone South-Valley REC Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Boone South | Valley REC Tap | 1 | 69 | 69 |  | 1.15 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22067 | 22067-Valley REC Tap-Valley REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Valley REC Tap | Valley REC | 1 | 69 | 69 |  | 3.21 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22068 | 22068-Valley REC Tap-Ogden Muni Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Valley REC Tap | Ogden Muni Tap | 1 | 69 | 69 |  | 9.8 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22069 | 22069-Ogden Muni Tap-Ogden Muni | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Ogden Muni Tap | Ogden Muni | 1 | 69 | 69 |  | 1.6 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22070 | 22070-Ogden Muni Tap-Ogden REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Ogden Muni Tap | Ogden REC | 1 | 69 | 69 |  | 0.9 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22071 | 22071-Ogden REC-Grand Junction | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Ogden REC | Grand Junction | 1 | 69 | 69 |  | 13.7 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22072 | 22072-Timber Creek-Haverhill | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Timber Creek | Haverhill | 1 | 69 | 69 |  | 7 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22073 | 22073-Haverhill-Melbourne REC Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Haverhill | Melbourne REC Tap | 1 | 69 | 69 |  | 9.46 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22074 | 22074-Melbourne REC Tap-Melbourne REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Melbourne REC Tap | Melbourne REC | 1 | 69 | 69 |  | 2.02 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22075 | 22075-Melbourne REC TAp-Rhodes | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Melbourne REC TAp | Rhodes | 1 | 69 | 69 |  | 5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22076 | 22076-Rhodes-Collins REC Tap | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Rhodes | Collins REC Tap | 1 | 69 | 69 |  | 4 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22077 | 22077-Collins REC Tap-Collins REC | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Collins REC Tap | Collins REC | 1 | 69 | 69 |  | 1.34 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22078 | 22078-Collins REC Tap-Maxwell North | Convert this line section to 69kVoperation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 436200 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Collins REC Tap | Maxwell North | 1 | 69 | 69 |  | 7.8 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22079 | 22079-Maxwell North-Substation | Add a 69kV breaker and terminal. | ITCM | M2 - Appendix A Approved | 200438 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Maxwell North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22423 | 22423-Dixon-Fulton | Rebuild 34.5 to 69kV and continue to operate at 34.5kV until conversion is ready. | ITCM | M4 - Project in Service | 1917600 | 2021-12-31 | Line Upgrade | Line rebuild on existing ROW | Dixon | Fulton | 1 | 35 | 35 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Other | 22424 | 22424-Dixon-Fulton | Convert this line section to 69kV operation. Includes the conversion of Wyoming South, Massillon, Lowden, and Wheatland distribution subs. | ITCM | M2 - Appendix A Approved | 261203 | 2032-02-09 | Line Upgrade | Line conversion to higher voltage | Dixon | Fulton | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22476 | 22476-Marshalltown-Ckt 0810 | Retire Marshalltown terminal 0810 | ITCM | M2 - Appendix A Approved | 72000 | 2026-12-31 | Substation | Small miscellaneous substation equipment | Marshalltown | Ckt 0810 | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22477 | 22477-Timber Creek-Substation | Upgrade 69kV terminal | ITCM | M2 - Appendix A Approved | 99222 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Timber Creek | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22478 | 22478-Timer Creek-Ckt 6030 retirements | Ckt 6030 line retirements. | ITCM | M2 - Appendix A Approved | 299976 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Timer Creek | Ckt 6030 retirements | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22479 | 22479-Boone-Ckt 3560 retirements | Ckt 3560 line retirements | ITCM | M2 - Appendix A Approved | 120000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Boone | Ckt 3560 retirements |  | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22480 | 22480-Boone-Ckt 1610 retirements | Retire Ckt 1610 that is no longer needed. | ITCM | M2 - Appendix A Approved | 48000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Boone | Ckt 1610 retirements | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22481 | 22481-Doud-69kV terminal | Add 69kV Harcourt terminal at the Doud sub | ITCM | M2 - Appendix A Approved | 259104 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Doud | 69kV terminal | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22482 | 22482-Harcourt-line taps | Perform line re-terminations to connect the new Harcourt 69kV sub. | ITCM | M2 - Appendix A Approved | 515672 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Harcourt | line taps |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22483 | 22483-Harcout-Capacitor | The capacitor bank should be sized for a single stage of 10.8 (9.18 effective) MVAR, set up to add an additional 10.8 (9.18 effective) MVAR stage. | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Voltage Device | Capacitor (switched capacitor) | Harcout | Capacitor |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22484 | 22484-Timber Creek-Substation | Add a 69kV breaker position at Timber Creek. | ITCM | M2 - Appendix A Approved | 37382 | 2027-12-31 | Substation | Small miscellaneous substation equipment | Timber Creek | Substation | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22485 | 22485-Marshalltown-Ckt 2640 retirements | Retire 34kV lines that are no longer needed. | ITCM | M2 - Appendix A Approved | 399224 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Marshalltown | Ckt 2640 retirements | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22486 | 22486-Ames-Substation | Retire Ames 34kV Sub | ITCM | M2 - Appendix A Approved | 180000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Ames | Substation |  | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22487 | 22487-Roland-Roland Tap | Retire Roland 34kV Tap | ITCM | M2 - Appendix A Approved | 194256 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Roland | Roland Tap | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22488 | 22488-Fishers-Fishers Tap | Retire the Fishers Tap | ITCM | M2 - Appendix A Approved | 57400 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Fishers | Fishers Tap | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22489 | 22489-Marshalltown-Ckt 2620 terminal | Retire the Marshalltown terminal 2620 | ITCM | M2 - Appendix A Approved | 102000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Marshalltown | Ckt 2620 terminal | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22490 | 22490-Fletcher-69kV expansion | Expand the Fletcher 69kV to allow for 2nd 161/69kV 150 MVA transformer and associated equipment. | ITCM | M2 - Appendix A Approved | 3762000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Fletcher | 69kV expansion |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22491 | 22491-Marshalltown-Ckt 2610 | Retire the 2610 terminal and associated equipment. | ITCM | M2 - Appendix A Approved | 102000 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Marshalltown | Ckt 2610 |  | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22492 | 22492-Marshalltown-Ckt 2620 | Line retirements for a portion of Ckt 2620 | ITCM | M2 - Appendix A Approved | 45872 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Marshalltown | Ckt 2620 | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22493 | 22493-Conrad-Substation | Retire old Conrad sub. | ITCM | M2 - Appendix A Approved | 180000 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Conrad | Substation |  | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22494 | 22494-Gladbrook-Gladbrook Tap | Retire Gladbrook tap. | ITCM | M2 - Appendix A Approved | 252000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Gladbrook | Gladbrook Tap | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22495 | 22495-Conrad-Conrad Tap | Retire Conrad tap. | ITCM | M2 - Appendix A Approved | 60000 | 2022-12-31 | Line New | New Transmission line, new ROW - may include terminations | Conrad | Conrad Tap | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21955 | 21955-White Pole Rd-Substation | Add 69kV terminal at the White Pole Rd substation. | ITCM | M4 - Project in Service | 248266 | 2020-12-31 | Substation | Substation (breakers only, no transformer) | White Pole Rd | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21956 | 21956-Anita-Anita Muni | Convert line to 69kV operation (already built for 69kV) | ITCM | M4 - Project in Service | 124800 | 2021-01-25 | Line Upgrade | Line conversion to higher voltage | Anita | Anita Muni | 1 | 69 | 69 |  | 3.5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21972 | 21972-Adair REC Tap-White Pole Rd | Convert line to 69kV operation (already built for 69kV). | ITCM | M4 - Project in Service | 165600 | 2020-12-31 | Line Upgrade | Line conversion to higher voltage | Adair REC Tap | White Pole Rd | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21973 | 21973-Railway-Substation | Build a new Railway 69kV breaker station. | ITCM | M4 - Project in Service | 4547318 | 2020-05-04 | Substation | Substation (breakers only, no transformer) | Railway | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21982 | 21982-Guthrie Junction (CIPCO)-Substation | CIPCO will add a 69kV terminal. | ITCM | M4 - Project in Service | 0 | 2020-05-04 | Substation | Substation (breakers only, no transformer) | Guthrie Junction (CIPCO) | Substation | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21984 | 21984-Grand Junction-Panorama REC | CIPCO will convert from Grand Junction-Rippey-Dawson REC-Dawson-Yale REC-Panorama REC to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2021-12-31 | Line Upgrade | Line conversion to higher voltage | Grand Junction | Panorama REC | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21985 | 21985-Grand Junction (CIPCO)-Substation | CIPCO will add a 161/69kV 100MVA transformer and associated upgrades. | ITCM | M2 - Appendix A Approved | 0 | 2021-12-31 | Substation | Substation (breakers only, no transformer) | Grand Junction (CIPCO) | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | DUKE ENERGY INDIANA, LLC | Central | 11999 | Attica 69 to Attica 230 69kV Rebuild | Other | 21987 | 21987-Attica 69-Attica 230 | Attica 69 to Harrison Stl Jct to Attica 230 69kV Rebuild - Rebuild 6936 ckt - 4.1 miles with 477acsr and steel poles; also rebuild 1.27 miles of 69121 where it is double circuited | DEI | M2 - Appendix A Approved | 5601000 | 2027-12-01 | Line Upgrade | Line rebuild on existing ROW | Attica 69 | Attica 230 | 1 | 69 |  |  | 5.37 | IN |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21988 | 21988-Scranton-Switch Station | Build the Scranton 69kV Switch Station. | ITCM | M2 - Appendix A Approved | 3266836 | 2023-12-31 | Substation | Substation (breakers only, no transformer) | Scranton | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21989 | 21989-Jefferson WCC-Substation | Add a 69kV breaker terminal. | ITCM | M2 - Appendix A Approved | 261830 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Jefferson WCC | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21990 | 21990-Scranton-Drager | Build a new 12.5 mile 69kV line. | ITCM | M2 - Appendix A Approved | 6978774 | 2022-12-31 | Line New | New Transmission line, new ROW - may include terminations | Scranton | Drager | 1 | 69 | 69 | 12.5 |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21991 | 21991-Scranton-Churdan REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 173700 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Scranton | Churdan REC Tap | 1 | 69 | 69 |  | 6.8 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21992 | 21992-Churdan REC Tap-Churdan REC | CIPCO will convert the 69kV tap to Churdan REC. | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Churdan REC Tap | Churdan REC | 1 | 69 | 69 |  | 3.13 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21993 | 21993-Churdan REC Tap-Farlin REC | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Churdan REC Tap | Farlin REC | 1 | 69 | 69 |  | 3.75 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21994 | 21994-Farlin REC-Jefferson WCC | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Farlin REC | Jefferson WCC | 1 | 69 | 69 |  | 4.78 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21995 | 21995-Hardin Hilltop Tap-Jefferson WCC | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Hardin Hilltop Tap | Jefferson WCC | 1 | 69 | 69 |  | 1.5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21996 | 21996-Hardin Hilltop-Hardin Hilltop Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Hardin Hilltop | Hardin Hilltop Tap | 1 | 69 | 69 |  | 0.7 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21997 | 21997-Grand Junction REC-Hardin Hilltop Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Grand Junction REC | Hardin Hilltop Tap | 1 | 69 | 69 |  | 7.3 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21998 | 21998-Grand Junction-Grand Junction REC | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 79500 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Grand Junction | Grand Junction REC | 1 | 69 | 69 |  | 0.02 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 21999 | 21999-Grand Junction (CIPCO)-Substation | CIPCO will add a 69kV terminal. | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Grand Junction (CIPCO) | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22000 | 22000-Drager (CBPC)-Substation | CBPC will add a 69kV terminal. | ITCM | M2 - Appendix A Approved | 0 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Drager (CBPC) | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22001 | 22001-Scranton-Switch Station | Add 69kV breaker at Scranton. | ITCM | M2 - Appendix A Approved | 389182 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Scranton | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22002 | 22002-Scranton Switch Station-Scranton Distribution | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2023-12-31 | Line Upgrade | Line conversion to higher voltage | Scranton Switch Station | Scranton Distribution | 1 | 69 | 69 |  | 0.9 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22003 | 22003-Scranton Distribution-Scranton REC | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2023-12-31 | Line Upgrade | Line conversion to higher voltage | Scranton Distribution | Scranton REC | 1 | 69 | 69 |  | 4 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22004 | 22004-Scranton REC-Railway | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2023-12-31 | Line Upgrade | Line conversion to higher voltage | Scranton REC | Railway | 1 | 69 | 69 |  | 12 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22005 | 22005-Railway-Substation | Add a 69kV breaker at Railway. | ITCM | M2 - Appendix A Approved | 344781 | 2023-12-31 | Substation | Substation (breakers only, no transformer) | Railway | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22006 | 22006-Railway-Substation | Add a 69kV breaker at Railway. | ITCM | M2 - Appendix A Approved | 273601 | 2024-12-31 | Substation | Substation (breakers only, no transformer) | Railway | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22007 | 22007-Railway-Bagley REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 83400 | 2024-12-31 | Line Upgrade | Line conversion to higher voltage | Railway | Bagley REC Tap | 1 | 69 | 69 |  | 2.5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22008 | 22008-Bagley REC Tap-Bagley REC | CIPCO will convert this line section to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2024-12-31 | Line Upgrade | Line conversion to higher voltage | Bagley REC Tap | Bagley REC | 1 | 69 | 69 |  | 3.5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22010 | 22010-Bagley REC Tap-Dawson | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 150600 | 2024-12-31 | Line Upgrade | Line conversion to higher voltage | Bagley REC Tap | Dawson | 1 | 69 | 69 |  | 10.5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22011 | 22011-Dawson-Substation | Build a new Dawson 69kV breaker station. | ITCM | M2 - Appendix A Approved | 2421247 | 2024-12-31 | Substation | Substation (breakers only, no transformer) | Dawson | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22012 | 22012-Dawson-Substation | Add 69kV breaker and relaying. | ITCM | M2 - Appendix A Approved | 1239560 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Dawson | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22013 | 22013-Dawson-Perry REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Dawson | Perry REC Tap | 1 | 69 | 69 |  | 3.62 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22014 | 22014-Perry REC Tap-Perry REC | CIPCO will convert this line section to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Perry REC Tap | Perry REC | 1 | 69 | 69 |  | 5 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22015 | 22015-Perry REC Tap-Berkley REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Perry REC Tap | Berkley REC Tap | 1 | 69 | 69 |  | 6.73 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22016 | 22016-Berkley REC Tap-Berkley REC | CIPCO will convert this line tap to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Berkley REC Tap | Berkley REC | 1 | 69 | 69 |  | 8.01 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22017 | 22017-Berkley REC Tap-Woodward REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Berkley REC Tap | Woodward REC Tap | 1 | 69 | 69 |  | 8.54 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22018 | 22018-Woodward REC Tap-Woodward REC | CIPCO will convert this line tap to 69kV operation. | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Woodward REC Tap | Woodward REC | 1 | 69 | 69 |  | 3.03 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22019 | 22019-Madrid North-Woodward REC Tap | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2025-12-31 | Line Upgrade | Line conversion to higher voltage | Madrid North | Woodward REC Tap | 1 | 69 | 69 |  | 5.14 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Other | 22021 | 22021-Madrid North-Substation | Add 69kV terminal and associated upgrades at the Madrid North sub. | ITCM | M2 - Appendix A Approved | 853225 | 2028-07-04 | Substation | Substation (breakers only, no transformer) | Madrid North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22022 | 22022-Fletcher-Garwin Road | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 600000 | 2021-12-31 | Line Upgrade | Line conversion to higher voltage | Fletcher | Garwin Road | 1 | 69 | 69 |  | 6.8 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22023 | 22023-Garwin Road-Conrad | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 600000 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Garwin Road | Conrad | 1 | 69 | 69 |  | 11.15 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22024 | 22024-Conrad-Union | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 240000 | 2022-12-31 | Line Upgrade | Line conversion to higher voltage | Conrad | Union | 1 | 69 | 69 |  | 12.65 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22025 | 22025-Conrad-Substation | New Conrad 69kV/distribution sub. | ITCM | M2 - Appendix A Approved | 1480393 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Conrad | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22026 | 22026-Marshalltown North-Substation | New Marshalltown North 69kV/distribution sub. | ITCM | M4 - Project in Service | 2028000 | 2018-12-06 | Substation | Substation (breakers only, no transformer) | Marshalltown North | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22027 | 22027-Fletcher-Marshalltown North | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Fletcher | Marshalltown North | 1 | 69 | 69 |  | 2.54 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22028 | 22028-East Nevada St-Marshalltown North | Convert this line section to 69kV operation (already built for 69kV). | ITCM | M4 - Project in Service | 302400 | 2018-03-16 | Line Upgrade | Line conversion to higher voltage | East Nevada St | Marshalltown North | 1 | 69 | 69 |  | 1.25 | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22029 | 22029-Fletcher-Transformer | Add a 2nd Fletcher 161/69kV 150 MVA transformer and associated equipment. | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Transformer | Transformer New | Fletcher | Transformer | 2 | 69 | 69 |  |  | IA |  | Not Shared
MTEP17 | A | ITC MIDWEST | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Other | 22030 | 22030-East Nevada St-Fletcher | Convert this line to 69kV operation (already built for 69kV). | ITCM | M4 - Project in Service | 302400 | 2018-11-09 | Line Upgrade | Line conversion to higher voltage | East Nevada St | Fletcher | 1 | 69 | 69 |  | 2.6 | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9910 | Fulda to Heron Lake 69 kV Rebuild | Other | 21318 | 21318-Fulda Junction-Heron Lake | Rebuild 69kV line from Fulda Junction to Heron Lake | ITCM | M2 - Appendix A Approved | 14976652 | 2028-12-31 | Line Upgrade | Line rebuild on existing ROW | Fulda Junction | Heron Lake | 1 | 69 | 69 |  | 20.14 | MN |  | Not Shared
MTEP16 | A | ITC | East | 9994 | Custer - Monroe 120 kV Line Rebuild | BRP | 27749 | 27749-Custer-Monroe | Rebuild the remaining 2.62 miles from structure 24317 to Monroe with new future double-circuit structures that are designed for either 1431 ACSR bundle or 2156 ACSS 84/19 conductor and install this with an OPGW path for the existing line only. A part of 2.62 mile rebuild, relocate approximately 1.8 miles of Monroe. The city has asked ITC to move the structures off the River Raisin National Battlefield to accommodate work they are doing on the battlefield and the visitor center. Relocate impacts structures (approximately) between structure 24322 and 24387. Pre-build it to 230kV FDC structures on south side of river, along Front Street, and to cross river and on north side. Continue to operate the existing line at 120 kV. Pre-build it to 230 kV construction and leave the vacant side for future circuit. Replace the existing 2000 A, 3 - way, full load break pole top switches with 3 new 3000 A, 1-way, full load break PTS to meet or exceed the summer emergency rating of 684 MVA/3291 A. | ITCT | M3 - Under Construction | 18100000 | 2026-12-31 | Line Upgrade | Line rebuild on existing ROW | Custer | Monroe |  | 120 |  |  |  | MI |  | Not Shared
MTEP16 | A | ITC | East | 9994 | Custer - Monroe 120 kV Line Rebuild | BRP | 27750 | 27750-Custer-Monroe | Rebuild 0.25 mile from Custer to structure 24317 with new underground future double circuit structures that are designed for 2500mm2 XLPE Parallel. Pre-build it to 230 kV construction and leave the vacant side for future circuit. Continue to operate the existing line at 120 kV. Pre-build it to 230 kV construction and leave the vacant side for future circuit. | ITCT | M4 - Project in Service | 15100000 | 2025-04-30 | Line New | New underground transmission line | Custer | Monroe |  | 120 |  |  |  | MI |  | Not Shared
MTEP16 | A | ITC | East | 9994 | Custer - Monroe 120 kV Line Rebuild | BRP | 27751 | 27751-Custer- | Replace equipment at HE pos at Custer | ITCT | M3 - Under Construction | 1480000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Custer |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP16 | A | ITC | East | 9994 | Custer - Monroe 120 kV Line Rebuild | BRP | 27752 | 27752-Monroe- | Replace equipment at GP pos at Monroe | ITCT | M3 - Under Construction | 1621000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Monroe |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP16 | A | ITC | East | 9994 | Custer - Monroe 120 kV Line Rebuild | BRP | 27753 | 27753-Monroe- | Replace equipment at GT pos at Monroe | ITCT | M3 - Under Construction | 1200000 | 2026-12-31 | Substation | Switching station (breakers only, no transformer) | Monroe |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21079 | 21079-New Hills area-Substation | Construct a new substation in the Hills area. | ITCM | M4 - Project in Service | 19029110 | 2021-04-07 | Substation | Substation (breakers only, no transformer) | New Hills area | Substation |  | 345 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21080 | 21080-New Hills area sub-Transformer | Install a new 345/161 kV 450 MVA transformer. | ITCM | M4 - Project in Service | 1 | 2021-04-02 | Transformer | Transformer New | New Hills area sub | Transformer | 1 | 345 | 161 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21081 | 21081-New Hills area-Transformer | CIPCO will install a new 161/69kV 150 MVA tranformer | ITCM | M4 - Project in Service | 1 | 2019-12-31 | Transformer | Transformer New | New Hills area | Transformer | 1 | 161 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21082 | 21082-ClearCreek-Switch Station | CIPCO will construct a new switch station | ITCM | M4 - Project in Service | 1 | 2019-12-31 | Substation | Switching station (breakers only, no transformer) | ClearCreek | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21084 | 21084-New Hills area-Clear Creek | New ITC owned 69 kv line double circuit with the new Hills area to North Liberty 161 kv line owned by CIPCO. | ITCM | M4 - Project in Service | 8678400 | 2022-10-31 | Line New | New Transmission line, new ROW - may include terminations | New Hills area | Clear Creek | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21087 | 21087-Swan Lake-Fairfax | New 161 kV line from CIPCO Swan Lake to ITCM Fairfax | ITCM | M2 - Appendix A Approved | 27788400 | 2027-12-01 | Line New | New Transmission line, new ROW - may include terminations | Swan Lake | Fairfax | 1 | 161 | 161 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21088 | 21088-Swan Lake - Squash Bend - Tharp | Double circuit 69 kV line from CIPCO Swan Lake to ITC MIdwest Squash Bend - Tharp 69 kV line | ITCM | M2 - Appendix A Approved | 6103750 | 2027-03-31 | Line New | New Transmission line, new ROW - may include terminations | Swan Lake | Tharp/Squash Bend | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21089 | 21089-Fairfax-Substation | Add a 161 kV terminal for the new North Liberty-Fairfax 161 kV line | ITCM | M2 - Appendix A Approved | 904828 | 2027-03-16 | Substation | Substation (breakers only, no transformer) | Fairfax | Substation |  | 161 | 161 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21090 | 21090-Homestead-Switch Station | New Homestead 69 kV switching station | ITCM | M2 - Appendix A Approved | 3979450 | 2030-06-05 | Substation | Switching station (breakers only, no transformer) | Homestead | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21091 | 21091-Conroy-Switch Station | New Conroy 69 kV switching station | ITCM | M2 - Appendix A Approved | 3979450 | 2030-06-05 | Substation | Switching station (breakers only, no transformer) | Conroy | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | BRP | 21092 | 21092-Conroy-Homestead | New CIPCO owned Conroy-Homestead 69 kV line | ITCM | M2 - Appendix A Approved | 1 | 2030-06-05 | Line New | New Transmission line, new ROW - may include terminations | Conroy | Homestead | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | NORTHERN STATES POWER COMPANY | West | 10076 | West St Cloud – Millwood Tap Rebuild | Other | 21535 | 21535-West St. Cloud-Milwood Tap | Rebuild 24 miles of line from West St. Cloud to Millwood Tap using 477 ACSR conductor. Rebuild 2 miles of line from St. John's tap to St. John's. | XEL | M2 - Appendix A Approved | 10400000 | 2026-05-15 | Line Upgrade | Line rebuild on existing ROW | West St. Cloud | Milwood Tap |  | 69 |  |  | 26 | MN |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 10022 | PCI-Mt.Vernon-Lisbon-76th AVE Conv | Other | 21434 | 21434-Lisbon North-Substation | Two (2) 69 kV breakers and associated equipment will be installed at the Lisbon North substation | ITCM | M4 - Project in Service | 598171 | 2022-12-31 | Substation | Substation (breakers only, no transformer) | Lisbon North | Substation | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 10022 | PCI-Mt.Vernon-Lisbon-76th AVE Conv | Other | 21435 | 21435-PCI-Substation | A 69 kV breaker and associated equipment will be installed at the PCI substation | ITCM | M2 - Appendix A Approved | 321361 | 2026-12-30 | Substation | Substation (breakers only, no transformer) | PCI | Substation | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 10022 | PCI-Mt.Vernon-Lisbon-76th AVE Conv | Other | 21436 | 21436-PCI-76th AVE (Eagle) | approximately 0.6 mile of new 69 kV transmission line will be constructed to complete the PCI to 76th Ave circuit | ITCM | M4 - Project in Service | 2037600 | 2022-12-31 | Line New | New Transmission line, new ROW - may include terminations | PCI | 76th AVE (Eagle) | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 10022 | PCI-Mt.Vernon-Lisbon-76th AVE Conv | Other | 21437 | 21437-76th AVE (Eagle)-Tharp | OPGW will need to be installed. | ITCM | M4 - Project in Service | 2175600 | 2020-12-03 | Line Upgrade | Line upgrade (increase clearance or other upgrade) not reconductor | 76th AVE (Eagle) | Tharp | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 10022 | PCI-Mt.Vernon-Lisbon-76th AVE Conv | Other | 21633 | 21633-PCI-Mt. Vernon | Convert to 69kV operation. | ITCM | M2 - Appendix A Approved | 661200 | 2026-12-30 | Line Upgrade | Line conversion to higher voltage | PCI | Mt. Vernon | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | LAFAYETTE UTILITIES SYSTEM | South | 8821 | Northeast to Peck | Other | 20746 | 20746-Northeast-Peck | 69kv line connecting Northeast station to Gilman/Peck stations via new SW 1478. | LAFA | M2 - Appendix A Approved | 3360000 | 2028-09-30 | Line New | New Transmission line, new ROW - may include terminations | Northeast | Peck |  | 69 |  |  |  | LA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21027 | 21027-Emerald Isle-Harrison | Convert Emerald Isle-Harrison line to 69 kV operation (already built for 69 kV) | ITCM | M2 - Appendix A Approved | 240000 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Emerald Isle | Harrison | 1 | 69 | 69 |  | 3.5 | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21028 | 21028-Emerald Isle-Substation | Add 69 kV terminal at Emerald Isle | ITCM | M2 - Appendix A Approved | 443671 | 2027-12-31 | Substation | Substation (breakers only, no transformer) | Emerald Isle | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21029 | 21029-Harrison-Taylor | Convert Harrison-Taylor line to 69 kv operation (already built for 69 kV) | ITCM | M2 - Appendix A Approved | 0 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Harrison | Taylor | 1 | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21030 | 21030-Taylor-Substation | New Taylor 69kV/distribution substation | ITCM | M2 - Appendix A Approved | 5590370 | 2027-12-31 | Substation | Distribution substation - may include trans high side | Taylor | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21032 | 21032-Taylor-Beverly | Convert the Beverly-Taylor line to 69kV operation | ITCM | M2 - Appendix A Approved | 1502754 | 2027-12-31 | Line Upgrade | Line conversion to higher voltage | Taylor | Beverly | 1 | 69 | 69 |  | 5.15 | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21033 | 21033-PCI-Beverly | Rebuild a portion of the PCI-Beverly line to double circuit 69 kV. | ITCM | M4 - Project in Service | 1466754 | 2021-05-28 | Line Upgrade | Line rebuild on existing ROW | PCI | Beverly | 1 | 69 | 69 |  | 1.2 | IA |  | Not Shared
MTEP16 | A | ITC MIDWEST | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Other | 21034 | 21034-Beverly-Substation | Add two new 69 kV line terminals and a 69 kV bus tie breaker at the Beverly substation. | ITCM | M2 - Appendix A Approved | 1461539 | 2028-02-28 | Substation | Substation (breakers only, no transformer) | Beverly | Substation |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | BIG RIVERS ELECTRIC CORPORATION | Central | 3435 | Rome Junction to West Owensboro 69 kV reconductor. | Other | 6338 | 6338-Rome Junction-West Owensboro | reconductor line | BREC | M2 - Appendix A Approved | 440000 | 2026-12-01 | Line Upgrade | Line reconductor | Rome Junction | West Owensboro | 1 | 69 |  | 0 | 5.8 | KY |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8150 | ITCM Belle Plaine Area Conversion | Other | 20534 | 20534-Belle Plaine-Substation | Add four 69kV breakers that are needed at Belle Plaine and add a 100MVA 161/69kV transformer. | ITCM | M2 - Appendix A Approved | 4891936 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | Belle Plaine | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8150 | ITCM Belle Plaine Area Conversion | Other | 20535 | 20535-Belle Plaine-Transformer | Add a 161/69kV 100MVA transformer at Belle Plaine | ITCM | M2 - Appendix A Approved | 0 | 2030-12-31 | Transformer | Transformer New | Belle Plaine | Transformer |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8150 | ITCM Belle Plaine Area Conversion | Other | 20536 | 20536-Belle Plaine South (River Valley)-Switch Station | Belle Plaine South (now named River Valley) Three (3) Terminal 69kV Switch Station | ITCM | M2 - Appendix A Approved | 3043446 | 2030-12-31 | Substation | Switching station (breakers only, no transformer) | Belle Plaine South (River Valley) | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8150 | ITCM Belle Plaine Area Conversion | Other | 20537 | 20537-Haven-Switch Station | Haven Three (3) Terminal 69kV Switch Station | ITCM | M2 - Appendix A Approved | 2987673 | 2030-12-31 | Substation | Switching station (breakers only, no transformer) | Haven | Switch Station |  | 69 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8151 | ITCM Belle Plaine-Vinton-Traer Conversion | Other | 20538 | 20538-Vinton-Substation | Two additional 69kV breakers are needed at the Vinton substation. | ITCM | M2 - Appendix A Approved | 1164487 | 2031-12-31 | Substation | Substation (breakers only, no transformer) | Vinton | Substation |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8151 | ITCM Belle Plaine-Vinton-Traer Conversion | Other | 20539 | 20539-Traer-Substation | One additional 69kV breaker is needed at the Traer substation. | ITCM | M2 - Appendix A Approved | 768124 | 2031-12-31 | Substation | Substation (breakers only, no transformer) | Traer | Substation |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8152 | ITCM Conroy-Parnell Conversion | Other | 20542 | 20542-Parnell-Substation | Three 69kV breakers are needed at the Parnell Substation. | ITCM | M2 - Appendix A Approved | 3812623 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | Parnell | Substation |  | 161 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8152 | ITCM Conroy-Parnell Conversion | Other | 20543 | 20543-Parnell-Transformer | A new 161/69kV 100MVA transformer is needed at the Parnell Substation. | ITCM | M2 - Appendix A Approved | 0 | 2030-12-31 | Transformer | Transformer New | Parnell | Transformer | 1 | 161 | 69 |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8153 | ITCM Parnell-Keswick Conversion | Other | 20544 | 20544-Keswick-Switch Station | Add a Keswick 3 terminal switch station | ITCM | M2 - Appendix A Approved | 2931083 | 2030-12-31 | Substation | Switching station (breakers only, no transformer) | Keswick | Switch Station |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8154 | ITCM Fairfax-Marengo Conversion | Other | 20545 | 20545-Fairfax-Substation | Two 69kV breakers are needed at the Fairfax Substation. | ITCM | M2 - Appendix A Approved | 1278863 | 2030-11-06 | Substation | Substation (breakers only, no transformer) | Fairfax | Substation |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8154 | ITCM Fairfax-Marengo Conversion | Other | 20546 | 20546-Marengo-Substation | Four 69kV breakers need to be installed at the Marengo Substation. | ITCM | M4 - Project in Service | 4198943 | 2017-05-19 | Substation | Substation (breakers only, no transformer) | Marengo | Substation |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8155 | ITCM Marshalltown-Tama-Laurel Conversion | Other | 20547 | 20547-Fletcher-Substation | One (1) 69kV Terminal at Fletcher Substation | ITCM | M2 - Appendix A Approved | 367444 | 2025-12-31 | Substation | Substation (breakers only, no transformer) | Fletcher | Substation |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8155 | ITCM Marshalltown-Tama-Laurel Conversion | Other | 20548 | 20548-Tama Paper-Switch Station | Three 69kV line breakers and one 69kV bus tie breaker are needed at the Tama Breaker Substation. | ITCM | M2 - Appendix A Approved | 3262754 | 2030-06-30 | Substation | Switching station (breakers only, no transformer) | Tama Paper | Switch Station |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8155 | ITCM Marshalltown-Tama-Laurel Conversion | Other | 20549 | 20549-Laurel-Switch Station | Three 69kV breakers and one 69kV bus tie breaker are needed at the Laurel switch station. | ITCM | M2 - Appendix A Approved | 2898200 | 2022-12-31 | Substation | Switching station (breakers only, no transformer) | Laurel | Switch Station |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | METC | East | 8072 | Riggsville to Port Calcite to Rockport 138 kV Rebuild | Other | 20394 | 20394-Riggsville-Port Calcite | Rebuild 45 miles of 336.4 ACSR strung on 138 kV single circuit wood poles installed in 1960. | METC | M3 - Under Construction | 90213143 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Riggsville | Port Calcite | 1 | 138 |  |  | 45 | MI |  | Not Shared
MTEP15 | A | METC | East | 8072 | Riggsville to Port Calcite to Rockport 138 kV Rebuild | Other | 20396 | 20396-Port Calcite-Rockport | Rebuild 24 miles of 266.8 ACSR strung on 138 kV single circuit wood poles installed in 1958. | METC | M4 - Project in Service | 33644721 | 2021-04-13 | Line Upgrade | Line rebuild on existing ROW | Port Calcite | Rockport | 1 | 138 |  |  | 24 | MI |  | Not Shared
MTEP15 | A | ITC | East | 8087 | Stratford 50 MVAR Capacitor Bank | BRP | 20411 | 20411-Stratford - Add Position HB Capacitor | Add a 50 MVAR capacitor bank along with a 120 kV, 3000 A, 40 kA, synchronous breaker at Stratford substation | ITCT | M2 - Appendix A Approved | 820000 | 2027-06-30 | Voltage Device | Capacitor (switched capacitor) | Stratford |  |  | 120 |  |  |  | MI |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8150 | ITCM Belle Plaine Area Conversion | Other | 20724 | 20724-34.5kV substation retirements- | Retire the 34.5kV substation equipment that is no longer needed. | ITCM | M2 - Appendix A Approved | 600000 | 2030-12-31 | Substation | Substation (breakers only, no transformer) | 34.5kV substation retirements |  |  | 35 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8155 | ITCM Marshalltown-Tama-Laurel Conversion | Other | 20726 | 20726-new switch stations- | Perform the 69kV line work for new switch stations for the conversion. | ITCM | M2 - Appendix A Approved | 600060 | 2025-12-31 | Line New | New Transmission line, new ROW - may include terminations | new switch stations |  |  | 69 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8154 | ITCM Fairfax-Marengo Conversion | Other | 20727 | 20727-various 34.5 kV subs- | retire 34.5kV subs | ITCM | M2 - Appendix A Approved | 180000 | 2028-12-31 | Substation | Substation (breakers only, no transformer) | various 34.5 kV subs |  |  | 35 |  |  |  | IA |  | Not Shared
MTEP15 | A | ITC MIDWEST | West | 8154 | ITCM Fairfax-Marengo Conversion | Other | 20728 | 20728-various 34.5kV-various 34.5kV | retire 34.5kV lines that are no longer needed | ITCM | M2 - Appendix A Approved | 974405 | 2030-12-24 | Line New | New Transmission line, new ROW - may include terminations | various 34.5kV | various 34.5kV |  | 35 |  |  |  | IA |  | Not Shared
MTEP15 | A | LAFAYETTE UTILITIES SYSTEM | South | 8820 | Northeast Station | Other | 20743 | 20743-Pont Des Mouton- | 230-69 autotransformer to feed new 69kv station | LAFA | M3 - Under Construction | 5500000 | 2027-11-01 | Transformer | Transformer New | Pont Des Mouton |  |  | 230 | 69 |  |  | LA |  | Not Shared
MTEP15 | A | LAFAYETTE UTILITIES SYSTEM | South | 8820 | Northeast Station | Other | 20744 | 20744-Pont Des Mouton-Northeast | New 69kv line from Pont Des Mouton to Northeast stations. | LAFA | M3 - Under Construction | 8000000 | 2027-11-01 | Line New | New Transmission line, new ROW - may include terminations | Pont Des Mouton | Northeast |  | 69 |  |  |  | LA |  | Not Shared
MTEP15 | A | LAFAYETTE UTILITIES SYSTEM | South | 8820 | Northeast Station | Other | 20745 | 20745-Northeast- | Station to alleviate distribution loading. | LAFA | M3 - Under Construction | 4250000 | 2027-11-01 | Substation | Substation (breakers only, no transformer) | Northeast |  |  | 69 |  |  |  | LA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8903 | 8903-North English-South English | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 2385000 | 2015-08-17 | Line New | New Transmission line, new ROW - may include terminations | North English | South English | 1 | 34 |  |  | 5.3 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8907 | 8907-Koszta REC Tap-Belle Plaine Jct | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 2565000 | 2018-09-03 | Line New | New Transmission line, new ROW - may include terminations | Koszta REC Tap | Belle Plaine Jct | 1 | 34 |  |  | 5.7 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8908 | 8908-Willaimsburg South-Parnell | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 6750000 | 2018-11-02 | Line New | New Transmission line, new ROW - may include terminations | Willaimsburg South | Parnell | 1 | 34 |  |  | 15 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8909 | 8909-Belle Plaine Jct-City of Belle Plaine | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 2160000 | 2018-01-31 | Line New | New Transmission line, new ROW - may include terminations | Belle Plaine Jct | City of Belle Plaine | 1 | 34 |  |  | 4.8 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8911 | 8911-Belle Plaine Jct-Vining REC Tap | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 5706000 | 2021-11-05 | Line New | New Transmission line, new ROW - may include terminations | Belle Plaine Jct | Vining REC Tap | 1 | 34 |  |  | 12.68 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8912 | 8912-Vining REC Tap-Tama East | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 7505760 | 2018-08-23 | Line New | New Transmission line, new ROW - may include terminations | Vining REC Tap | Tama East | 1 | 34 |  |  | 10.63 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8913 | 8913-Ferguson-Timber Creek Tap | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 1687500 | 2019-05-17 | Line New | New Transmission line, new ROW - may include terminations | Ferguson | Timber Creek Tap | 1 | 34 |  |  | 3.75 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8914 | 8914-Sutherland-LeGrand | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 5366227 | 2019-11-15 | Line New | New Transmission line, new ROW - may include terminations | Sutherland | LeGrand | 1 | 34 |  |  | 6.27 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8915 | 8915-Traer-Dysart | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 3726000 | 2021-08-23 | Line New | New Transmission line, new ROW - may include terminations | Traer | Dysart | 1 | 34 |  |  | 8.28 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8916 | 8916-Ferguson REC Tap-Gilman Tap | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 1687500 | 2019-04-08 | Line New | New Transmission line, new ROW - may include terminations | Ferguson REC Tap | Gilman Tap | 1 | 34 |  |  | 3.75 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8917 | 8917-Hills-Frytown | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 4986000 | 2019-08-05 | Line New | New Transmission line, new ROW - may include terminations | Hills | Frytown | 1 | 34 |  |  | 11.08 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8918 | 8918-Frytown Tap-Kalona South Tap | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M4 - Project in Service | 2709000 | 2018-12-21 | Line New | New Transmission line, new ROW - may include terminations | Frytown Tap | Kalona South Tap | 1 | 34 |  |  | 6.02 | IA |  | Not Shared
MTEP14 | A | ITC MIDWEST | West | 4704 | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | Other | 8919 | 8919-Kalona South Tap-Iowa Jct | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | ITCM | M2 - Appendix A Approved | 2212000 | 2020-06-30 | Line New | New Transmission line, new ROW - may include terminations | Kalona South Tap | Iowa Jct | 1 | 34 |  |  | 4.92 | IA |  | Not Shared
MTEP14 | A | DUKE ENERGY INDIANA, LLC | Central | 4415 | Veedersburg West 230-69kv Bk 2 addition | Other | 8434 | 8434-Veedersburg West-xmr addition | Veedersburg West: Add 75MVA 230/69 Bk 2 with LTC at Veedersburg West sub; add breaker to 69kV ring bus and tie in new bank; convert 230kV bus into 4-breaker ring | DEI | M3 - Under Construction | 15262408 | 2026-05-26 | Transformer | Transformer New | Veedersburg West | xmr addition |  | 230 | 69 |  |  | IN |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4099 | Albert Lea Westside-South Broadway 69kV Rebuild | Other | 7763 | 7763-Albert Lea Westside-South Broadway | Rebuild the Albert Lea Westside-South Broadway 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 840000 | 2026-12-31 | Line New | New Transmission line, new ROW - may include terminations | Albert Lea Westside | South Broadway | 1 | 69 | 69 |  | 2 | MN |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4102 | Columbus Jct-Newport 69kV Rebuild | Other | 7767 | 7767-Newport-Cairo REC | Rebuild the Newport-Cairo REC 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 6242696 | 2027-07-29 | Line New | New Transmission line, new ROW - may include terminations | Newport | Cairo REC | 1 | 69 | 69 |  | 8.65 | IA |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4102 | Columbus Jct-Newport 69kV Rebuild | Other | 7768 | 7768-Cairo REC-Winfield Tap | Rebuild the Cairo REC-Winfield Tap 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 1991889 | 2027-07-29 | Line New | New Transmission line, new ROW - may include terminations | Cairo REC | Winfield Tap | 1 | 69 | 69 |  | 2.76 | IA |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4102 | Columbus Jct-Newport 69kV Rebuild | Other | 7769 | 7769-Winfield Tap-IBP Tap | Rebuild the Winfield Tap-IBP Tap 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 5492130 | 2027-07-29 | Line New | New Transmission line, new ROW - may include terminations | Winfield Tap | IBP Tap | 1 | 69 | 69 |  | 7.61 | IA |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4102 | Columbus Jct-Newport 69kV Rebuild | Other | 7770 | 7770-IBP Tap-Columbus Jct | Rebuild the IBP Tap-Columbus Jct 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 72170 | 2027-07-29 | Line New | New Transmission line, new ROW - may include terminations | IBP Tap | Columbus Jct | 1 | 69 | 69 |  | 0.1 | IA |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4105 | Decorah-Waukon 69kV Rebuild | Other | 7775 | 7775-Decorah-Ludlow Tap | Rebuild the Decorah-Ludlow Tap 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 8600000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Decorah | Ludlow Tap | 1 | 69 | 69 |  | 20.48 | IA |  | Not Shared
MTEP13 | A | ITC MIDWEST | West | 4105 | Decorah-Waukon 69kV Rebuild | Other | 7776 | 7776-Ludlow Tap-Waukon - IPL | Rebuild the Ludlow Tap-Waukon 69kV to T2-4/0. | ITCM | M2 - Appendix A Approved | 1060000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Ludlow Tap | Waukon - IPL | 1 | 69 | 69 |  | 2.51 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7108 | 7108-Marion Tap-County Home REC Tap | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 1050000 | 2013-06-10 | Line New | New Transmission line, new ROW - may include terminations | Marion Tap | County Home REC Tap | 1 | 34 |  | 1.5 | 1.5 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7109 | 7109-Coggon-Manchester Industrial | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 0 | 2018-06-04 | Line New | New Transmission line, new ROW - may include terminations | Coggon | Manchester Industrial | 1 | 34 |  | 2.5 |  | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7110 | 7110-Rome Tap-Rome | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 5898850 | 2024-03-19 | Line New | New Transmission line, new ROW - may include terminations | Rome Tap | Rome | 1 | 34 |  | 2 |  | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7111 | 7111-Clarence-Clarence REC | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 1627555 | 2023-03-09 | Line New | New Transmission line, new ROW - may include terminations | Clarence | Clarence REC | 1 | 34 |  | 2 |  | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7112 | 7112-Manchester Tap-Manchester Industrial | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 1001400 | 2018-06-04 | Line New | New Transmission line, new ROW - may include terminations | Manchester Tap | Manchester Industrial | 1 | 34 |  | 0.5 |  | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7113 | 7113-Mt Vernon-Lisbon | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 3358200 | 2018-10-19 | Line New | New Transmission line, new ROW - may include terminations | Mt Vernon | Lisbon | 1 | 34 |  | 2 | 2 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7114 | 7114-PCI-Putnam | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M2 - Appendix A Approved | 175000 | 2026-09-22 | Line New | New Transmission line, new ROW - may include terminations | PCI | Putnam | 1 | 34 |  | 0.5 |  | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7115 | 7115-Zwingle-Mosalem REC | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 0 | 2015-12-31 | Line New | New Transmission line, new ROW - may include terminations | Zwingle | Mosalem REC | 1 | 34 |  | 8 |  | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 7116 | 7116-Dixon-Fulton | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M2 - Appendix A Approved | 10890000 | 2029-12-18 | Line New | New Transmission line, new ROW - may include terminations | Dixon | Fulton | 1 | 34 |  |  | 17 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3630 | Adams to Stewartville 69 kV Rebuild | Other | 6739 | 6739-Adams-Stewartvillle 6th Street | Rebuild 69kV line to T2-4/0 ACSR | ITCM | M2 - Appendix A Approved | 10500000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Adams | Stewartvillle 6th Street | 1 | 69 |  |  | 29.88 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3630 | Adams to Stewartville 69 kV Rebuild | Other | 6740 | 6740-Stewartvillle 6th Street-Stewartville Junction | Rebuild 69kV line to T2-4/0 ACSR | ITCM | M2 - Appendix A Approved | 1700000 | 2028-12-31 | Line New | New Transmission line, new ROW - may include terminations | Stewartvillle 6th Street | Stewartville Junction | 1 | 69 |  |  | 4.68 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3644 | Knoxville to Lucas County 69 kV Rebuild | Other | 6766 | 6766-Knoxville-Lucas | Rebuild the 69kV line section | ITCM | M2 - Appendix A Approved | 3750000 | 2029-12-31 | Line New | New Transmission line, new ROW - may include terminations | Knoxville | Lucas | 1 | 69 |  |  | 10.6 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3645 | Triboji 6750 (Oleans Tap) 69 kV Rebuild | Other | 6767 | 6767-Triboji-Montgomery | Rebuild the 69kV line section | ITCM | M2 - Appendix A Approved | 2000000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Triboji | Montgomery | 1 | 69 |  |  | 5.75 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3645 | Triboji 6750 (Oleans Tap) 69 kV Rebuild | Other | 6768 | 6768-Bosworth-Montgomery | Rebuild the 69kV line section | ITCM | M2 - Appendix A Approved | 750000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Bosworth | Montgomery | 1 | 69 |  |  | 2.16 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3645 | Triboji 6750 (Oleans Tap) 69 kV Rebuild | Other | 6769 | 6769-Bosworth-Spirti Lake | Rebuild the 69kV line section | ITCM | M2 - Appendix A Approved | 400000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Bosworth | Spirti Lake | 1 | 69 |  |  | 1.17 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3645 | Triboji 6750 (Oleans Tap) 69 kV Rebuild | Other | 6770 | 6770-Spirti Lake-Orleans Tap | Rebuild the 69kV line section | ITCM | M2 - Appendix A Approved | 200000 | 2027-12-31 | Line New | New Transmission line, new ROW - may include terminations | Spirti Lake | Orleans Tap | 1 | 69 |  |  | 0.4 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6808 | 6808-Coggon Muni-Central City | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 2100000 | 2013-09-09 | Line New | New Transmission line, new ROW - may include terminations | Coggon Muni | Central City | 1 | 34 |  |  | 6 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6809 | 6809-Hopkinton-Hopkinton Tap | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 1050000 | 2014-08-01 | Line New | New Transmission line, new ROW - may include terminations | Hopkinton | Hopkinton Tap | 1 | 34 |  |  | 2 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6810 | 6810-Ely REC- | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 1750000 | 2013-06-10 | Line New | New Transmission line, new ROW - may include terminations | Ely REC |  | 1 | 34 |  |  | 5 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6811 | 6811-Bertram JU-Mt Vernon | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 4900000 | 2013-09-27 | Line New | New Transmission line, new ROW - may include terminations | Bertram JU | Mt Vernon | 1 | 34 |  |  | 14 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6812 | 6812-Ryan REC-Ryan REC tap | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 886800 | 2018-04-30 | Line New | New Transmission line, new ROW - may include terminations | Ryan REC | Ryan REC tap | 1 | 34 |  |  | 1 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6813 | 6813-Cascade Muni-Cascade Muni Tap | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 0 | 2017-12-31 | Line New | New Transmission line, new ROW - may include terminations | Cascade Muni | Cascade Muni Tap | 1 | 34 |  |  | 1 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6814 | 6814-Clarence-Clarence Tap | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M2 - Appendix A Approved | 389000 | 2025-06-30 | Line New | New Transmission line, new ROW - may include terminations | Clarence | Clarence Tap | 1 | 34 |  |  | 1 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6815 | 6815-Clarence-Wyoming | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 4881061 | 2020-02-03 | Line New | New Transmission line, new ROW - may include terminations | Clarence | Wyoming | 1 | 34 |  |  | 11 | IA |  | Not Shared
MTEP12 | A | ITC MIDWEST | West | 3647 | Eastern Iowa Project Rebuilds | Other | 6816 | 6816-Prairie Creek-Bertam JU | Rebuild the 34kV line section to 69kV for future conversion | ITCM | M4 - Project in Service | 3880200 | 2019-03-18 | Line New | New Transmission line, new ROW - may include terminations | Prairie Creek | Bertam JU | 1 | 34 |  |  | 6 | IA |  | Not Shared
MTEP10 | A | GREAT RIVER ENERGY | West | 2577 | Columbus (CE) 69 kV Substation | Other | 4588 | 4588-Columbus-Columbus Tap | New Distribution | GRE | M2 - Appendix A Approved | 1000065 | 2028-10-02 | Substation | Substation (breakers only, no transformer) | Columbus | Columbus Tap | 1 | 69 |  | 0 |  | MN |  | Not Shared
MTEP10 | A | GREAT RIVER ENERGY | West | 2579 | Foster Lake (WH) 69 kV Substation | Other | 4590 | 4590-Foster Lake-Foster Lake Tap | New Distribution | GRE | M2 - Appendix A Approved | 533240 | 2027-11-01 | Substation | Substation (breakers only, no transformer) | Foster Lake | Foster Lake Tap | 1 | 69 |  | 0 |  | MN |  | Not Shared
MTEP10 | A | NORTHWESTERN WISCONSIN ELECTRIC CO. | West | 3092 | Webb Lake 69KV line | Other | 5410 | 5410-Lake 26-Webb Lake | Rebuild 34.5KV line to Webb Lake at 69KV with horizontal post construction and #4/0 ACSR | NWEC | M2 - Appendix A Approved | 650000 | 2026-06-01 | Line Upgrade | Line rebuild on existing ROW | Lake 26 | Webb Lake |  | 69 |  | 0 | 2.6 | WI |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3048 | Jefferson Co-Perlee 69kV Rebuild | Other | 5266 | 5266-Jefferson Co-Perlee | Rebuild Jefferson Co-Perlee line | ITCM | M2 - Appendix A Approved | 2700000 | 2027-07-21 | Line New | New Transmission line, new ROW - may include terminations | Jefferson Co | Perlee | 1 | 69 | 69 | 0 | 7.38 | IA |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3057 | West Branch 34kV Load Shift Projects | Other | 5303 | 5303-Moscow Tap-Magmet T | Tap the Muscatine Switch Station to Magmet T69kV line for new tap to Moscow. | ITCM | M2 - Appendix A Approved | 0 | 2021-12-01 | Line New | New Transmission line, new ROW - may include terminations | Moscow Tap | Magmet T | 1 | 69 | 69 | 0 | 0 | IA |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3057 | West Branch 34kV Load Shift Projects | Other | 5304 | 5304-New Liberty-New Liberty Tap | Build a new 2 mile 69kV tap to New Liberty & retire 9.4 mile 34kV tap. | ITCM | M2 - Appendix A Approved | 714000 | 2023-12-31 | Line New | New Transmission line, new ROW - may include terminations | New Liberty | New Liberty Tap | 1 | 69 | 69 | 2 | 0 | IA |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3057 | West Branch 34kV Load Shift Projects | Other | 5305 | 5305-Bennett-New Liberty Tap | Tap the Bennett Switch Station to Dixon Jct 69kV line for a new 69kV tap to New Liberty. | ITCM | M2 - Appendix A Approved | 0 | 2023-12-31 | Line New | New Transmission line, new ROW - may include terminations | Bennett | New Liberty Tap | 1 | 69 | 69 | 0 | 0 | IA |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3057 | West Branch 34kV Load Shift Projects | Other | 5306 | 5306-New Liberty Tap-Dixon Jct | Tap the Bennett Switch Station to Dixon Jct 69kV line for a new 69kV tap to New Liberty. | ITCM | M2 - Appendix A Approved | 0 | 2023-12-31 | Line New | New Transmission line, new ROW - may include terminations | New Liberty Tap | Dixon Jct | 1 | 69 | 69 | 0 | 0 | IA |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3057 | West Branch 34kV Load Shift Projects | Other | 6418 | 6418-Moscow Tap-Moscow | Retire the Moscow 34kV 7 mile tap | ITCM | M2 - Appendix A Approved | 210000 | 2022-12-30 | Line New | New Transmission line, new ROW - may include terminations | Moscow Tap | Moscow | 1 | 34 | 34 |  |  | IA |  | Not Shared
MTEP10 | A | ITC MIDWEST | West | 3057 | West Branch 34kV Load Shift Projects | Other | 6419 | 6419-New Liberty-New Liberty Tap | Retire the New Liberty 34kV 9.4 mile tap | ITCM | M2 - Appendix A Approved | 282000 | 2027-12-28 | Line New | New Transmission line, new ROW - may include terminations | New Liberty | New Liberty Tap | 1 | 34 | 34 |  |  | IA |  | Not Shared

## hiddenSheet (hidden)
miso_projectfacilitydetail:bpiq1v2O1shm2NlpPfGHkOHKuHJDWOFipBB2dhthoI5L4120cxR9KV6QOyxmEW0NrJe9dTwzDD4HH8hhvUmnsQ==:miso_projectfacilitydetailid=%28Do%20Not%20Modify%29%20Project%20Facility%20Detail&checksumLogicalName=%28Do%20Not%20Modify%29%20Row%20Checksum&modifiedon=%28Do%20Not%20Modify%29%20Modified%20On&8a12c61e-0c71-4e6a-b1a6-a02e2d11068f.miso_targetmtepcycleid=Target%20MTEP%20Cycle%20%28Project%29%20%28Project%29&8a12c61e-0c71-4e6a-b1a6-a02e2d11068f.miso_currentappendixcode=Current%20Appendix%20%28Project%29%20%28Project%29&miso_submittingtoid=Submitting%20TO&miso_planningregioncode=Planning%20Region&8a12c61e-0c71-4e6a-b1a6-a02e2d11068f.miso_mtepprojectid=MTEP%20Project%20ID%20%28Project%29%20%28Project%29&miso_projectid=Project&8a12c61e-0c71-4e6a-b1a6-a02e2d11068f.miso_projecttypeid=Project%20Type%20%28Project%29%20%28Project%29&miso_facilityid=Facility%20ID&miso_name=Name&miso_facilitydescription=Facility%20Description&miso_facilityowners=Facility%20Owner%28s%29&miso_planningstatusid=Planning%20Status&miso_currentcost=Current%20Cost&miso_expectedisd2date=Expected%20ISD&miso_facilitytypeid=Facility%20Type&miso_facilitysubtypeid=Facility%20Sub-Type&miso_fromsub=From%20Sub&miso_tosub=To%20Sub&miso_circuitid=Circuit%20ID&miso_maxkv=Max%20kV&miso_minkv=Min%20kV&miso_milesnew=Miles%20New&miso_milesupgrade=Miles%20Upgrade&miso_state1id=State%201&miso_state2id=State%202&miso_costsharedcode=Cost%20Shared%20Status
A | B
Central | East | South | West
Not Shared | Shared