## Prj Legend
MTEP Database Export
Project Table Field Legend
Appendix A contains Transmission projects which are being or have been approved by MISO Board of Directors.
Transmission Owners are obligated to make a good faith effort to construct projects in Appendix A.
Appendix B Transmission projects have been reviewed by MISO staff for need and effectivenes.
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Project Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEPyy planning cycle. Example: "A in MTEP15" projects were reviewed in MTEP15. .
App AB | Appendix the project is in. B>A for projects moving during current planning cycle.
Region | MISO Planning Region: Central, East, West or South
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Project ID: MISO project identifier
Project Name | Project name (short name)
Project Description | A description of the project's components
State 1 | State project is located or first state if in multiple states
State 2 | If applicable, the second state the project is located
Allocation Type per FF | Project Type per Attachment FF of Tariff. BaseRel is Baseline Reliability, GIP is Generator Interconnection Project, TDSP is Transmission Delivery Service Project, MEP is Market Efficiency Project, MVP is Multi Value Project, Other is none of the above. Preliminary project allocation types may be designated for projects in Appendix B
Share Status | Cost allocation status for projects in Appendix A or moving to Appendix A in current planning cycle. Projects are Shared, Not Shared or Excluded. Preliminary sharing designations may be input for Appendix B projects
Other Type | Indicates the project driver behind Other type projects.
Estimated Cost | Total estimated project cost from Facility table
Expected ISD (Min/Max) | Dates when project is expected to be in service. Min and Max dates. Expected ISD are in Facility table.
Max kV | Maximum facility voltage in project. Summary information from Facility table
Min kV | Minimum facility voltage in project. Summary information form Facility table
Transmission Project Type | Bottom-Up, Top-Down or Externally Driven per BPM-020 r12 section 2.3

## MTEP18_AppAB_Projects
MTEP18 MISO Transmission Expansion Plan 2018 (All projects contain transmission facilities only and no distribution facilities are included) | [18 empty] | Appendices A, B
Appendices A, B: Project Table 12/07/2018
Target Appendix | App ABC | Planning Region | Geographic Location by TO Member System | PrjId | Prj_Rec_Date | Owner_PrjID | Project Name | Project Description | State1 | State2 | Allocation Type per FF | Share Status | Other Type | Estimated Cost | Expected ISD (Min) | Expected ISD (Max) | Max kV | Min kV | Transmission Project Category
A in MTEP18 | A | South | AECC | 10203 | 2018-08-22 |  | Shaw to Sardis 115kV | 15.00 mile 115kV line from the AECC Shaw substation to the proposed AECC Vimy Ridge switching station (near the Sardis substation) tie into a proposed 115kV ring bus at the Sardis substation | AR | AR | Other |  | Reliability |  | 2023-06-01 | 2023-12-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | South | AECC | 13993 | 2018-08-06 |  | Tap EAI Harrison East - Osage Creek: Construct Dry Creek 161 kV switching station | AECC will construct the new Dry Creek 161 kV switching station on the Entergy Harrison East to Osage Creek 161 kV transmission line. Entergy's interconnection requirements will likely require the switching station to be a 4 breaker ring bus. From the point of interconnection, Carroll Electric Cooperative Corporation (AECC's member), will construct two new 161 kV transmission lines. The first 161 kV transmission line will head north approximately 16 miles and tie into the existing Osage Creek 69 kV system via the new Long Creek 161/69 kV substation to be constructed by AECC. The second 161 kV transmission line will head south approximately 30 miles and tie into the existing Osage Creek 69 kV system via the new Smyrna 161/69 kV substation to be constructed by AECC. | MO | AR | Other |  | Reliability | 12000000 | 2020-12-31 | 2023-02-01 | 161 | 0 | Bottom-up
A in MTEP18 | A | South | AECC | 14384 | 2018-08-22 |  | Brazil Road | 115/13.2kV 20MVA distribution substation on Entergy's River Ridge to Cheetah 115kV line | AR | AR | Other |  | Load Growth | 3000000 | 2020-04-01 | 2020-04-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | South | AECC | 14444 | 2018-08-22 |  | Zion Hill to Mountain Springs Line Conversion | Convert Zion Hill to Mountain Springs 69kV line to 115kV | AR | AR | Other |  | Reliability | 4900000 | 2023-12-01 | 2023-12-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | South | AECC | 14445 | 2018-08-22 |  | Mountain Springs to Ward Line Conversion | Convert Mountain Springs to Ward 69kV line to 115kV | AR | AR | Other |  | Reliability | 3450000 | 2023-12-01 | 2023-12-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | South | AECC | 14446 | 2018-08-22 |  | Sardis South 115/13.2kV substation | 115/13.2kV substation on the proposed Mabelvale South to Shaw 115kV line | AR | AR | Other |  | Load Growth | 2500000 | 2023-06-01 | 2023-06-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | Central | AmerenIL | 3033 | 2018-10-03 | AMRN18 | New Beehive 345/138 kV substation (Dupo Area) | Build a new Beehive 345/138 kV substation including a 345 kV ring bus and a 138 kV Breaker and a Half (BAAH) bus arrangement with the initial transmission supply from the existing C-BLWN-4511 345 kV line (in and out). Install two 345/138 kV 700 MVA transformers at Beehive substation with outlet transmission to the existing Cahokia – Meramec – 1 & 2 138 kV lines (in and out) of Beehive substation. Re-conductor/Rebuild the Mississippi river crossing and Beehive – Watson – 1351 138 kV line and Beehive – Mackenzie section of Beehive – Lakeshire – 1468 138 kV line with conductor having a minimum summer emergency capability of 2000 Amps. | IL | IL | Other |  | Reliability | 0 | 2022-12-01 | 2022-12-01 | 345 | 138 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 4068 | 2017-12-13 |  | Reconductor South Bloomington-Clinton Rt. 54 138 kV line (1372) | Replace 23.0 miles of 336ACSR between S Bloomington and Clinton Rt54 with conductor capable of carrying 1200A under SE conditions. Add new double circuit line from Tabor (N. Clinton) to Clinton Rte. 54. | IL | IL | BaseRel |  |  | 28800000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 4069 | 2017-12-04 |  | Rebuild Stalllings 138 kV substation w/ ten breaker positions | Re-configure the existing Stallings Substation to accommodate an initial 7-position Breaker-and-a-half arrangement with an ultimate of 10 positions. | IL | IL | Other | Not Shared | Reliability | 18600000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 11954 | 2017-10-27 |  | New Tabor 138 kV breaker station (Formerly New North Clinton) | Establish 138 kV ring bus | IL | IL | Other |  | Reliability | 8100000 | 2018-05-11 | 2018-05-11 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13544 | 2017-08-28 |  | New Tibbs 138 kV breaker substation | Construct an initial 3-position (ultimate 4-position) ring bus at the Sparta Tap in the Prest-Steeleville-1476 138 kV line. Ring bus to have a minimum of 2000A continuous current carrying capability. | IL | IL | Other |  | Reliability | 7300000 | 2021-12-01 | 2021-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13546 | 2018-10-03 |  | New County Highway 20 138 kV breaker station | Construct a 3-position (ultimate 4-position) ring bus at the existing County Highway 20 Substation location in the N. Decatur-Clinton Rt. 54-1313 138 kV line. Ring bus to be rated for a minimum of 2000A continuous current carrying capability. | IL | IL | Other |  | Reliability | 8900000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13548 | 2018-10-03 |  | Reconfigure McLean County 138 kV Switching Station | Re-configure the McLean County 138 kV Switching Station to accommodate an initial 3-position (ultimate 4-position) ring bus. Ring bus should be capable of 3000A continuous current operation. | IL | IL | Other |  | Reliability | 10000000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13549 | 2017-09-06 |  | Rebuild Benton NW-Ina-1 and Benton NW-W. Frankfort-1 to 2000 A | Rebuild the Benton NW-Ina-1 and Benton NW-W. Frankfort-1 138 kV circuits using conductor capable of 2000A under summer emergency conditions. Install OPGW. | IL | IL | Other |  | Age and Condition | 14000000 | 2017-12-07 | 2017-12-07 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13550 | 2017-08-28 |  | New ADM North 138 kV Capacitor Bank | Upgrade the existing 50 Mvar 138 kV capacitor bank in the ADM North Substation to a 120 Mvar capacitor bank. Remove the existing 14.4 Mvar and 18.0 Mvar capacitor banks presently installed in the Faries Parkway Substation on the 34.5 kV bus. | IL | IL | Other |  | Reliability | 600000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13551 | 2018-08-24 |  | New Shockey 138 kV breaker substation | Construct a 5-position (Ultimate 6-position) 138 kV ring bus breaker station at structure 380 of the San Jose-Rail-Interstate-1318 138 kV line to tie the Havana-East Springfield-1422 and the the San Jose Rail-Interstate-1318 138 kV lines together. A minimum 2000A continuous currently carrying capability is required for the ring bus. | IL | IL | Other |  | Reliability | 13100000 | 2022-12-01 | 2022-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13564 | 2018-08-24 |  | New Docket 138 kV breaker station | Construct a 3-position (ultimate 4-position) 138 kV ring bus breaker station near structure 423 on the N. Dectur-Latham-1342 138 kV line. Ring bus to have minimum 2000A current carrying capability. | IL | IL | Other |  | Reliability | 7200000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13565 | 2018-01-08 |  | Replace Mount Vernon West 345/138 kV transformer No. 4 | Replace the 345-138 kV 450 MVA transformer #4 at Mount Vernon West Substation with a 560 MVA unit. | IL | IL | Other |  | Age and Condition | 4300000 | 2018-12-01 | 2018-12-01 | 345 | 138 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13566 | 2017-09-14 |  | Rebuild Ina-Mt. Vernon 42nd Street line 1332 to 2000 A | Rebuild the INA-MTVS-1322 138 kV line from Ina to Mt. Vernon 42nd Street using conductor capable of 2000A under summer emergency conditions. Install OPGW. | IL | IL | Other |  | Age and Condition | 8800000 | 2018-05-05 | 2018-05-05 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13567 | 2017-08-30 |  | Increase Havana-East Springfield 138 kV line 1422 clearance | Upgrade the clearance from 93°C to 120°C on the 138 kV HAV-SPFL-1422A line from Elkhart Switching Station to Turris Coal Tap. | IL | IL | Other |  | Age and Condition | 1900000 | 2017-12-12 | 2017-12-12 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13569 | 2018-10-03 |  | New Roodhouse West 138 kV Substation | Re-configure the existing Roodhouse West Substation to accommodate an initial 3-position ring bus with an ultimate of 6 positions. | IL | IL | Other |  | Reliability | 7800000 | 2021-12-01 | 2021-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13570 | 2018-01-08 |  | Reconductor Cahokia-Baldwin 345 kV line | In the Cahokia-Baldwin 345 kV line 4511, reconductor 0.83 miles of 1113 kcmil ACSR/T2 Finch conductor from structures 148 to 153 with conductor capable of carrying 3000 A under summer emergency conditions. | IL | IL | Other |  | Reliability | 1100000 | 2019-10-01 | 2019-10-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13571 | 2018-10-03 |  | New South Clinton 138 kV Substation | Construct a 138 kV, 6-position Ring Bus at the current site of the South Clinton Tap utilizing bus conductors of at least 3000 Amps continuous capability. Install 4 new breakers, and associated switches of at least 3000 Amps continuous capability. Install 3 motorized line disconnect switches of at least 2000 Amps continuous capability. Install 1 circuit switcher for high-side transformer protection of at least 2000 Amps continuous capability and 40k Amps fault interrupting capability. | IL | IL | Other |  | Reliability | 6700000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13585 | 2018-10-03 |  | New Gillett 138 kV breaker substation | Install new 3-position (ultimate 4-position) ring bus at tap to Turris Coal. | IL | IL | Other |  | Reliability | 8100000 | 2023-12-01 | 2023-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13619 | 2018-10-03 |  | New Ruby 345 kV breaker substation | Construct a 3-position initial (6-position ultimate), 3000 A 345 kV switching station in a ring bus configuration at structure 100 in the Kansas-Sidney 345 kV line 4560 for the interconnection of Broadlands Wind Farm. | IL | IL | GIP | Shared |  | 8425441 | 2019-10-01 | 2019-10-01 | 345 | 0 | Externally Driven
A in MTEP18 | A | Central | AmerenIL | 13664 | 2017-09-06 |  | Reconductor Pana North-Moeaqua 138 kV line 1462 | In Pana – Route 51 Decatur 138 kV line 1462, rebuild the backbone (Pana North to the Moweaqua tap), from 1272 kcmil ACSR to conductor capable of carrying 2000 A under summer emergency conditions. | IL | IL | Other |  | Age and Condition | 7800000 | 2017-12-05 | 2017-12-05 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13665 | 2017-09-12 |  | New Tazewell 120 Mvar capicitor bank | Install 120 Mvar 138 kV Cap Bank at Tazewell Substation | IL | IL | Other |  | Reliability | 3800000 | 2019-11-15 | 2019-11-15 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13666 | 2018-10-03 |  | Replace Sidney 345/138 kV Transformer No. 1 | Replace transformer #1 345-138 kV 560 MVA due to age and condition. | IL | IL | Other |  | Age and Condition | 4800000 | 2019-06-01 | 2019-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13668 | 2017-09-12 |  | Reconductor Crab Orchard-Herrin East 138 kV line | Upgrade the section of Crab Orchard-Herrin East-1 going from Crab Orchard to Marion North from 100C MOT to 110C. | IL | IL | Other |  | Age and Condition | 3200000 | 2018-06-04 | 2018-06-04 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13669 | 2017-09-12 |  | Rebuild West Frankfort East-West Frankfort 138 kV line to 120 degrees C capability | Replace 10 wood-pole H-Frame structures to raise conductor clearance from 100C-capable to 120C-capable. ( Line to be operated at 110 degrees C pending future project.) | IL | IL | Other |  | Age and Condition | 3300000 | 2017-12-23 | 2017-12-23 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13670 | 2017-09-12 |  | Rebuild Fargo-Pioneer 138 kV line to 100 degrees C | Upgrade line to 100 degrees C and add OPGW. | IL | IL | Other |  | Age and Condition | 3100000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13671 | 2017-09-12 |  | Rebuild Muddy-Norris City North 138 kV line to 2000A capability | Rebuild line to 2000A Capability. OPGW is required | IL | IL | Other |  | Age and Condition | 10800000 | 2018-11-11 | 2018-11-11 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13675 | 2017-09-12 |  | Rebuild Pana-R51D 138 kV line 1462 to 2000A | From the Moweaqua Tap to Blue Mound/Mount Auburn Tap to Route51 Decatur: Rebuild to 2000A. Replace 7 structures. | IL | IL | Other |  | Age and Condition | 5700000 | 2018-05-25 | 2018-05-25 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13677 | 2017-09-12 |  | New Edwards 138 kV substation capacitor bank (120 Mvar) | Install 120 Mvar 138 kV cap bank | IL | IL | Other |  | Reliability | 2200000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13691 | 2017-09-12 |  | New Albion South 138 kV substation capacitor bank (40 Mvar) | Install 138 kV capacitor bank on the North Bus at Albion South. | IL | IL | BaseRel |  |  | 1000000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13695 | 2017-09-14 |  | Rebuild Brokaw-Weed-Mahomet 138 kV lines 1376 & 1303 to 1800A | Rebuild to 1800A (795 ACSR T2). Upgrade the Mahomet bus-tie to 2000A. Rebuild the 1.55 mile Mahomet-Mahomet Tap section of RISN-NCMP-1592 with conductor capable of a minimum of 1200A. | IL | IL | Other |  | Age and Condition | 18800000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13696 | 2017-09-14 |  | Reconfigure Jerseyville NW 138 kV to a ring bus | Construct initial 4-position (ultimate 6-position) Ring bus. | IL | IL | Other |  | Reliability | 8000000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13710 | 2018-10-03 |  | New Stallings Substation: FACTS device | Install +250/-100 Mvar FACTS device at Stallings Substation | IL | IL | Other |  | Reliability | 28900000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 13794 | 2017-09-29 |  | Rebuild Hennepin-Woodhall 138 kV line 1512 | Rebuild HENN-WDHL-1512 to 795 ACSR T2 conductor. | IL | IL | Other |  | Age and Condition | 13400000 | 2018-06-15 | 2018-06-15 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 14061 | 2017-12-19 |  | Rebuild Towerline – Tazewell 138 kV line to 2000 Amps | Rebuild 6.19 miles of 477 ACSR with conductor having a capability of 2000 Amps under summer emergency conditions. | IL | IL | BaseRel |  |  | 8800000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 15225 | 2018-08-08 |  | Rebuild Lawrencevile-Olney 138 kV line to 2000 A | Rebuild Lawrenceville South – Olney North – 1, 22.8 mile, 138 kV line with conductor capable of 2000 A under summer emergency conditions | IL | IL | Other |  | Age and Condition | 11600000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 15226 | 2018-08-08 |  | Rebuild Jerseyville NW–Roodhouse West 138 kV line 1561 to 1200 A | Rebuild 28.3 miles of the Jerseyville NW – Roodhouse West portion of the Jerseyville NW – Ballard 1561 line. Replace existing 477 kcmil ACSR T/2 conductor with conductor having a minimum capability of 1200A under summer emergency conditions. | IL | IL | Other |  | Age and Condition | 21700000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenIL | 16227 | 2018-10-05 |  | Marblehead 161/138 kV | Terminal equipment (disconnect switch and bus conductor) | IL | IL | TMEP | Shared |  | 175000 | 2021-06-01 | 2021-06-01 | 161 | 138 | Top-Down
A in MTEP18 | A | Central | AmerenMO | 9828 | 2017-10-13 | AMRN50 | Uprate Joachim-Boyd Branch-St. Francois 138 kV circuit | Increase ground clearance | MO | MO | Other |  | Age and Condition |  | 2018-06-01 | 2018-06-01 | 138 | 138 | Bottom-Up
A in MTEP18 | A | Central | AmerenMO | 13547 | 2018-10-03 |  | Upgrade Lutesville-St. Francois 345 kV line | Replace 55 structures in the Lutesville-St. Francois-1 345 kV line to achieve a conductor MOT 0f 120 degrees C and add OPGW | MO | MO | Other |  | Age and Condition | 9600000 | 2018-06-08 | 2018-06-08 | 345 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenMO | 13568 | 2018-10-03 |  | Upgrade Eldon-Barnett-California-Overton 161 kV line | Replace structures on portions of 53.5 miles of 161kV line to provide ground clearance for a future maximum conductor operating temperature of 120 degrees C. Replace bus conductor at California substation with a minimum rating of 1200 amps. | MO | MO | Other |  | Age and Condition | 4800000 | 2018-10-01 | 2018-10-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenMO | 13672 | 2018-03-20 |  | Reconfigure Cahokia-Meramec 138 kV lines 1&2. New Lakeshire 138 kV substation breakers | Energize the 138 kV line section between Mackenzie and Lemay by closing the normally open switches (#21 & # 22) at Lemay. At Mackenzie switch rack, remove the 138 kV switches and connect C – MER – 1 & 2 138 kV lines with MER – WAT – 2 138 kV line by creating Cahokia – Meramec – Lemay – Watson circuit and Cahokia – Meramec – Lemay – Lakeshire circuit. Also, route existing MER-WAT-2 138 kV line in and out of Lakeshire substation. Replace 138 kV breaker in position #G with breaker having a minimum continuous capability of 2000 Amps. Move the Marshall – Lakeshire – 4 138 kV line to a new position on 138 kV Bus # 1 at Lakeshire and install a breaker and two disconnect switches with a minimum continuous capability of 2000 Amps. Connect the new MER –LKSH – 6432 138 kV line in position # E and install a breaker and a disconnect switch with a minimum continuous capability of 2000 Amps. | MO | MO | Other |  | Reliability | 3200000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenMO | 13673 | 2017-09-12 |  | Reconductor Bland-Miller Tap 138 kV line 6030 | For the Bland-Gasco Tap-Belle Tap-Meta Tap-Former Miller Tap sections -Upgrade conductor to 120 degrees MOT. Install OPGW. | MO | MO | Other |  | Age and Condition | 21950000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | AmerenMO | 13676 | 2017-09-12 |  | Rebuild Overton-Sedalia 138 kV line to 120 degrees C | Upgrade line to 120 degrees C MOT - Replace 22 wood pole H-frame structures. Install 2 mid-span structures. | MO | MO | Other |  | Age and Condition | 2000000 | 2018-07-17 | 2018-07-17 | 161 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 4726 | 2018-08-13 | PR04983, F3600, F3601 | Hillman - Darlington 138kV (X-14/X-101), rebuild | Rebuild Hillman - Darlington (X-14/X-101) 138kV line -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild a portion of the 12.35 mile line (X-14) and 6.38 mile line (X-101) -1950's vintage original construction | WI | WI | Other |  | Age and Condition | 20480000 | 2025-12-31 | 2025-12-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 7584 | 2018-08-13 | PR04986, F3632 | New Holstein SW STA - Custer SS 69kV (P68), rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration -Rebuild all 21.55 miles line with singular tubular poles -1947 vintage original construction | WI | WI | Other | Not Shared | Age and Condition | 27000000 | 2025-12-31 | 2025-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 7763 | 2018-08-13 | PR06467, F4847, F5141 | McKenna - Castle Rock, 69kV (Y-47), rebuild | Rebuild Y-47 from McKenna - Castle Rock 69 kV -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild a portion of the 8.52 mile line -1950's vintage original construction | WI | WI | Other |  | Age and Condition | 12050000 | 2025-12-31 | 2025-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 7764 | 2018-08-13 | PR06465, F4475 | Wautoma - Chaffee Creek 69 kV (Y-49) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild 11.7 miles of 13.1 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 14500000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 7765 | 2018-08-13 | PR06467, F4847, F5141, | Lincoln - McKenna 69kV (Y-145), rebuild | Rebuild Y-145 from Lincoln Pumping Station - McKenna 69 kV -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild a portion of the 12.06 mile line -1950, 1960 and 1980 vintage original construction | WI | WI | Other |  | Age and Condition | 9000000 | 2025-12-31 | 2025-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 8444 | 2018-08-13 | PR07820, PR07950, F5348 | Sawyer Sw St - First Avenue SS 69kV (T-46), Rebuild | *Total line length approximately 0.84 miles of which .3 miles is underground cables under the Sturgeon Bay shipping channel which will be replaced by approximately 0.4 miles of new cables. *Placement of the southerly riser structure will eliminate a dwelling clearance issue with the overhead line along Neenah Avenue. | WI | WI | Other | Not Shared | Age and Condition | 11300000 | 2020-12-31 | 2020-12-31 | 69 | 69 | Bottom-up
A in MTEP18 | A | West | ATC | 10486 | 2018-08-13 | PR06461, F4829 | Chaffee Creek - Lincoln Pump Station 69 kV (Y-18) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild 9.0 miles of 13.6 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 9600000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 12134 | 2018-08-13 | PR06458, F4445 | Finger Rd SW Station - Wesmark 69KV (FIRY11), rebuild | Rebuild Finger Rd SW Station - Wesmark 69KV (FIRY11) -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and line equipment show decay, deterioration -Rebuild all 10.98 miles of line. -1950's vintage original construction. | WI | WI | Other | Not Shared | Age and Condition | 14400000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 12135 | 2018-08-13 | PR04987, F3626 | Wesmark - Rapids 69KV (R-44), rebuild | Wesmark - Rapids 69KV (R-44) -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and line equipment show decay, deterioration -Rebuild 19.65 miles of line -1940's vintage original construction | WI | WI | Other | Not Shared | Age and Condition | 21500000 | 2024-12-21 | 2024-12-21 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 12137 | 2018-08-13 | F3622 | Hwy V - Oak St 69 kV (Z-26) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay and deterioration. -Rebuild 6.2 miles. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 9000000 | 2025-12-21 | 2025-12-21 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 12140 | 2018-08-13 | F3622 | Finger Rd - Hwy V 69 kV (U-47) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay, deterioration and woodpecker damage. -Rebuild 0.81 miles. -1940's vintage original construction. | WI | WI | Other |  | Age and Condition | 1520000 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 12141 | 2018-08-13 | PR0499, F3621,F3622 | Danz - Finger Rd 69 kV (L64) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay and deterioration. -Rebuild 3.1 miles of 3.3 mile line. -1940's and 1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 4230000 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 12147 | 2018-08-13 | PR06460, F4828 | Wild Rose - Harrison 69 kV (Y19) Partial Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild 15.0 miles of 21.0 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 14400000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13104 | 2018-08-17 | PR07720 | Juneautown SS, new DIC | - Construct new 138 kV GIS substation for the Distribution Interconnection request. - Loop the Harbor - Haymarket 138 kV underground line into the new substation. - Includes the new underground line extension, two river crossings, and line breakers for both incoming line positions. | WI | WI | Other |  | Load Growth | 34600000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13243 | 2018-08-17 | PR07735 | Winneconne SS, Relay and Breaker Replacement | Update Relays. Replace 2 69 kV Breakers. Replace 4 Disconnect Switches. | WI | WI | Other |  | Age and Condition | 2150000 | 2019-12-01 | 2019-12-01 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13713 | 2018-08-17 | F5007 | Liberty Street SS, DIC - Replace Transformer | - Liberty Street SS - WPS Transformer Replacement. - ATC Installing new jumpers and insulators. | WI | WI | Other |  | Load Growth | 30777 | 2017-07-19 | 2017-07-19 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13715 | 2018-08-17 | F4996 | Westfield SS,DIC - Add 2nd Transformer | - Westfield SS - Pioneer Power & Light 2nd transformer addition. - ATC to add 3-way GOAB and 300 Foot 69 kV line extension. | WI | WI | Other |  | Load Growth | 428782 | 2017-09-30 | 2017-09-30 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13717 | 2018-08-17 | F5043 | Huiskamp SS, Relay and Breaker Replacement | Upgrade relays Replace 1 69 kV Breaker | WI | WI | Other |  | Age and Condition | 506490 | 2018-12-15 | 2018-12-15 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13718 | 2018-08-17 | F5239 | Hooterville SS, DIC - Replace Transformer | - Hooterville SS - Alliant Transformer Replacement - ATC Installing two new poles, new jumpers and insulators | WI | WI | Other |  | Load Growth | 338663 | 2018-02-25 | 2018-02-25 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13719 | 2018-08-17 | F4982 | Cooney SS, DIC - Replace High Side Circuit Switcher | - Cooney SS - Oconomowoc Utilities Replacing high-side Circuit Switchers - ATC Installing new Jumpers and Insulators | WI | WI | Other |  | Other Local Needs | 35096 | 2017-11-01 | 2017-11-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13720 | 2018-08-17 | F5237 | Velp SS, DIC - Replace Transformer | - Velp SS - WPS Transformer and high-side protection replacement - ATC Replacing 77 & 88 Remote controlled MODs. | WI | WI | Other |  | Load Growth | 225050 | 2018-07-01 | 2018-07-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13721 | 2018-08-17 | F5253 | Sherman Street SS, DIC - Replace High Side Circuit Switcher | Sherman Street SS - WPS BK5 high Side Circuit Switcher replacement - ATC Bus Modification | WI | WI | Other |  | Other Local Needs | 68962 | 2018-07-01 | 2018-07-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13722 | 2018-08-17 | F4970 | Eastom SS, Relay and Circuit Switcher Replacement | WPS - Installing a new Control House ATC - Replacing Relays and Circuit Switcher | WI | WI | Other |  | Age and Condition | 1033443 | 2018-12-31 | 2018-12-31 | 115 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13723 | 2018-08-17 | F5235 | Perch Lake SS, DIC - Upgrade High Side Circuit Breaker | Perch Lake SS - UPPCo high side circuit breaker upgrade. ATC New Jumpers and Insulators | MI | MI | Other |  | Other Local Needs | 85000 | 2017-09-08 | 2017-09-08 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13724 | 2018-08-17 | F4722 | Walworth SS, DIC - Replace Transformers | Walworth SS - Alliant Replace both transformers and upgrade to high side circuit breakers. ATC install new Jumpers and Insulators. | WI | WI | Other |  | Load Growth | 33481 | 2017-08-05 | 2017-08-05 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13725 | 2018-08-17 | F4947 | Three Lakes SS, DIC - Add 2nd Transformer | Three Lakes SS - WPS 2nd Transformer addition ATC - Install 69 kV bus-tie switch and replace MODs | WI | WI | Other |  | Load Growth | 603151 | 2017-04-18 | 2017-04-18 | 115 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13726 | 2018-08-17 | F5211 | Plover SS, DIC - Replace Transformers | Plover SS, DIC - WPS Transformer Replacement and Substation Rebuild. ATC Upgrade S-45 Breaker/Line terminal, and install new 115 kV Bus | WI | WI | Other |  | Load Growth | 1770286 | 2019-06-30 | 2019-06-30 | 115 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13727 | 2018-08-17 | F4942 | Pulliam SS, Relay Upgrades and Replacements | Install redundant bus differentials on 69 kV and 138 kV busses Replace Electromechanical relays | WI | WI | Other |  | Age and Condition | 1873282 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13728 | 2018-08-17 | F5205 | Cloverleaf SS, Replace Dead End and Switches | Replace damaged switches | WI | WI | Other |  | Age and Condition | 1062784 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13731 | 2018-08-17 | F5031 | Juneau Northside SS, DIC - Replace Transformer | Juneau Northside SS -Juneau Utilities Transformer Replacement. ATC Install new Jumpers and Insulators | WI | WI | Other |  | Load Growth | 137387 | 2017-10-01 | 2017-10-01 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13732 | 2018-08-13 | F5195 | Paris - Burlington 138 kV (8962) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay, deterioration. -Rebuild 13.5 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 12560000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13733 | 2018-08-17 | F4650 | N Monroe SS, Relay Replacements | Relay Replacement Replace 2 OCBs with GCBs | WI | WI | Other |  | Age and Condition | 1623849 | 2018-04-15 | 2018-04-15 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13734 | 2018-08-17 | F5252 | Berryville SS, DIC - Add 2nd Transformer | Berryville SS - We Energies 2nd Transformer addition. ATC Install bus-tie breaker. | WI | WI | Other |  | Load Growth | 528612 | 2018-06-01 | 2018-06-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13735 | 2018-08-13 | F5194 | St Lawrence-Barton (8032) Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles show decay, deterioration. -Rebuild 8.3 miles of 13.1 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 8400000 | 2023-12-31 | 2023-12-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13736 | 2018-08-17 | F4874 | Hillman SS, DIC - Add Transformer | Hillman SS - Alliant Transformer addition. ATC Expand Substation and add 138 kV Bus. | WI | WI | Other |  | Load Growth | 2324874 | 2018-06-01 | 2018-06-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13737 | 2018-08-17 | F4608 | Victoria SS, Relay and RTU Replacement | UPPCo - Installing new control house ATC - Replacing Electromechanical Relays and 3 OCBs - Upgrading RTU | MI | MI | Other |  | Age and Condition | 1770698 | 2017-12-01 | 2017-12-01 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13738 | 2018-08-17 | F5246 | Lincoln SS, Relay and Breaker Replacements | Replace 2 Electro-Mechanical Relays Replace 2 138 kV Circuit Breakers This also includes adding a circuit breaker to reconfigure the straight bus to a (6) position ring bus configuration | WI | WI | Other |  | Age and Condition | 4100000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13740 | 2018-08-17 | F4708 | Darlington SS, DIC - Replace Transformer and Construct New Control House | Darlington SS, - Alliant; Replace Transformer T32 with new High-Side Breaker, Construct new Control House. ATC; Install new Insulators and Jumpers, Replace Relays and OCBs, RTU and OPGW termination | WI | WI | Other |  | Load Growth | 1882294 | 2018-10-31 | 2018-10-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13742 | 2018-08-17 | PR07733, F5245 | Waukesha SS, Relay and Breaker Replacements | Relay Replacement Replace 2 OCBs | WI | WI | Other |  | Age and Condition | 836447 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13743 | 2018-08-13 | F5192 | Barton-Auburn 138 kV (9752) Partial Rebuild | -Line inspection reports indicate wood H-Frame segment of the line requires rebuild to continue reliable operation. -Wood poles show decay and deterioration. -Rebuild 6.9 miles of 11.7 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 7050000 | 2024-12-31 | 2024-12-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13746 | 2018-08-17 | F5244 | St Lawrence SS, Breaker Replacement | Replace 1 First Generation ABB SF6 Breaker (Leakage issues) | WI | WI | Other |  | Age and Condition | 219619 | 2018-07-31 | 2018-07-31 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13747 | 2018-08-17 | F5176 | Wesmark SS, Relays and Breakers | Replace Electromechanical Relays Replace 2 69 kV OCBs and 4 Disconnect Switches Upgrade RTU | WI | WI | Other |  | Age and Condition | 811572 | 2019-04-12 | 2019-04-12 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13749 | 2018-08-17 | F5170 | West Towne SS, Relay Replacement | MGE - Control House Replacement ATC - Relay Replacements | WI | WI | Other |  | Age and Condition | 3185723 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13754 | 2018-08-17 | F4388 | Enzyme Bio SS, DIC - Add 2nd Transformer | Enzyme Bio SS - Alliant 2nd Transformer addition. ATC Install 2 new GOABs with remote control on the Colley Road - Tiger 69 kV Line (Y32) and Retire existing GOAB | WI | WI | Other |  | Load Growth | 988101 | 2017-04-30 | 2017-04-30 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13755 | 2018-08-17 | F5165 | Osceola SS, Breaker Replacement | Replace 69kV Breaker 765, OA3 mechanism prone to delayed tripping | MI | MI | Other |  | Age and Condition | 348998 | 2019-12-01 | 2019-12-01 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13756 | 2018-08-17 | F5302 | Edgewater SS, 345 kV Asset Renewal and Bus Reconfiguration | Substation Equipment Asset Renewal - Replace four 345 kV model GW oil circuit breakers, breaker mechanism and bushing type cause units to have a history of chronic oil leakage. - Retire two 345 kV live tank line circuit breakers and six associated free standing CTs. Three of these CTs are a model with a history of failures. - Retire 345 kV outdoor SF6 GIS bus. Heaved foundations have caused past leaks and future shifting of foundations risks continued leakage. Bus reconfiguration is coordinated with the retirement of select Edgewater generation units. | WI | WI | Other | Not Shared | Reliability | 10400000 | 2020-12-01 | 2020-12-01 | 345 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13758 | 2018-08-17 | F5164 | Straits SS, Replace 3 138 kV Breakers | Replace 3 138 kV Breakers designed with OA3 mechanism, prone to delayed tripping | MI | MI | Other |  | Age and Condition | 1086498 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13760 | 2018-08-17 | F4338 | Lone Rock SS, Replace Relays and Breakers | Lone Rock SS Asset Management work schedule coordinated with Alliant DIC Transformer Replacement. ATC Replacing Electromechanical Relays and (3) OA3 mechanism OCBs, prone to delayed tripping. Replacing RTU. | WI | WI | Other |  | Age and Condition | 1939148 | 2017-10-31 | 2017-10-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13761 | 2018-08-17 | F4804 | Okray SS, DIC - Add 2nd Transformer | Okray SS - WPS add 2nd Transformer. ATC Install line and bus-tie breakers | WI | WI | Other |  | Load Growth | 1812667 | 2018-06-01 | 2018-06-01 | 115 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13762 | 2018-08-17 | F5161 | Dyckesville SS, Relay, Breaker and Switch Replacement | Replace Electromechanical Relays Replace 1 OCB Replace 2 Disconnect Switches | WI | WI | Other |  | Age and Condition | 599728 | 2019-10-11 | 2019-10-11 | 138 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13766 | 2018-08-17 | F4787 | Baraboo SS, Bus Uprate and RTU Replacement | Replace 69 kV Bus Conductor for Increased Capacity RTU and Control House Upgrades | WI | WI | Other |  | Age and Condition | 1799436 | 2018-10-31 | 2018-10-31 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13768 | 2018-08-17 | F4767 | Pflaum SS, Replace Failed 69 kV Underground Cable | Replace failed underground 69 kV Cable with Overhead Circuit. Coordinated work - Replace Relays, 3 Breakers, Circuit Switcher and CTs | WI | WI | Other |  | Age and Condition | 2075688 | 2025-12-01 | 2025-12-01 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | ATC | 13769 | 2018-08-23 | PR08006, F5132, F5135 | J704/J711 GIC- Silver River SS-Interconnection and Network Upgrades | Project governed by MPFCA. Construct a new eight-position 138-kV Silver River Substation in a breaker and a half configuration adjacent to the M38 substation. The substation will be designed for a ten-position ultimate design and will tie in all network elements from the M38 substation excluding the transformer and cap bank. There will be one new transmission line between Silver River and the M38 substation. | MI | MI | GIP | Shared |  | 19700000 | 2019-01-31 | 2019-01-31 | 138 | 0 | Externally Driven
A in MTEP18 | A | West | ATC | 13770 | 2018-08-13 | F4828 | Wautoma - Wild Rose 69kV (Y-180) Partial Rebuild | -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodp ecker activity. -Rebuild 6.0 miles of 10.5 mile line. -1950's vintage original construction. | WI | WI | Other |  | Age and Condition | 5500000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13773 | 2018-08-13 | PR04980, F3666 | Pine River - Hiawatha 69kV (ESE_6908) Partial Rebuild | -Line inspection reports indicate selected poles require rebuild to continue reliable operation. -Partial Rebuild and Re-insulation of the line. -1950's vintage original construction. | MI | MI | Other |  | Age and Condition | 7200000 | 2020-03-01 | 2020-03-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13774 | 2018-08-17 | PR05842, F4131 | Hancock SS - DIC, Replace Transformers | Hancock DIC – Alliant and ACEC joint rebuild Hancock Substation. ATC add line breakers to sectionalize Chaffee Creek - Sand Lake 69 kV Line (Y-90), Relocate cap banks, and Add sync close breakers. | WI | WI | Other |  | Load Growth | 4721140 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13784 | 2018-08-17 | PR08005, F5134 | J703 GIC- Huron SS, Interconnection and Network Upgrades | Construct a new six position 138-kV Huron Substation in a breaker and a half configuration constructed adjacent to the new power plant. The substation will: -be designed for a ten-position ultimate design -tie in the Freeman-National 138-kV (FREG11) and Presque Isle – Empire (Goose Lake) 138-kV lines creating a double circuit loop | MI | MI | GIP | Shared |  | 17100000 | 2019-01-23 | 2019-01-23 | 138 | 138 | Externally Driven
A in MTEP18 | A | West | ATC | 13786 | 2018-08-17 | F4750 | Richland Center SS, DIC - Add Transformer | - Richland Center SS - City Utilities of Richland Center Transformer Addition. - ATC Installing new jumpers and insulators. | WI | WI | Other |  | Load Growth | 203040 | 2017-07-13 | 2017-07-13 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13787 | 2018-08-17 | F5124 | Wittenberg SS, DIC - Replace Transformer | Wittenberg SS - Alliant Transformer Replacement. ATC New Jumpers and Insulators | WI | WI | Other |  | Load Growth | 123085 | 2018-06-01 | 2018-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13788 | 2018-08-17 | F5284 | Nine Mile SS, Install MODS for Sectionalizing | Install MODS for System Sectionalizing Construct New Control House to provide space for new equipment Replace Relays | MI | MI | Other |  | Reliability | 3443060 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13789 | 2018-08-17 | F4734 | Kilbourn SS, Bus Reconfiguration and Relay Replacement | Alliant - Generator Step Unit Replacement ATC - Bus Reconfiguration for Reliability ATC - Relay Replacement | WI | WI | Other |  | Reliability | 6900000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13790 | 2018-08-17 | F5091 | Oak St SS, DIC - Replace Tramsformer | Oak St SS - WPS BK1 Transformer replacement and High-side circuit breaker addition. ATC Install jumpers and insulators and install new panels in WPS Control house. | WI | WI | Other |  | Load Growth | 879600 | 2018-10-01 | 2018-10-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13791 | 2018-08-17 | F5267 | New Holstein SS, Install 69 kV Breaker | Replace Line Fuses with 69 kV Breaker to upgrade protection | WI | WI | Other |  | Reliability | 784901 | 2019-12-01 | 2019-12-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13792 | 2018-08-17 | PR04698, F3699 | Keel Ridge SS, New DIC | UMERC will: • construct a new Keel Ridge Substation • install one 69/13.8 kV, 18 MVA transformer ATC will: • loop through line 6820 (Armory-Quinnesec Fall) • extend 0.6 mile double-circuited 69 kV T-Line • install two line switches (load-break), and one bus-tie switch | MI | MI | Other |  | Load Growth | 2600000 | 2022-06-01 | 2022-06-01 | 69 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13802 | 2018-08-17 | PR07730, F5171 | Hillside SS, Relay and Breaker Replacements | Replace Relays. Replace 1 69kV breaker and replace line and bus disconnect switches. Replace PT. | WI | WI | Other |  | Age and Condition | 670000 | 2019-12-01 | 2019-12-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 13821 | 2018-08-17 |  | Small Capital Project and Asset Renewal Current Cycle | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2018. | WI,MI | WI,MI | Other |  | Age and Condition | 38457451 | 2021-06-30 | 2021-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13822 | 2018-08-17 |  | Small Capital Project and Asset Renewal 2019 | Asset replacements and upgrades with short project life cycles not compatible with the MTEP 18-month review cycle. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2019. | WI,MI | WI,MI | Other | Not Shared | Age and Condition | 8007814 | 2022-06-30 | 2022-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13823 | 2018-08-17 |  | Communication Reliability Upgrades Current Cycle | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2018. | WI,MI | WI,MI | Other |  | Other Local Needs | 34461836 | 2021-06-30 | 2021-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13824 | 2018-08-17 |  | Line Clearance Mitigation Projects Current Cycle | Line Clearance Mitigation Project life cycles typically require limited infrastructure modifications and additions with shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2018. | WI,MI | WI,MI | Other |  | Other Local Needs | 18718669 | 2021-06-30 | 2021-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13825 | 2018-08-17 |  | Line Clearance Mitigation Projects 2019 | Line Clearance Mitigation Project life cycles are not compatible with the MTEP 18-month review cycle. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2019. | WI,MI | WI,MI | Other | Not Shared | Other Local Needs | 5832204 | 2022-06-30 | 2022-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13826 | 2018-08-17 |  | Physical Security Current Cycle | Physical Security Project life cycles typically require limited infrastructure modifications and additions with shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2018. | WI,MI | WI,MI | Other |  | Other Local Needs | 67198396 | 2021-06-30 | 2021-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13828 | 2018-08-17 |  | Physical Security 2019 | Physical Security Project life cycles are not compatible with the MTEP 18-month review cycle. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2019. | WI,MI | WI,MI | Other |  | Other Local Needs | 3000000 | 2022-06-30 | 2022-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13829 | 2018-08-17 |  | Communication Reliability Upgrades 2019 | Communications network system upgrades with short project life cycles not compatible with the MTEP 18-month review process. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2019. | WI,MI | WI,MI | Other |  | Other Local Needs | 1422500 | 2022-06-30 | 2022-06-30 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13831 | 2018-08-17 | PR07800 | Big Pond SS, Retire Substation | Bypass Big Pond substation, reuse and retire Big Pond substation equipment | WI | WI | Other | Not Shared | Other Local Needs | 454000 | 2020-12-31 | 2020-12-31 | 138 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 13832 | 2018-05-24 | PR07779 | Riverside SS, 69 kV Bus Uprate | Replace existing 69k kV strain bus and support structures | WI | WI | Other |  | Reliability | 80000 | 2022-01-01 | 2022-01-01 | 69 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 14039 | 2018-08-13 | F5122 | Walker Tap Underground Cable Removal | De-energize, isolate and ground the 96SG41 underground (UG) pipe-type cable | WI | WI | Other |  | Other Local Needs | 700000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14073 | 2018-08-17 | PR07814 | Mount Pleasant Tech Interconnection Project | Construct New 345 - 138 kV Mount Pleasant Substation For Load Interconnection Request. Loop the Racine - Pleasant Prairie 345 kV Line (PLPL101) Into the New Substation (Approx. 1.2 Miles). String a New Racine Substation to Pleasant Prairie Substation 345 kV Circuit (Approx. 12 Miles) In The Vacant Position on Existing Structures, Loop This New Circuit Into the New Substation (Approx 1.2 Miles). Reconfigure the Racine Substation 345 kV Bus and Construct a New 345 kV Line Terminal at the Pleasant Prairie Substation. Construct 4 New 138 kV Short Underground Lines To Serve Approx. 230 MW of Customer Load. | WI | WI | Other |  | Load Growth | 140000000 | 2019-12-31 | 2019-12-31 | 345 | 138 | Bottom-Up
A in MTEP18 | A | West | ATC | 14184 | 2018-08-17 | PR07832 | Cranberry SS, New 115 kV Inductor Bank | This project consists of removing the existing 115 kV, 14.4 MVAR capacitor bank at the Cranberry substation and installing a new 115 kV, 10.4 MVAR oil-filled inductor bank to the vacated bay position. | WI | WI | Other |  | Reliability | 1700000 | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14185 | 2018-08-17 | PR07831; PR07998 | M-38 SS and Silver River SS, New 138 kV Inductor Banks | This project consists of installing two new 138 kV, 8 MVAR oil-filled inductor banks at the M-38 substation and Silver River substation. | MI | MI | Other |  | Reliability | 4100000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14186 | 2018-08-17 | PR07830, F5398 | Iron Grove SS, New 138 kV Inductor Bank | This project consists of installing a new 138 kV, 15 MVAR, oil-filled inductor bank at the Iron Grove substation to the 138 kV straight bus. | MI | MI | Other |  | Reliability | 1900000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14204 | 2018-08-23 | PR08007, F5338 | J704/J711 GIC- Network Upgrades | Project governed by MPFCA. - M38G22 and ATLANTIC69 line reroutes to accommodate generator lead line. (J711 only) - Upgrade the Silver River to North Lake 138-kV line to a minimum emergency rating of 474 Amps for all seasons. - Upgrade the Silver River to Perch Lake 138-kV line to a minimum emergency rating of 463 Amps for all seasons. | MI | MI | GIP | Shared |  | 18700000 | 2020-09-23 | 2020-09-23 | 138 | 0 | Externally Driven
A in MTEP18 | A | West | ATC | 14604 | 2018-08-17 | PR07959 | State Line SS, new DIC | State Line SS - New We Energies T-D interconnection. ATC to construct a new 0.5 mile 138 kV double circuit line looping in 63141 (Bain – Spring Valley) with line and bus tie breakers. ATC will also install two 16 Mvar cap banks at each of the State Line and Balsam Substations. | WI | WI | Other |  | Load Growth | 8200000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | Bayport-Pioneer, rebuild as double-circuit 138 kV | *Rebuild and convert 22 miles of 69 kV line between Bayport area and Pioneer Substation to 138 kV operation *Rebuild using double circuit structures and string both lines *Jumper together, combine, and operate as a single 138 kV line | WI | WI | Other |  | Age and Condition | 51700000 | 2022-06-30 | 2022-06-30 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14805 | 2018-08-17 | PR07999 | Winona SS, New 138 kV Inductor Bank | This project consists of installing a new 138 kV, 8 MVAR inductor bank at the Winona substation in an open bay position. | MI | MI | Other | Not Shared | Reliability | 1900000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14806 | 2018-08-17 | PR07942, F5036 | Venus SS, Capacitor Bank Retirement | This project consists of removing the existing 115 kV, 14.4 MVAR capacitor bank at the Venus substation. | WI | WI | Other |  | Other Local Needs | 140000 | 2020-06-01 | 2020-06-01 | 115 | 115 | Bottom-Up
A in MTEP18 | A | West | ATC | 14904 | 2018-08-17 |  | Load Interconnection Current Cycle | These Distribution load Interconnections are customer need driven and typically require limited infrastructure modifications and additions with shorter project life cycles These projects have limited scope and cost. Initial capital spend for this program expected in 2018. | WI,MI | WI,MI | Other |  | Load Growth | 6436258 | 2021-06-30 | 2021-06-30 | 138 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 14905 | 2018-08-17 |  | Load Interconnection 2019 | These Distribution load Interconnections are customer need driven and typically require limited infrastructure modifications and additions with shorter project life cycles These projects have limited scope and cost. Initial capital spend for this program expected in 2019. | WI,MI | WI,MI | Other |  | Load Growth | 10570000 | 2022-06-30 | 2022-06-30 | 138 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 14925 | 2018-08-17 | PR07995, F5438, F5437 | J505 GIC, Apollo SS, Generator Interconnection and Network Facilities | - Construct a new Apollo 138-kV substation to interconnect the J505 generation interconnection request. - The new substation will be built as a three position ring bus expandable to six positions. - The new station will be located adjacent to the existing Kewaunee-Shoto 138-kV line. - Loop in the existing Kewaunee-Shoto 138-kV line to the new station. - Perform required remote end work at Kewaunee and Shoto substations. | WI | WI | GIP | Shared |  | 8300000 | 2021-01-28 | 2021-01-28 | 138 | 138 | Externally Driven
A in MTEP18 | A | West | ATC | 14926 | 2018-08-13 | PR08029, F5468, F5469 | Pioneer-Crivitz, retire double-circuit 69 kV | -Retire/remove 69 kV lines between Pioneer and Crivitz Substations -Relocate/convert Lena and Pound Substations underneath nearby 138 kV lines -Remove Pioneer 138/69 kV transformer | WI | WI | Other |  | Age and Condition | 20400000 | 2022-12-01 | 2022-12-01 | 138 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 14986 | 2018-08-17 | PR08084 | Caroline SS – Transformer (T31) Breaker and Relay Asset Renewal | Replace transformer (T31) with standard 115-69kV, 60MVA, LTC transformer. -Transformer has main tank gassing issues Replace the OCB transformer low side breaker and additional breaker. -Poor CT performance | WI | WI | Other | Not Shared | Age and Condition | 4500000 | 2021-12-01 | 2021-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14987 | 2018-08-17 | PR07558, PR07877 | Whitcomb SS - Transformer (T31) 69kV Breaker Asset Renewals | Replace transformer (T31) with standard 115-69kV, 60MVA, LTC transformer. -Transformer has main tank gassing issues Replace three OCB line breakers and one transformer breaker. -Poor CT performance Replace the failing 69kV bus insulation and retire one CT | WI | WI | Other | Not Shared | Age and Condition | 5500000 | 2021-12-01 | 2021-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 14988 | 2018-08-17 | PR08036 | Shoto SS - Transformer (T1) and Breaker Asset Renewal | Retire existing T1 station power transformer due to performance and install new. -Include provisions to quickly replace T2 Install new low side breakers for T1 and T2 on 69kV adjacent bay. Retire existing 69kV K-11 and C-55 OCBs, replace and relocate new SF6 breakers and arresters. | WI | WI | Other | Not Shared | Age and Condition | 5700000 | 2021-12-01 | 2021-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15044 | 2018-08-17 | PR08039 | Stratford SS, DIC, add 2nd transformer and substation rebuild | WPS will: • rebuild and expand Stratford Substation • add 2nd transformer • replace the existing transformer ATC will: • loop through line B-54 (Wien-McMillan) • install two (2) supervisory-controlled, load-break capable MODs • replace the existing 21.6 MVar cap bank with 2-stage (1-13.6 MVar, 1-6.8 MVar) cap bank • upgrade the cap bank high-side protection to circuit breakers | WI | WI | Other | Not Shared | Load Growth | 3700000 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15045 | 2018-08-17 | PR08025 | Dam Heights SS, DIC, add a new radial line | ATC will: • Reconfigure, expand bus no. 2 and add new line terminal at Dam Heights SS • build half mile of new 69 kV single circuit along HWY 78 • build quarter mile partially double circuit with Y-75 | WI | WI | Other | Not Shared | Load Growth | 3300000 | 2020-06-01 | 2020-06-01 | 69 | 69 | Bottom-Up
A in MTEP18 | A | West | ATC | 15124 | 2018-08-17 |  | Muscoda SS, DIC, add 2nd transformer and substation rebuild | Village of Muscoda will: -add a second transformer and rebuild a substation ATC will: -loop through the 69 kV line Y-124 with line breakers | WI | WI | Other |  | Load Growth | 3290000 | 2020-06-30 | 2020-06-30 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15126 | 2018-08-17 |  | Edgewater SS, DIC, replace transformer and substation rebuild | Alliant will: - rebuild and relocate Edgewater Substation ATC will: - loop through the 138 kV line X-37 with line breakers | WI | WI | Other |  | Load Growth | 3000000 | 2023-12-31 | 2023-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15127 | 2018-08-17 |  | Portage Industrial Park SS, DIC, replace transformers and substation rebuild | Alliant will: - rebuild and relocate Portage Industrial Park Substation -replace distribution transformer ATC will: - loop through the 138 kV line X-67 with line switches | WI | WI | Other |  | Load Growth | 3000000 | 2021-06-01 | 2021-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15128 | 2018-08-17 |  | Birnamwood SS, DIC, replace transformer and substation rebuild | Alliant will: - replace transformer and rebuild Birnamwood Substation ATC will: - build a new switching station near Birnamwood tap to loop through 69 kV line Y-86 with line breakers | WI | WI | Other |  | Load Growth | 4500000 | 2021-06-01 | 2021-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15129 | 2018-08-17 |  | Green County, new DIC | New substation in Green County, WI | WI | WI | Other |  | Load Growth | 4500000 | 2021-05-15 | 2021-05-15 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15130 | 2018-08-17 | PR07436, F5025 | Eastern UP, new DIC | Load addition in Eastern UP, MI | MI | MI | Other |  | Load Growth | 12593000 | 2021-03-01 | 2021-03-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15131 | 2018-08-17 | PR08126 | Milton Lawn SS, DIC, add 2nd transformer and substation rebuild | Alliant will: - add 2nd transformer and rebuild Milton Lawn Substation ATC will: - loop through 69 kV line Y-79 with line breakers | WI | WI | Other |  | Load Growth | 3000000 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15132 | 2018-08-17 | PR08136 | Quincy Street SS, new DIC | WPS will: • construct a new Quincy Street Substation • install two 138/13.8 kV, 60/80/100 MVA transformers • install two 138 kV circuit breakers as high-side protection ATC will: • loop through 138 kV line S-123 (Pulliam-Eastman) • install two 138 kV line breakers and one bus-tie breaker • uprate 138 kV line X-154 (Highway V-Preble-Tower Drive) to 300 | WI | WI | Other |  | Load Growth | 6466513 | 2020-07-01 | 2020-07-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15133 | 2018-08-17 | PR07793, F5293 | Central UP, new DIC | Load addition in Central UP, MI | MI | MI | Other |  | Load Growth | 6200000 | 2019-07-01 | 2019-07-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15145 | 2018-08-22 | PR 08090, F5479 | Mackinac - McGulpin 138 kV (9901 and 9903), submarine cable replacement | Remove and Replace Existing Fluid Dielectric Insulated 138 kV Cables connecting Mackinac and Mc Gulpin Substations. - Remove the three electrically inoperable (2 severed and 1 electrically damaged) Fluid Dielectric Insulated 138 kV cables. - Replace them with a new Solid Dielectric insulated circuit operated at 138 kV. - Remove the three operational Fluid Dielectric Insulated 138 kV cables. - Replace them with a new Solid Dielectric insulated circuit operated at 138 kV. - Construct on shore Riser Termination facilities compatible with the new Solid Dielectric Insulated cables. | MI | MI | Other |  | Age and Condition | 105000000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | ATC | 15284 | 2018-08-13 | PR08113, F5518 | North Lake SS - M-38 SS 138kV (NLKG31), select rebuild | The J711 interconnection project required network upgrades to NLKG31. Asset renewal work is needed on 78 structures on NLKG31 identified during a heavy loaded ice analysis. Due to difficult and costly access to this line for efficiency replacement of these 78 structures will be timed with the J711 network upgrade of 126 structures on NLKG31. | MI | MI | Other |  | Age and Condition | 8500000 | 2020-12-30 | 2020-12-30 | 138 | 138 | Bottom-Up
A in MTEP18 | A | West | ATC | 16164 | 2018-10-01 |  | Elkhart Lake SS, 138 kV – Relieve Market Congestion | Relieve market Congestion | WI | WI | Other | Not Shared | Other Local Needs | 2000000 | 2022-12-31 | 2022-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | BREC | 16204 | 2018-10-04 | BREC | Wilson-BR Tap-Paradise 161 kV Modification | Construct a new 161kV line from Wilson to BR Tap, re-conductoring BR Tap to Paradise 161 kV, upgrading terminal equipment at Matanzas and removing switch at BR Tap. Scoping level cost estimate $16 million. | KY | KY | Other |  | Other Local Needs | 16020000 | 2023-01-01 | 2023-05-30 | 161 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 13962 | 2017-09-13 |  | CE Relay Replacement Program - 2019 | Replace protective relays as needed to coordinate with adjacent Transmission Owners | MI | MI | Other |  | Other Local Needs | 640000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 13963 | 2017-09-13 |  | CE Breaker Replacement Program - 2020 | Replace damaged or defective circuit breakers with new circuit breakers | MI | MI | Other |  | Other Local Needs | 1170000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 13965 | 2017-09-13 |  | CE Substation Equipment Replacement Program - 2020 | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI | MI | Other |  | Other Local Needs | 1410000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 13966 | 2017-09-13 |  | CE Pole & Line Equipment Replacement Program - 2020 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | MI | Other |  | Other Local Needs | 840000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 13967 | 2017-09-13 |  | Muskegon Heights #2 Line Rebuild | Rebuild a portion of the Muskegon Heights #2 138 kV Line, approximately 2 miles, utilizing 138 kV single circuit construction | MI | MI | Other |  | Age and Condition | 800000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 14164 | 2017-09-21 |  | Boardman Line Upgrade | Add optical fiber to the Boardman #1 and Boardman #2 138 kV Lines to coordinate with WPSC's Grand Traverse Station Upgrade project | MI | MI | Other |  | Reliability | 200000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 14725 | 2018-05-16 |  | Summerton Station Upgrade (J589) | Replace existing relaying at Summerton Substation on the Luce (J589) line exit with dual pilot schemes | MI | MI | Other |  | Reliability | 371500 | 2018-12-10 | 2018-12-10 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | CETO | 14864 | 2018-03-19 |  | Polkton Spur 138 kV New Line | Construct a new 138 kV line from the Cobb-Tallmadge #2 138 kV Line to the new Polkton Substation. | MI | MI | Other |  | Reliability | 200000 | 2020-03-01 | 2020-03-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | CLECO | 9716 | 2017-09-25 |  | Coughlin - Plaisance 138 kV Reconductor | Rebuild Coughlin to Plaisance 138 kV line for 230 kV with 2- 954 ACSS conductor. | LA | LA | BaseRel |  |  | 12320000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13750 | 2017-09-07 | TIN1863 | Greenfield to Fountaintown 69kV Rebuild | Greenfield to Westland Jct to Fountaintown 69166 (Pt1) 69kV Rebuild w/ 954ACSR; Replace Westland Jct #1 and #2 switches | IN | IN | Other |  | Age and Condition | 7478000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13759 | 2017-09-07 | TIN1862 | HE Raysville to Knightstown 69kV Rebuild | HE Raysville to Knightstown 69140 (Part 1) 69kV Rebuild w/ 954ACSR; Replace Raysville #1 and #2 switches | IN | IN | Other |  | Age and Condition | 4732000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13765 | 2017-09-07 | TIN1857 | Metea to Lucerne 69kV Rebuild | Metea to Lucerne 6926 (Part 1) 69kV Rebuild w/ 477ACSR | IN | IN | Other |  | Age and Condition | 7078000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13772 | 2017-09-07 | TIN1840 | Seymour 138 Reliability Upgrades | Seymour 138 Reliability Upgrades: Replace (3) 138kV circuit switchers – 13869-1, 13869-2; (12) 138kV line CCVTs; 13829 and 13830 wave traps; 13830 & 13851 MOLB Sw's; 13880 switch 2000 amp load break; Add new ctrl bldg; Misc relay upgrades; Replace (3) 69kv breakers and main bus (954acsr) | IN | IN | Other |  | Age and Condition | 4508000 | 2019-12-31 | 2019-12-31 | 138 | 69 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13775 | 2017-09-07 | AMIN1741 | Gallagher 230 Reliability Upgrades | Gallagher 230 Reliability Upgrades: Replace misc. relays; (4) 230kV breakers – 23004, 23005, 230138-10, 230kV TR; (11) misc. 230kV switches; (4) 138kV breakers – 13827, 13885, 13822, 138TR; (3) wave traps - 13852, 23004, 23005 | IN | IN | Other |  | Age and Condition | 4072000 | 2018-12-31 | 2018-12-31 | 230 | 138 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13796 | 2018-08-10 | TIN1897 | J515 Cayuga CT 345kV Ring Bus Expansion | Cayuga CT 345kV Ring Bus Expansion - to accommodate wind farm connection - J515 | IN | IN | GIP | Shared |  | 3511382 | 2019-06-01 | 2019-06-01 | 345 | 0 | Externally Driven
A in MTEP18 | A | Central | DEI | 13808 | 2017-09-27 | M17SG0009 | McCordsville (WVPA) New 69-12kV Sub | McCordsville (WVPA) New 69-12kV Sub: DEI to provide PM support, system protection engineering, metering, substation testing, for new WVPA-owned sub | IN | IN | Other |  | Load Growth | 100000 | 2019-06-01 | 2019-06-01 | 69 | 12 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13812 | 2018-07-10 | M180405 | Intelliplex (HE) New 138-12kV Sub | Intelliplex (HE) New 138-12kV Sub: DEI to provide PM support, system protection engineering, metering, substation testing, for new HE-owned sub in the 13803 ckt. | IN | IN | Other |  | Load Growth | 300000 | 2019-12-31 | 2019-12-31 | 138 | 12 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13820 | 2017-09-08 | DIN1773 | Galveston New 69-12kV Sub | Galveston New 69-12kV Sub: loop 69173 ckt thru with (3) 1200A switches and 954AAC bus; 22.4MVA NLTC xfmr | IN | IN | Other |  | Load Growth | 1702880 | 2019-12-31 | 2019-12-31 | 69 | 12 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13827 | 2017-09-08 | DIN1697 | Westfield Dunbar Rd. New 69-12kV Sub | Westfield Dunbar Rd. New 69-12kV Sub: loop 6917 ckt thru; 22.4MVA xfmr | IN | IN | Other |  | Load Growth | 1609000 | 2019-06-01 | 2019-06-01 | 69 | 12 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13830 | 2017-09-08 | DIN1719 | Westfield Casey Rd. New 69-12kV Sub | Westfield Casey Rd. New 69-12kV Sub: loop 69142 ckt thru; 22.4MVA xfmr | IN | IN | Other |  | Load Growth | 1544000 | 2019-06-01 | 2019-06-01 | 69 | 12 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13844 | 2017-09-11 | TIN1822 | Washington Muni. 138kV Ring Bus | Washington Muni. 138kV Ring Bus: add 2 breakers and replace 1; relocate metering; add control building; install wave traps on the 13825 and 13856 line terminals | IN | IN | Other |  | Age and Condition | 3882000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13845 | 2018-07-12 | M170016 | Crawfordsville Jct 69kV Ring Bus | Crawfordsville Jct 69kV Ring Bus Switching Station: build 3 breaker ring at existing junction in the 6935 ckt and close in Crawfordsville 69 #1 switch. | IN | IN | Other |  | Reliability | 6420000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 13849 | 2017-09-11 | DIN1666 | Brazil to Carbon - New 69kV Ckt. | Brazil to Carbon - New 69kV Ckt. to remove Carbon loads from the 6938 ckt. | IN | IN | Other |  | Load Growth | 4353000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | DEI | 14624 | 2018-01-02 | M170127 | Andersonville to Andersonville Jct 69kV Rebuild | Rebuild 6919 from Andersonville 69 sub (pole # 840-1272) to Andersonville Jct (pole # 840-1175) using light-duty steel poles, 477ACSR conductor and OPGW static | IN | IN | Other |  | Age and Condition | 14093000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | DPC | 16184 | 2018-10-03 |  | Rebuild Wabaco to Rochester 161kV | Rebuild existing ~13.1 miles Wabaco to Rochester 161kV line by using 795kcmil Drake ACSS conductor. No substation work is needed. Existing ROW is adequate (No additional ROW required). Some terrain work is needed as well as one OPGW and one steel shieldwire. | MN | MN | Other |  | Other Local Needs | 11000000 | 2023-12-31 | 2023-12-31 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 9694 | 2017-08-29 | 16-EAI-003 | Camden Maguire - Smackover 115kV: Rebuild Line | Re-build 14.32 mile long line to a minimum rating of 882A. | AR | AR | BaseRel |  |  | 16418417 | 2021-06-01 | 2021-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 12663 | 2018-08-06 | 17-EAI-016 | Palestine 161kV: Construct new substation | Construct the Palestine 161/13.8kV substation near Highway 70 on the Brinkley East to Moses 161kV T-Line between structures #84 - #92. | AR | AR | Other |  | Load Growth | 12484101 | 2023-06-01 | 2023-06-01 | 161 | 13.8 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 12664 | 2018-08-06 | 17-EAI-011 | Skunk Hollow 161kV: Construct new substation | Construct a new substation on Highway 64 east of Conway, AR. Install one 40 MVA 161/13.8kV LTC and four feeder breaker bays. | AR | AR | Other |  | Load Growth | 7351525 | 2021-06-01 | 2021-06-01 | 161 | 13.8 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 12668 | 2018-08-07 | 17-EAI-025 | Sierra 115kV: New Substation | Install a new substation with a 40 MVA load transformer on the Cheetah - Danville 115kV line. | AR | AR | Other |  | Load Growth | 15015860 | 2020-05-01 | 2020-05-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13604 | 2018-08-06 | 18-EAI-033 | Social Hill 115kV: Construct new distribution substation | Build a new distribution 115/13.8kV substation with a new 40 MVA 115/13.8kV transformer and provisions for a future second 40 MVA transformer. | AR | AR | Other |  | Load Growth | 11607797 | 2021-06-01 | 2021-06-01 | 115 | 13.8 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13621 | 2017-09-26 | 18-EAI-015 | Norfork - Southland 161kV: Rebuild line | Rebuild the ~9 mile line segment and upgrade all station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | AR | BaseRel |  |  | 14434622 | 2027-12-01 | 2027-12-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13622 | 2018-09-04 | 18-EAI-017 | Southland - Mt. Home 161kV: Rebuild line | Rebuild the ~1.4 mile line segment and upgrade all station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | AR | BaseRel |  |  | 4239252 | 2023-06-01 | 2023-06-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13624 | 2017-09-26 | 18-EAI-014 | Everton Road - Harrison East 161kV: Rebuild line | Rebuild the ~8.3 mile line segment along with upgrading any station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | AR | BaseRel |  |  | 14890896 | 2025-12-01 | 2025-12-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13625 | 2017-09-26 | 18-EAI-013 | St. Joe - Everton Road 161kV: Rebuild line | Rebuild the ~13.5 mile line segment and upgrade the station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | AR | BaseRel |  |  | 18582810 | 2024-12-01 | 2024-12-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13626 | 2017-09-26 | 18-EAI-012 | Hilltop - St. Joe 161kV: Rebuild line | Rebuild the ~3.9 mile line segment along with upgrading all station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | AR | BaseRel |  |  | 6535668 | 2023-06-01 | 2023-06-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13630 | 2018-05-22 | 18-EAI-024 | Little Rock Fourche - Little Rock East 115kV Rebuild line | Upgrade the ~1.4 mile LR Fourche - LR East 115kV line and all station equipment to achieve a minimum 1492 Amps (297 MVA) flow though rating. | AR | AR | BaseRel |  |  | 2674070 | 2021-06-01 | 2021-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13632 | 2017-09-26 | 18-EAI-029 | Conway South - Conway Industrial 161kV: Rebuild line | Rebuild ~1 mile of the Conway South - Conway Industrial 161kV line and any substation equipment to obtain a minimum flow through rating of 1950 Amos (546 MVA) | AR | AR | BaseRel |  |  | 2087033 | 2020-12-01 | 2020-12-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13635 | 2017-09-26 | 18-EAI-002 | Cheetah - Hot Springs Village 115kV: Rebuild line | Rebuild the ~2.85 mile line segment along with any station equipment to achieve a through path rating of 1300 Amps (259 MVA). | AR | AR | BaseRel |  |  | 4424101 | 2020-12-01 | 2020-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13636 | 2017-09-26 | 18-EAI-005 | Paragould 161/115kV: Install Station Service for Auto | Install station service to power the auto transformer's fans and pumps to operate the auto to a minimum of 110 MVA. | AR | AR | BaseRel |  |  | 532374 | 2021-12-01 | 2021-12-01 | 161 | 115 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 13637 | 2017-09-26 | 18-EAI-001 | Jacksonville North - Holland Bottoms 115kV: Upgrade to 100C Operation | Upgrade all structures and distribution lines to eliminate all clearance issues and upgrade the line to 100C operation. | AR | AR | BaseRel |  |  | 164409 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 14984 | 2018-06-05 | 18-EAI-036 | Moses 161kV: New Breaker Station | A new 4 ring breaker station will be constructed adjacent to the exiting Moses 161kV station due to the demolish project of the retired MOSES plant. | AR | AR | Other | Not Shared | Load Growth | 7438862 | 2019-06-01 | 2019-06-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-AR | 15107 | 2018-05-14 | 18-EAI-035 | Mabelvale 500kV: B8859 Switch Replacement | As part of the MISO TSR (OASIS # 84658477), the Mabelvale 500kV switch B8859 will be upgraded to a 3000 Amp switch. This will increase the rating on the Mabelvale - Wrightsville 500kV line to 2546 MVA. | AR | AR | TDSP | Not Shared |  | 285025 | 2018-12-01 | 2018-12-01 | 500 | 0 | Externally Driven
A in MTEP18 | A | South | Entergy-LA | 9793 | 2017-09-25 | 16-EGL-031 | Esso to Delmont 230 kV: Reconductor Line | Reconductor the Esso to Delmont 230 kV line. | LA | LA | BaseRel |  |  | 2322052 | 2021-06-01 | 2021-06-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 9797 | 2018-08-17 | 16-EGL-036 | Nelson to Lake Charles Bulk 138 kV: Upgrade Structures | Upgrade/Rebuild multiple structures to achieve full 100 deg C rating of conductor | LA | LA | BaseRel |  |  | 8682037 | 2019-08-01 | 2019-08-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 12101 | 2018-09-26 | 17-ELF-001 | East ALP Project: Conrad to Cecelia 230 kV: New Line & 230-138 kV Auto | Construct a 230 kV line from Cecelia to Conrad and install a 230-138 kV auto at new 230 kV Conrad station. | LA | LA | BaseRel |  |  | 105479468 | 2022-06-01 | 2022-06-01 | 230 | 138 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 12105 | 2017-09-25 | 17-ELB-010 | Fancy Point to Horseshoe 230 kV: New 2nd Line | Construct approx. 7 miles of 2nd Fancy to Horseshoe 230 kV line. The new line will be constructed to a minimum of 1900 amps. This line should not share structures with any other line. | LA | LA | BaseRel |  |  | 24610733 | 2021-12-01 | 2021-12-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 12769 | 2018-08-15 | 17-ELC-009 | Goosport 138 kV: Convert Sub from 69 kV | Build new distribution substation | LA | LA | Other |  | Load Growth | 12893410 | 2025-06-01 | 2025-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 12773 | 2018-08-06 | 17-ELS-012 | Chackbay 230 kV: New Substation | Build new distribution substation. | LA | LA | Other |  | Load Growth | 19500747 | 2021-06-01 | 2021-06-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 13890 | 2017-09-25 | 18-ELB-001 | Conway 230-138 kV Auto: Upgrade Substation Equipment | 1) Upgrade the bus work on 138 kV Conway substation to a minimum of 2000 Amp. 2) Replace all 138 kV Conway Oil circuit breakers to a minimum of 2000 Amp GCBs. Also replace all 138 kV switches to a minimum of 2000 Amps. Replace any additional equipment to achieve a final rating of 2000 Amps on the Conway 230-138 kV transformer. | LA | LA | BaseRel |  |  | 2359929 | 2020-04-01 | 2020-04-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 13895 | 2018-08-06 | 18-ELB-003 | Mt. Houmas New 230 kV station | New 230 kV 3 breaker ring bus customer station to replace the Licar substation cut in between the AAC Corp and Belle Helene 230 kV stations. Install 60 MVA 230-34.5 kV transfomer. The Licar station will be decommisioned following the load being moved. | LA | LA | Other |  | Load Growth | 10168815 | 2018-10-01 | 2018-10-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 13902 | 2018-05-10 | 18-ELC-002 | Mossville to Lockmoor 69 kV: Rebuild/Reconductor line | Rebuild or re-conductor the approximately 2.10 mile long Mossville to Lockmoor 69 kV transmission circuit to a minimum of 1200 A, 143 MVA. Open line 253 between Mossville and Alfol 69 kV and designate it as normally open. | LA | LA | BaseRel |  |  | 2968717 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 13909 | 2017-09-25 | 18-ENO-001 | Curran 230 kV: Install breakers | Install breakers at the Curran 230 kV station. | LA | LA | Other |  | Reliability | 3725376 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | Lake Charles Power Station Deliverability Projects | Action Plan: • Reconductor / Rebuild the Nelson – Spanish Trail – Mossville 138 kV line sections (approximately 3.35 miles) using 1272 ACSS conductor and upgrade substation equipment to achieve a through path rating of 1958 A. • Reconductor / Rebuild the Nelson – Mossville 138 kV line section (approximately 3.56 miles) using 1272 ACSS conductor and upgrade substation equipment to achieve a through path rating of 1958 A. • Replace the following breakers at Nelson with 80 kA IPO breakers Substation Breaker Substation Breaker Nelson 138 kV 7925 Nelson 230 kV 13025 Nelson 138 kV 7930 Nelson 230 kV 13030 Nelson 138 kV 7935 Nelson 230 kV 13035 Nelson 138 kV 7940 Nelson 230 kV 13040 Nelson 138 kV 7945 Nelson 230 kV 13140 Nelson 138 kV 7965 Nelson 230 kV 18145 Nelson 138 kV 7980 Nelson 230 kV 18155 Nelson 138 kV 7985 Nelson 230 kV 18160 Nelson 138 kV 7990 Nelson 230 kV 18165 Nelson 138 kV 18640 Nelson 230 kV 18170 Nelson 138 kV 18645 Nelson 230 kV 18175 Nelson 138 kV 18590 Nelson 230 kV 18185 Nelson 138 kV 18595 Nelson 230 kV 18190 Nelson 138 kV 18600 Nelson 230 kV 18210 Nelson 138 kV 18605 Nelson 230 kV 27105 Nelson 138 kV 7900 Nelson 230 kV 37455 Nelson 138 kV 7905 Nelson 230 kV 37460 Nelson 138 kV 7910 Nelson 138 kV 7915 Nelson 138 kV 7920 • Replace the following breakers at Alfol 69 kV and Conoco 138 kV with breakers having interrupting capability of at least 22 kA and 23 kA respectively Substation Breaker Alfol 69 kV 17695 Conoco 138 kV 18035 | LA | LA | GIP |  |  | 50681159 | 2020-02-28 | 2020-02-28 | 230 | 69 | Externally Driven
A in MTEP18 | A | South | Entergy-LA | 15270 | 2018-08-09 | 18-ELS-009 | Leonard 115 kV: New Customer Station | This project is driven by a new Industrial Customer Interconnection. The new 115 kV station will be located east of Highway 308 and will be served on an existing radial 115 kV line from the Clovelly 115 kV station. | LA | LA | Other |  | Load Growth | 1916583 | 2019-09-01 | 2019-09-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA | 15271 | 2018-08-09 | 18-ELB-006 | Luce 230 kV: New Customer Station | This project is driven by a new Industrial Customer Interconnection. The new substation will be located southwest of Geismar near Old Jefferson Highway. The interconnection will cut in and out of the existing 230 kV line between AAC Corp and Licar (Mt. Houmas), at approximately 2.5 miles from AAC Corp 230 kV station. | LA | LA | Other |  | Load Growth | 17932040 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-LA, Entergy-MS | 13867 | 2017-09-25 | 18-EMI-003 | Natchez SES - Red Gum 115 kV: Rebuild line | Rebuild the Natchez SES – Red Gum 115 kV line to a minimum of 1300 Amps or 259 MVA. | MS | LA | BaseRel |  |  | 46013706 | 2021-04-01 | 2021-04-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 9829 | 2017-09-12 | 16-EMI-004 | Ray Braswell 500/115 upgrade 115 kV breakers | Upgrade 2-2500A 115 kV breakers on the low side of the Ray Braswell 500/115 kV autotransformer. | MS | MS | BaseRel |  |  | 1552276 | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 13865 | 2017-09-15 | 18-EMI-001 | Star - Mendenhall 115 kV: Rebuild line | Rebuild the Star to Mendenhall 115 kV line to a minimum of 1300 Amps or 259 MVA. | MS | MS | BaseRel |  |  | 15500045 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 13866 | 2017-09-15 | 18-EMI-002 | Mendenhall - Magee 115 kV: Rebuild line | Rebuild the Mendenhall to Magee 115 kV line to a minimum of 1300 Amps or 259 MVA. | MS | MS | BaseRel |  |  | 11485197 | 2020-12-01 | 2020-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 13899 | 2018-08-27 |  | Build new Redwood Switching Station | Construct a new switching station with breakers at Redwood to increase reliability of the IP Redwood member delivery point and relocate a member communication tower impacted by station construction. | MS | MS | Other |  | Reliability | 3700000 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 13900 | 2018-04-11 | 18-EMI-005 | Flowers Improvement Project | Remove the Flowers SS and tie the existing Tinsley - Flowers SS and Flowers SS - Flowers 115kV line sections together. Construct a new 115kV line from Bovina to Flowers utilizing the existing Bovina to Flowers SS line and extending a new section of line from the Flowers SS area to Flowers. Create a new 115 kV line section from Openwood to Flowers by utilizing the existing Openwood - Bovina 115 kV line section and extending a new section of line from the Bovina area to Flowers. Construct a new 115 kV switching substation adjacent to the existing Flowers substation. | MS | MS | Other |  | Reliability | 21900000 | 2020-12-01 | 2020-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 13908 | 2017-09-15 | 18-EMI-013 | Snowden Park 115kV Substation | Construct new 115kV load serving substation in Southaven, MS that cuts into the Greenbrook to Plum Point 115kV line. | MS | MS | Other |  | Load Growth | 15527746 | 2023-06-01 | 2023-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 13992 | 2017-09-15 | 18-EMI-015 | Pine Tree 115kV Substation | Construct a 115kV line out of Hernando substation to a new substation west of Hernando named Pine Tree 115kV. Add breakers at Hernando. | MS | MS | Other |  | Load Growth | 15678288 | 2023-06-01 | 2023-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-MS | 15084 | 2018-05-08 | 17-EMI-014 | Horn Lake - Allen 161 kV rebuild (to MS/TN state line) | Upgrade the existing 161 kV transmission line from Horn Lake Substation toward Allen SES to a new rating of 430 MVA stopping at the TN/MS state line. Upgrade the relays at Horn Lake to take into account the Freeport cut in. | MS | MS | TDSP |  |  |  | 2022-12-01 | 2022-12-01 | 161 | 0 | Externally Driven
A in MTEP18 | A | South | Entergy-TX | 12066 | 2018-09-04 | 17-ETI-013 | Lewis Creek 138 kV: Install Breaker | Install a 138 kV breaker and construct bus work required to include the Lewis Creek to Alden 138 kV line in a double-bus-double-breaker configuration at Lewis Creek 138 kV. | TX | TX | BaseRel |  |  | 1574517 | 2021-06-01 | 2021-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 12090 | 2018-08-15 | 17-ETI-006 | Longmire to Ponderosa 138 kV: Reconductor Line | • Reconductor/Rebuild the Longmire – Ponderosa 138 kV using approximately 3.13 miles of conductor rated a minimum of 1950 Amps. i. Upgrade CTs at Longmire to a minimum of 2000 Amps. ii. Upgrade line bay riser at Ponderosa to a minimum of 2000 Amps. iii. Upgrade line bay bus and line bay riser at Longmire (Ponderosa line bay - currently 2-649.5 ACAR rated at 1494Amps) to allow for the conductor through path rating of 1957 Amps (468 MVA). iv. During the rebuild of this line section, double circuit structures between Longmire and Ponderosa should be replaced with separate structures for L-106 and L-569 so that the two lines do not share structures for the entire route. v. Longmire to Ponderosa line will continue to be limited by 1600 Amp switches at Longmire (382 MVA) | TX | TX | BaseRel |  |  | 6446221 | 2021-06-01 | 2021-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 12767 | 2018-08-03 | 17-ETI-017 | Timberland 230 kV: New Substation | Build new distribution substation. Station to be cut into the China to Porter 230 kV line. | TX | TX | Other |  | Load Growth | 56123385 | 2021-12-01 | 2021-12-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 13926 | 2017-09-13 | 18-ETI-001 | South Beaumont to Virginia 69 kV: Rebuild/Reconductor | Rebuild approximately 2.77 miles of 69kV line between South Beaumont and Virginia substations. The new line should be rated at least 880A. | TX | TX | BaseRel |  |  | 1292701 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 13929 | 2018-08-16 | 18-ETI-002 | Hankamer 138 kV: Install transformer and add breakers | Install 2nd transformer at Hankamer and add three 138 kV breakers. | TX | TX | Other |  | Load Growth | 7410604 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | Montgomery County Power Station Deliverability Projects | Action Plan: • Construct new 230 kV line from Lewis Creek to Porter with a minimum through path rating of 1956 Amps. Construct a 230 kV ring bus at Porter • Rebuild Lewis Creek – Goree 138 kV line section and upgrade terminal equipment to achieve a minimum through path rating of 1300 Amps • Rebuild Goree - Rivtrin 138 kV line section and upgrade terminal equipment to achieve a minimum through path rating of 1200 Amps • Reconductor/Rebuild Lewis Creek – Sheawill – Fort Worth Pipe 138 kV and upgrade terminal equipment to achieve a minimum through path rating of 1300 Amps Replace the following breakers at Lewis Creek with 63 kA IPO breakers. All breakers at Lewis Creek 138 kV and 230 kV must be 63 kA, IPO breakers. Substation Breaker Lewis Creek 138 kV 1600 Lewis Creek 138 kV 1605 Lewis Creek 138 kV 1615 Lewis Creek 138 kV 1625 Lewis Creek 138 kV 1630 Lewis Creek 138 kV 1635 Lewis Creek 138 kV 1640 Lewis Creek 138 kV 1645 Lewis Creek 138 kV 1650 Lewis Creek 138 kV 1655 Lewis Creek 138 kV 1660 Lewis Creek 138 kV 1665 Lewis Creek 138 kV 26225 | TX | TX | GIP |  |  | 98969890 | 2021-05-30 | 2021-06-01 | 230 | 138 | Externally Driven
A in MTEP18 | A | South | Entergy-TX | 15025 | 2018-05-22 |  | Gibbs 138kV Switching Station | A new ETEC owned 138kV switching station to be constructed in Walker County, TX on the Entergy owned L-509 Cedar Creek to Bishop 138kV transmission line. The new Gibbs switching station will connect to the new Gibbs distribuition substation to serve future Brazos Electric Power Cooperative, Inc (“Brazos”) – Mid-South Synergy member cooperative customer load. | TX | TX | Other |  | Load Growth | 8350500 | 2019-01-15 | 2019-04-15 | 138 | 26.4 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 15105 | 2018-05-10 | 18-ETI-021 | Dobbin: Install 138 kV Line Breakers | Install 2 138kV line breakers at the Dobbin 138 kV substation by the summer of 2020. | TX | TX | Other |  | Reliability | 1700136 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 15106 | 2018-05-10 | 18-ETI-019 | Fish Creek - Ponderosa 138 kV Reconductor | Reconductor the Fish Creek to Ponderosa 138kV transmission line using a minimum of 882 Amperes conductor. Upgrade all equipment to achieve a minimum through path rating of 882A on the Fish Creek to Ponderosa 138 kV line section. | TX | TX | BaseRel |  |  | 5549331 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | South | Entergy-TX | 15331 | 2018-07-23 |  | Stryker 138kV Substation | A new ETEC owned 138KV substation to be constructed in Polk County, TX on the Entergy owned L-93, Corrigan Bulk – Doucette between SHECO Corrigan and Entergy Camden Substations. The new Stryker substation will provide service to the TransCanada (PS 40) pumping station. | TX | TX | Other |  | Load Growth | 3560800 | 2019-10-31 | 2019-10-31 | 138 | 6.9 | Bottom-Up
A in MTEP18 | A | West | GRE | 16304 | 2018-10-18 |  | GRE Winnebago Reactive Installation | 8 Mvar reactive compensation installation at the Winnebago 69 kV substation. The installation specifications will be detailed in an EMTP analysis. Multiple steps of switched capacitors, statcom, or a combination will be used to ensure area VFDs are not impacted. | MN | MN | Other |  | Reliability | 1400000 | 2019-06-30 | 2019-06-30 | 69 | 0 | Bottom-up
A in MTEP18 | A | West | GRE | 8920 | 2017-09-12 | 20477 | Elisha 115/34.5 | Construct a new 115/34.5 kV substation to be named Elisha, build approximately 2.0 miles of 115 kV transmission to interconnect Elisha to the Itasca Mantrap’s Potato Lake, and build approximately 12.0 miles of 69 kV transmission, to be operated at 34.5 kV, to interconnect to Itasca Mantrap’s Pine Point substation. The 230/115/34.5 kV Hubbard substation will retire all of its 34.5 kV assets and the Elisha substation will utilize the remaining 115/34.5 kV transformer at Hubbard. The newly established 34.5 kV loop served by Elisha and Long Lake will have a normally open point at the Osage substation. | MN | MN | Other |  | Reliability | 9432036 | 2020-10-31 | 2020-10-31 | 115 | 34.5 | Bottom-Up
A in MTEP18 | A | West | GRE | 9200 | 2018-05-24 | 203613 | Two Inlets Pumping Station (X1A) | Tap the IM-PT line near Potato Lake substation and build ~7.5 miles of 115kV transmission line to connect the future Two Inlets substation. The substation will supply power to the Enbridge Two Inlets pump station. | MN | MN | Other |  | Load Growth | 5800000 | 2019-10-19 | 2019-10-19 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE | 9201 | 2018-05-24 | 203610 | Backus Pumping Station (X2A) | Build 115 kV line from a new interconnection to the MP?s 115 kV #142 line (Badoura ? Pine River) to the Bull Moose substation - Backus Pump Station | MN | MN | Other |  | Load Growth | 2600000 | 2019-10-01 | 2019-10-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE | 9203 | 2018-09-13 | 203612 | Gowan Pumping Station (X4A) | Build new 115 kV line from the GRE LC-CS line to the Gowan Pumping Station. The project was formerly named Cromwell Pumping Station (X4A) and located at a different site. | MN | MN | Other |  | Load Growth | 943332 | 2019-10-01 | 2019-10-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE | 12206 | 2018-05-28 | 205965 | Benson Cap Bank | Install 14.4 Mvar cap bank at Benson. | MN | MN | BaseRel |  |  | 582643.02 | 2018-01-23 | 2018-01-23 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE | 12211 | 2018-04-03 | 204611 | Lebanon Hills 115 kV | Build 1.25 miles of double circuit 115 kV transmission line to the Dakota Electric Association Lebanon Hills substation. | MN | MN | Other |  | Reliability | 2900274.96 | 2020-05-01 | 2020-05-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE | 13464 | 2017-09-12 | 203796 | Brooks Lake Distribution Substation | Construct 0.2 mile, in/out, 115 kV line from NSP’s Big Swan to Crow River 115 kV line with 795 ACSS conductor to interconnect WHECA’s Brooks Lake distribution substation. GRE will construct the high side, and install two 2000A, 115 kV load break switches and metering equipment at WHECAA’s Brooks Lake substation. | MN | MN | Other |  | Reliability | 650000 | 2019-12-19 | 2019-12-19 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE | 13851 | 2018-08-22 | 206050 | Hawick Re-Route | Construct approximately 4 miles of new 69 kV line. Move and rebuild approximately 2.5 miles of existing 69 kV transmission line to accommodate the MNDOT Highway 23 project near Paynesville. Project schedule determined by MNDOT road move schedule. | MN | MN | Other |  | Reliability | 3269716.97 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE, MP | 9202 | 2018-08-22 | 203611 | Swatara 230 kV Substation (X3A) | The Swatara 230 kV (X3A) Project includes the development of a new, 230 kV tap substation to be called Swatara, interconnecting to the existing Minnesota Power (MP) Riverton – Blackberry 230 kV Line (92 Line). The Swatara tap will source an Enbridge pumping station via 230/6.6 kV transformer as part of their Line 3 Replacement Project and will be located at the intersection of the 92 Line and MP’s +/- 250 kV DC Line. As part of the project, an additional 230 kV “92L” breaker will be required at the Riverton Substation to facilitate operation of the Swatara tap switches. The project was formerly named Palisade Pumping Station (X3A) and served from a different source. | MN | MN | Other |  | Load Growth | 3199370 | 2019-10-01 | 2019-10-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | West | GRE, MP | 13484 | 2017-08-17 | Two Harbors 115 kV Project | Two Harbors 115 kV Project | Reconfigure Two Harbors area system to put GRE Waldo Tap on a radial from Two Harbors. Upgrade Two Harbors - Silver Bay 115 kV Line rating. | MN | MN | BaseRel |  |  | 6913616 | 2019-10-31 | 2019-12-31 | 115 | 0 | Bottom-Up
A in MTEP18 | A | Central | IPL | 13608 | 2017-08-29 |  | Southeast #9 Breaker Replacement | Replacement of one (1) 138 kV breaker at Southeast, #9 | IN | IN | Other |  | Reliability |  | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | IPL | 13924 | 2017-09-13 |  | 132-08 Retirement | 132-08 line retirement | IN | IN | Other |  | Reliability |  | 2019-01-01 | 2019-01-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | IPL | 16228 | 2018-10-05 |  | Gibson - Petersburg 345 kV | Terminal equipment (switches, breakers, relays, bus work) | IN | IN | TMEP | Shared |  | 4300000 | 2021-06-01 | 2021-06-01 | 345 | 0 | Top-Down
A in MTEP18 | A | West | ITCM | 13752 | 2017-12-04 | SndSpring-Hopkinton Retire | ITCM Sand Springs to Hopkinton 34kV Retirement | Retire 34kV line that will no longer be needed. | IA | IA | Other |  | Other Local Needs | 780000 | 2020-12-01 | 2020-12-01 | 34 | 34 | Bottom-Up
A in MTEP18 | A | West | ITCM | 13877 | 2017-12-04 | Cust Interconnect Blanket | ITCM Customer Interconnects with short lead time 2021 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | Other |  | Other Local Needs | 2400000 | 2021-12-31 | 2021-12-31 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ITCM | 13879 | 2017-12-04 | ITCM Asset Blanket | ITCM Asset Replacement Program 2021 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | IA,MN,IL | Other |  | Age and Condition | 37080000 | 2021-12-31 | 2021-12-31 | 345 | 69 | Bottom-Up
A in MTEP18 | A | West | ITCM | 13889 | 2017-12-04 | Ottumwa East Substation | ITCM Ottumwa East 161/25kV Distribution Substation | Alliant Energy is converting the town of Ottumwa to be served off the 161kV system. As part of this plan, load will be transferred off the Excel and Wapello County distribution substations onto the new distribution transformers at Woody. | IA | IA | Other |  | Load Growth | 1886183 | 2019-12-31 | 2019-12-31 | 161 | 161 | Bottom-Up
A in MTEP18 | A | West | ITCM | 13891 | 2017-12-04 | Columbus Junction 14MVAR Cap | ITCM Columbus Junction 69kV 14MVAR Capacitor | Install a 14MVAR capacitor with a synchronous breaker at the Columbus Junction 69kV substation. | IA | IA | Other |  | Reliability | 2542407 | 2019-05-01 | 2019-05-01 | 69 | 69 | Bottom-Up
A in MTEP18 | A | West | ITCM | 13893 | 2017-12-04 | Osage Junction 69kV 7MVAR Capacitor | ITCM Osage Junction 69kV 7MVAR Capacitor | Install a 7MVAR capacitor with a synchronous breaker at the Osage Junction substation. | IA | IA | Other |  | Reliability | 654900 | 2019-05-01 | 2019-05-01 | 69 | 69 | Bottom-Up
A in MTEP18 | A | West | ITCM | 14024 | 2017-12-04 | J041 | ITCM J041 Generator Interconnection | Rebuild Wellsburg 161 kV to a breaker and 1/2 configuration; customer dedicated facilities at Wellsburg (TOIF);161 kV Line relocation; and Newton to Maytag terminal upgrade at Newton | IA | IA | GIP |  |  | 7751624 | 2019-09-01 | 2019-09-01 | 161 | 69 | Externally Driven
A in MTEP18 | A | West | ITCM | 14025 | 2017-12-04 | J438 FCA | ITCM J438 FCA Affected System Upgrade | Replace existing 161/69 kV transformer at Poweshiek | IA | IA | GIP |  |  | 2386020 | 2018-12-14 | 2018-12-14 | 161 | 69 | Externally Driven
A in MTEP18 | A | West | ITCM | 14030 | 2017-12-04 | J407 | ITCM J407 Generator Interconnection | Expand 161 kV ring and add a 161kV terminal at Glenworth; customer dedicated facilities at Glenworth; Replace Glenworth 161/69 kV transformer with a 150 MVA unit | MN | MN | GIP |  |  | 3383715 | 2020-08-07 | 2020-08-07 | 161 | 69 | Externally Driven
A in MTEP18 | A | West | ITCM | 14032 | 2018-10-03 | J449 | ITCM J449 Generator Interconnection | Change relay settings at Mitchell County 345 to allow for project J449 interconnection via common facilities with existing project G172. | IA | IA | GIP | Not Shared |  | 60000 | 2018-09-01 | 2018-09-01 | 345 | 345 | Externally Driven
A in MTEP18 | A | East | ITCT | 4515 | 2018-04-30 | ITC_14_021 | Quaker to Sunset 120 kV Rebuild | Rebuild 0.265 miles of 1431 ACSR using 1431 ACSR X2 and replace limiting station equipment at Quaker and Sunset 120 kV stations. | MI | MI | BaseRel |  |  | 1490000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13326 | 2018-08-03 |  | ITCT Waterman Control Relocation Project | Replace ITCT relaying and controls at Waterman Substation. Locate the new relaying and controls in a new dedicated ITCT control center. Install dedicated ITCT AC and DC systems. | MI | MI | Other |  | Age and Condition | 3300000 | 2020-12-31 | 2020-12-31 | 230 | 120 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13646 | 2018-08-07 |  | Midas 120kV | ITC will construct a new station with a single section breaker, and two line breaker. Station will be fed by looping in the Robin - Wabash 120kV line. | MI | MI | Other |  | Load Growth | 4580000 | 2019-12-20 | 2019-12-20 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13804 | 2018-04-30 | ITC_17_019 | Adams – Burns 2 120 kV Sag Remediation | Remediate the sag limit on the Adams – Burns2 120 kV section to the conductor summer emergency rating of 314 MVA (1512 Amp). | MI | MI | BaseRel |  |  | 222000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13805 | 2018-04-30 | ITC_17_030 | Belle River – St. Clair 345 kV Station Equipment Upgrade | Upgrade the station equipment at St. Clair to a minimum rating of 2200 MVA (3682 Amp) summer emergency. | MI | MI | BaseRel |  |  | 274000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13806 | 2018-04-30 | ITC_17_020 | Bismarck - Jewell 345 kV Sag Remediation | Raise the sag limit on the Bismarck – Jewell 345 kV line to at least 1661 MVA (2780 Amp) summer emergency. Also upgrade the station equipment at Bismarck “BQ” position to at least 1661 MVA summer emergency. | MI | MI | BaseRel |  |  | 340000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13807 | 2018-04-30 | ITC_17_021 | Northeast - Stephens 230 kV Sag Remediation | Raise the Sag Limit on the Northeast – Stephens 230 kV line to at least 700 MVA (1757 Amp) summer emergency. | MI | MI | BaseRel |  |  | 370000 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13809 | 2018-04-30 | ITC_17_022 | Stephens 345 kV – Upgrade DM & DT Station Equipment | Upgrade station equipment at Stephens 345 kV position DM and DT to at least 1540 MVA (2577 Amp) summer emergency. | MI | MI | BaseRel |  |  | 845000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13810 | 2018-04-30 | ITC_17_023 | Elm 120 kV - Upgrade HF Station Equipment | Upgrade station equipment at Elm’s position “HF” to at least 314 MVA (1511 Amp) summer emergency. | MI | MI | BaseRel |  |  | 73000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13811 | 2018-04-30 | ITC_17_024 | Brownstown – Monroe #1 345 kV Station Equipment Upgrades | Upgrade 345 kV station equipment at Brownstown and Monroe so that the summer emergency rating meets or exceeds 2000 MVA (3347 Amp). | MI | MI | BaseRel |  |  | 1076000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13813 | 2018-04-30 | ITC_17_025 | Monroe – Wayne 345 kV Station Equipment Upgrades | Upgrade 345 kV station equipment at Monroe and Wayne so that the summer emergency rating meets or exceeds 1714 MVA (2868 Amp). | MI | MI | BaseRel |  |  | 580000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13814 | 2018-06-20 | ITC_17_026 | Monroe 345 kV – Lallendorf 345 kV Station Equipment Upgrades | Upgrade Monroe 345 kV station equipment so that the summer emergency rating meets or exceeds 2000 MVA (3347 Amp). | MI | MI | BaseRel |  |  | 763000 | 2018-12-31 | 2018-12-31 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13815 | 2018-04-30 | ITC_17_027 | Riverview 120 kV – Upgrade Switches and Trainer | Upgrade 120 kV station equipment at Riverview position “HB” to meet or exceed 424 MVA (2040 Amp) summer emergency. | MI | MI | BaseRel |  |  | 191000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13816 | 2018-04-30 | ITC_17_028 | Pioneer – Superior 120 kV Rebuild | Rebuild approximately 3.16 miles of 477 ACSR to 954 ACSR from Pioneer to McAuley to Superior on double-circuit, 120 kV towers. Upgrade station equipment at Superior to 954 ACSR. Also, 3.16 miles of 477 ACSR conductor of the Noble to Superior 120 kV line that shares common structure with Pioneer – Superior 120 kV will be upgraded to 954 ACSR. Install OPGW on the rebuilt section. | MI | MI | BaseRel |  |  | 4940000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13817 | 2018-04-30 | ITC_17_029 | River Rouge – Zug B 120 kV Rebuild | Rebuild approximately 0.5 mile of 795 ACSR to 954 ACSR and upgrade station equipment at River Rouge position JB to at least 371 MVA (1785 Amp). | MI | MI | BaseRel |  |  | 581000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13818 | 2018-04-30 | ITC_17_031 | Jewell – St. Clair 345 kV Station Equipment Upgrades | The proposed solution is to upgrade station equipment at St. Clair 345 kV position “CM” to at least 2000 MVA (3347 Amp) summer emergency. | MI | MI | BaseRel |  |  | 360000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 13819 | 2018-04-30 | ITC_17_032 | St. Clair – Stephens #2 345 kV – Station Equipment Upgrade | Upgrade station equipment at Stephens 345 kV and St. Clair 345kV stations to at least 1786 MVA (2989 Amp) summer emergency. | MI | MI | BaseRel |  |  | 714000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14007 | 2018-08-03 | ITC-17-040 | Enrico Fermi-Shoal 120kV Rebuild | Rebuild 1.3 miles wood pole circuit from Enrico Fermi to Toll Road 120kV and 3.7 miles wood pole section of the Toll Road - Shoal 120kV circuit utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on both circuits and replace line entrance at Enrico Fermi. | MI | MI | Other |  | Age and Condition | 5085909 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14027 | 2018-08-03 |  | ITCT Customer Interconnections - Year 2021 | Customer interconnection requests and retirements less than $1 million with in service date in year 2021. | MI | MI | Other |  | Load Growth | 2000000 | 2021-12-31 | 2021-12-31 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14064 | 2018-08-03 |  | 2021 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. | MI | MI | Other |  | Age and Condition | 49000000 | 2021-12-31 | 2021-12-31 | 345 | 120 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14068 | 2018-04-30 | ITC_17_036 | Golf – St. Clair 120 kV Station Equipment Upgrades | Upgrade station equipment at St. Clair 120 kV position “JE” to at least 314 MVA (1512 Amp) summer emergency. | MI | MI | BaseRel |  |  | 123000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14069 | 2018-04-30 | ITC_17_037 | St. Clair 120 kV – Upgrade HF-GU-JD Station Equipment | Upgrade station equipment at position “HF” to at least 417 MVA (2004 Amp). Upgrade station equipment at position “GU” to at least 557 MVA (2680 Amp). Upgrade station equipment at position “JD” to at least 450 MVA (2165 Amp). | MI | MI | BaseRel |  |  | 835000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14071 | 2018-04-30 | ITC_17_039 | Trenton Channel 120 kV – Upgrade HJ-IM-IQ Station Equipment | Upgrade station equipment at positions “HJ”, “IM”, and “IQ” to at least 747 MVA (3594 Amp). | MI | MI | BaseRel |  |  | 986000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14284 | 2018-08-03 | ITC_17_044 | Lee DVAR Decommission | Decommission and remove DVAR capacitor and all related equipment at Lee 120 kV position HJ | MI | MI | Other |  | Other Local Needs | 360000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 14804 | 2018-08-03 | ITC_18_005 | Waterman-Cato & Waterman-St. Antoine 120kV UG Cable Relocations | Relocate ~0.5 mile portions of the Waterman-Cato & Waterman St. Antoine underground 120kV cables to allow for MDOT installation of sewer drains under I-75. | MI | MI | Other |  | Other Local Needs | 15000000 | 2019-09-15 | 2019-09-15 | 120 | 0 | Bottom-Up
A in MTEP18 | A | East | ITCT | 15064 | 2018-08-03 | ITC_18_003 | Magneto Interconnection | Construct a new 120 kV 3 breaker station named Magneto and cut in the ITCT Quaker - Southfield 120 kV circuit. Install fiber for relay communication between Quaker and Magneto and between Magneto and Southfield. | MI | MI | Other |  | Load Growth | 5660000 | 2019-06-01 | 2019-06-01 | 120 | 0 | Bottom-Up
A in MTEP18 | A | South | LAFA | 13445 | 2017-12-04 |  | Bonin and Labbe Relay Upgrade | Addition of redundant relays for bus differential protection to the Bonin 138 kV, Bonin 230 kV, and Labbe 230 kV stations. | LA | LA | Other |  | Reliability | 249999 | 2018-12-31 | 2018-12-31 | 230 | 0 | Bottom-Up
A in MTEP18 | A | West | MDU | 13869 | 2018-03-28 |  | Stanley Substation | Rebuild Stanley 115 kV tap to a three position ring bus and replace 115/69 kV transformer | ND | ND | Other |  | Reliability | 4720000 | 2019-12-31 | 2019-12-31 | 115 | 69 | Bottom-Up
A in MTEP18 | A | West | MEC | 2937 | 2017-09-12 | G0103 | Sub 39: Second 345-161 kV Xfmr | Add a second 345-161 kV xfmr. Expand 345 kV and 161 kV buses. | IL | IL | BaseRel |  |  | 12575000 | 2018-12-01 | 2019-12-01 | 345 | 161 | Bottom-Up
A in MTEP18 | A | West | MEC | 13833 | 2018-01-23 | T90E1 | Council Bluffs: Retire 13 kV Reactors | Remove two 25 MVAr 13.8 kV tertiary reactors Council Bluffs from Council Bluffs 345-161-13 kV transformer WL9T1. | IA | IA | Other |  | Other Local Needs | 100000 | 2018-03-31 | 2018-03-31 | 13.8 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13834 | 2017-12-04 |  | Sycamore: Replace Six 69 kV Circuit Breakers | Replace six existing 69 kV circuit breakers at Sycamore Substation with breakers having higher current interrupting ratings. | IA | IA | Other |  | Reliability | 1936000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13835 | 2017-12-04 |  | 109th & Clark: Replace Circuit Switcher |  | IA | IA | Other |  | Reliability | 452000 | 2019-12-31 | 2019-12-31 | 161 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13836 | 2017-10-31 |  | Sub K Tiffin: Add New 345 kV Circuit Breaker | Add a new 345 kV circuit breaker at Sub K Tiffin on the line to Duane Arnold Energy Center. | IA | IA | Other |  | Reliability | 1800000 | 2018-12-31 | 2018-12-31 | 345 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13837 | 2017-12-04 |  | Sub A-Sub 39 Second 161 kV Line | Construct a second 161 kV line from Sub A to Sub 39 in the Quad Cities area. | IL,IA | IL,IA | Other |  | Load Growth | 3700000 | 2020-06-01 | 2020-06-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13838 | 2017-12-04 |  | Sub 18: Third 161-69 kV Transformer | Add a third 161-69 kV transformer at Sub 18 in the Quad Cities area. | IL | IL | Other |  | Reliability | 500000 | 2019-06-01 | 2019-06-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13839 | 2017-12-04 |  | Sub 18: Replace 69 kV Breaker 574 | Replace 69 kV circuit breaker 574 at Sub 18 with a circuit breaker with a higher fault current interrupting rating. | IL | IL | Other |  | Reliability | 220000 | 2018-12-01 | 2018-12-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13840 | 2017-12-04 |  | Sub P: 69 kV Capacitor | Add a new 69 kV capacitor bank at Sub P in Moline, Illinois. | IL | IL | Other |  | Reliability | 950000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 13901 | 2018-08-20 |  | Raccoon Trail Substation | Construct a new Raccoon Trail 345 kV Substation to tap the existing Booneville to Grimes 345 kV line and the existing Fallow Avenue to Grimes 345 kV line. | IA | IA | Other |  | Load Growth | 49620000 | 2020-03-01 | 2020-03-01 | 345 | 25 | Bottom-Up
A in MTEP18 | A | West | MEC | 14108 | 2017-12-04 |  | Lehman Avenue Substation | New distribution substation cutting into the Hills-Sub E 161 kV line. Includes 161 kV line circuit breakers and a 33 MVA transformer. | IA | IA | Other |  | Load Growth | 1900000 | 2020-06-01 | 2020-06-01 | 161 | 13.8 | Bottom-Up
A in MTEP18 | A | West | MEC | 14625 | 2018-08-15 |  | J475/J555 North English | Add one new circuit breaker and associated equipment at the existing Montezuma 345 kV Substation. | IA | IA | GIP | Shared |  | 2750000 | 2018-07-01 | 2018-07-01 | 345 | 0 | Externally Driven
A in MTEP18 | A | West | MEC | 14626 | 2018-08-15 |  | J438 English Farms | Construct a new Deep River 161 kV Substation tapping the existing Poweshiek to Parnell 161 kV line. | IA | IA | GIP |  |  | 4800000 | 2018-12-15 | 2018-12-15 | 161 | 0 | Externally Driven
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | Circuit Breaker Additions and Replacements 2018-2020 | Blanket project to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV and 161 kV circuit breakers to increase reliability and operating flexibility. | IA | IA | Other |  | Other Local Needs | 21970000 | 2018-06-01 | 2020-12-01 | 345 | 161 | Bottom-Up
A in MTEP18 | A | West | MEC | 14985 | 2018-05-29 |  | Franklin 161 kV Switch Replacements | Replace failed 161 kV switches 9210L & 9910L with new 2000 A switches at Franklin Substation. | IA | IA | Other |  | Other Local Needs | 75293 | 2016-04-08 | 2016-04-08 | 161 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 15404 | 2018-08-13 |  | Sub 91 Replace Failed 345-161 kV Transformer | Replace failed 345-161 kV transformer at Sub 91. | IA | IA | Other |  | Other Local Needs | 4500000 | 2018-08-22 | 2018-08-22 | 345 | 161 | Bottom-Up
A in MTEP18 | A | West | MEC | 14664 | 2018-08-15 |  | Clarksville-Waverly West Tap 69 kV Rebuild | Rebuild 7.4 miles of 69 kV poles and conductor from Clarksville Substation to the Waverly West Tap. | IA | IA | Other |  | Age and Condition | 3477000 | 2018-12-01 | 2018-12-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | MEC | 14666 | 2018-08-15 |  | Ackley 161-12.5 kV Substation | New 161-12.5 kV distribution substation tapping the Franklin-Butler 161 kV line with two new 161 kV circuit breakers. | IA | IA | Other |  | Load Growth | 2114000 | 2018-12-01 | 2018-12-01 | 161 | 12.5 | Bottom-Up
A in MTEP18 | A | East | METC | 3135 | 2017-09-14 | METC_17_046 | Airport – Long Rapids 2 138 kV line | Rebuild the Airport – Long Rapids 138 kV line from Long Rapids to Str. #103G100 (~6.3 miles) by replacing the existing single-circuit structures with new double-circuit structures and reinstalling the existing conductor on one side for the Airport – Long Rapids 1 138 kV line and installing new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps) on the other side for the Airport – Long Rapids 2 138 kV line. Utilize the existing assets of the Airport – Mio 138 kV line from Str. #103A7743 to the Airport station’s new location in the construction of the new Airport – Long Rapids 2 138 kV line. Any new conductor used in jumpering from Str. #103G100 to Str. #103A7743 should meet or exceed the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). Acquire new ROW and construct new transmission assets for the Airport – Mio 138 kV line utilizing single-circuit structures heading north from Str. #103A7707 to the Airport station’s new location (~2.6 miles). Install new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). The conductor from Str. #103A7707 to Str. #103A7742 will now be de-energized. Construct Row 4 at the Long Rapids 138 kV switchyard and install the necessary 138 kV station equipment to terminate the Airport 2 138 kV line at Pos. BM4. The summer emergency rating of all new 138 kV equipment should be no less than the summer emergency rating of 477 ACSR conductor (260/1088 Amps). The details of how the new line is connected to Airport are preliminary and will need to be coordinated with Wolverine Power Supply Cooperative (WPSC) as they are the owner of the Airport station. | MI | MI | BaseRel |  |  | 17500000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 3921 | 2018-06-11 | METC-17-054 | Campbell to Tyler 345 kV | The proposed solution is to build approximately 4.1 miles of 345kV line from Campbell to Tyler. Also install a 345/138 kV transformer at Tyler. This project will require new line terminating equipment and protection devices at both stations. Relocate the Campbell-Tyler 138 kV line termination from position “8MB” to position “6MB”. Relocate the Black River-Tyler 138kV line termination from position “6MB” to position “8MB”. Remove the RAS for Campbell 3 345kV breaker 34H9. Remove Campbell Runback Scheme (RAS) on Campbell 3 generator. | MI | MI | BaseRel |  |  | 22528000 | 2021-12-31 | 2021-12-31 | 345 | 138 | Bottom-Up
A in MTEP18 | A | East | METC | 13324 | 2017-06-27 |  | METC Claremont Control Relocation Project | Replace METC relaying and controls at Claremont Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other |  | Other Local Needs | 3300000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13325 | 2017-06-27 |  | METC Dort Control Relocation Project | Replace METC relaying and controls at Dort Substation. Locate the new relaying and controls in a single dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other |  | Other Local Needs | 3300000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13327 | 2017-06-27 |  | METC Beecher Control Relocation Project | Replace METC relaying and controls at Beecher Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other |  | Other Local Needs | 3300000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13329 | 2017-09-22 |  | METC Wealthy Control Relocation Project | Replace METC relaying and controls at Wealthy Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other |  | Other Local Needs | 3300000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13685 | 2017-09-12 | METC-17-031 | Gaines 138kV – Station Equipment Upgrade | The proposed solution is to replace breakers at the Gaines 138kV station. Also increase CTs ratio so that the CTs have a minimum summer emergency rating of 647 MVA/2706 Amps (summer emergency). | MI | MI | BaseRel |  |  | 718000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13687 | 2017-09-12 | METC-17-033 | Morrow 138kV – Station Equipment Upgrade | The proposed solution is to upgrade the station equipment at Morrow position “500” to meet or exceed 338 MVA/1413 Amps (summer emergency). | MI | MI | BaseRel |  |  | 31000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13688 | 2017-09-15 | METC-17-034 | Battle Creek – Verona #1 138kV Rebuild | The proposed solution is to rebuild approximately 3.35 miles of 795 ACSR from Battle Creek-Verona #1 138kV circuit using 1431 ACSR on new future double circuit structures constructed to 230kV standards operated at 138kV. The remaining 0.74 miles of the 4.09 mile circuit already has 1431 ACSR installed and does not need replacement. The other side from structure #088X22006 to Verona will be left vacant and available for a potential future circuit. No changes on the remaining 0.74 mile section that currently has another 138kV circuit on it. Install OPGW along the entire length of the line (~4.09 miles) from Battle Creek to Verona. This project also involves replacing station equipment at Verona 377 position to meet or exceed summer emergency rating of 517 MVA/2163 Amps. | MI | MI | BaseRel |  |  | 6554000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13870 | 2018-01-08 | METC_17_035 | Bauer - Hampton 1 345 kV Sag Remediation | Remediate the sag limit on the Bauer - Hampton 1 345 kV line to a minimum of 1179 MVA/1973 Amps. | MI | MI | BaseRel |  |  | 365000 | 2020-12-31 | 2020-12-31 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13871 | 2017-09-13 | METC_17_042 | Alpena - Rockport 138 kV Sag Remediation | Remediate the sag limit on the Alpena - Rockport 138 kV line to a minimum of 145 MVA/607 Amps. | MI | MI | BaseRel |  |  | 250000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13872 | 2017-09-12 | METC_17_038 | Riggsville - Vanderbilt 138 kV Rebuild | Rebuild the Riggsville – Vanderbilt 138 kV portion (~30.4 miles) of the Livingston – Riggsville 138 kV line (~40.1 miles) utilizing .230 kV double circuit construction. Replace the existing assets (all structures, 266 ACSR conductor, and 266 ACSR line entrances at Rondo and Riggsville) with new double-circuit structures that are designed for 954 ACSR conductor on each side and install this conductor along with OPGW for the existing line only. | MI | MI | BaseRel |  |  | 42000000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13873 | 2018-01-08 | METC_17_036 | MCV - Tittabawassee 1 345 kV Station Equipment Upgrades | Replace station equipment at both ends of the line to increase its summer emergency rating to 1687 MVA (2823 Amps). | MI | MI | Other |  | Reliability | 850000 | 2020-12-31 | 2020-12-31 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13878 | 2018-01-08 | METC_17_037 | MCV - Tittabawassee 2 345 kV Sag Remediation | Remediate the sag limit on the entire ~2.4 mile-long length of 2156 ACSR conductor of the MCV – Tittabawassee 2 345 kV line and replace station equipment at both ends of the line to achieve at least the planned target summer emergency rating of 1687 MVA (2823 Amps). | MI | MI | Other |  | Reliability | 900000 | 2020-12-31 | 2020-12-31 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13934 | 2018-01-08 | METC_17_048 | Pere Marquette 345/138 kV Transformer #1 and Station Expansion | Install a second 345/138 kV transformer at Pere Marquette facilitated through the construction of a new 345 kV switchyard and terminate this transformer along with the existing Ludington – Pere Marquette 345 kV line and 345/138 kV Transformer #2 at it. Install a new Row 9 at the 138 kV switchyard and terminate the new 345/138 kV Transformer #1 and Lake County – Pere Marquette 138 kV line in it. | MI | MI | BaseRel |  |  | 22590000 | 2021-12-31 | 2021-12-31 | 345 | 138 | Bottom-Up
A in MTEP18 | A | East | METC | 13948 | 2018-04-06 | METC_18_011 | Stronach Breaker and a Half Station Rebuild | Rebuild Stronach 138KV station, creating a 3 row breaker and a half station. Connect a new Stronach-Boxboard (CE) 138kV circuit, re-terminate the Pere Marquette, Tippy and Filer City lines into the new station. Reconnect the CE Trans 1 to the new station. | MI | MI | Other |  | Other Local Needs | 10895000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13949 | 2017-09-13 | METC_17_008 | Long Rapids Station | Build a new breaker and half scheme station in a less flood prone location and move all METC Alpena lines into the new station. Build three tie lines between the new station and Alpena’s station. Utilize existing line sections where possible. Remove all METC equipment at the existing Alpena station. | MI | MI | Other |  | Reliability | 13165000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13953 | 2018-03-27 | METC_17_064 | Donaldson Creek WPSC Connections | Expand METC's Donaldson Creek 138kV station to connect two WPSC 138kV circuits (to Rodgers and Plains Jct.). | MI | MI | Other |  | Reliability | 2000000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 13997 | 2017-11-09 | METC-17-053 | Argenta 138kV – Terminal Equipment Upgrade | The proposed solution is to upgrade relaying at Argenta 138kV to meet or exceed summer emergency rating of 602 MVA/2520 Amps. | MI | MI | BaseRel |  |  | 126000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14031 | 2017-09-15 | METC_17_043 | Ransom Ring Bus | The proposed solution is to install two 138 kV breakers and create a ring bus at Ransom station. This will increase reliability and operability of the Ransom 138 kV station and surrounding area. | MI | MI | Other |  | Reliability | 2500000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14040 | 2018-01-08 | METC_17_057 | Keystone 345/138 kV Transformer #2 Replacement | Replace the Keystone 345/138 kV Transformer #2 to increase the facility’s summer emergency rating to 478 MVA/2000 Amps. | MI | MI | Other |  | Reliability | 3700000 | 2020-12-31 | 2020-12-31 | 345 | 138 | Bottom-Up
A in MTEP18 | A | East | METC | 14042 | 2017-10-18 | METC_17_059 | Goss 138 kV Station Equipment Upgrades | Upgrade station equipment at Positions 11W8 and 13W8 at Goss to increase the open breaker summer emergency rating to 585 MVA/2447 Amps and account for open breaker scenarios at each position. | MI | MI | BaseRel |  |  | 475000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14060 | 2018-06-20 | METC_17_072 | Blendon 138KV METC Upgrades | Retire and remove all equipment at METC’s Blendon station. METC to purchase all WPSC assets at Blendon and convert their recently rebuilt 69kV Blendon ring bus station to 138kV (is prebuilt to 138kV). Relocate METC’s Four Mile and Campbell 138kV lines to the new METC station. Relocate Zeeland’s 138kV line to new METC 138kV station. WPSC to convert existing Blendon-Fairview 69kV line to 138kV. | MI | MI | Other |  | Other Local Needs | 4730000 | 2020-02-01 | 2020-02-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14065 | 2018-01-08 |  | 2021 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. | MI | MI | Other |  | Age and Condition | 43500000 | 2021-12-31 | 2021-12-31 | 345 | 138 | Bottom-Up
A in MTEP18 | A | East | METC | 14067 | 2018-05-31 |  | Bradley - Extend METC Connections | Re-terminate the Gaines - Bradley and Warner - Bradley 138kV METC circuits into the new Bradley 138kV WPSC Station | MI | MI | Other |  | Reliability | 506000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14072 | 2017-09-15 |  | METC Customer Interconnections -Year 2021 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2021. | MI | MI | Other |  | Load Growth | 2500000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14107 | 2018-01-08 | METC_15_039 | Weeds Lake Wave Traps for Hiple | NIPSCO is construction a new station to be called Hiple, which will connect to METC's Weeds lake station. Weeds lake will no longer connect to AEP's Robinson Park station. Hiple will have a strong connection to AEP's 765 kV system. METC needs to install wave traps at Weeds Lake on the Weeds Lake to Robinson Park (future Hiple) 345kV line and modify relaying. | MI | MI | Other |  | Other Local Needs | 150000 | 2019-12-31 | 2019-12-31 | 345 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14244 | 2017-10-30 | METC_17_017 | Orr Road Capacitor Decommission | Decommission and remove 75 MVAR capacitor with adjacent breaker and switch at Orr Road 138 kV station. | MI | MI | Other |  | Other Local Needs | 95000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14344 | 2017-10-31 | METC_17_066 | Airport - Hillman Tap 138 kV Sag Remediation | Remediate the sag limit on ~17.0 miles of 266 ACSR conductor of the ~21.3 mile-long Airport - Hillman Tap 138 kV section of the Airport - Mio 138 kV line to at least the planned target summer normal/summer emergency rating of 133 MVA/556 Amps. | MI | MI | BaseRel |  |  | 400000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14424 | 2017-10-31 |  | Cobb-Meyer 138kV Sag Remediation | The proposed solution is to remediate the sag limit on the Cobb – Meyer 138kV line to the full conductor summer emergency limit of 260 MVA (1088 A). | MI | MI | BaseRel |  |  | 2500000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 14464 | 2017-11-30 | METC-17-070 | Battle Creek 138kV - Terminal Equipment Upgrade | The proposed solution is to upgrade relaying at Battle Creek Positions 9MB and 9M9 to meet or exceed 574 MVA/2400 Amps. | MI | MI | BaseRel |  |  | 32000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 15364 | 2018-08-16 |  | Polkton Interconnection | METC will construct Wilson Street 138kV station as a three breaker ring bus. METC will cut in the Cobb – Tallmadge #2 line near tower 1762 about 15 miles from Tallmadge 138kV. Consumers will connect to Wilson Street 138kV using a single 138/46kV transformer with a circuit switcher for highside protection. CE owned Polkton 46kV will be networked having connections to Rochester Products 46kV and Coopersville Jct. 46kV. | MI | MI | Other |  | Load Growth | 4200000 | 2020-03-01 | 2020-03-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 15464 | 2018-10-03 | METC-18-022 | Morenci Interconnection Request | Tap the Moore Road- Beecher 138kV circuit and build approximately 12 miles of new 138kV transmission circuit from the tap to a new substation, tentatively named Morenci. | MI | MI | Other |  | Load Growth | 20703000 | 2020-11-01 | 2020-11-01 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | METC | 15493 | 2018-10-03 |  | J538 Network Upgrades | Build a new 138 kV 3 breaker ring substation named Knowles cut in from the Moore Rd - Beecher 138 kV circuit. OPGW will be installed between Knowles and Moore Rd. | MI | MI | GIP | Shared |  | 6920000 | 2020-10-01 | 2020-10-01 | 138 | 0 | Externally Driven
A in MTEP18 | A | East | METC | 15496 | 2018-10-03 |  | J533 Network Upgrades | Install a 345 kV breaker and 2 disconnects to complete the row at Slate substation. | MI | MI | GIP | Shared |  | 1456000 | 2019-10-01 | 2019-10-01 | 345 | 0 | Externally Driven
A in MTEP18 | A | West | MP | 9646 | 2017-08-22 | Nashwauk 14 Line Upgrade | Nashwauk 14 Line Upgrade | Increase capacity of Nashwauk - 14 Line Tap 115 kV line | MN | MN | BaseRel |  |  | 820000 | 2020-05-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | MP | 9647 | 2017-09-18 | 53 Line Upgrade | 53 Line Upgrade | Increase capacity of existing Nashwauk - National 115 kV Line (53 Line) | MN | MN | BaseRel |  |  | 800000 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | North Shore Transmission Line Upgrades | The North Shore Transmission Line Upgrades project consists of thermal upgrades, reconductored segments, and terminal equipment upgrades on four 115 kV lines within the North Shore Loop between the Arrowhead Substation and the Two Harbors Switching Station. | MN | MN | BaseRel |  |  | 4635000 | 2019-12-31 | 2019-12-31 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | MP | 13485 | 2017-12-05 | Hoyt Lakes 115 kV Project | Hoyt Lakes 115 kV Project | Reconfigure & extend existing Forbes - Laskin 115 kV line to Hoyt Lakes Substation. | MN | MN | BaseRel |  |  | 7000000 | 2020-12-31 | 2020-12-31 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | MP | 13504 | 2018-04-03 |  | Laskin-Tac Harbor Transmission Line Upgrades | Increases the line rating multiple existing transmission lines between Hoyt Lakes and Tac Harbor. | MN | MN | BaseRel |  |  | 1200000 | 2019-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | MP | 13526 | 2018-08-16 | Tioga | Tioga 115/23 kV Substation | Extend existing 115 kV tap from Boswell - Blandin 115 kV Line (MP "27 Line") to new Tioga 115/23 kV Substation | MN | MN | Other |  | Reliability | 2000000 | 2018-12-31 | 2018-12-31 | 115 | 23 | Bottom-Up
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | Blackberry Substation Upgrades | Replaced several aging and overdutied 115 kV and 230 kV breakers at the Blackberry Substation and other substation equipment necessary to optimize facility ratings | MN | MN | BaseRel |  |  | 1130000 | 2019-12-31 | 2019-12-31 | 230 | 0 | Bottom-Up
A in MTEP18 | A | West | MP | 15144 | 2018-05-25 |  | Square Butte East Cap Bank | Relocate existing Bison Cap 230 kV Bank to Square Butte 230 kV Substation | ND | ND | Other |  | Other Local Needs | 150000 | 2018-08-24 | 2018-08-24 | 230 | 0 | Bottom-Up
A in MTEP18 | A | East | MPPA | 14124 | 2017-09-21 |  | Riley 138/69 kV Transformer Addition | This project will provide additional 138/69 kV transformer capacity at the Riley station, with the addition of a second Riley 138/69 kV transformer and associated switching equipment. | MI | MI | Other |  | Reliability | 2450000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | MPPA | 14188 | 2018-05-25 |  | Relocation of Riley 138/69 kV Transformer to Fairview | This project will provide additional Zeeland Import capacity for the forced or maintenance outage of the Blendon to Riley 138kV line and/or Riley 138/69kV transformer, by relocation of the second Riley 138/69kV transformer (project 14124) and associated switching to the Zeeland Fairview station. | MI | MI | Other |  | Reliability | 550000 | 2022-12-31 | 2022-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | MPPA | 14724 | 2018-03-06 |  | Riley 138 kv Line Reroute | Blendon Station Line Reroute project needed for rerouting the Blendon termination of the Blendon to Riley line as part of the Blendon Area Support Project. This project is tied to MPPA project 14188 and Wolverine project 14001 | MI | MI | Other |  | Reliability | 300000 |  |  | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | MRES | 13647 | 2018-03-27 | DLIndReconfig | Detroit Lakes Industrial Substation Reconfiguration | Convert the high-side of Detroit Lakes Industrial Substation from a line breaker configuration to a ring bus configuration. A distribution transformer will also be added. | MN | MN | Other |  | Reliability | 2208000 | 2020-12-01 | 2020-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | MRES | 13648 | 2018-06-20 | AuduCBReplace | Audubon Circuit Breaker Replacements | Replace the 115 kV circuit breakers and 230 kV circuit switcher at Audubon substation (CBs 1415 and 1435, CS 2128). Also, upgrade some outdated RTU equipment. | MN | MN | Other |  | Age and Condition | 500000 | 2019-05-01 | 2019-05-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | MRES | 13852 | 2017-09-11 | DLSthIntrcnct | Detroit Lakes South Substation Interconnection | The substation will interconnect with GRE's Cormorant Jct. to Frazee 115 kV line with a three-way motorized load break switch. There would be radial 115 kV line from this tap point to the Detroit Lakes South Substation. The approximate point of interconnection is 7.09 miles from Frazee on the Cormorant Jct. to Frazee 115 kV line (7.95 miles from Cormorant Jct.). The Detroit Lakes South Substation is expected to have radial tap line of about 2.5 miles going north from the point of interconnection to the new substation. | MN | MN | Other |  | Reliability | 266667 | 2019-10-01 | 2019-10-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | East | NIPS | 15384 | 2018-08-02 |  | Maple to LNG - Maple Substation Conductor | Project will increase the capacity of the Maple to LNG 138 kV line (13812). Current Ratings of the line are SN/SE/WN/WE=138/138/190/197 which is limited by 300Cu substation Conductor. At Maple Substation, replace the 300CU line drop. Also, replace the 300CU and 750CU substation conductor from the 13812 bus side disconnect switch to the bus. New Ratings SN/SE/WN/WE=149/158/190/197. | IN | IN | BaseRel |  |  | 140181 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | NIPS | 15385 | 2018-08-02 |  | Dune Acres Breaker upgrade | Project is to upgrade the 13806 Breaker at Dune acres. Dune Acres transformer is currently operated normally open due to interrupting capability of five existing 138kV circuit breakers at Dune Acres. Four of these breakers are currently scheduled for upgrade under the NIPSCO TDSIC program in the 2019-2021 time frame. The 13806 breaker is not on the TDSIC program and will need to be upgraded to allow the Dune Acres #3 345-138kV Transformer in-service on a normal basis. | IN | IN | BaseRel |  |  | 310234 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | West | OTP | 14056 | 2018-09-21 |  | Parkers Prairie 115/12.5 kV Tap | Parkers Prairie existing 41.6 kV load will be moved to a Parkers Prairie 115/12.5 kV Tap | MN | MN | Other |  | Reliability | 224400 | 2021-11-30 | 2021-11-30 | 115 | 12.5 | Bottom-Up
A in MTEP18 | A | West | OTP | 14057 | 2018-09-28 |  | Veblen 41.6 kV Substation Upgrades | Veblen 41.6 kV relay work is due to thermal issues and inaccurate field data. With newer findings to this study it is determined that 2 stages of 1.35 MVAR cap banks would be needed because of low voltage issues. Substation work including a new control house, an additional 41.6 kV breaker and site expansion is needed due to the addition of the cap banks. | SD | SD | Other |  | Reliability | 1100000 | 2019-09-01 | 2019-09-01 | 41.6 | 0 | Bottom-Up
A in MTEP18 | A | West | OTP | 14059 | 2018-05-29 |  | Bagley North 115kV Switching Station | Bagley North 115 kV Switching Substation - Add 115 kV 3 Circuit Breaker Ring Bus | MN | MN | Other |  | Reliability | 2500000 | 2019-01-31 | 2019-01-31 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | OTP | 15164 | 2018-09-28 | OTP 15164 | Cass Lake Town Conversion to 115 kV Service | Convert the Cass Lake town distribution substation from 69 kV to 115 kV through the installation of a new 10 MVA 115/12.5 kV transformer. The new transformer will be placed in the existing Cass Lake 230/115 kV substation. This project will consist of two facilities: 1. New 10 MVA 115/12.5 kV transformer 2. Modifications to the Cass Lake 230/115 kV substation- The transformer will be utilizing the existing open 115 kV breaker at Cass Lake. | MN | MN | Other |  | Load Growth | 1393000 | 2018-11-30 | 2018-11-30 | 230 | 12.5 | Bottom-Up
A in MTEP18 | A | West | OTP | 15165 | 2018-05-24 | OTP 15165 | Mapleton Town Conversion to 115 kV Service | Convert the Mapleton town distribution substation from 41.6 kV to 115 kV through the installation of a new 10 MVA 115/12.5 kV transformer. The new transformer will be placed in the existing Mapleton 115 /41.6 kV substation. This project will consist of two facilities: 1. New 10 MVA 115/12.5 kV transformer 2. Modifications to the Mapleton 115 / 41.6 kV substation – The new transformer will be utilizing a new 115 kV breaker off of the 115 kV bus in the Mapleton 115 / 41.6 kV substation. | ND | ND | Other |  | Load Growth | 1198700 | 2018-07-15 | 2018-07-15 | 115 | 12.5 | Bottom-Up
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | OTP Lake Norden 115 kV Transmission Project | This project will consist of two phases: 1. Build Radial from Hetland to Lake Norden 2. New 115 kV tie at the planned 345 kV Astoria substation, along with new 115 kV lines from Astoria – Toronto and Toronto – Lake Norden | SD | SD | Other |  | Load Growth | 38052490 | 2019-03-01 | 2020-12-31 | 345 | 12.5 | Bottom-Up
A in MTEP18 | A | Central | PPI | 13950 | 2018-09-17 |  | New Oxville 138 kV Industrial Load | Split the Ballard-Pittsfield 138 kV line into a Ballard-Oxville and Oxville-Pittsfield segment. Construct a 10 mile 138 kV double circuit line from the Ballard-Pittsfield line to the Oxville plant. | IL | IL | Other |  | Load Growth | 12500000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | PPI | 13952 | 2018-08-06 |  | New Meppen 138/69 kV Substation | New Meppen 138/69 kV substation and new 15 mile 69 kV line to from Hardin to Eldred including an Illinois river crossing. | IL | IL | Other |  | Load Growth | 12000000 | 2021-12-31 | 2021-12-31 | 138 | 69 | Bottom-Up
A in MTEP18 | A | Central | PPI | 13960 | 2018-09-17 |  | New Rattlesnake 69/12.47 kV Distribution Substation | New Rattlesnake 69/12.47 kV distribution substation, includes the following... 1) New Rattlesnake 69/12.47 kV substation with a 5/7 MVA transformer 2) New 9 mile Liberty-Rattlesnake 69 kV line. | IL | IL | Other |  | Load Growth | 5700000 | 2022-12-31 | 2022-12-31 | 69 | 12.47 | Bottom-Up
A in MTEP18 | A | Central | PPI | 13964 | 2018-09-17 |  | New Naples 69 kV Capacitor Bank | Add 4.8 MVAR capacitor bank at Naples 69 kV breaker station. | IL | IL | Other |  | Load Growth | 300000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | PPI | 14006 | 2018-08-06 |  | New Walkerville 69 kV Breaker Station | New three breaker station at the Walkerville tap with terminals to Pearl, Roodhouse, and Meppen. | IL | IL | Other |  | Load Growth | 2100000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14074 | 2017-09-15 | 2018SIGE1 | Green Oaks 69/12 Dist. XFMR Repl | Replace 69/12 kV distribution transformer | IN | IN | Other |  | Age and Condition | 1677000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14075 | 2017-09-15 | 2018SIGE2 | Ft. Branch 69/12 Dist. XFMR T2 | Replace 69/12 kV distribution transformer | IN | IN | Other |  | Age and Condition | 1293500 | 2018-12-31 | 2018-12-31 | 69 | 12 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14076 | 2017-09-15 | 2018SIGE3 | St. Meinrad 69/12 kV Dist. XFMR T1 | Replace 69/12 kV distribution transformer. | IN | IN | Other |  | Age and Condition | 1272795 | 2018-12-31 | 2018-12-31 | 69 | 12 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14077 | 2017-09-15 | 2018SIGE4 | Y68 Lynnville - Lynnville Meter Rebuild | Rebuild ~12.3 miles of 69 kV line. Replacing 477 (18/1) ACSR with 477 (26/7) ACSR. | IN | IN | Other |  | Age and Condition | 8195000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14078 | 2018-09-13 | 2018SIGE5 | Boonville Pioneer 199 CB | Replace CB 199 at Boonville Pioneer station | IN | IN | Other |  | Age and Condition | 13700 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14079 | 2017-09-15 | 2018SIGE6 | Broadview 69/12 kV T1 | Replace 69/12 kV dist. transformer T1 at Broadview | IN | IN | Other |  | Age and Condition | 1108400 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14080 | 2017-09-15 | 2018SIGE7 | Lynnville CBs 377 & 477 | Replacing two 69 kV oil breakers at Lynnville station | IN | IN | Other |  | Age and Condition | 274000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14081 | 2017-09-15 | 2018SIGE8 | Z85-2 Heidelbach - Angel Mounds | Rebuild ~6.7 miles of 138 kV line between Heidelbach & Angel Mounds stations | IN | IN | Other |  | Age and Condition | 6263500 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14082 | 2017-09-15 | 2018SIGE9 | Modification 69/12 kV T1 | Replace 69/12 kV dist. transformer at Modification station | IN | IN | Other |  | Age and Condition | 981000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14083 | 2017-09-15 | 2018SIGE10 | Slaughter 69/12 kV T1 & T2 & CB 500 | Replace 69/12 kV dist. transformers T1 & T2, and bus tie breaker (OCB) 500 at Slaughter station | IN | IN | Other |  | Age and Condition | 2240400 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14084 | 2017-09-15 | 2018SIGE11 | Smythe 69/12 kV T1 & T2 | Replace 69/12 kV T1 & T2 at Smythe station | IN | IN | Other |  | Age and Condition | 2216800 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14085 | 2017-09-15 | 2018SIGE12 | Rolling Hills 69/12 kV T1 | Replace 69/12 kV T1 at Rolling Hills | IN | IN | Other |  | Age and Condition | 1138300 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14086 | 2017-09-15 | 2018SIGE13 | Angel Mounds GCBs 188, 288, 200, 177, & 100 | Replace five 69 kV gas circuit breakers (GCBs) at Angel Mounds | IN | IN | Other |  | Age and Condition | 1049000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14087 | 2017-09-15 | 2018SIGE14 | Y58 Loop to Paradise Sub | Build new 69 kV loop feed (~1.8 miles) for Paradise station, currently served from a radial | IN | IN | Other |  | Reliability | 3119500 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14088 | 2018-09-13 | 2018SIGE15 | Y68 Culley - Boonville 69 kV Rebuild | Rebuild ~0.6 miles of 69 kV line from Culley - Boonville station | IN | IN | Other |  | Age and Condition | 973700 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14089 | 2017-09-15 | 2018SIGE16 | Buckwood 69/12 kV T1 & T2 | Replace 69/12 kV dist. transformers T1 & T2 at Buckwood station | IN | IN | Other |  | Age and Condition | 2276600 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14090 | 2017-09-15 | 2018SIGE17 | Civic Center T1 | Replace 69/12 kV dist. transformer and underground exit at Civic Center | IN | IN | Other |  | Age and Condition | 2950000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14091 | 2018-09-13 | 2018SIGE18 | Garvin Sub Loop | Build new 69 kV loop for Garvin station, currently served by a radial | IN | IN | Other |  | Age and Condition | 1742300 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14092 | 2017-09-15 | 2018SIGE20 | Grimm Rd. 69/12 kV T1 | Replace 138/12 kV T1 at Grimm Rd. | IN | IN | Other |  | Age and Condition | 1138300 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14093 | 2017-09-15 | 2018SIGE21 | Mulberry Dist. XFMR T3 & T4 | Replace two dist. transformers at Mulberry station | IN | IN | Other |  | Age and Condition | 3214700 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14094 | 2017-09-15 | 2018SIGE22 | Mt. Vernon 69 kV OCB 177 & 277 | Replace two oil circuit breakers (OCBs) at Mt. Vernon station | IN | IN | Other |  | Age and Condition | 320000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14095 | 2017-09-15 | 2018SIGE24 | New Harmony 69 kV OCB 277 | Replace 69 kV oil circuit breaker (OCB) 277 at New Harmony | IN | IN | Other |  | Age and Condition | 160000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14096 | 2018-09-13 | 2018SIGE25 | Y31 Leonard Rd - Z93 69 kV Rebuild | Rebuild 6.8 miles of 69 kV line from Leonard Rd. station to the Z93 line crossing | IN | IN | Other |  | Age and Condition | 3528600 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | Central | SIGE | 14097 | 2017-09-15 | 2018SIGE26 | Dubois 138 kV OCB 2000 & 3000 | Replace two oil circuit breakers (OCB) 2000 & 3000 at Dubois station | IN | IN | Other |  | Age and Condition | 582000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | SIGE | 15819 | 2018-10-03 | SIGE19-1 | Y36 Lynnville to SR61 Rebuild | Rebuild 4.98 miles of 69 kV line from Lynnville substation to SR61. Include installation of OPGW | IN | IN | Other |  | Age and Condition | 2950000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 12215 | 2018-08-27 |  | West Hattiesburg Delivery Point | In order to serve the West Hattiesburg delivery point reliably and more economically, service will be established through Cooperative Energy's existing 69 kV Line 97 (West Hattiesburg SS - West Hattiesburg) by closing in the switch at the West Hattiesburg Substation. | MS | MS | Other |  | Load Growth | 0 | 2019-01-01 | 2019-01-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13881 | 2017-09-12 |  | Rebuild L59 (Magee - Maddox) 69kV Line | Abandon 2 miles of Line 59 (Magee - Maddox, 6.63 mi.) in the city of Magee and reroute as double circuit along Line 163A. | MS | MS | Other |  | Other Local Needs | 1156000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13882 | 2017-09-12 |  | Rebuild L73 (Rocky Creek - Agricola) 69kV Line | Completely rebuild Line 73 (Rocky Creek - Agricola, 8.2 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Reliability | 2460000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13883 | 2017-09-12 |  | Rebuild L71 (Benndale - Basin) 69kV Line | Completely rebuild Line 71 (Benndale - Basin, 12.14 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Age and Condition | 3642000 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13884 | 2017-09-12 |  | Rebuild L53 (Columbia - Goss GOAB) 69kV Line | Completely rebuild Line 53 (Columbia - Goss GOAB, 9.04 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Age and Condition | 2712000 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13885 | 2017-09-12 |  | Rebuild L37C (Wiggins GOAB - Stillmore) 69kV Line | Completely rebuild Line 37C (Wiggins GOAB - Stillmore, 7.22 mi.) at 161kV construction with more reliable concrete structures. | MS | MS | Other |  | Age and Condition | 3104600 | 2021-06-01 | 2021-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13886 | 2017-09-12 |  | Rebuild L53A (Goss GOAB - Hathorn) 69kV Line | Completely rebuild Line 53A (Goss GOAB - Hathorn, 3.53 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Age and Condition | 1059000 | 2021-06-01 | 2021-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13887 | 2017-09-12 |  | Rebuild L72 (Basin - Agricola) 69kV Line | Completely rebuild Line 72 (Basin - Agricola, 9.15 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Age and Condition | 2745000 | 2021-06-01 | 2021-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13896 | 2017-09-12 |  | Rebuild L33B (Rocky Creek - Sawmill Rd) 69kV Line | Completely rebuild Line 33B (Rocky Creek - Sawmill Road, 5.54 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Age and Condition | 1662000 | 2022-06-01 | 2022-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13897 | 2017-09-12 |  | Rebuild L33D (Sawmill Rd - SE Greene) 69kV Line | Completely rebuild Line 33D (Sawmill Road - SE Greene, 1.39 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | MS | Other |  | Age and Condition | 417000 | 2022-09-01 | 2022-09-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | South | SMEPA | 13898 | 2017-09-12 |  | Rebuild L53B (Hathorn - Oakvale) 69kV Line | Close a fiber path from Columbia to Oakvale by a complete rebuild of Line 53B (Hathorn - Oakvale, 5.33 mi.) with 795 ACSR and OPGW. | MS | MS | Other |  | Other Local Needs | 1599000 | 2022-06-01 | 2022-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | SMPA | 14484 | 2018-08-16 |  | Rutland 161kV Substation - Ring Bus Addition | Add breakers to reconfigure the Rutland substation into a ring bus. Lines and transformers will be altered to avoid loss of both 161/69 transformers for a single breaker failure contingency. | MN | MN | Other |  | Reliability | 2750000 | 2018-12-05 | 2018-12-05 | 161 | 0 | Bottom-Up
A in MTEP18 | A | West | SMPA | 16065 | 2018-10-03 |  | West Owatonna Substation - 161kV Load Interconnection | Re-configuring the existing 161 kV yard to a ring and installing a new 161kV/12.5kV 50MVA transformer in SMMPA's West Owatonna Substation. | MN | MN | Other |  | Load Growth | 1500000 | 2019-09-01 | 2019-09-01 | 161 | 0 | Bottom-Up
A in MTEP18 | A | Central | Vectren | 9953 | 2018-10-03 | SIGE19-17 | New Toyota South Distribution Substation | 138kV/12kV distribution substation for existing customer load expansion. | IN | IN | Other |  | Load Growth | 11500000 | 2019-04-01 | 2019-04-01 | 138 | 12 | Bottom-Up
A in MTEP18 | A | East | WPSC | 4383 | 2018-02-22 | Bradley Xmsn | Bradley New Station | This project alleviates an identified thermal violation on the Bradley to Gaines line which is limited by equipment in the Bradley station. In addition, the current configuration of the Bradley and Wayland stations are not desirable from a planning or protection standpoint. The transformer protection clears the entire 138kV bus, there is primarily electromechanical relaying in the Bradley station and there are oil breakers in the Bradley station. This project will upgrade both the Wayland and Bradley busses to ring bus configurations, put the current 138kV and 69kV stations in a common fence, replace oil breakers with SF6 and bring the design up to current Wolverine standards. | MI | MI | Other | Not Shared | Reliability | 8400000 | 2020-06-01 | 2020-06-01 | 138 | 69 | Bottom-Up
A in MTEP18 | A | East | WPSC | 8222 | 2018-03-06 | Bradley line mods | Bradley Station Line Modifications | This project will construct the line modifications required to route lines into the new Bradley station. | MI | MI | Other |  | Other Local Needs | 1000000 | 2022-12-31 | 2022-12-31 | 138 | 69 | Bottom-Up
A in MTEP18 | A | East | WPSC | 9920 | 2017-08-25 | GRX Station Upgrade | Graves Crossing Station Upgrade | Upgrade the Graves Crossing station | MI | MI | Other |  | Reliability | 500000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 12199 | 2017-09-15 | Grand Traverse Station Upgrade | Grand Traverse Station Upgrade | Upgrade the Grand Traverse Station, including the protection and control system, switches, bus and circuit breakers. Note: The project cost will be split 50/50 between TCLP and Wolverine, the cost for this MTEP project is the total cost of the project. | MI | MI | Other |  | Reliability | 2150000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 12243 | 2017-08-25 | 2020 Battery Bank Replacement Project | 2020 Battery Bank Replacement | This project will replace one battery bank at a Transmission Station. | MI | MI | Other |  | Reliability | 35000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13575 | 2017-08-25 |  | Crawford to Weidman Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | MI | Other |  | Reliability | 9000000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13576 | 2017-08-25 |  | Airport to Hillman Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | MI | Other |  | Reliability | 4500000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13577 | 2017-08-25 |  | Atlanta to Hillman Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | MI | Other |  | Reliability | 11000000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13578 | 2017-08-25 |  | Gun Lake Junction to Otsego Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 336ACSR conductor and OPGW | MI | MI | Other |  | Reliability | 4000000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13579 | 2017-08-25 |  | South Boardman Station Rebuild | The control house and controls will be upgraded to include Wolverine’s standard protection and control system. The existing 69 kV switches limit facility ratings to sub-standard capacity and will be replaced. The existing bus configuration will be upgraded to a ring bus and will be built to 138 kV design. | MI | MI | Other |  | Reliability | 3000000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13580 | 2017-08-25 |  | 2021 Transmission Battery Bank Replacement Project | This project will replace one battery bank at a Transmission Station. | MI | MI | Other |  | Reliability | 35000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | Oden Area Support Project | The Oden area experiences severe undervoltage issues under matenance + contingency conditions. This project will upgrade the conductor, significantly reducing the line impedance, to provide support to the area from the Atlanta and Airport stations. | MI | MI | BaseRel |  |  | 66000000 | 2020-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 13667 | 2017-09-01 |  | Hersey to Leroy Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW. | MI | MI | Other |  | Reliability | 7500000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14000 | 2018-02-22 |  | Burnips to Portland Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | MI | Other |  | Reliability | 29700000 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | Blendon Area Upgrade | This project will provide a third 138kV source into the Blendon station from the Bradley station. The existing 69kV lines between the Bradley and Blendon are constructed to 138kV design and will be converted as part of this project. Additional Projects Associated with the Conversion: Bradley Station - MTEP#4383 Bradley Line Mods (Wolverine) - MTEP#8222 Fairview Station - MTEP#9916 Burnips Station - MTEP#3335 Burnips to Portland Rebuild - MTEP#14000 Other Company Work Required: ZBPW: Fairview Transformer and Associated Equipment MTEP#14188 METC: Blendon 138kV upgrades MTEP#14060 and Bradley Connections MTEP#14067 | MI | MI | Other |  | Reliability | 12000000 | 2020-06-01 | 2024-12-31 | 138 | 69 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14003 | 2017-09-14 |  | Grand Lake Interconnection Line | Construct approximately 0.5 miles of new 138kV transmission line to connect the Grand Lake Distribution Station to METC’s 138 kV Port Calcite to Rockport transmission line. | MI | MI | Other |  | Reliability | 400000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14144 | 2017-09-20 |  | Airport Station 138kV Terminal Addition | The Airport station has been designed for expansion and can accept additional line terminations without major reconfiguration. A structure must be installed for the transmission line termination. A circuit breaker and disconnect switches will be installed in their planned positions. Line relay protection equipment and interconnection metering will be installed. | MI | MI | BaseRel |  |  | 600000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14304 | 2017-10-13 |  | 2019 Fiber Retrofit | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). Install approximately 100 miles per year for four years, starting in 2019 | MI | MI | Other |  | Other Local Needs | 6000000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14326 | 2017-10-13 |  | 2020 Fiber Retrofit | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). Install approximately 100 miles per year for four years, starting in 2019 | MI | MI | Other |  | Other Local Needs | 6000000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14327 | 2017-10-13 |  | 2021 Fiber Retrofit | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). Install approximately 100 miles per year for four years, starting in 2019 | MI | MI | Other |  | Other Local Needs | 6000000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14584 | 2018-01-18 |  | WPSC Pere Marquette Line Relocation | Relocate Pere Marquette to Lake County line termination into Pere Marquette station to coordinate with METC project #13934. | MI | MI | Other |  | Other Local Needs | 250000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14644 | 2018-01-16 |  | Gaylord OCB to Lewiston Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW.(18mi) | MI | MI | BaseRel |  |  | 9000000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | East | WPSC | 14704 | 2018-02-02 |  | Stoney Corners Interconnection Tap | Install tap pole and 2 switches at Stoney Corners road on Richland to Cadillac line section to allow Consumers to interconnect service for new Stoney Corners substation. | MI | MI | Other |  | Reliability | 200000 | 2019-05-01 | 2019-05-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 12011 | 2018-04-13 |  | Bluff Siding Area Reconfiguration | -Upgrade Winona and Goodview bus. -Close normally open from Merrick to Goodview -Close normally open from Goodview 1 to Goodview 2 -Open normally closed from Winona Tap to Goodview Tap -Install remote operators at Winona Tap. | WI | WI | Other |  | Reliability | 2500000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14028 | 2018-04-13 |  | Stanley Distribution Transformer 1 Upgrade | Replace the existing TR1 with a new 28 MVA unit with Load Tap Changers (LTC) | WI | WI | Other |  | Load Growth | 1836000 | 2019-07-01 | 2019-07-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14029 | 2018-04-13 |  | Cable Distribution Transformer Replacement | Replace the existing transformer with a new 7 MVA unit | WI | WI | Other |  | Reliability | 800000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14033 | 2018-04-13 |  | Coulee Ave Transformer Replacements | Replace the aging units at Coulee Ave with 2 new 50 MVA LTC units | WI | WI | Other |  | Age and Condition | 3200000 | 2018-12-31 | 2018-12-31 | 69 | 13.8 | Bottom-Up
A in MTEP18 | A | West | XEL | 14034 | 2018-04-13 |  | Gateway Bus Tie Breaker | Install a bus tie breaker to redue the loss of both Transformers at Gateway. Also install revenue metering | ND | ND | Other |  | Reliability | 470000 | 2018-01-31 | 2018-01-31 | 69 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14035 | 2018-04-13 |  | Twin Cities Fault Current - Aldrich | Open 2x115 kV breakers at Aldrich to create a bypass from St Louis Park to Medicine Lake. Will require the capacity on St Louis Park to Edina 115 kV line to be rerated to 4 ft/sec. Also replace the switch at Edina to increase capacity. | MN | MN | BaseRel |  |  | 1200000 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14036 | 2018-04-13 |  | Twin Cities Fault Current - Terminal | Swap the line terminations of the Gopher and Merriam Park 115 kV lines at Terminal. Swap line terminations of the Arden Hills and the Rose Place 115 kV lines at Terminal. Then open 2x115 kV breakers at Aldrich to create a bypass from Gopher to Rose Place. | MN | MN | BaseRel |  |  | 1200000 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14037 | 2018-04-13 |  | Sauk River - Install 2nd Transformer | Install a second 70 MVA transformer at Sauk River and a new 115 kV breaker | MN | MN | Other |  | Reliability | 2400000 | 2018-12-01 | 2018-12-01 | 115 | 34.5 | Bottom-Up
A in MTEP18 | A | West | XEL | 14038 | 2018-04-13 |  | Wilson Distribution 4th Transformer | This project will install a 4th distribution transformer at Wilson substation. | MN | MN | Other |  | Reliability | 4000000 | 2020-05-01 | 2020-05-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14043 | 2018-04-13 |  | Salida Crossing - New 34.5 kV Transformer | Install a 70 MVA transformer at Salida Crossing and a new 115 kV breaker | MN | MN | Other |  | Load Growth | 3900000 | 2019-06-01 | 2019-06-01 | 115 | 34.5 | Bottom-Up
A in MTEP18 | A | West | XEL | 14045 | 2018-04-24 |  | Louise - Install 2nd Distribution Transformer | This project will install a 2nd 115/13.8 kV 50 MVA transformer, circuit switcher, 2 new feeders, and one 115 kV breaker at Louise substation. | SD | SD | Other |  | Reliability | 4900000 | 2020-05-01 | 2020-05-01 | 115 | 13.8 | Bottom-Up
A in MTEP18 | A | West | XEL | 14046 | 2018-04-13 |  | Falls Capacitor Bank | Install a 30 MVAR capacitor bank at Falls substation. | SD | SD | BaseRel |  |  | 2000000 | 2021-06-01 | 2021-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14047 | 2018-04-13 |  | Lincoln County Capacitor Bank | Install a 30 MVAR capacitor bank at Lincoln County substation. | SD | SD | BaseRel |  |  | 2000000 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14048 | 2018-01-08 |  | Forbes SVC Retirement | The project will retire the existing SVC located at the forbes 500 kV substation | MN | MN | Other |  | Other Local Needs | 1000000 | 2020-06-01 | 2020-06-01 | 500 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14049 | 2018-04-13 |  | Line Relocation for Bottineau LRT | This project relocates a total of 4.25 miles of transmission line within the BNSF Corridor which are affected by the new Metro Blue Line Extension light rail project. | MN | MN | Other |  | Other Local Needs |  | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | Plymouth-Area Power Upgrade | This project is needed for load serving in Plymouth, MN and the surrounding area. This is a joint transmission and distirbution project, and replaces MTEP Project 3773. | MN | MN | BaseRel |  |  | 42300000 | 2017-12-31 | 2020-06-01 | 115 | 13.8 | Bottom-Up
A in MTEP18 | A | West | XEL | 14844 | 2018-04-24 |  | Red Rock Transformer Upgrade | Replace existing 345/115 kV transformers at Red Rock substation. Rebuild the existing 115 kV substation to 3000A 63 kA standard and add bus tie breakers to split the substation for maintenance under high fault current conditions. | MN | MN | BaseRel |  |  | 46000000 | 2023-06-01 | 2023-06-01 | 345 | 115 | Bottom-Up
A in MTEP17 | A | South | AECC | 12603 | 2018-08-22 |  | Olmstead to Zion Hill 115kV line | Olmstead to Zion Hill 115kV line | AR | AR | Other |  | Load Growth | 4500000 | 2018-12-31 | 2018-12-31 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | AECC | 13123 | 2018-08-22 |  | Oppelo 161kV line breakers | Install breakers and relays at Oppelo 161 kV Substation. | AR | AR | Other |  | Reliability | 800000 | 2019-11-01 | 2019-11-01 | 161 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 7801 | 2017-12-08 |  | Reconductor Cahokia-Ashley 138 kV line | Reconductor 2.6 miles of parallel 350 kcmil copper conductor with conductor capable of carrying 2000 A under summer emergency conditions. | MO,IL | MO,IL | BaseRel |  |  | 2200000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 9719 | 2017-12-08 |  | Upgrade Cahokia 3-Cahokia 4 138 kV bus-tie | Upgrade Bus-Tie 3-4 position to 3000 A capability | IL | IL | BaseRel |  |  | 2500000 | 2018-12-01 | 2018-12-01 | 138 | 138 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 9724 | 2017-12-08 |  | Reterminate Newton 345/138 kV transformer No. 1 | Relocate Newton 345/138 kV Xfmr #1 345 kV connection point | IL | IL | BaseRel |  |  | 7300000 | 2018-12-01 | 2018-12-01 | 345 | 138 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 9841 | 2017-12-08 |  | New South Bloomington 138/34.5 kV transformer No. 3 | Install 112 MVA Transformer | IL | IL | Other |  | Load Growth | 5600000 | 2018-09-01 | 2018-09-01 | 138 | 34.5 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 9842 | 2018-09-28 |  | New Hershey substation (formerly Normal East 138/69 kV transformer) | Install new ultimate 6 position ring bus and new 112 MVA, 138-69 kV Transformer. | IL | IL | Other |  | Load Growth | 9100000 | 2020-12-01 | 2020-12-01 | 138 | 69 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 10883 | 2018-08-24 |  | New Ina 138 kV ring bus addition | Install 138 kV ring bus | IL | IL | Other |  | Reliability | 7300000 | 2019-06-01 | 2025-12-01 | 138 | 138 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 10885 | 2017-12-08 |  | Upgrade Cahokia-Ridge 138 kV line | Upgrade terminal equipment at Cahokia and Ridge Substations. | IL | IL | Other |  | Age and Condition | 100000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 11863 | 2017-12-08 |  | Replace Havana 138 kV breakers | Replace six 138 kV breakers | IL | IL | Other |  | Age and Condition | 9400000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 11924 | 2017-12-08 |  | New Mississippi 138 kV substation ring bus | Establish 138 kV ring bus, install 138 kV breaker at Cottage Hills, install 2 miles OPGW from Mississippi to Laclede Tap of Line 1456. | IL | IL | Other |  | Reliability | 9800000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 11945 | 2017-12-08 |  | New Herzog 138 kV substation ring bus | Establish a 3-position initial (6-position ultimate) 138 kV ring bus. | IL | IL | Other |  | Reliability | 6600000 | 2018-10-15 | 2018-10-15 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 11946 | 2017-12-08 |  | New Granite City-23rd Street 138 kV ring bus | Construct 4-position, 138 kV ring bus | IL | IL | Other |  | Reliability | 11600000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 11958 | 2018-04-12 |  | New Campbell-Venice-Hall Street 138 kV double circuit tower Mississippi river crossing | Construct new double-circuit Mississippi River crossing, install 138 kV breakers at Hall Street Substation | MO | IL,MO | Other |  | Other Local Needs | 14300000 | 2018-10-31 | 2018-10-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 11973 | 2017-12-08 |  | New Cane 138 kV breaker station (formerly Grand Island) | Establish a 3-position 138 kV ring bus to connect to the Havana, South-Mason City, West-1406 Line to provide a connection to PPI's Grand Island 138/69 kV Substation. | IL | IL | Other |  | Load Growth | 7900000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | AmerenIL | 12191 | 2017-12-08 |  | New Decatur-Latham 138 kV line (line 1342) | Split line at Latham, install new 138 kV, 2000 A Breaker at Latham Substation, and construct approximately 1 mile of 138 kV line | IL | IL | Other |  | Reliability | 5000000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 7581 | 2017-12-08 | PR06425, F4434, WO601064 | Install 138 kV Forest Jct Inductor | Install a 138 kV 25 Mvar inductor at Forest Jct | WI | WI | Other |  | Reliability | 1762635 | 2020-01-14 | 2020-01-14 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 7600 | 2017-12-08 | PR06459 | Rebuild Sheepskin - Stoughton 69 kV | Rebuild Y-12 Sheepskin to Stoughton with T2-4/0 ACSR | WI | WI | Other |  | Age and Condition | 12524014 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 9930 | 2017-12-08 | PR07296, 602003, 602026 | Uprate Lost Dauphin - Red Maple 138kV | Lost Dauphin - Red Maple 138-kV line uprate. | WI | WI | Other |  | Reliability | 180000 | 2019-09-27 | 2019-09-27 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 9968 | 2017-12-08 |  | Rebuild 138KV Line X-6 Portage - Staff Substation | Rebuild 138KV Line X-6 Portage - Staff Substation. | WI | WI | Other |  | Age and Condition | 12000000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 9974 | 2017-12-08 |  | Rebuild 138KV Line X-98 Staff - North Randolph Substation | Rebuild 138KV Line X-98 Staff - North Randolph Substation. | WI | WI | Other |  | Age and Condition | 5000000 | 2020-07-06 | 2020-07-06 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12031 | 2017-12-08 | PR07555 | Install 69KV Breakers Hilltop SS | Install 69KV Hilltop Breakers | WI | WI | Other |  | Load Growth | 1000000 | 2020-11-01 | 2020-11-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12038 | 2017-12-08 | PR07560, PR07033, F4576 | Install 138KV Breaker Arpin SS | Install 138KV Breaker Arpin SS | WI | WI | Other |  | Load Growth | 5000000 | 2019-05-22 | 2019-05-22 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12044 | 2017-12-08 | PR07559 | Install 69KV Circuit Breaker Wells Street SS | Install Circuit Breaker Wells Street SS | WI | WI | Other |  | Load Growth | 260000 | 2019-03-01 | 2019-03-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12046 | 2017-12-08 | PR07558 | Install 69KV Breaker Whitcomb SS | Install 69KV Breaker Whitcomb SS | WI | WI | Other |  | Load Growth | 1500000 | 2020-12-01 | 2020-12-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12051 | 2017-12-08 | PR07554 | Install 69KV Breaker Harrison SS | Install 69KV Breaker Harrison SS | WI | WI | Other |  | Load Growth | 580000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12054 | 2017-12-08 | PR07552 | Install 115kV Breakers Highway 8 SS | Install 115kv Breakers Highway 8 | WI | WI | Other |  | Load Growth | 1300000 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12058 | 2017-12-08 | PR07515 | Install 138KV Breakers Burlington SS | Install 138KV Breakers Burlington SS | WI | WI | Other |  | Load Growth | 1400000 | 2019-03-01 | 2019-03-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12062 | 2017-12-08 | PR07550 | Install 138KV Breakers Nordic SS | Install 138KV Breakers Nordic Asset SS | WI | WI | Other |  | Load Growth | 5500000 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12100 | 2017-12-08 | PR07527 | Rebuild Waupun 69KV Substation | Waupun Substation Rebuild | WI | WI | Other |  | Age and Condition | 4200000 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12103 | 2017-12-08 | PR07548 | Upgrade 138KV Ellinwood SS | Upgrade 138KV Ellinwood SS. | WI | WI | Other |  | Load Growth | 2400000 | 2019-12-28 | 2019-12-28 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12115 | 2017-12-08 |  | Construct T-D 115KV Baker Street SS | Construct T-D 115KV Baker Street SS | WI | WI | Other |  | Load Growth | 4360493 | 2020-12-31 | 2020-12-31 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12148 | 2017-12-08 |  | Rebuild Cedar Ridge Wind – Mullet River 138kV (X-97) | Rebuild Cedar Ridge Wind – Mullet River 138kV (X-97) | WI | WI | Other |  | Age and Condition | 22800000 | 2020-06-30 | 2020-06-30 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12150 | 2017-12-08 | PR07525, F5011,WO602384 | Rebuild Ohmstead Substation - Cedar Ridge 138kV (X-2) | Rebuild Ohmstead Substation - Cedar Ridge 138kV (X-2) | WI | WI | Other |  | Age and Condition | 6900000 | 2019-09-30 | 2019-09-30 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12177 | 2017-12-08 | PR07233 | Rebuild 69kV Dane Substation – Waunakee SW Station (Y-143) | Rebuild 69kV Dane Substation – Waunakee SW Station (Y-143) | WI | WI | Other |  | Age and Condition | 7000000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12178 | 2017-12-08 | PR4969,F3630,F3636,W00693999,WO069407 | Rebuild 115kV Line Saratoga Substation – Coyne Substation (T-72) | Rebuild 115kV Line Saratoga Substation – Coyne Substation (T-72) | WI | WI | Other |  | Age and Condition | 6600000 | 2020-12-31 | 2020-12-31 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12183 | 2017-12-08 | PR07574, F5182 | Install 69KV Breakers Sycamore SS | Install 69KV Breakers Sycamore SS | WI | WI | Other |  | Load Growth | 1220000 | 2019-12-01 | 2019-12-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12184 | 2017-12-08 | PR07575 | Install 69KV Breakers Manrap SS | Install 69KV Breakers Manrap SS | WI | WI | Other |  | Load Growth | 1336964 | 2019-04-15 | 2019-04-15 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12185 | 2017-12-08 |  | Rebuild 138 KV Butte des Morts - Sunset Point | Rebuild 138 KV Butte des Morts- Neevin - Woodenshoe - Mears Corners - Sunset Point. Line 43021, Line 80952, Line A-79, Line MCRG21 | WI | WI | Other |  | Age and Condition | 20600000 | 2021-06-30 | 2021-06-30 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12346 | 2017-12-08 |  | New T-D Alliant Energy Dane County Substation on Line 13898 | Interconnect a proposed Alliant Energy Dane County Substation to line 13898 via a loop through configuration. | WI | WI | Other |  | Load Growth | 26000000 | 2021-03-31 | 2021-03-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12464 | 2017-12-08 | PR07605 | Install 69KV Breaker Glenview SS | Install 69KV Breaker Glenview SS | WI | WI | Other |  | Load Growth | 750000 | 2018-12-01 | 2018-12-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12465 | 2017-12-08 | PR07604 | Install 138KV Breaker Maplewood SS | Install 138KV Breaker Maplewood SS. | WI | WI | Other |  | Load Growth | 1000000 | 2018-08-31 | 2018-08-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12466 | 2017-12-08 | PR07591 | Install 115KV Breaker Venus SS | Install 115KV Breaker Venus SS. | WI | WI | Other |  | Load Growth | 900000 | 2020-09-15 | 2020-09-15 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12467 | 2017-12-08 | PR07590 | Install 138KV Breakers Howard SS | Install 138KV Breakers Howard SS. | WI | WI | Other |  | Load Growth | 1400000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 12903 | 2017-12-08 | PR07690 | Install 69KV Mount Horeb SS Breakers | Install breaker to Y-175 tap and replace breaker 822-S. | WI | WI | Other |  | Load Growth | 2300000 | 2019-12-28 | 2019-12-28 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13004 | 2017-12-08 | PR07595 | X-53 Series Reactor - Paddock SS | Install a 4.98 Ohm series Reactor in line X-53 at the Paddock SS. | WI | WI | BaseRel |  |  | 6139927 | 2019-05-30 | 2019-05-30 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13064 | 2017-12-08 | PR07710 | Uprate N-144 (McMillan-Wildwood 115 kV line) | Relieve economic congestion on N-144, uprate the line to 144 MVA. | WI | WI | Other |  | Other Local Needs | 187000 | 2018-06-29 | 2018-06-29 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13065 | 2017-12-08 | PR07674 | Construct D-T Plymouth 4 | 138 kV Line Breaker Additions. | WI | WI | Other |  | Load Growth | 2845750 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13066 | 2017-12-08 | PR07673 | Construct Edgerton T-D 138 KV | Edgerton DIC – New Alliant/REC T-D Substation on Line X-31, ATC loop in and out 138 kV bus | WI | WI | Other |  | Load Growth | 1600000 | 2019-07-30 | 2019-07-30 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13067 | 2017-12-08 | PR07648 | Construct Arcadian 138KV D-T | Bus upgrades to accomodate transformer additions. | WI | WI | Other |  | Load Growth | 260000 | 2020-04-01 | 2020-04-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13068 | 2017-12-08 | PR07572 | Construct Tripp Rd 138KV D-T | Upgrade 138 kV line circuit swtichers to circuit breakers. | WI | WI | Other |  | Load Growth | 2000000 | 2019-06-08 | 2019-06-08 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ATC | 13103 | 2017-12-08 | PR07512 | West Riverside GIC J390 Kittyhawk Substation | 345 kV Kittyhawk Substation and 345 kV Line to interconnect the new substation. | WI | WI | GIP | Shared |  | 42067880 | 2019-04-30 | 2019-04-30 | 345 | 0 | Externally Driven
A in MTEP17 | A | West | ATC | 13572 | 2017-12-08 | PR07803 F5305 | Marquette BLP NITS Network Upgrades | Uprate Plains - Arnold 138 kV line 78652 | MI | MI | Other |  | Reliability | 2000000 | 2018-11-09 | 2018-11-09 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | BREC | 12186 | 2017-12-08 | Project No. 1043 | Coleman Cap Bank Modification | This project involves the relocation and upgrade of the existing Coleman Switchyard 161 kV #2 46.8 MVAR capacitor bank to the Coleman EHV substation to reduce the capacitive switching currents between the existing capacitor banks. As part of the project, a power circuit breaker will be added to this bank for maintenance and reliability. | KY | KY | Other |  | Reliability | 345000 | 2017-02-20 | 2017-02-20 | 161 | 0 | Bottom-Up
A in MTEP17 | A | Central | BREC | 12205 | 2017-12-21 | Project No. 1046 | Reid Cap Bank Modification | This project involves the relocation and upgrade of the existing Reid Switchyard 161 kV #1 46.8 MVAR capacitor bank to the Reid EHV substation to reduce the capacitive switching currents between the existing capacitor banks. As part of the project, a power circuit breaker will be added to this bank for maintenance and reliability. | KY | KY | Other |  | Reliability | 350000 | 2017-09-05 | 2017-09-05 | 161 | 0 | Bottom-Up
A in MTEP17 | A | Central | BREC | 12303 | 2017-12-21 | Project No. 1035 | Reid EHV 161/69 KV Substation | The project involves the addition of one (1) 161/69 kV transformer and one (1) 69 kV line terminal in the existing Reid EHV Substation located in Webster County near Sebree, Kentucky. | KY | KY | Other |  | Reliability | 1000000 | 2017-12-31 | 2017-12-31 | 161 | 69 | Bottom-Up
A in MTEP17 | A | Central | BREC | 12304 | 2017-12-08 | Project No. 817 | Wilson to Sacramento 69 kV Line | This system improvement involves 11 miles of new right-of-way (100 foot width) and a terminal addition at the Wilson substation (no physical expansion of the existing substation is necessary). | KY | KY | Other |  | Reliability | 3635000 | 2020-06-30 | 2020-06-30 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12070 | 2017-12-08 |  | CE Breaker Replacement Program - 2018 | Replace damaged or defective circuit breakers with new circuit breakers | MI | MI | Other |  | Age and Condition | 1300000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12071 | 2017-12-08 |  | CE Breaker Replacement Program - 2019 | Replace damaged or defective circuit breakers with new circuit breakers | MI | MI | Other |  | Age and Condition | 1000000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12074 | 2017-12-08 |  | CE Substation Equipment Replacements - 2018 | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI | MI | Other |  | Age and Condition | 860000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12075 | 2017-12-08 |  | CE Substation Equipment Replacements - 2019 | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI | MI | Other |  | Age and Condition | 980000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12077 | 2017-12-08 |  | CE Pole & Line Equipment Replacement Program - 2018 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | MI | Other |  | Age and Condition | 360000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12078 | 2017-12-08 |  | CE Pole & Line Equipment Replacement Program - 2019 | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI | MI | Other |  | Age and Condition | 770000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 12164 | 2017-12-08 |  | Amber 138 kV Bus Rebuild | Rebuild the 138 kV portion of Amber Substation to a five breaker ring bus | MI | MI | Other |  | Reliability | 4800000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | CETO | 14325 | 2017-12-08 |  | Buck Creek 138 kV Substation Expansion | This project consists of two phases. The first phase (phase 1) will complete the Buck Creek 138 kV bus as a breaker-and-a-half design by adding two 138 kV breakers and bus work. The estimated cost for phase 1 is $2.7 million. The expected in-service date of phase 1 is December 31, 2018. The second phase (phase 2) will add two 138 kV line exits to the Buck Creek 138 kV Station to accommodate cutting the Beals Road – Hazelwood 138 kV Line into the station. Phase 2 of this project will be needed to accommodate METC’s project 14324. The estimated cost of phase 2 is $2.8 million. The expected in-service date is December 31, 2020. Relay modifications at Buck Creek may be needed for this project. The estimated total cost of this project (the two phases) is $5.5 million. | MI | MI | BaseRel |  |  | 5500000 | 2018-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | CLECO | 12985 | 2017-12-08 | CLEC | Segura to Teche to Bayou Vista 230 kV line | Build 25 miles of 230 kV construction from Segura substation to Teche substation and 22 miles of 230 kV construction from Teche Substation to Bayou Vista. Expand Teche Substation for a new 3 terminal 230 kV ring. Add a 500 MVA 230/138 kV Auto at Teche Substation. | LA | LA | BaseRel |  |  | 137412079 | 2020-09-24 | 2021-10-25 | 230 | 138 | Bottom-Up
A in MTEP17 | A | South | CLECO, Entergy-LA | 12138 | 2017-12-08 | 17-ELS-010 | Robert 230 kV: New substation | Construct a new 230 kV substation to serve load growth in the area. | LA | LA | Other |  | Reliability | 76454543.26 | 2019-04-01 | 2019-06-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | Central | DEI | 1900 | 2017-12-08 | DIN1730 | Avon Industrial Park 138-12kV new dist sub | Avon Industrial Park - Construct 138-12kV - 22.4 MVA sub in the All Points Industrial Park and 2.5 miles of 138kV line | IN | IN | Other | Not Shared | Load Growth | 3318000 | 2019-06-01 | 2019-06-01 | 138 | 12 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11912 | 2017-12-08 | AMIN1292-2 | Kokomo H.P. 69kV Tertiary Breakers N.C. Operation | Close in Kokomo H.P. Bks 4, 5, and 6 tertiary windings (69kV) after upgrades completed on separate project. | IN | IN | Other |  | Load Growth | 0 | 2018-12-31 | 2018-12-31 | 230 | 69 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11957 | 2017-12-08 | DEI-MTEP2017-1 | Wabash River Station new industrial load | Wabash River Station new industrial load @ 50MW on the 230kV bus section #2 or #3 | IN | IN | Other |  | Load Growth | 300000 | 2021-06-01 | 2021-06-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11983 | 2017-12-08 | DIN1579 | Bracken West 69/12kV Distribution Sub | Bracken West 69/12kV Distribution Sub - North Manchester area on the 6923 ckt. | IN | IN | Other |  | Load Growth | 678000 | 2019-06-01 | 2019-06-01 | 69 | 12 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11984 | 2017-12-08 | TIN1681 | Seymour Cummins to HE Chestnut Ridge 69kV Rebuild | Seymour Cummins Jct to HE Chestnut Ridge 69kV Rebuild - 69156 ckt - use 477acsr - 3.66 miles | IN | IN | Other |  | Load Growth | 4825000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11988 | 2017-12-08 | TIN1538 | Edwardsport to Wheatland 345kV Structural Improvements | Edwardsport to Wheatland 345kV Structural Improvements: insert double deadend structures every 2.5 miles in the 34540 ckt. | IN | IN | Other |  | Reliability | 1790000 | 2018-12-31 | 2018-12-31 | 345 | 0 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11991 | 2017-12-08 | TIN1546 | Whitesville South 230kV and 69kV Ring Buses | Whitesville South 230kV and 69kV add breakers, bus, switches, etc. to complete (2) 3-position ring buses | IN | IN | Other |  | Reliability | 5180000 | 2018-10-01 | 2018-10-01 | 230 | 69 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11992 | 2017-12-08 | TIN1544 | Oakland City 138kV and 69kV Relays | Oakland City 138kV and 69kV Relays - replace relays on all 138 and 69kV line breakers | IN | IN | Other |  | Age and Condition | 5572000 | 2018-12-31 | 2018-12-31 | 138 | 69 | Bottom-Up
A in MTEP17 | A | Central | DEI | 11999 | 2017-12-08 | TIN1712 | Attica 69 to Attica 230 69kV Rebuild | Attica 69 to Harrison Stl Jct to Attica 230 69kV Rebuild - Rebuild 6936 ckt - 4.1 miles with 477acsr and steel poles; also rebuild 1.27 miles of 69121 where it is double circuited | IN | IN | Other |  | Age and Condition | 5601000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | Central | DEI | 12005 | 2017-12-08 | DEI-MTEP2017-2 | Bloomington Rogers St. Substation Upgrades | Bloomington Rogers St. Substation Upgrades: 5-phase project to replace and add distribution/sub-transmission transformers, expand sub site, establish a 138kV breaker-and-a-half bus configuration, and establish a 69kV ring bus. | IN | IN | Other |  | Load Growth | 13271000 | 2017-12-31 | 2021-12-31 | 138 | 12 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 9702 | 2017-12-08 | 16-EAI-016 | Sylvan Hills - Jacksonville North 115kV: Equipment Upgrade | The line is currently limited to 975 Amps by line bay bus at Sylvan Hills. Upgrading the terminal equipment to a minimum rating of 1200 Amps will eliminate the thermal overloads due to breaker failures. | AR | AR | BaseRel |  |  | 128427 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12039 | 2017-12-08 | 17-EAI-003 | Hot Springs EHV - Happy Valley 500kV: Build new line | Tap ANO-Mabelvale and Mayflower-Mabelvale 500 kV lines near the point where the lines start sharing common ROW, to build a new switching station Happy Valley. Build ~35 mile Hot Springs-Happy Valley 500 kV line | AR | AR | BaseRel |  |  | 180272477 | 2024-06-01 | 2024-06-01 | 500 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12041 | 2018-09-05 | 17-EAI-028 | Russellville East 161kV: Add series reactor | Add a 10 Ohm series reactor at Russellville East 161 kV station. | AR | AR | BaseRel |  |  | 6129867 | 2020-06-01 | 2020-06-01 | 161 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12042 | 2017-12-08 | 17-EAI-004 | West Helena: Close N.O. point and install breakers | Close the Normally-Open point at West Helena, and convert the station to a transmission breaker substation. | AR | AR | BaseRel |  |  | 11534538 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12045 | 2017-12-08 | 17-EAI-023 | Independence: Upgraded 500/161 kV autotransformers | Split the current 2-transformer bank into 2 separate transformer banks. Upgrade 500/161 kV auto-transformers at ISES EHV, both rated a minimum of 800 MVA. | AR | AR | BaseRel |  |  | 23138117 | 2019-12-01 | 2019-12-01 | 500 | 161 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12047 | 2017-12-08 | 17-EAI-022 | Greyhawk 161kV: Construct new substation | Construct a new 161kV substation with a 40 MVA 161/13.8kV LTC transformer and four feeder breaker bays. | AR | AR | BaseRel |  |  | 7723996 | 2020-06-01 | 2020-06-01 | 161 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12063 | 2018-08-31 | 17-EAI-026 | Big Creek 115kV: Construct new substation | Construct a new 115kV substation called Big Creek (previously Sheridan East) with two 115kV breakers, a 40 MVA load transformer, and four feeder breakers. | AR | AR | Other |  | Load Growth | 8645632 | 2020-05-01 | 2020-05-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12666 | 2017-12-08 | 17-EAI-012 | MacArthur 115kV: Construct new substation | Construct a new substation on Highway 365 that will include one 40 MVA 115/13.8kV LTC transformer and four feeder breaker bays. | AR | AR | Other |  | Load Growth | 9972694 | 2019-11-01 | 2019-11-01 | 115 | 13.8 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12667 | 2017-12-08 | 17-EAI-017 | Pecan Street 161kV: Construct new substation | Construct a new substation on the Newport to Parkin 161kV line. Install one 40 MVA LTC transformer and one 2000 Amp main breaker with four 1200 Amp feeder breakers. | AR | AR | Other |  | Load Growth | 8053322 | 2019-11-15 | 2019-11-15 | 161 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12669 | 2017-12-08 | 17-EAI-014 | Tarleton 230kV: Construct new substation | Construct a new 230/13.8kV substation with two 20 MVA load transformers. | AR | AR | Other |  | Load Growth | 14692523 | 2019-06-01 | 2019-06-01 | 230 | 13.8 | Bottom-Up
A in MTEP17 | A | South | Entergy-AR | 12745 | 2017-12-08 | 17-EAI-013 | Russellville Industrial 161kV: Construct new substation | Construct a new substation on E. 6th street and Tyler Road in Russellville, AR. Install one 40 MVA 161/13.8kV LTC and four feeder breaker bays. Split the Russellville East D220 and D260 circuits into three feeders. | AR | AR | Other |  | Load Growth | 10499680 | 2020-06-01 | 2020-06-01 | 161 | 13.8 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 4608 | 2017-12-08 | 11-EGL-017 | Five Points to Line Tap 281 to Line 247 Tap- Upgrade 69 kV line | Upgrade the existing Five Points to Line Tap 281 to Line 247 Tap 69 kV line sections to a minimum of 105 MVA | LA | LA | BaseRel |  |  | 4711363 | 2020-12-01 | 2020-12-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | West Monroe Area 230 kV Reliability Improvement Plan | Install 500/230 kV autotransformer at Perryville 500 kV. Construct double circuit 230 kV and utilize existing 230 kV construct facilities to wind up with Perryville - Selman Field - Rilla 230 kV circuit and Perryville - Dunn 230 kV circuit. Install 230/115 kV autotransformers at Dunn and Rilla. Install 230/69 kV auto at Selman Field. | LA | LA | BaseRel |  |  | 119639016 | 2021-06-01 | 2021-06-01 | 500 | 69 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9688 | 2017-12-08 | 16-ELN-007 | Dunn - Winnsboro 115 kV: New line | Construct new 230 kV line (energized to 115 kV) from Dunn to Winnsboro. | LA | LA | BaseRel |  |  | 51127726 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9689 | 2017-12-08 | 16-ELN-008 | Beekman: New distribution substation | Construct a new 115 kV substation on the North Bastrop - Crossett North 115 kV line. | LA | LA | Other |  | Load Growth | 15828104 | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9766 | 2017-12-08 | 16-EGL-007 | Gloria to Flannery REA 69 kV: Reconductor Line | Upgrade the Gloria to Flannery REA 69 kV line section. | LA | LA | BaseRel |  |  | 3127596 | 2019-12-01 | 2019-12-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9781 | 2017-12-08 | 17-ELC-010 | Jennings to Lawtag 69 kV L-13/L-19 and L-14: Rebuild lines | Reconductor both Jennings to Lawtag 69 kV lines (L-13, L-14). | LA | LA | BaseRel |  |  | 7675841 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9798 | 2017-12-08 | 16-ELL-001 | Gypsy to Claytonia 115 kV: Reconductor Line | Reconductor the Gypsy to Claytonia 115 kV line. | LA | LA | BaseRel |  |  | 8072964 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 9804 | 2017-12-08 | 16-ELL-008 | Avenue C to Paris Tap 115 kV: Reconductor Line | Reconductor the Avenue C to Paris Tap 115 kV line. | LA | LA | BaseRel |  |  | 212807 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12040 | 2018-09-06 | 17-ELN-005 | Carson Road - Delhi 115 kV: Rebuild line | Upgrade Carson Road - Delhi 115 kV transmission line to minimum 260 MVA rating. | LA | LA | BaseRel |  |  | 6785081 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12073 | 2017-12-08 | 17-ELB-001 | Ellem 138 kV: New Substation | Reconfigure the local 138 kV network via tying the Monochem to Alchem and Monochem to Southwood 138 kV lines into the new substation adjacent to Geismar 138 kV substation. The new 138 kV substation should be configured as a 6 breaker ring with a minimum rating of 2000A. Increased short-circuit current requires replacement of following 138 kV breakers to a minimum rating of 40KA: Alchem 138 kV Breaker : 14405, 20165 Geismar 138 kV breaker : 14005, 14015 | LA | LA | BaseRel |  |  | 26236261 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12076 | 2017-12-08 | 17-ELC-002 | Mud Lake to Big Lake 230 kV: New Line | Construct a 10 mile 230 kV line from Mud Lake to Big Lake using a conductor rated at a minimum of 1950 A. | LA | LA | BaseRel |  |  | 33036959 | 2022-12-01 | 2022-12-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12079 | 2017-12-08 | 17-ELC-004 | Lake Charles 138-69 kV Autos: Upgrade Autos | Replace the existing Lake Charles Bulk 138-69 kV Autotransformers with 200 MVA units and replace necessary terminal equipment to achieve a through path rating of 200 MVA for each autotransformer. | LA | LA | BaseRel |  |  | 7851334 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12082 | 2017-12-08 | 17-ELC-006 | Goosport to L271 TP to East Broad 69 kV: Upgrade Line | Upgrade line switches at Goosport and Gillis Gas Tap to 1200 A. The new limit will be the conductor at 93 MVA. | LA | LA | Other |  | Reliability | 146395 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12110 | 2017-12-08 | 17-ELF-005 | Meaux 138 kV: Install new breaker | Install new breaker at he Meaux 138 kV substation. | LA | LA | Other |  | Reliability | 1012376 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12112 | 2017-12-08 | 17-ELF-006 | North ALP Project: Cankton 230-138 kV: New Substation & Auto Cankton to Cecelia 230 kV: New line & Auto | Build a new Cankton 230-138 kV substation, construct a 230 kV line from Cankton to Cecelia substation. Install an auto at Cankon and Cecelia. | LA | LA | BaseRel |  |  | 107621804 | 2021-12-01 | 2021-12-01 | 230 | 138 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12120 | 2017-12-08 | 17-ELS-001 | Waterford to Raceland 230 kV: Upgrade Line | Upgrade the line bay riser at Waterford 230 kV to a minimum of 1600 Amps. | LA | LA | BaseRel |  |  | 82726 | 2019-06-01 | 2019-06-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12129 | 2017-12-08 | 17-ELS-005 | Snakefarm 230-115 kV: Add 2nd Auto | Install 2nd 230-115 kV Autotransformer at Snakefarm. | LA | LA | BaseRel |  |  | 12198867 | 2019-12-01 | 2019-12-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12132 | 2017-12-08 | 17-ELS-007 | Jefferson Parish Area Reliability Plan Phase 1 | This project involves: 1) The construction of a new 230 kV substation named Churchill, south of the Ninemile station. Construct a breaker and a half 3000 Amp 230 kV bus to accommodate five 230 kV lines immediately, with room for expansion due to load requests/growth in the area. The Ninemile to Waterford and the Ninemile to Estell 230 kV lines should be cut in an out of Churchill. 2) Build a new 230 kV station at Barataria to accommodate the line from Churchill .The new Barataria 230 kV substation will be configured to a minimum of (3) Breaker ring, rated to a minimum of 3000A .Convert the existing Ninemile to Barataria 115 kV line to Churchill to Barataria 230 kV line (Line is being rebuilt to 230 kV specs by Asset Management).Convert the Barataria to Alliance 115 kV line to 230 kV operation. This line is currently built to 230 kV specs. Expand the 230 kV Alliance substation to a minimum of a three breaker ring with room for expansion to accommodate transmission lines to Oakville, Barataria, and the 230-115 kV Autotransformer. 3) Install a new 230-115 kV autotransformer at Barataria Substation, rated at 300 MVA minimum. Install a new 2nd 230-115 kV autotransformer at Alliance rated at 300 MVA. 4) Once above phases are completed utilize the existing abandoned Ninemile to Barataria 115 kV line to the point shown on the map below(highlighted as Pink line) and extend to Westwego 115 kV substation. The reutilized portion of Ninemile to Barataria 115 kV line will need to be upgraded to a minimum of 1600amps to achieve a final circuit rating of 1600 amps. | LA | LA | BaseRel |  |  | 109013048 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12133 | 2017-12-08 | 17-ENO-001 | Gulf Outlet 115 kV: Add Cap bank | Install a cap bank at the Gulf Outlet 115 kV substation | LA | LA | BaseRel |  |  | 1867901 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12136 | 2018-08-20 | 17-ELS-013 | Cullichia 230 kV: New substation | Construct a new 230 kV substation to replace the existing Arabi substation. Station name is changed to Cullichia. | LA | LA | Other |  | Load Growth | 38956808 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12544 | 2017-12-08 | 17-ELB-011 | Pecue 230 kV: Install transmission breakers | Install line breakers at the Pecue substation. | LA | LA | Other |  | Reliability | 2025727 | 2018-11-01 | 2018-11-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12743 | 2017-12-08 | 17-ELN-008 | Fairbanks 115 kV: Construct new substation | Construct new 115 kV distribution substation on the Sterlington - Swartz 115 kV line circuit. | LA | LA | Other |  | Load Growth | 16730933 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 12770 | 2017-12-08 | 17-ELC-008 | Kim Street 230 kV: New Substation | Build new distribution substation. | LA | LA | Other |  | Load Growth | 22659748 | 2020-10-31 | 2020-10-31 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-LA | 13999 | 2017-12-08 | 17-ELC-002 | Carlyss 230-138 kV Autotransformer: Upgrade Station Equipment | •Replace two air break switches (17549 and 17551) at Carlyss 138 kV to a minimum of 1600 A •The 138 kV bus and the line bay bus at Carlyss (138 kV autotransformer line bay) will also be upgraded to at least 1600 A •Rating on Carlyss 230/138kV transformer increases to 300MVA from 243MVA | LA | LA | Other |  | Other Local Needs | 267776 | 2019-12-31 | 2019-12-31 | 230 | 138 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 7906 | 2017-12-08 | 15-EMI-004 | Greenwood to Greenwood SS 115 kV: Upgrade line | Upgrade Greenwood - Greenwood SS 115 kV from 70 MVA to at least 239 MVA. | MS | MS | BaseRel |  |  | 9319353 | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 7914 | 2017-12-08 | 15-EMI-008 | Medical Center Solution: Constuct new 115 kV substation and upgrade 115 kV line | Construct new 115 kV breaker station on Monument Street - Fondren 115 kV line to provide second distribution load serving source to Medical Center complex. Construct new Rex Brown - NEW breaker station 115 kV utilizing the existing HICO - Fondren 115 kV line path to minimum 260 MVA. | MS | MS | BaseRel |  |  | 31298368 | 2020-12-01 | 2020-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12023 | 2017-12-08 | 17-EMI-002 | Conehoma Creek - Carthage 115 kV: Upgrade line | Likely rebuild of facility to upgrade line capacity to 260 MVA. Facilities will be reconstructed to 230 kV specifications. | MS | MS | BaseRel |  |  | 13375147 | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12024 | 2017-12-08 | 17-EMI-003 | Carthage - Scott 115 kV: Upgrade line | Likely rebuild of the 14.49mi long line from Carthage - Scott 115 kV to minimum 260 MVA rating. The line will be reconstructed to 230 kV specifications. | MS | MS | BaseRel |  |  | 13213965 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12025 | 2017-12-08 | 17-EMI-004 | Scott - Pelahatchie 115 kV: Upgrade line | Upgrade 16.79mi from Scott - Pelahatchie to a minimum rating of 260 MVA. The facilities will be reconstructed to 230 kV specifications for potential future conversion. | MS | MS | BaseRel |  |  | 18711399 | 2021-12-01 | 2021-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12027 | 2017-12-08 | 17-EMI-005 | Henderson Road 230 kV: New substation | Construct new Henderson Road 230 kV substation on the Lakeover - Rankin 230 kV circuit. Due to the number of customers on the line circuit, transmission breakers will also be installed at Luckney to reduce customer exposure. | MS | MS | BaseRel |  |  | 17687485 | 2019-06-01 | 2019-06-01 | 230 | 13.8 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12029 | 2017-12-08 | 17-EMI-006 | Byhalia 230 kV: New distribution substation | Construct new substation in eastern Desoto County, MS along currently under-construction I-69 corridor. | MS | MS | Other |  | Load Growth | 17337028 | 2021-06-01 | 2021-06-01 | 230 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12207 | 2018-08-27 |  | Carter 115kV Delivery Point | The Carter delivery point requires installing one (1) 115kV switching station with 3 motor operated switches within the distribution substation fence. | MS | MS | Other |  | Load Growth | 1660000 | 2019-05-01 | 2019-05-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12208 | 2018-08-27 |  | Holmsville 115kV Delivery Point | The Holmesville delivery point requires installing one (1) 115kV switching station with 3 motor operated switches within the distribution substation fence. | MS | MS | Other |  | Load Growth | 2060000 | 2019-05-31 | 2019-05-31 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12219 | 2017-12-08 |  | Install new Switching Station at Acona | Install a new switching station with breakers at Acona. | MS | MS | Other |  | Reliability | 3760000 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-MS | 12824 | 2017-12-08 | 17-EMI-010 | Coldwater 115kV: Install transmission breakers | Installation of substation transmission breakers at the Coldwater 115 kV substation in Brandon, MS, which is located on the Batesville - Getwell 115 kV transmission circuit. | MS | MS | Other |  | Reliability | 4673908 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-TX | 4623 | 2017-12-08 | 13-ETI-014 | Panorama to Longmire 138 kV Line: Reconductor | Reconductor approximately 2.73 miles of 138 kV line to a minimum of 468 MVA ( 1272 ACSS). The line rating will continue to be limited by the 1494 amp Line Bay Bus and Risers at Longmire (357 MVA). Line Bay Bus and risers at Panorama (currently 649.5 ACAR rated at 860 amps and 1033 AAC rated at 1017 amps) will also need to be replaced to meet or exceed the conductor rating of 468 VA (1957 amps). | TX | TX | BaseRel |  |  | 3647461 | 2020-04-01 | 2020-04-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-TX | 12763 | 2017-12-08 | 17-ETI-014 | Commerce 138 kV: New Substation | Build new distribution substation to serve load. | TX | TX | Other |  | Load Growth | 12199370 | 2020-05-15 | 2020-05-15 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | Entergy-TX | 13864 | 2017-12-08 |  | Hartburg to Sabine Junction 500 kV Economic Project | Construct a new 500/230kV substation. Re-configure the existing Sabine to McFadden and Sabine to Nederland 230 kV transmission lines into the new substation. Construct a new 500kV line from Hartburg to New Substation. Install a new 500/230kV 1200 MVA transformer at the new substation. | TX | TX | MEP | Shared |  | 129679192 | 2023-06-01 | 2023-06-01 | 500 | 230 | Top-Down
A in MTEP17 | A | South | Entergy-TX | 14002 | 2017-12-08 | 17-ETI-023 | Sam Rayburn to Doucette 138 kV: Upgrade Line Rating | •Replace 26 transmission structures on the Sam Rayburn to Fort Creek to Turkey Creek to Doucette 138kV transmission line •Rating increases to 137MVA from 112MVA | TX | TX | Other |  | Other Local Needs | 796387 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | ETEC | 8203 | 2017-12-08 | SHECO_03_MTEP17 | Fred SW - Fred 138kV | Construct new Fred switching station on Dogwood-Warren 138 kV line, construct new 138kV Fred substation, construct new 138 kV line from Fred switching station to new Fred substation. | TX | TX | Other |  | Reliability | 24200000 | 2020-08-01 | 2020-08-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | ETEC | 11990 | 2017-12-08 | SHECO_01_MTEP17 | Staley 138kV Station Upgrade | Upgrade SHECO Staley 138kV substation to 6 BKR ring bus configuration. Cut-in existing ETI 138kV line 419 Rivtrin - Gulf Trinity and connect into Staley 138kV substation | TX | TX | BaseRel |  |  | 4650000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | ETEC | 12883 | 2018-02-22 | SHECO_04_MTEP17 | Corrigan 138kV Station Upgrade | Upgrade of existing switch substation with addition of 138kV line breakers for through-bus operation | TX | TX | Other |  | Reliability | 900000 | 2019-10-25 | 2019-10-25 | 138 | 0 | Bottom-Up
A in MTEP17 | A | South | ETEC | 12884 | 2018-02-22 | SHECO_05_MTEP17 | Deer 138kV Station Upgrade | Upgrade of existing switch substation with addition of 138kV line breakers for through-bus operation | TX | TX | Other |  | Reliability | 900000 | 2019-10-25 | 2019-10-25 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12006 | 2017-12-08 |  | McHenry 230 kV Ring Buildout | The McHenry substation expansion is to accommodate a new 230 kV line being built by Xcel Energy to serve Minot area load. GRE will design a five breaker ring bus that will have 4 positions filled including the new line and the existing 230/115 kV transformer and 230 kV lines to Coal Creek/Stanton and Balta. | ND | ND | Other |  | Reliability | 5682611.09 | 2018-11-06 | 2018-11-06 | 230 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12104 | 2017-12-08 | 204551 | Burnsville-River Hills Rebuild/Reconductor | Rebuild 1.11 mile 4/0 ACSR conductor along the Burnsville to River Hills 69 kV line (DA- BR line) with 795 ACSS conductor to 115 kV standards. This line will continue to operate at 69 kV, but design and construction will be to 115 kV standards for future 115 kV operation. | MN | MN | Other |  | Reliability | 2610042.43 | 2019-02-14 | 2019-02-14 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12106 | 2017-12-08 | 204296 | Scenic Substation 69 kV Project | Build 13.5 mile 69 kV tap line to a new North Itasca distribution substation. | MN | MN | Other |  | Reliability | 6022225.3 | 2020-05-29 | 2020-05-29 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12117 | 2017-12-08 | 204636 | Moon Lake Breaker Project | Install new breaker station at the Lake Wilson distribution site and string one mile of conductor on new Xcel double-circuit 69 kV line from Chandler tap to the Moon Lake Breaker Station. Formerly known as Lake Wilson Breaker Project. | MN | MN | Other |  | Reliability | 3726311 | 2019-09-30 | 2019-09-30 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12122 | 2017-12-08 | 204146 | Knife Falls 115 kV Project | Build 1.0 mile of 115 kV transmission to the new Lake Country Power Knife Falls substation. Formerly known as Brevator. | MN | MN | Other |  | Load Growth | 968851.61 | 2018-09-28 | 2018-09-28 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12165 | 2017-12-08 | 204147 | Vermillion 69 kV Project | Build 0.5 miles of 69 kV transmission line to Lake Country Power's upgraded Vermillion 69 kV distribution substation. | MN | MN | Other |  | Load Growth | 1013275.56 | 2019-09-30 | 2019-09-30 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | GRE | 12166 | 2017-12-08 | 204191 | Star Lake Casino 41.6 kV Project | Build approximately 10.0 mile 41.6 kV transmission line to interconnect the new substation to Lake Region Electric Cooperatives existing, Maine substation. | MN | MN | Other |  | Load Growth | 5475331.01 | 2018-01-01 | 2018-01-01 | 41.6 | 0 | Bottom-Up
A in MTEP17 | A | Central | HE | 13528 | 2017-12-08 |  | Worthington-Linton Junction 138kV Line Upgrade | Upgrade 138 kV Line from Worthington - Linton Junction | IN | IN | Other | Not Shared | Reliability | 650000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | IPL | 12483 | 2017-12-08 |  | Guion Substation #10 Breaker Replacement | Replacement of one (1) 138 kV breaker at Guion Substation; Breaker #10. | IN | IN | BaseRel |  |  | 300000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | IPL | 13424 | 2017-12-08 |  | Georgetown - Westlane line Rating Upgrade | Upgrade Georgetown - Westlane line to 343 MVA | IN | IN | BaseRel |  |  | 0 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | ITCM | 10783 | 2017-12-08 | Lore-Gardners lane TEQ | Lore-Garndners Lane 69kV Terminal Upgrades | Upgrade terminals at Lore and Gardeners Lane, to improve line rating. At Gardner's Lane, retire the transfer bus and associated equipment and add a 69kV synchronous breaker to tie the existing cap bank to the 69kV bus. | IA | IA | Other |  | Reliability | 559108 | 2018-06-06 | 2018-08-01 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 11963 | 2017-12-08 | Squash Bend | North Liberty Squash Bend Customer Interconnection | Connect new distribution customer Squash Bend substation in North Liberty, IA. | IA | IA | Other |  | Load Growth | 2600000 | 2018-07-01 | 2018-07-01 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 11964 | 2017-12-08 | Oak Hill-Marion 69kV Conv | Oak Hill-Marion 34.5 to 69kV Conversion | Convert 34.5 kV system between Oak Hill and Marion to 69 kV operation | IA | IA | Other |  | Age and Condition | 1396466 | 2019-12-31 | 2019-12-31 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Convert 34.5 kV system in Marshalltown - Grand Junction area to 69 kV operation. | IA | IA | Other |  | Age and Condition | 21875845 | 2017-12-21 | 2027-05-01 | 69 | 34 | Bottom-Up
A in MTEP17 | A | West | ITCM | 11974 | 2017-12-08 | Mediapolis-New London | Mediapolis-New London Tap 69kV Rebuild | Rebuild 6.61 miles of 69 kV line from Mediapolis to New London Tap. | IA | IA | Other |  | Age and Condition | 5460000 | 2019-02-05 | 2019-02-05 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Convert the 34.5 kV system between Anita and Grand Junction to 69 kV operation, with associated line conversions, breaker stations and transformers. | IA | IA | Other |  | Age and Condition | 21602220 | 2020-12-31 | 2025-12-31 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 12167 | 2017-12-08 | J416 | J416 Generator Interconnection | Construct new Quinn 345 kV Switching Station as Network Upgrade and approximately 9.5 miles of 345 kV gen-tie line as TOIF. | IA | IA | GIP | Shared |  | 26230018 | 2019-04-01 | 2019-04-01 | 345 | 345 | Externally Driven
A in MTEP17 | A | West | ITCM | 12168 | 2017-12-08 | J278 | J278 Hazleton-Mitchell 345kV Uprate | Raise structures on the Mitchell to Hazelton 345 kV line to achieve 995 MVA summer rating. | IA | IA | GIP | Shared |  | 3360000 | 2020-12-31 | 2020-12-31 | 345 | 345 | Externally Driven
A in MTEP17 | A | West | ITCM | 12200 | 2017-12-08 | Cust Interconnect Blanket | ITCM Customer Interconnects with short lead time 2020 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | Other |  | Load Growth | 2400000 | 2020-12-31 | 2020-12-31 | 345 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 12201 | 2017-12-08 | ITCM Asset Blanket | ITC Midwest Asset Replacement Program 2020 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | IA,MN,IL | Other |  | Age and Condition | 37080000 | 2020-12-31 | 2020-12-31 | 345 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | Kalona-Iowa Junction 34.5 to 69kV Conversion | Convert the 34.5kV system between Kalona and Iowa Junction to 69kV operation, with associated line conversion & breaker stations. | IA | IA | Other |  | Age and Condition | 14526178 | 2018-12-31 | 2023-12-31 | 69 | 34 | Bottom-Up
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | Eastern Iowa Wyoming Area 69kV Conversions | Eastern Iowa Study Wyoming Area Conversion Projects: Upgrade the Wyoming Substation - add 69kV terminals. Wyoming to Monticello Industrial line conversion. Wyoming to Bennett conversion. Wyoming to Maquoketa conversion. Wyoming to Wyoming REC conversion. Wyoming to Dixon conversion. | IA | IA | Other |  | Age and Condition | 25968200 | 2018-12-31 | 2021-12-31 | 161 | 34.5 | Bottom-Up
A in MTEP17 | A | West | ITCM | 13083 | 2018-05-03 | Van Allen | ITCM Van Allen 69kV Distribution Interconnection | Construct a new 69/12.5kV substation with a 33 MVA TRF and two 69kV line breakers. Tap the existing Rock Creek-Mill Creek 69kV line about 1 mile from the Mill Creek substation. Install OPGW from the Rock Creek terminal 161 out to the new Van Allen distribution substation ~4 miles. The transformer will have dual low side voltage (25/12.5kV) for a future conversion to 25kV. The conversion will require upgrading to a 69/25kV 50MVA transformer and the smaller dual low side unit will be moved by Alliant to another location (10-20 years out). The new Van Allen substation will serve a portion of the existing Mill Creek and 2nd Avenue loads. The 2nd Avenue substation will then be retired (sketched separately) and the Mill Creek substation will remain with a reduced load of ~5MW. | IA | IA | Other |  | Load Growth | 4613724 | 2019-12-31 | 2019-12-31 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM | 13084 | 2017-12-08 | West Okoboji | ITCM West Okoboji Lakes 69kV Interconnection | Construct a new 69/25kV distribution substation with a single 20MVA transformer. ITC will install a bus tie breaker and a single line breaker initially. A second line breaker will be added when IPL installs a second transformer. This sub will tap the Pelican-Triboji #1 69kV circuit. | IA | IA | Other |  | Load Growth | 2434935 | 2019-04-16 | 2019-04-16 | 69 | 69 | Bottom-Up
A in MTEP17 | A | West | ITCM, MEC | 13644 | 2017-12-08 |  | J412 | J412 Network Upgrades and Interconnection Facilities | IA | IA | GIP | Shared |  | 10000000 | 2019-10-01 | 2019-10-01 | 345 | 0 | Externally Driven
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 6-Wire Trenton Channel - Jefferson 120 kV Circuits | Six-wiring the Trenton Channel-Jefferson #4 120 kV and Trenton Channel-Horn-Jefferson 120 kV circuits with the existing decommissioned lines on their common structures. This will also require the construction of approximately 0.16 mile of double circuit 954 ACSR to complete the loop in-and-out of Horn station. Additionally, rebuild approximately 0.3 mile of 954 ACSR conductor to 1431 ACSR on the Jefferson-Riverview #2 120 kV circuit. Upgrade the station equipment at Trenton Channel, Horn, Jefferson, and Riverview. Also, remediate the Sag on Trenton Channel-Horn 120 kV, Horn-Riverview 120 kV, and Jefferson-Riverview #2 120 kV lines to the conductor limit. | MI | MI | BaseRel |  |  | 1700000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 12004 | 2017-12-08 | ITCT_16_022 | Elm 230 kV Line Breakers | Install two 230 kV line breakers at the Elm 230 kV station to terminate the Brownstown - Elm #2 and Elm - Rotunda 230 kV lines. | MI | MI | Other |  | Reliability | 3000000 | 2019-12-31 | 2019-12-31 | 230 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 12187 | 2017-12-08 |  | ITCT Pole Top Switch Additions/Replacement Program 2019 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | Other |  | Age and Condition | 2400000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 12188 | 2017-12-08 |  | ITCT Pole Top Switch Additions/Replacement Program 2020 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | Other |  | Age and Condition | 2400000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 12193 | 2017-12-08 |  | 2020 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Other |  | Age and Condition | 58100000 | 2020-12-31 | 2020-12-31 | 345 | 120 | Bottom-Up
A in MTEP17 | A | East | ITCT | 12194 | 2017-12-08 |  | ITCT Customer Interconnections - Year 2020 | Customer interconnection requests and retirements less than $1 million. | MI | MI | Other |  | Load Growth | 2000000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 12443 | 2017-12-21 | ITC_16_031 | Nitro Interconnection | Construct the new 120 kV Nitro station. Station will be two disconnected busses. Station will be fed by taping the Coventry - Baltic 120kV line and the Hager - Hines 120kV line | MI | MI | Other |  | Load Growth | 5365000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 13144 | 2017-12-08 | ITC_17_003 | Zephyr Load Interconnection | Construct a new 120 kV substation and cut in the Brownstown - Navarre 1 120 kV circuit. | MI | MI | Other |  | Load Growth | 3700000 | 2018-05-01 | 2018-05-01 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 13573 | 2017-12-08 | ITC_16_018 | Bunce Creek - Menlo 120 kV Sag Remediation | Fully remediate the sag limit on the 266.8 ACSR from the Bunce Creek - Menlo 120 kV circuit in order to increase its summer emergency rating to 730 A (152 MVA). This is an alternative to the Bunce Creek – Menlo120 kV Rebuild project (#4501). | MI | MI | Other |  | Reliability | 60000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP17 | A | East | ITCT | 14265 | 2018-01-29 |  | Monroe - Bayshore 345 kV | MISO-PJM interregional upgrade, ATSI to replace river span (reconductor), no ITCT capital work. The cost reported is the total MISO share. | MI,OH | MI,OH | TMEP | Shared |  | 110000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Top-Down
A in MTEP17 | A | East | ITCT, METC | 9864 | 2018-06-20 | METC_15_021 | Whiting - Custer 120 kV Rebuild | Rebuild 9.98 miles of 636 ACSR from the Whiting – Custer 120 kV circuit using 1431 ACSR and OPGW on new 230 kV future double circuit structures. Replace limiting equipment at both the Whiting and Custer stations | MI | MI | BaseRel | Shared |  | 14300000 | 2020-09-30 | 2020-09-30 | 120 | 0 | Bottom-Up
A in MTEP17 | A | West | MDU | 12787 | 2017-12-08 |  | Watford City Substation | A new 230/34.5 kV substation near Watford City, ND and a new 230 kV line (< 1 mile) to the WAPA Watford City Substation | ND | ND | Other |  | Reliability | 3500000 | 2019-06-30 | 2019-06-30 | 230 | 34.5 | Bottom-Up
A in MTEP17 | A | West | MEC | 12049 | 2017-12-08 |  | 34th Ave. NW Substation Expansion | Expand the 34th Avenue NW Substation to accommodate two additional terminals on the ring bus by adding three 161 kV circuit breakers. | IA | IA | Other |  | Load Growth | 1650000 | 2018-06-01 | 2018-06-01 | 161 | 0 | Bottom-Up
A in MTEP17 | A | West | MEC | 12064 | 2017-12-08 |  | Willow Creek Substation Expansion #3 | Add three new 161 kV circuit breakers to accommodate the addition of a new 50 MVA 161-13 kV transformer to meet increasing customer load. | IA | IA | Other |  | Load Growth | 1420000 | 2018-12-31 | 2018-12-31 | 161 | 13.2 | Bottom-Up
A in MTEP17 | A | West | MEC | 12107 | 2017-12-08 |  | Valley Drive Substation 69-13 kV | Install a new 69-13 kV substation with 69 kV circuit breakers & distribution transformer. Will bisect the Sub A - Sub 84 69 kV line, creating Sub A - Criswell St & Criswell St - Sub 84 69 kV lines. | IA | IA | Other |  | Load Growth | 4270000 | 2019-06-01 | 2019-06-01 | 69 | 13 | Bottom-Up
A in MTEP17 | A | West | MEC | 12363 | 2017-12-08 |  | Bondurant: Replace Circuit Breaker 803 | Replace 161 kV circuit breaker DAH803 at Bondurant Substation with a 40 kA breaker. | IA | IA | BaseRel |  |  | 325000 | 2019-12-01 | 2019-12-01 | 161 | 0 | Bottom-Up
A in MTEP17 | A | West | MEC | 12503 | 2017-12-08 |  | Prairie City-Monroe 69 kV Line Rebuild | Rebuild the Prairie City to Monroe 69 kV line. | IA | IA | Other |  | Age and Condition | 3712100 | 2019-03-31 | 2019-03-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | MEC | 12723 | 2017-12-08 |  | J499 Arbor Hill | J499 Network Upgrades and Affected System Upgrades | IA | IA | GIP | Shared |  | 10000000 | 2018-09-01 | 2018-09-01 | 345 | 0 | Externally Driven
A in MTEP17 | A | West | MEC | 12725 | 2017-12-08 |  | J500 Orient | J500 Network Upgrades and Affected System Upgrades | IA | IA | GIP | Shared |  | 24571000 | 2018-12-01 | 2019-12-01 | 345 | 0 | Externally Driven
A in MTEP17 | A | West | MEC | 13584 | 2017-12-08 | T90LH | J529/J590 Palo Alto | J529/J590 Network Upgrades and Interconnection Facilities | IA | IA | GIP | Shared |  | 10000000 | 2019-08-01 | 2019-08-01 | 345 | 0 | Externally Driven
A in MTEP17 | A | East | METC | 11663 | 2017-12-08 | METC_16_036 | Blackstone–Leoni #1 138kV Sag Remediation | Remediate the sag limit on the Blackstone–Leoni #1 138kV circuit to 308 MVA. | MI | MI | BaseRel |  |  | 90000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 11664 | 2017-12-08 | METC_16_037 | Blackstone–Leoni #2 138kV Sag Remediation | Remediate the sag limit on the Blackstone–Leoni #2 138kV circuit from 194 MVA to 636 ACSR conductor limit of 310 MVA. | MI | MI | BaseRel |  |  | 266000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 11665 | 2017-12-08 | METC_16_038 | Blackstone–Leoni #3 138kV Sag Remediation | Remediate the sag limit on the Blackstone–Leoni #3 138kV circuit from 221 MVA to 636 ACSR conductor limit of 310 MVA. | MI | MI | BaseRel |  |  | 53000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 11884 | 2017-12-08 | METC_15_020 | Batavia – Barnum Creek Jct. 138 kV Rebuild | Rebuild 6.62 miles of 266.8 ACSR from the Barnum Creek Jct. – Alder Creek section and 15.62 miles of 266.8 ACSR from the Alder Creek – Batavia section of the Verona – Batavia 138 kV circuit using 954 ACSR and OPGW on new double circuit structures constructed at 230 kV standards. The structures will have one side vacant and available for a future circuit. This project also involves replacing PTS 3199 as well as limiting terminal equipment at the Batavia 138 kV station. | MI | MI | Other |  | Reliability | 34360000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12032 | 2017-12-08 | METC_16_039 | Rice Creek–Denso J. 138kV Sag Remediation | Remediate the sag limit on the Rice Creek–Denso J. 138kV section from 89 MVA to 150 MVA. | MI | MI | BaseRel |  |  | 468000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12128 | 2017-12-08 | METC_16_032 | Stover-Alba Jct.-Van Tyle 138 kV Rebuild | Rebuild about 21.7 miles of 266.8 ACSR and 0.19 mile of 336.4 ACSR to 954 ACSR on Stover – Alba Junction - Van Tyle 138kV utilizing 954 ACSR conductor on 230 kV double circuit towers. Also upgrade the Van Tyle relay to address tripping limits. | MI | MI | BaseRel |  |  | 28800000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12189 | 2017-12-08 |  | METC Pole Top Switch Additions/Replacement Program 2019 | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points . | MI | MI | Other |  | Age and Condition | 3600000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12190 | 2017-12-08 |  | METC Pole Top Switch Additions/Replacement Program 2020 | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points . | MI | MI | Other |  | Age and Condition | 3600000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12192 | 2017-12-08 |  | 2020 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Other |  | Age and Condition | 49000000 | 2020-12-31 | 2020-12-31 | 345 | 138 | Bottom-Up
A in MTEP17 | A | East | METC | 12197 | 2017-12-08 |  | METC Customer Interconnections - Year 2020 | Customer interconnection requests and retirements less than $1 million. | MI | MI | Other |  | Load Growth | 2500000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12385 | 2018-03-27 | METC_16_041 | Henry Interconnection Request | Consumers Energy had requested a new 138 kV interconnection to serve a new industrial customer via looped service off of METC's Gaines-Plaster Creek 138 kV line | MI | MI | Other |  | Load Growth | 7000000 | 2022-01-01 | 2022-01-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12423 | 2018-07-10 |  | Campbell-Hudsonville Jct. Sag Remediation | Perform sag remediation to get the rating of Campbell-Hudsonville Junction section of the Campbell-Ransom 138 kV line to at least 330 MVA (1381 A) | MI | MI | BaseRel |  |  | 80000 | 2022-01-01 | 2022-01-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 12444 | 2017-12-08 |  | Tallmadge SPOF Remediation | Install redundant station battery at Tallmadge 138 kV substation to remove single point of failure (SPOF). | MI | MI | BaseRel |  |  | 73000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | METC | 13384 | 2017-12-08 | METC_17_027 | Luce 138kV Station (J589) | METC to construct new Luce 138kV substation to support the J589 interconnection. Station will be fed by looping in the Regal - Summerton 138kV line. Station will be built as a 2 row breaker and half station in a ring bus configuration. OPGW will be required for Luce - Regal 138kV and Luce - Summerton 138kV. This is for the network upgrades to accommodate J589 interconnection. | MI | MI | GIP | Shared |  | 8115000 | 2018-10-26 | 2018-10-26 | 138 | 0 | Externally Driven
A in MTEP17 | A | East | METC | 13444 | 2017-12-08 |  | G934 Nelson Rd Interconnection | Installation of 4-345kV breakers and associated disconnect switches at the Nelson Rd 345kV station. | MI | MI | GIP | Shared |  | 4281000 | 2020-09-01 | 2020-09-01 | 345 | 0 | Externally Driven
A in MTEP17 | A | East | METC | 14324 | 2017-12-08 |  | Beals Road – Hazelwood 138kV line cutting into Buck Creek | This project will be needed in conjunction with phase 2 of Consumers Energy’s project 12163. This project will cut the Beals Road –Hazelwood 138kV line into Buck Creek. Relay modifications at Beals Road, and Hazelwood may be needed for this project. Also this project will raise Beals Road to Buck Creek 138kV sag limit to at least 282 MVA (1180Amp). The estimated cost is $1.8 million. The expected in-service date is December 31, 2020. | MI | MI | BaseRel |  |  | 1816000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | MP | 12323 | 2017-12-08 | 93 Line Upgrade | 93 Line Upgrade | Thermal upgrade from 75C to 100C to increase summer normal/emergency rating to 470/517 MVA | MN | MN | BaseRel |  |  | 3500000 | 2019-03-31 | 2019-03-31 | 230 | 0 | Bottom-Up
A in MTEP17 | A | West | MP | 12563 | 2017-12-08 | Boswell 230/115 kV Transformer | Boswell 230/115 Transformer | Add 230/115 kV transformer between the 230 kV Boswell substation and the expanded 115 kV Boswell Substation. | MN | MN | BaseRel |  |  | 11432394 | 2018-12-31 | 2018-12-31 | 230 | 115 | Bottom-Up
A in MTEP17 | A | West | MP | 12583 | 2017-12-08 | 76 Line Upgrade | 76 Line Upgrade | Replace limiting terminal equipment on Hibbard - Winter Street 115 kV Line | MN | MN | BaseRel |  |  | 250000 | 2018-05-01 | 2018-05-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | MP | 12644 | 2017-12-08 | North Shore STATCOM | North Shore STATCOM | Install +/-75 MVAR STATCOM system at planned North Shore Switching Station | MN | MN | BaseRel |  |  | 19000000 | 2019-09-01 | 2019-09-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | MPW | 2935 | 2018-07-10 | MPW-WR | Rebuild 69 kV lines South - Wiggins - Power Plant (Lines 81 & 82) | MPW is looking at upgrading the 69 kV transmission lines from 633501 South Sub to 633511 Wiggins Road (Line 82) by 9/1/17 and from 633511 Wiggins Road to our 633408 Power Plant (Line 81) from 58 MW to at least 89 MW (T-2 Linnet) by 6/1/20. | IA | IA | Other | Not Shared | Reliability | 2585000 | 2017-08-31 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | MPW | 9001 | 2018-06-14 | MPW-WS-TT-L95 | MPW Terminal upgrade West to Isett (69 kV Line 95) | Upgrade CT limits at Isett and West substations to obtain the 89 MVA conductor rating at both terminals. | IA | IA | Other |  | Reliability | 82000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | MPW | 9022 | 2017-12-08 | MPW-PS-TT-L98 | MPW Line Reconductoring Pine St to Isett (69 kV Line 98) | Reconductor MPW Pine St to Isett Line 98 to 89 MVA. | IA | IA | Other |  | Reliability | 1930000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | MPW | 12227 | 2018-09-28 | MPW-PP-GV-L90 | MPW Terminal upgrade MPW GEN to Grandview Tap (69 kV Line 90PP-GV) | Upgrade Power Plant terminals for Line 90 (Power Plant to Grandview) to obtain 89 MVA conductor rating. | IA | IA | Other |  | Reliability | 15000 | 2019-09-01 | 2019-09-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | MPW | 13223 | 2018-09-28 | MPW-TT | Add 69 kV capacitors at Isett | Phase 1: Add 6 MVAR of 69 kV capacitors at MPW bus 633451 Isett 8 by 6/1/2019 Phase 2: Add additional 4 MVAR of 69 kV capacitors at MPW bus 633451 Isett 8 for a total of 10 MVAR by 6/1/2023 | IA | IA | Other |  | Reliability | 180000 | 2020-06-01 | 2023-06-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | NIPS | 14264 | 2017-12-08 |  | Burnham - Munster 345 kV | Upgrade Burnham - Munster 345 kV: Reconfigure Munster to ring bus | IN | IN | TMEP | Shared |  | 864000 | 2020-06-01 | 2020-06-01 | 345 | 0 | Top-Down
A in MTEP17 | A | East | NIPS | 14266 | 2017-12-08 |  | Michigan City - Bosserman 138 kV | Reconductor Michigan City - Bosserman 138 kV | IN | IN | TMEP | Shared |  | 600000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Top-Down
A in MTEP17 | A | East | NIPS | 14267 | 2017-12-08 |  | Reynolds - Magnetation 138 kV | Substation work (replace switches) at Reynolds | IN | IN | TMEP | Shared |  | 70800 | 2020-06-01 | 2020-06-01 | 138 | 0 | Top-Down
A in MTEP17 | A | East | NIPS | 14268 | 2017-12-08 |  | Roxana - Praxair 138 kV | Reconductor Roxana - Praxair 138 kV | IN | IN | TMEP | Shared |  | 4636000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Top-Down
A in MTEP17 | A | West | OTP | 12923 | 2018-06-29 |  | OTP Crown Ridge Wind Farm- G736 | Interconnection Customer shall interconnect a 200 MW wind Generating Facility to the Big Stone South substation. | SD | SD | GIP |  |  | 0 | 2018-12-31 | 2018-12-31 | 230 | 0 | Externally Driven
A in MTEP17 | A | West | OTP | 13043 | 2018-06-29 | OTP | Donaldson 115 kV - Add Capacitor Banks | Add two 15 MVAR cap banks to the Donaldson 115 kV substation to improve reliability of area loads. | MN | MN | Other |  | Reliability | 975000 | 2019-11-30 | 2019-11-30 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | OTP | 13344 | 2018-06-29 | 13344 | Red Lake Falls Wind/Solar R-101 | Interconnection Customer shall interconnect a 4.6 MW wind and solar combination Generating Facility on the Red Lake Falls Southwest to Gentilly 41.6 kV line. | MN | MN | GIP |  |  | 72630 | 2018-09-01 | 2018-09-01 | 115 | 41.6 | Externally Driven
A in MTEP17 | A | Central | PPI | 11976 | 2017-12-08 | 1 | New Grand Island 138/69 kV substation | 1) New Grand Island 138/69 kV substation, includes an 84 MVA LTC transformer 2) Reconductor Grand Island--Poplar City 69 kV line 3) New 9.0 miles from Poplar City- Kilbourne 69 kV line. 4) New Kilbourne 69/12.47 kV distribution substation. | IL | IL | Other |  | Load Growth | 22155000 | 2019-06-01 | 2019-12-31 | 138 | 12.47 | Bottom-Up
A in MTEP17 | A | Central | PPI | 12844 | 2018-09-17 |  | New Mechanicsburg 69/12.47 kV distribution substation | New Mechanicsburg 69/12.47 kV distribution substation, includes the following... 1) New Mechanicsburg 69/12.47 kV substation with a 5.0 MVA transformer 2) New 9.2 mile Mechanicsburg-Lanesville 69 kV line. 3) Add 2 69 kV breakers at E. Lanesville. | IL | IL | Other |  | Load Growth | 6473200 | 2017-12-31 | 2020-12-31 | 69 | 12.47 | Bottom-Up
A in MTEP17 | A | Central | PPI | 12845 | 2017-12-08 |  | New Williams 69/12.47 kV distribution substation | New Williams 69/12.47 kV distribution substation, includes the following… 1) New Williams 69/12.47 kV substation with a 7.4MVA transformer 2) New 7.9 mile Athens-Williams 69 kV line. | IL | IL | Other |  | Load Growth | 5200000 | 2025-12-31 | 2025-12-31 | 69 | 12.47 | Bottom-Up
A in MTEP17 | A | South | SMEPA | 12209 | 2018-08-27 |  | Cole Road 69kV Source Project | Rebuild Line 80A (Cole Rd – Breland GOAB) as a double circuit 69kV line and rebuild Line 40A (Breland GOAB – W. Hattiesburg S.S.) using 795 ACSR conductor. Loop Line 40 (Rawls Springs to Breland GOAB) into Cole Road substation. The existing Breland GOAB will be retired with the new 69kV line configuration of Rawls Springs – Cole Road and West Hattiesburg S.S. – Cole Road. | MS | MS | Other |  | Reliability | 1442500 | 2018-11-01 | 2018-11-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | South | SMEPA | 12213 | 2017-12-08 |  | New Oak Grove 161/69kV Substation | A 161kV source will be established at the Oak Grove substation by rebuilding approximately 2.5 miles of SMEPA’s existing de-energized 161kV Line 170 (Morrow to Purvis Bulk) and building approximately 0.5 miles of new transmission line to the substation site. A breakered 161/69kV substation will be constructed with a single 112MVA, 161/69kV transformer. SMEPA’s existing 69kV Lines 39, 39B and 91 will be routed into the 161/69kV substation utilizing the same transmission right-of-way corridor. | MS | MS | Other |  | Reliability | 6991000 | 2021-01-01 | 2021-01-01 | 161 | 69 | Bottom-Up
A in MTEP17 | A | South | SMEPA | 12214 | 2018-08-27 |  | Cole Road Delivery Point | The new delivery point is adjacent to SMEPA’s Cole Road substation and will require adding a 69kV bay and breaker to SMEPA’s existing Cole Road substation. A short 69kV service feed will be constructed to the new delivery point. | MS | MS | Other |  | Load Growth | 540000 | 2018-11-01 | 2018-11-01 | 69 | 0 | Bottom-Up
A in MTEP17 | A | Central | Vectren | 9950 | 2017-12-08 | 2016SIGE15 | Y76 69kV Line Rebuild from New Harmony to Northwest | 69kV (Line Y76) rebuild from New Harmony to Northwest> | IN | IN | Other |  | Age and Condition | 9250000 | 2018-10-31 | 2018-10-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | Central | Vectren | 11844 | 2017-12-08 | 2017SIGE06 | Y32 Mead Jo - Mead Jo Tap 69kV Reconductor | 69kV line Y32 re-conductor from Mead Jo - Mead Jo Tap | IN | IN | Other |  | Age and Condition | 485000 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | Central | Vectren | 11845 | 2017-12-08 | 2018SIGE07 | Culley 138 kV OCB Replacement 2018 | Culley 138 kV OCB Replacement of four breakers 2018 | IN | IN | Other |  | Age and Condition | 950000 | 2018-09-28 | 2018-09-28 | 138 | 0 | Bottom-Up
A in MTEP17 | A | Central | Vectren | 11848 | 2017-12-08 | 2018SIGE10 | Perry Twp 69 kV Loop/Substation Modification | 69kV line Y32 Loop for Perry Twp Sub and Perry Twp Sub Modifications | IN | IN | Other |  | Reliability | 3600000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | Central | Vectren | 11850 | 2017-12-08 | 2018SIGE12 | Y36 Winslow to SR61-E 800S | 69kV line Y36 Winslow to SR61-E 800S re-build (7 miles) | IN | IN | Other |  | Age and Condition | 2000000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 8362 | 2017-12-08 | CV-WC Rebuild | Casnovia to White Cloud Rebuild | Rebuild the Casnovia to White Cloud 69kV line, install new poles and hardware with 795ACSS Conductor. | MI | MI | Other |  | Age and Condition | 11500000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 8363 | 2017-12-08 | VB-CF rebuild | Vestaburg to Crawford Rebuild | Rebuild the Vestaburg to Crawford 69kV line, install new poles and hardware with 795ACSS Conductor | MI | MI | Other |  | Age and Condition | 4500000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 9903 | 2017-12-08 | WC-RG Rebuild | White Cloud to Rogers | Rebuild the White Cloud to Rogers 69kV line, install new poles and hardware with 795ACSS conductor | MI | MI | Other |  | Age and Condition | 18500000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 10266 | 2017-12-08 |  | East Jordan Station Rebuild | This project will replace the existing equipment at the East Jordan station and upgrade the steel, install new controls, 125v DC battery system and a circuit breaker. | MI | MI | Other |  | Age and Condition | 350000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12195 | 2017-12-08 | 2018 Battery Replacement Project | 2018 Battery Bank Replacement Project | This project replaces battery banks and chargers that have reached the end of their useful life | MI | MI | Other |  | Age and Condition | 70000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12196 | 2017-12-08 | 2019 Battery Bank Replacement Project | 2019 Battery Bank Replacement Project | This project replaces battery banks and chargers that have reached the end of their useful life | MI | MI | Other |  | Age and Condition | 35000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12216 | 2017-12-08 | Cadillac to Hersey OPGW | Cadillac to Hersey OPGW | Replace existing shield wire with OPGW on the Cadillac to Hersey line section. | MI | MI | Other |  | Age and Condition | 2300000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12221 | 2017-12-08 |  | Leroy to Tustin Rebuild | Rebuild line to 138kV design with 336ACSR | MI | MI | Other |  | Age and Condition | 4000000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12223 | 2017-12-08 | Leroy to Hartwick Rebuild | Leroy to Hartwick Rebuild | Rebuild line to 138kV design with 336ACSR | MI | MI | Other |  | Age and Condition | 5000000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12224 | 2017-12-08 | Lemon Junction to Silver Lake Rebuild | Lemon Junction to Silver Lake Rebuild | Rebuild line to 138kV design with 336ACSR | MI | MI | Other |  | Age and Condition | 3300000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 12285 | 2017-12-08 | Altona to Vestaburg Rebuild | Altona to Vestaburg Rebuild | Rebuild the Altona to Vestaburg 69kV line, install new poles and hardware with 795ACSS conductor | MI | MI | Other |  | Age and Condition | 10000000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 13163 | 2017-12-08 |  | Iron Works Interconnection | Great Lakes Energy Cooperative requested interconnection service for a new industrial load off of Wolverine’s Advance – Van Tyle 138kV transmission line. The load is expected to be 24.4MW and is a combination of induction furnace load and plant auxiliary system load. To connect this load, the following transmission facilities are planned: - Approximately 3 miles of new 138kV double circuit transmission line will be built to serve the new EJ Iron Works distribution station. The line will be constructed using steel monopoles, 795 ACSS conductor, and optical ground wire on new right-of-way. The new double circuit will be used the connect the new EJ station to Wolverine’s Van Tyle to Advance transmission line between the Deer Lake and Elmira distribution stations just west of Elmira, Michigan. - Wolverine will construct an in-and-out 138kV transmission station bus configuration for the purpose of providing transmission service to the new EJ distribution substation. The station will include two load-break motor operated air break switches (MOABs) with SCADA open/close functionality. | MI | MI | Other |  | Load Growth | 5085482 | 2018-03-01 | 2018-03-01 | 138 | 0 | Bottom-Up
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 138kV Voltage Conversion Alternate | Convert the following lines already constructed 138kV design • Lake County to Plains Junction (constructed to 138kV) • Redwood to Hart (constructed to 138kV) • Plains Junction to Hersey (constructed to 138kV) • Redwood to Lemon Junction (constructed to 138kV) Construct and convert the following MTEP Target A projects in MTEP17 due to condition • White Cloud to Rogers (MTEP Project 9903, Target A MTEP17) • Lemon Junction to Silver Lake (MTEP Project 12224, Target A MTEP17) Construct/upgrade the following lines not currently in MTEP • Replace Conductor only on Rogers to Lemon Junction (10.29mi) • Rebuild Plains Junction to Hart (22.09mi) • Add conductor on Hersey to Lincoln, designed for double circuit, continue to supply 69kV service to Lincoln substation (3.29mi) • Rebuild Hersey to White Cloud (25.37 mi) • Rebuild Paris Junction to Paris (1.26 mi) • Rebuild Brohman Junction to Brohman (1.34 mi) • Rebuild White Cloud to Casnovia (22.85 mi) • Rebuild Newaygo to Brooks (3.22 mi) • Rebuild Casnovia to Sternberg (19.39 mi) • Rebuild Lake County to Pere Marquette (18.25 mi) Construct the following new stations to replace existing 69kV stations: • Plains Junction (138kV station) • White Cloud (138kV station) • Rogers (138kV single breaker station) • Lemon Junction (138kV single breaker station) • Casnovia (138/69kV station Upgrades to the following stations: • Hersey (add 138/69kV transformer, utilize existing bus work to the extent practical) • Lake County (relocate 69kV line to 138kV bus, available position on 138kV bus currently installed) | MI | MI | Other |  | Reliability | 68425000 | 2018-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP17 | A | West | XEL | 4695 | 2017-12-08 |  | Rebuild Wilson 115 kV Substation | Convert Wilson straight bus into a breaker-and-a-half scheme | MN | MN | Other |  | Reliability | 17000000 | 2021-06-01 | 2021-06-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | XEL | 11644 | 2017-12-08 |  | G261 - Mankato Energy Center Expansion (XEL portion) | The Mankato Energy Center expansion, identified as G261, is causing the existing 115 kV line between Wilmarth and Swan Lake to overload. This was identified in the G261 Facilities Study as needing a 150 MVA rating. To achieve the necessary rating, Xcel Energy will mitigate clearance issues on this line. The new line rating will be 150.7 MVA for both summer normal and emergency conditions. | MN | MN | GIP |  |  | 500000 | 2018-10-01 | 2018-10-01 | 115 | 0 | Externally Driven
A in MTEP17 | A | West | XEL | 11987 | 2017-12-08 |  | French Island Overstressed Breakers | Replace breakers identified in overstressed breaker study in French Island substation | WI | WI | Other |  | Age and Condition | 375000 | 2018-12-20 | 2018-12-20 | 69 | 0 | Bottom-Up
A in MTEP17 | A | West | XEL | 11993 | 2017-12-08 |  | Black Dog - Wilson #1 and #3 Line Uprates | Replace equipment at Black Dog substation to allow an uprate of the existing Black Dog-Wilson #1 and Black Dog-Wilson #3 115 kV lines. | MN | MN | BaseRel |  |  | 5383000 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | XEL | 12007 | 2017-12-08 |  | Farmers Inn - 2nd Distribution Transformer | Installing a 2nd 69/12.47 kV transformer and 1 new feeder at Farmers Inn | WI | WI | Other |  | Load Growth | 1100000 | 2019-06-01 | 2019-06-01 | 69 | 12.5 | Bottom-Up
A in MTEP17 | A | West | XEL | 12008 | 2017-12-08 |  | Griffin Street - 2nd Distribution Transformer | Installing a 2nd 69/12.47 kV transformer and 2 new feeders at Griffin Street | WI | WI | Other |  | Load Growth | 330000 | 2018-11-15 | 2018-11-15 | 69 | 12.5 | Bottom-Up
A in MTEP17 | A | West | XEL | 12009 | 2017-12-08 |  | Ironwood 115 kV Bus Tie Breaker | Installing a 115 kV bus tie breaker at Ironwood to separate the two 115 kV lines and two 115/34.5 kV transformers | MI | MI | Other |  | Load Growth | 2670482 | 2018-12-31 | 2018-12-31 | 115 | 0 | Bottom-Up
A in MTEP17 | A | West | XEL | 12013 | 2017-12-08 |  | Nordic TR3 | Install a third Distribution transformer to accommodate increasing demand in the area | ND | ND | Other |  | Load Growth | 400000 | 2018-12-15 | 2018-12-15 | 115 | 12.5 | Bottom-Up
A in MTEP17 | A | West | XEL | 12623 | 2017-12-08 |  | J426 Expand Chanarambie | Expand Chanarambie substation to accommodate TR3, bus tie breaker, and 34.5 kV feeders. This project is required as part of J426 wind farm generation interconnection. Project cost is paid by generation interconnection customer. | MN | MN | GIP |  |  | 5250000 | 2018-12-15 | 2018-12-15 | 115 | 34.5 | Externally Driven
A in MTEP16 | A | South | AECC | 9663 | 2017-01-09 |  | Tap EAI Newport - Balch 161 kV line: Construct South Newport 161/13.2 kV substation | Construct 20 MVA, 161/13.2 kV substation under EAI Newport - Parkin 161 kV line. The load for this substation will be transferred from the Newport and Cherokee Acres distribution delivery points. Once the load is transferred the two distribution delivery points will no longer be needed. Edit: POD/substation name will likely be changed from South Newport to Newport East. | AR | AR | Other |  | Load Growth | 500000 | 2020-04-01 | 2020-04-01 | 161 | 13.2 | Bottom-Up
A in MTEP16 | A | South | AECC | 10204 | 2018-08-22 |  | Tap EAI Moses to Bailey 161kV line, Construct 161/13.2kV Hunter North substation | Tap EAI Moses to Bailey 161kV line, Construct 161/13.2kV Hunter North substation | AR | AR | Other |  | Reliability | 500000 | 2018-12-31 | 2018-12-31 | 161 | 0 | Bottom-Up
A in MTEP16 | A | South | AECC | 10206 | 2017-01-09 |  | Clinton West to Partain 161kV line, 161/69kV Partain substation | Build 5 position ring bus at the AECC Clinton West substation, Build 14 mile 161kV line from the existing Clinton West substation to the proposed Partain substation, Build 3 position ring bus at the proposed Partain substation, Build the proposed Partian 161/69kV substation. | AR | AR | Other |  | Reliability | 27000000 | 2020-12-01 | 2020-12-01 | 161 | 69 | Bottom-Up
A in MTEP16 | A | Central | AmerenIL | 9726 | 2017-01-09 |  | Fogarty 138-34.5 kV Transformer Connection | Provide 138 kV connection to supply 138-34.5 kV transformer | IL | IL | Other |  | Load Growth | 1900000 | 2021-06-01 | 2021-06-01 | 138 | 34.5 | Bottom-Up
A in MTEP16 | A | Central | AmerenIL | 9727 | 2017-01-09 |  | Wakefield Substation | Establish 138 kV ring bus; connect to South Bloomington-Clinton-1372 line to supply Wakefield Substation | IL | IL | Other |  | Load Growth | 7360755 | 2021-12-01 | 2021-12-01 | 138 | 34.5 | Bottom-Up
A in MTEP16 | A | Central | AmerenIL | 9853 | 2018-09-28 |  | Mt. Vernon, West Terminal Equipment | Upgrade terminal equipment in Prairie State-Mt. Vernon, West position | IL | IL | Other |  | Age and Condition |  | 2040-06-01 | 2040-06-01 | 345 | 345 | Bottom-Up
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | Rebuild Lone Rock - Boscobel 69 kV | Rebuild Y-124 from Lone Rock to Boscobel with T2-4/0 ACSR. Inlcudes partial rebuild of Y-78 Lone Rock - Richland Center | WI | WI | Other |  | Age and Condition | 32400000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 7986 | 2017-01-13 | PR05253 | Install 138 kV Highway V Breakers | Install 138-69 kV transformer high side breaker additions to T1 and T2. | WI | WI | Other |  | Load Growth | 9000000 | 2019-04-01 | 2019-04-01 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 8640 | 2017-01-09 |  | Upgrade City Limits Bus 138 kV | Replace bus conductors at City Limits | WI | WI | Other |  | Reliability | 300000 | 2018-12-20 | 2018-12-20 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | Rebuild Finger Rd - Canal 69 KV | This project is a Asset Management driven project to rebuild the main section of J-10 from Finger Road to Beardsley to Canal. The tapped lines off of J-10 and East Krok to Beardsley are not included in this scope. No substation work is included in scope. | WI | WI | Other |  | Reliability | 60717000 | 2020-03-31 | 2020-03-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 9923 | 2017-01-09 |  | Mukwanago Substation 138kV | Install line breaker on line 67K61. | WI | WI | Other |  | Load Growth | 900000 | 2018-12-30 | 2018-12-30 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 9934 | 2017-01-09 | PR07285 | Upgrade Oak Creek - Hayes 138-kV line | Oak Creek - Hayes 138-kV line 811 upgrade and reconfiguration | WI | WI | Other |  | Reliability | 18000000 | 2019-04-15 | 2019-04-15 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 9954 | 2017-01-09 | PR07375 | Replace Lost Dauphin T1 Transformer | Replace Lost Dauphin T1 Transformer. | WI | WI | Other |  | Reliability | 6700000 | 2019-09-27 | 2019-09-27 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 9961 | 2017-01-09 |  | Replace Nelson Dewey T31/T32 Transformers | Replace Nelson Dewey T31/T32 Transformers. | WI | WI | Other |  | Reliability | 5375625 | 2019-12-01 | 2019-12-01 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 9977 | 2017-01-09 |  | Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation | Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation. | WI | WI | Other |  | Age and Condition | 28225000 | 2020-06-30 | 2020-06-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 9986 | 2017-01-09 | PR07410, 602097,602099 | Rebuild 138KV Line 762 Port Washington - Saukville Substation | Rebuild 138KV Line 762 Port Washington - Saukville Substation. | WI | WI | BaseRel |  |  | 21000000 | 2021-05-31 | 2021-05-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 10484 | 2017-01-09 | PR07373 | Construct Eaton 138 kV T- D | Construct a new ATC 138KV loop through at Eaton Substation. | WI | WI | Other |  | Load Growth | 2500000 | 2023-12-01 | 2023-12-01 | 138 | 24.9 | Bottom-Up
A in MTEP16 | A | West | ATC | 10485 | 2017-01-09 | PR007372 | Construct Bay Ridge 138 kV T- D | Construct a new ATC 138KV loop through at Bay Ridge Substation. | WI | WI | Other |  | Load Growth | 2122335 | 2022-06-01 | 2022-06-01 | 138 | 24.9 | Bottom-Up
A in MTEP16 | A | West | ATC | 10603 | 2017-01-09 | PR07299 | Construct T - D Springwater Substation | Construct T - D Springwater Substation. | WI | WI | Other |  | Load Growth | 3800000 | 2018-08-31 | 2018-08-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | ATC | 10686 | 2017-01-09 | PR07392 | Construct T - D Roosevelt Road Substation | ATC bus expansion and T-D distribution transformer addition. | WI | WI | Other |  | Load Growth | 1102365 | 2021-06-01 | 2021-06-01 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | CFU-PMEU | 11383 | 2017-01-09 | Pella RRHD | J329 Network Upgrades | Network upgrades associated with J329 for substations in Pella Iowa. | IA | IA | GIP |  |  | 1043700 | 2017-08-01 | 2017-08-01 | 69 | 0 | Externally Driven
A in MTEP16 | A | Central | DEI | 2873 | 2017-01-09 | DIN0216 | Danville E. 69kV looped feed | Construct new Danville East substation near HRH hospital - single 22.4MVA transformer - 6945 ckt to be looped through | IN | IN | Other | Not Shared | Load Growth | 1040000 | 2018-12-31 | 2018-12-31 | 69 | 12 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9834 | 2018-07-11 | AMIN1055 | Noblesville to Tipton W. 230kV Rebuild | Noblesville to Tipton West 23008 ckt: Replace all single/H-frame pole structures with steel poles, reconductor with 954ACSR45X7 OVAL / OPGW and build Switching Station with 3-2000A line switches near existing Carmel 146th St. junction. | IN | IN | Other |  | Age and Condition | 3000000 | 2020-12-31 | 2020-12-31 | 230 | 0 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9855 | 2017-01-09 | TIN1422 | Columbus North Brkr / Relay Replacements | Columbus North: Replace OCB 6975, 6929, 69230-1, 6950 and obsolete relays on CIR 6929, 6950, 6975, 6982. Also replace relays on CIR 23019. | IN | IN | Other |  | Age and Condition | 2711016 | 2020-12-31 | 2020-12-31 | 230 | 69 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9858 | 2017-01-09 | TIN1469 | Bedford 345 Brkr / Xfmr Replacements | Bedford 345: Replace 345/138kV Bank 7; Replace relays on CIR 6995, 13829, 13837, 34506, 34521. Replace all 69kV and 138kV Oil Circuit Breakers. | IN | IN | Other |  | Age and Condition | 12078813 | 2018-12-31 | 2018-12-31 | 345 | 69 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9888 | 2017-01-09 | TIN1528 | MiddleFork to Deer Crk. Jct. 69kV rebuild | Rebuild 6988 ckt. from MiddleFork sub to deadend 879/1041-01 and from Deer Cr Jct to 879/1046. 477acsr@120C w/ OPGW - 187 wood poles to be replaced with light duty steel. | IN | IN | Other |  | Age and Condition | 4860632 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9889 | 2017-01-09 | TIN1530 | Sharpsville to Kokomo SE 69kV rebuild | Rebuild 69174 ckt. from Sharpsville sub to Kokomo SE. 477acsr@120C w/ OPGW - 174 wood poles to be replaced with light duty steel. | IN | IN | Other |  | Age and Condition | 4287945 | 2018-08-01 | 2018-08-01 | 69 | 0 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9890 | 2017-01-09 | TIN1536 | Gibson Sta. to Merom Sta. 345kV Deadend Structures | Gibson to Merom: Install (10) double deadend structures in the 34511 ckt. | IN | IN | Other |  | Age and Condition | 4433734 | 2020-12-31 | 2020-12-31 | 345 | 0 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9891 | 2017-01-09 | TIN1534 | Flat Rock to Hope Jct. 69kV Pole Replacements | Flat Rock to Hope Jct. 6975 ckt. pole replacements (45), replace line switches at both ends. Transfer existing conductor to new poles. | IN | IN | Other |  | Age and Condition | 1087274 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9892 | 2017-01-09 | TIN1533 | Lewis Crk. to Flat Rock 69kV Pole Replacements | Lewis Crk. to Flat Rock 6975 ckt. pole replacements (100), replace line switches at Lewis Crk with 1200A. Transfer existing conductor to new poles. | IN | IN | Other |  | Age and Condition | 1875342 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9893 | 2017-01-09 | TIN1581 | Shelbyville Northeast CB and Relay Replacements | Shelbyville Northeast - Replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | IN | IN | Other |  | Age and Condition | 3511433 | 2021-06-01 | 2021-06-01 | 138 | 69 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9897 | 2017-01-09 | DIN1393 | River Ridge Gateway 138-12kV New Sub. | River Ridge Gateway 138-12kV Sub. to be inserted in the 13857 ckt. between Clark Maritime and HE Northport | IN | IN | Other |  | Load Growth | 1141000 | 2018-12-31 | 2018-12-31 | 138 | 12 | Bottom-Up
A in MTEP16 | A | Central | DEI | 9926 | 2017-01-09 | DIN1620 | Spelterville 138-34kV Sub Expansion | Spelterville: expand sub footprint, Install 138/34kV 60MVA Bank | IN | IN | Other |  | Age and Condition | 1332000 | 2019-12-31 | 2019-12-31 | 138 | 34 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 4665 | 2017-01-09 | 12-EAI-019 | Mabelvale: Replace 500-115 Autos | Upgrade both Mabelvale 500/115 kV autotransformers to 598MVA. | AR | AR | BaseRel |  |  | 23540744 | 2019-06-30 | 2019-06-30 | 500 | 115 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 7942 | 2017-01-09 | 15-EAI-004 | Mayflower - Morgan: Rebuild 115kV line | Mayflower - Morgan: Rebuild 115kV line | AR | AR | BaseRel |  |  | 5415875 | 2019-06-01 | 2019-06-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 9673 | 2017-01-09 | 16-EAI-002 | El Dorado Install 2nd 500/115 Autotransformer | Install 2nd-598MVA 500/115 kV autotransformer at El Dorado EHV. | AR | AR | BaseRel |  |  | 14155715 | 2019-06-30 | 2019-06-30 | 500 | 115 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 9696 | 2017-01-09 | 16-AI-017 | Newport 161 kv: Address Newport Flicker Issues | Build a breaker switching station "Mallory" near Newport Industrial and re-terminate the Newport-Swifton, Newport - Newport Industrial and Newport Industrial - Newport Air Base 161kV lines into Mallory. The 3.5 mile long line Newport - Mallory should be upgraded to a minimum of 545MVA (1956 Amps). | AR | AR | BaseRel |  |  | 18233177 | 2018-12-01 | 2018-12-01 | 161 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 9698 | 2017-01-09 | 16-EAI-006 | El Dorado East - El Dorado Jackson 115kV rebuild | Upgrade El Dorado East - El Dorado Jackson 115 kV line to minimum 1300A. | AR | AR | BaseRel |  |  | 6614767 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 9704 | 2017-01-09 | 16-EAI-008 | London North: New 161kV Substation | Construct new London North 161kV substation | AR | AR | Other |  | Load Growth | 6592341 | 2018-12-31 | 2018-12-31 | 161 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-AR | 9709 | 2018-01-03 | 16-EAI-012 | Mabelvale 115kV: Reconfigure Station | Reconfigure the Mabelvale 115 kV substation so that a single bus tie breaker failure will not open all the elements in the Mabelvale 115 kV substation. Some potential configurations are double bus double breaker, breaker and a half, and ring bus. The final configuration will be decided during project scoping. | AR | AR | BaseRel |  |  | 11563954 | 2021-06-01 | 2021-06-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 7949 | 2017-01-09 | 15-EGL-010 | Solac 230-69 kV: Upgrade Both Autos | Replace both 230/69 kV AT with 300MVA | LA | LA | BaseRel |  |  | 17034225 | 2019-03-10 | 2019-03-10 | 230 | 69 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 7950 | 2017-01-09 | 15-EGL-011 | East Broad to Ford 69 kV line: Reconductor line | Re-conductor East Broad to Ford 69 kV line | LA | LA | BaseRel |  |  | 2946372 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 7952 | 2017-01-09 | 15-EGL-012 | Contraband to Solac 69 kV line: Reconductor line | Re-conductor Contraband to Solac 69 kV line | LA | LA | BaseRel |  |  | 9015967 | 2018-09-01 | 2018-09-01 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9686 | 2017-01-09 | 16-ELN-005 | Lake Providence: New distribution substation | Construct a new radial 115 kV transmission line to the Lake Providence area to serve area load. | LA | LA | Other |  | Load Growth | 50446621 | 2023-06-01 | 2023-06-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9690 | 2017-01-09 | 16-ELN-010 | Hodge: Replace existing substation | Construct a new 230 kV substation to serve area load in the Hodge area. | LA | LA | Other |  | Load Growth | 26660631 | 2019-12-01 | 2019-12-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9763 | 2017-01-09 | 16-EGL-004 | Baker to Blount 69kV: Reconductor Line | Upgrade the rating on the Baker to Blount 69 kV line. This includes recondutor and upgrading station equipment. | LA | LA | BaseRel |  |  | 4385051 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9771 | 2017-01-09 | 16-EGL-012-1 | SWLA69IP Phase 1: Construct Jefferson Davis 138/69 kV Substation | Construct new Jefferson Davis 138/69 kV substation. | LA | LA | BaseRel |  |  | 102266403 | 2018-09-30 | 2018-09-30 | 138 | 69 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9772 | 2017-01-09 | 16-EGL-012-2 | SWLA69IP Phase 1: Colonial Welsh TP to Jefferson Davis 138 kV: Construct 138 kV line | Construct a new line from Colonial Welsh Tap to the new Jefferson Davis 138 kV station. | LA | LA | BaseRel |  |  |  | 2018-10-31 | 2018-10-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9773 | 2017-01-09 | 16-EGL-012-3 | SWLA69IP Phase 1: Jefferson Davis to Carter Construct 69 kV line | Build a new 69 kV line from Jefferson Davis to Carter substation | LA | LA | BaseRel |  |  |  | 2019-02-28 | 2019-02-28 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9774 | 2017-01-09 | 16-EGL-012-4 | SWLA69IP Phase 1: Jefferson Davis to Compton Construct 69 kV line | Construct 5 miles of double circuit 69 kV with a conductor rating of at least 880 A to a cut in point on 69 kV L-13 two miles south of the existing Compton 69 kV substation. Rebuild 2 miles of 69 kV L-13 from new cut in point to Compton with a conductor rating of at least 880 A. | LA | LA | BaseRel |  |  |  | 2019-06-30 | 2019-06-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9775 | 2017-01-09 | 16-EGL-012-5 | SWLA69IP Phase 1: Derouen 69 kV Cut into L-11 | Cut the Derouen 69 kV substation in and out of Line 11. | LA | LA | BaseRel |  |  |  | 2019-04-30 | 2019-04-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9776 | 2017-01-09 | 16-EGL-012-6 | SWLA69IP Phase 1: Lawtag 69 kV Cut into L-13 & Close NO @ L-13A | Cut line number 13 in and out of the Lawtag 69 kV substation. Also, close the normally open point on line number 13A. | LA | LA | BaseRel |  |  |  | 2019-03-30 | 2019-03-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9777 | 2017-01-09 | 16-EGL-012-7 | SWLA69IP Phase 1: Welsh 69 kV Cut into L-13A | Cut the Welsh 69 kV substation in and out of line 13A. | LA | LA | BaseRel |  |  |  | 2019-03-30 | 2019-03-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9778 | 2017-01-09 | 16-EGL-012-8 | SWLA69IP Phase 1: Colonial Welsh TP to Jefferson Davis 138 kV Reconductor | Reconductor the Colonial Welsh Tap to Jefferson Davis 138 kV line. | LA | LA | BaseRel |  |  |  | 2018-10-31 | 2018-10-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9779 | 2017-01-09 | 16-EGL-013 | SWLA69IP Phase 2: Carter to Serpent 69 kV Reconductor | Reconductor the Carter to Serpent 69 kV line. | LA | LA | BaseRel |  |  |  | 2019-11-30 | 2019-11-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9780 | 2017-01-09 | 16-EGL-014 | SWLA69IP Phase 3: Compton to Elton 69 kV Reconductor | Reconductor Comton to Elton 69 kV line. | LA | LA | BaseRel |  |  |  | 2019-09-30 | 2019-09-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9782 | 2017-01-09 | 16-EGL-016 | SWLA69IP Phase 4: Lake Arthur 69 kV Move NO Point | Move the normally open point at the Lake Arthur 69 kV substation. | LA | LA | BaseRel |  |  |  | 2019-03-30 | 2019-03-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9791 | 2017-01-09 | 16-EGL-027 | Thompson Road 230 kV: Construct New Substation | Construct a new substation to serve area load. | LA | LA | Other |  | Load Growth | 23792173 | 2020-04-01 | 2020-04-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9792 | 2017-01-09 | 16-EGL-028 | Lowe Grout Road 138 kV: Construct New Substation | Construct a new substation to serve area load. | LA | LA | Other |  | Load Growth | 19003650 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 9805 | 2017-01-09 | 16-ENO-001 | Patterson to Pontchartrain Park 115 kV: Reconductor Line | Reconductor the Patterson to Pontchartrain Park 115 kV line | LA | LA | BaseRel |  |  | 4279679 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 10008 | 2017-01-09 | 15-EGL-023 | Nelson to Menena 230 kV: Construct New Line | Construct new 230 kV line from Nelson to Menena. | LA | LA | BaseRel |  |  | 14234001 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 10583 | 2017-01-09 | 16-EGL-037 | Coly 230 kV: Add Breaker | Add a breaker at the Coly 230 kV substation. | LA | LA | Other |  | Reliability | 1073527 | 2018-10-01 | 2018-10-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 10584 | 2017-01-09 | 16-EGL-038 | Tiger 230 kV: Add Breaker | Add a 230 kV breaker at the Tiger substation. | LA | LA | Other |  | Reliability | 996703 | 2018-11-01 | 2018-11-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 10588 | 2017-01-09 | 16-ELL-010 | Fleur 230 kV Substation: New Substation | Construct a new 230 kV substation on the Oakville to Alliance 230 kV transmission line. This substation will be the primary feed to a customer in the area. Load will move from other substations in the area. Rebuild the Ninemile to Barataria 115 kV line. | LA | LA | Other |  | Load Growth | 62855610 | 2019-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 10623 | 2018-09-19 | 16-EGL-042 | Sadie 230 kV: Construct New Substation | Construct a new 230 kV substation on the PPG to Rosebluff 230 kV line. | LA | LA | Other |  | Load Growth | 19953332 | 2022-12-31 | 2022-12-31 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 10624 | 2017-01-09 | 16-EGL-043 | Big Lake 230 kV: Construct New Substation | Construct a new 230 kV substation on the Vincent to Graywood 230 kV line. | LA | LA | Other |  | Load Growth | 16936133 | 2022-07-01 | 2022-07-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-LA | 12017 | 2017-01-09 |  | Southeast Louisiana Project | Construction a new 230 kV substation called Churchill. Construction of approximately 26 miles of new 230 kV transmission line connecting the existing 230 kV Waterford substation to the Churchill 230 kV substation crossing the Down Stream Gypsy load pocket interface. Re-configuration of the existing Waterford to Ninemile and Ninemile to Estelle 230 kV lines into the Churchill 230 kV substation and out to the existing Ninemile 230 kV substation to provide access to the strong sources at the Ninemile substation. Add a breaker at the Michoud 115 kV substation to address the findings during the reliability no-harm robustness analysis. | LA | LA | Other |  | Other Local Needs | 97159798 | 2022-06-01 | 2022-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-MS | 9822 | 2017-01-09 | 16-EMI-001 | Harper 115 kV new switching station | Construct a new 115 kV breaker switching station. | MS | MS | Other |  | Reliability | 8307991 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-MS | 9833 | 2017-01-09 | 16-EMI-007 | Greenville North Install 2nd Capacitor | Install 2nd 20.5 MVAR capacitor bank at Greenville North 115 kV. | MS | MS | BaseRel |  |  | 1736875 | 2018-11-01 | 2018-11-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-MS | 9949 | 2018-08-27 |  | Cloverdale 115kV Delivery Point | The Cloverdale DP will be served from the existing Entergy IP to Johns Manville 115kV transmission line via a looped transmission feed into a new switching station to be constructed at the DP site. | MS | MS | Other |  | Load Growth | 1896000 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-MS | 10943 | 2017-01-09 | 16-EMI-016 | Norrel Road: Construct new 230 kV substation | Construct new 230 kV substation on the Clinton Industrial - Gerald Andrus (new Tinnin substation will be cut-in during 2017-2018) 230 kV line. | MS | MS | Other |  | Load Growth | 10741044 | 2018-11-01 | 2018-11-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-MS | 11783 | 2017-01-09 | 16-EMI-019 | McAdams Upgrade Autotransformers | Remove and replace the both a banks of autotransformers with new autotransformers with a minimum rating of at least 750 MVA per bank. Replace the existing spare single phase auto and re-configure the bus so that is usable for either bank. Add 1 – 35 MVAR reactor to autotransformer bank # 2, so there are 4 reactors for each autotransformer bank. | MS | MS | BaseRel |  |  | 5379046 | 2019-12-01 | 2019-12-01 | 500 | 230 | Bottom-Up
A in MTEP16 | A | South | Entergy-MS | 12015 | 2017-01-09 |  | Lakeover 500/230 kV XFMR | Relocate existing 500/230 kV transformer from McAdams to Lakeover | MS | MS | Other |  | Other Local Needs | 9116231 | 2019-12-01 | 2019-12-01 | 500 | 230 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 7930 | 2017-01-09 | 15-ETI-008 | Heights 230 kV: Construct New Substation | Construct new 230 kV substation for load growth in the Woodlands area to offload the New Caney 138 kV substation. New substation will be tapped into 230 kV line between China and Porter. | TX | TX | Other |  | Load Growth | 38504354 | 2019-06-01 | 2019-06-01 | 230 | 34.5 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9806 | 2017-01-09 | 16-ETI-001 | Bryan 138-69 kV: Replace Autos & Reconfigure 138 & 69 kV Bus | Replace the 2 138/69 kV autotransformers at the Bryan substation and reconfigure the 69 kV and 138 kV buses. | TX | TX | BaseRel |  |  | 35577866 | 2020-06-01 | 2020-06-01 | 138 | 69 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9807 | 2017-01-09 | 16-ETI-002 | Pintail 138 kV: Construct new Switching Substation | Expand an existing substation to include breakers and switchs. This will allow a normally open point to be closed. | TX | TX | Other |  | Load Growth | 9758690 | 2020-03-01 | 2020-03-01 | 138 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9809 | 2017-01-09 | 16-ETI-007 | Hull to Sour Lake 69 kV: Reconductor Line | Reconductor the Hull to Sout Lake 69 kV line. | TX | TX | BaseRel |  |  | 45999870 | 2020-12-01 | 2020-12-01 | 69 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9812 | 2017-01-09 | 16-ETI-014-1 | PARIP Garden 230 kV: Construct New 230 kV Substation | Port Arthur Reliability Improvement Plan: Cut the Sabine to China 230 kV line and the Nederland to Mid County 230 kV line into a new 230 kV substation named Garden. | TX | TX | BaseRel |  |  | 72661738 | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9813 | 2017-01-09 | 16-ETI-014-2 | PARIP Garden to Legend 230 kV: Construct New Line | Port Arthur Reliability Improvement Plan: Construct a new line from the new Garden substation to the new Legend substation. | TX | TX | BaseRel |  |  |  | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9814 | 2017-01-09 | 16-ETI-014-3 | PARIP Legend 230 kV: Construct New Substation | Port Arthur Reliability Improvement Plan: Construct a new substation and cut in 230 kV line 829(Port Acres to Keith Lake). The new substation will be named Legend. | TX | TX | BaseRel |  |  |  | 2020-06-01 | 2020-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9817 | 2017-01-09 | 16-ETI-016 | Helbig 230 kV: Reconfigure Bus | Reconfigure the bus work at the Helbig 230 kV substation to represent a ring bus. | TX | TX | BaseRel |  |  | 6626348 | 2019-12-01 | 2019-12-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | South | Entergy-TX | 9818 | 2017-01-09 | 16-ETI-017 | Stowell to Himex 69 kV: Convert to 138 kV | Convert the Stowell to Himex 69 kV line to 138 kV. The line is already built to 138 kV standards. | TX | TX | BaseRel |  |  | 12730884 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | GRE | 7884 | 2017-01-09 | 203079 | Riverview 345/115/69 kV Substation | Construct the new Riverview 345/115/69 kV substation directly off the CapX 345 kV line between the Melrose East and Millwood 69 kV substations. The transformers will be a 448 MVA, 345/115 kV transformer and a 70 MVA 115/69 MVA transformer. This substation will initially have two 345 line terminating breakers, a single 345 kV breaker on the high side of the transformer, two 69 kV line termination breakers in addition to a low side 69 kV breaker. The substation should be designed for future development and be laid out for nine 345 breaker (3 rows of 345 kV breakers in a breaker and half scheme), six 115 kV (2 rows of 115 kV breakers in a breaker and half scheme), and four 69 kV breakers in a straight bus configuration. | MN | MN | Other |  | Reliability | 21008516.22 | 2018-12-10 | 2018-12-10 | 345 | 69 | Bottom-Up
A in MTEP16 | A | West | GRE, MP | 4378 | 2017-01-09 | 202970 | Menahga Area Project | Build Hubbard to Blueberry to Red Eye 115 kV | MN | MN | Other |  | Load Growth | 29360748.68 | 2016-11-16 | 2020-09-01 | 115 | 34.5 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | Guthrie-White Pole Rd-Panora 34 to 69 kV Conversion | Convert 34.5 kV system between Guthrie - White Pole Rd (new breaker station) - Menlo - Redfield - Panora - Guthrie to 69 kV operation | IA | IA | Other |  | Age and Condition | 3385176 | 2018-12-31 | 2019-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9665 | 2018-05-17 | PCI-Oak Hill 34 to 69 Conv | PCI-Oak Hill 34 to 69 kV Conv | Convert 34.5 kV system between PCI and Oak Hill to 69 kV operation | IA | IA | Other |  | Age and Condition | 33600 | 2019-04-01 | 2019-04-01 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | Emerald Isle-Beverly 34 to 69 kV Conv | Convert 34.5 kV system between Beverly and Emeral Isle to 69 kV operation. | IA | IA | Other |  | Age and Condition | 10705088 | 2020-12-31 | 2021-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | Cedar Rapids-North Liberty area-Hills Upgrades | Add a new Hills area 345/161kV source and upgrade the 161 and 69kV systems in the North Liberty area. This includes a new North Liberty 161/69kV substation also. | IA | IA | BaseRel |  |  | 75440438 | 2019-12-31 | 2025-12-31 | 345 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9670 | 2017-01-09 | Columbus Junction Breaker add | Columbus Junction 69 kV Breaker Addition | Add 69 kV breaker at the Columbus Junction substation. | IA | IA | Other |  | Load Growth | 932101 | 2020-12-31 | 2020-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9672 | 2017-01-09 | 76th AVE SW | 76th AVE SW Substation | ITC will need to construct a new four (4) terminal, four (4) breaker 69 kV substation southeast of the city of Cedar Rapids, Iowa in order to eliminate the coordination and system protection issues. The existing PCI – Tharp 69 kV transmission line will need to be tapped and re-routed into the new substation. The existing Prairie Creek Ckt. 0210 will need to be re-routed and terminated into the new substation when the area is converted as well. A 13.2 MVAR capacity bank will be installed at the new substation to provide voltage support for the area. | IA | IA | Other |  | Age and Condition | 4056304 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | Doud-Lyon 34 to 69 kV Conv | Construct a new 69 kV breaker station near Lyon with 3 line terminals. The station should be laid out to accommodate a future additional breaker position for an Alliant Energy distribution transformer. Re-connect or extend 69 kV taps to the connected distribution substations and convert to 69 kV operation from the new station near Lyon to Doud. | IA | IA | Other |  | Age and Condition | 4638479 | 2020-12-31 | 2021-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9901 | 2017-01-09 | Mount Ayr 69 kV Sub Rebuild | Mount Ayr 69 kV Substation Rebuild | Complete rebuild of the substation with all new equipment was proposed. Due to space limitations at the existing site, a new Kneedler (Mt. Ayr) 69kV breaker station will be constructed just north of the Mt. Ayr site. The existing 8.1MVAr cap will be replaced with a 3-stage 8.4MVAr (25.2MVAr total) capacitor bank at the Kneedler sub site. | IA | IA | Other |  | Age and Condition | 4118915 | 2018-08-01 | 2018-08-01 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9907 | 2018-05-09 | Summit to Dovray 69 kV Rebuild | Summit to Dovray 69 kV Rebuild | Phase 1: Rebuild ~12.9 miles of old line to new T2-4/0 ACSR | MN | MN | Other |  | Age and Condition | 9162091 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9908 | 2018-05-09 | Dovray to Fulda 69 kV Rebuild | Dovray to Fulda 69 kV Rebuild | Rebuild ~14.5 miles of old line to new T2-4/0 ACSR | MN | MN | Other |  | Age and Condition | 9410124 | 2023-12-31 | 2023-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9910 | 2018-05-09 | Fulda to Heron Lake 69 kV Rebuild | Fulda to Heron Lake 69 kV Rebuild | Rebuild ~20.14 miles of old line to new T2-4/0 ACSR | MN | MN | Other |  | Age and Condition | 14976652 | 2024-12-31 | 2024-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9985 | 2017-01-09 | Newhall-Williamsburg 161 kV | Newhall-Williamsburg 161 kV Rebuild | Rebuild Williamsburg 115kV tap to 161kV | IA | IA | Other |  | Age and Condition | 40174153 | 2020-05-04 | 2020-05-04 | 161 | 161 | Bottom-Up
A in MTEP16 | A | West | ITCM | 9988 | 2017-01-09 | Newhall 161 kV Breaker Station | Newhall 161 kV Breaker Station | Construct a new 3 position 161kV breaker station | IA | IA | Other |  | Age and Condition | 8090882 | 2019-12-31 | 2019-12-31 | 161 | 161 | Bottom-Up
A in MTEP16 | A | West | ITCM | 10022 | 2017-01-09 | PCI-Mt.Vernon-Lisbon-76thAVE Conv | PCI-Mt.Vernon-Lisbon-76th AVE Conv | ITC will be converting the PCI to Mt. Vernon to Lisbon North to 76th Ave. substation from 34.5 kV operation to 69 kV operation. To accommodate the conversion, a 69 kV breaker and associated equipment will be installed at the PCI substation, two (2) 69 kV breakers and associated equipment will be installed at the Lisbon North substation, approximately 0.6 mile of new 69 kV transmission line will be constructed to complete the PCI to 76th Ave circuit and OPGW will need to be installed. | IA | IA | Other |  | Age and Condition | 5793932 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 10023 | 2017-01-09 | ITCM Asset Blanket | ITC Midwest Asset Replacement Program | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance have increased potential for misoperations and higher maintenance costs associated with their ongoing use. | IA,MN,IL | IA,MN,IL | Other |  | Age and Condition | 111600000 | 2017-12-31 | 2019-12-31 | 345 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 10024 | 2017-01-09 | Cust Interconnet Blanket | ITCM Customer Interconnects with short lead time | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | Other |  | Load Growth | 2000000 | 2019-12-31 | 2019-12-31 | 345 | 69 | Bottom-Up
A in MTEP16 | A | West | ITCM | 10303 | 2017-01-09 | Willaimsburg 161kV Temp Conv | Williamsburg 161kV Temp Conversion | To provide a reliable conversion to 69kV the 34.5kV will need temporary configurations to provide a reliable transition. The Williamsburg 115kV high side will be converted to 161kV. The two aging and miss-matched 115/34.5kV transformers will be replaced with a newer and larger 161/36kV transformer from the Hiawatha Substation. This will provide an increased level of reliability to Williamsburg by serving the high-side from a newly rebuilt and shorter 161kV line compared to an older and longer 115kV line. | IA | IA | Other |  | Reliability | 1204368 | 2019-03-18 | 2019-03-18 | 161 | 34 | Bottom-Up
A in MTEP16 | A | West | ITCM | 11163 | 2018-05-08 | Devils Creek | Devils Creek | 69 kV customer interconnection near Ft. Madison, IA. Build a new Devils Creek 69kV distributions substation. | IA | IA | Other |  | Load Growth | 2724521 | 2018-12-01 | 2018-12-01 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | ITCM, XEL | 11883 | 2017-01-09 |  | Huntley - Wilmarth 345 kV | Huntley to Wilmarth 345 kV Single Ckt Transmission Line - 38.5 miles | MN | MN | MEP | Shared |  | 108000000 | 2022-01-01 | 2022-01-01 | 345 | 0 | Top-Down
A in MTEP16 | A | East | ITCT | 9685 | 2017-01-19 | ITC_15_016 | Jacob - St. Clair 120 kV Sag Remediation | Remediate the Sag Limit on Jacob-St. Clair 120 kV to 292 MVA (1405 Amp) | MI | MI | BaseRel |  |  | 139000 | 2018-06-01 | 2018-06-01 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9692 | 2017-01-09 | ITC_15_022 | Seneca - Spokane 120 kV Sag Remediation | Remediate the Sag Limit on Seneca-Spokane 120 kV to 283 MVA (1362 Amp) | MI | MI | BaseRel |  |  | 339000 | 2018-12-31 | 2018-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9883 | 2017-01-09 | ITC_15_025 | Ironton 120 kV-Install Two Line Breakers | Install two 120 kV breakers to terminate the two River Rouge–Ironton 120 kV connections at Ironton | MI | MI | BaseRel |  |  | 910000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9884 | 2017-01-09 | ITC_15_015 | Belle River - Pontiac 345 kV Sag Remediation | Raise the Sag Limit on Belle River-Pontiac 345 kV to 1414 MVA (2366 Amp) | MI | MI | Other |  | Reliability | 340000 | 2019-12-31 | 2019-12-31 | 345 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9887 | 2017-01-09 | ITC_15_019 | Pontiac - Wixom 345 kV Sag Remediation | Raise the Sag Limit on Pontiac-Wixom 345 kV to 1185 MVA (1983 Amp) | MI | MI | Other |  | Reliability | 305000 | 2019-12-31 | 2019-12-31 | 345 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9900 | 2017-01-09 | ITC_15_020 | River Rouge - Ironton #2 120 kV Sag Remediation | Raise the Sag Limit on River Rouge-Ironton #2 120 kV to 271 MVA (1304 Amps) | MI | MI | BaseRel |  |  | 340000 | 2018-12-31 | 2018-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9902 | 2017-01-09 | ITC_15_030 | Sterling 120 kV Ring Bus | Install a new 120 kV bus and one 120 kV breaker to convert Sterling to a ring bus. Also move the Sterling transformer #201 connection to the new bus and install a disconnect switch on the low side. Breaker “HT” will become the bus-tie between bus #101 and #104 | MI | MI | BaseRel |  |  | 1100000 | 2018-12-31 | 2018-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9994 | 2017-01-09 | ITC_15_007 | Custer - Monroe 120 kV Line Rebuild | Rebuild the entire Custer – Monroe 120 kV line. Pre-build it to 230 kV construction to facilitate possible future 230 kV expansion in southern Michigan. Replace all existing structures and conductor with new double-circuit structures that are designed for bundled 954 ACSR 54/7 conductor and install this conductor along with an OPGW path. Also, upgrade terminal equipment at Custer and Monroe | MI | MI | BaseRel |  |  | 14500000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 9999 | 2017-01-09 |  | 2018 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Other |  | Reliability | 53250000 | 2018-12-31 | 2018-12-31 | 345 | 120 | Bottom-Up
A in MTEP16 | A | East | ITCT | 10000 | 2017-01-09 |  | 2019 ITCT Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Other |  | Reliability | 53310000 | 2019-12-31 | 2019-12-31 | 345 | 120 | Bottom-Up
A in MTEP16 | A | East | ITCT | 10010 | 2017-01-09 |  | ITCT Customer Interconnections - Year 2019 | Customer interconnection requests and retirements. | MI | MI | Other |  | Load Growth | 2000000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 10243 | 2017-01-09 |  | Navarre 120 kV Breakers HX Replacement | Upgrade the existing Navarre 120 kV breaker HX to have an interrupting capability of 50 kA. | MI | MI | Other |  | Reliability | 70000 | 2018-06-30 | 2018-06-30 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 10425 | 2018-06-18 |  | J340 Generation Interconnection | Rebuild 5.3 miles of the existing 120 kV Cosmo tap to double circuit steel poles, relocate the Harvest Wind tap point, and string 954 ACSR to create the new J340-Harvest Wind-Grassmere 120 kV line. Expand the Grassmere station and install 1-345 kV breaker, a 345/120 kV transformer, and a 120 kV breaker on the low side of the transformer to tie in the new line. | MI | MI | GIP | Shared |  | 15150000 | 2017-09-01 | 2018-12-31 | 345 | 120 | Externally Driven
A in MTEP16 | A | East | ITCT | 10924 | 2017-01-09 |  | ITCT Pole Top Switch Additions/Replacement Program 2018 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | Other |  | Reliability | 2400000 | 2018-12-31 | 2018-12-31 | 120 | 0 | Bottom-Up
A in MTEP16 | A | East | ITCT | 11583 | 2017-06-27 |  | J301 Generation Interconnection | TO Interconnection Facilities and Network Upgrades associated with the J301 generation interconnection project. This includes a new 345 kV, 3-breaker substation fed by looping the 345 kV Bauer-Ringle line. | MI | MI | GIP | Shared |  | 9497000 | 2018-10-15 | 2018-10-15 | 345 | 0 | Externally Driven
A in MTEP16 | A | East | ITCT | 11584 | 2017-06-27 |  | J308 Generation Interconnection | 345 kV, 3 Breaker Substation with relay upgrades and 0.1 miles of dbl ckt 345 kV to new substation (tapping greenwood-rapson) | MI | MI | GIP |  |  | 9421000 | 2018-10-15 | 2018-10-15 | 345 | 0 | Externally Driven
A in MTEP16 | A | East | ITCT | 11604 | 2017-01-24 |  | J419 Generation Interconnection | Network Upgrades and TOIFs associated with the J419 project. These include extending bus 103 and installing a 120 kV breaker with associated disconnects at Milan substation. | MI | MI | GIP | Shared |  | 803000 | 2019-06-30 | 2019-06-30 | 120 | 0 | Externally Driven
A in MTEP16 | A | South | LAFA | 8821 | 2018-07-27 |  | Northeast to Peck | 69kv line connecting Northeast station to Peck station. | LA | LA | Other |  | Load Growth | 3360000 | 2020-06-30 | 2020-06-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | MDU | 4140 | 2017-01-09 | Bowdle | Bowdle Jct | Build a new Bowdle Jct to replace old Bowdle substation | SD | SD | Other |  | Reliability | 5500000 | 2019-03-31 | 2019-03-31 | 115 | 41.6 | Bottom-Up
A in MTEP16 | A | West | MDU | 9120 | 2017-01-09 |  | Leola | A new 115 kV transmission line from the Ellendale Jct. Substation to a new Leola Jct. 115/41.6 Substation. The new Leola Jct. substation will connect to the existing Ellendale-Bowdle 41.6 kV line. | SD,ND | SD | Other |  | Reliability | 12835000 | 2018-12-31 | 2019-09-30 | 115 | 41.6 | Bottom-Up
A in MTEP16 | A | West | MEC | 9947 | 2018-08-28 |  | Polk City Substation and Lines | Build a new 33 MVA 161-13 kV distribution substation near Polk City, Iowa with 161 kV line taps connecting to the Bittersweet-NE Ankeny 161 kV line. **The name of Polk City was updated to "Big Creek" and is represented in modeling data as such** | IA | IA | Other |  | Load Growth | 7000000 | 2018-12-31 | 2018-12-31 | 161 | 13 | Bottom-Up
A in MTEP16 | A | East | METC | 2809 | 2017-01-09 | 87 | Garfield Avenue – Hemphill 138 kV Rebuild | Rebuild a ~9.5 mile-long portion of 336 ACSR conductor utilizing 1431 ACSR conductor on double-circuit, 138 kV structures, relocate a portion of the Weadock – Hemphill 138 kV line to the other side of the new structures. | MI | MI | BaseRel | Excluded |  | 11000000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 3133 | 2017-01-09 | METC_15_022 | Bell Road - Cornell 138 kV Rebuild | Rebuild a ~4.3 mile-long portion of the Claremont – Cornell 2 line between Bell Road and Cornell. | MI | MI | BaseRel | Not Shared |  | 4350000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9695 | 2017-01-09 | METC_15_028 | Bullock 138 kV Terminal Equipment Upgrade (Dow Corning Line) | Upgrade terminal equipment at Bullock on the Dow Corning 138 kV line | MI | MI | BaseRel |  |  | 300000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9705 | 2017-01-09 | METC_15_024 | Alma - Regal #2 138 kV Sag Remediation | Remediate the sag limit on the Alma – Regal 2 138 kV line to a minimum of 208 MVA / 871 Amps | MI | MI | BaseRel |  |  | 200000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9876 | 2017-06-23 | METC_15_027 | Karn - Manning 138 kV Sag Remediation | Remediate the sag limit on the Karn - Manning 138 kV line to a minimum of 396 MVA / 1657 Amps and upgrade terminal equipment at Karn | MI | MI | BaseRel |  |  | 620000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9932 | 2017-01-09 | METC_14_026 | Karn - Saginaw River 138 kV Line Rebuild | Rebuild a ~2.7 mile-long portion of six-wired 3/0 copper conductor utilizing 1431 ACSR conductor on single-circuit, 138 kV structures, remediate the sag limit on the existing 1431 ACSR conductor to a minimum of 412 MVA / 1724 Amps, and upgrade terminal equipment at both Karn and Saginaw River stations | MI | MI | BaseRel |  |  | 8500000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9956 | 2017-01-09 |  | 2018 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs | MI | MI | Other |  | Age and Condition | 49398000 | 2018-12-31 | 2018-12-31 | 345 | 138 | Bottom-Up
A in MTEP16 | A | East | METC | 9959 | 2017-01-09 |  | METC Customer Interconnections - Year 2019 | Customer interconnection requests and retirements. | MI | MI | Other |  | Load Growth | 2500000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9960 | 2017-01-09 |  | 2019 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | MI | Other |  | Age and Condition | 49398000 | 2019-12-31 | 2019-12-31 | 345 | 138 | Bottom-Up
A in MTEP16 | A | East | METC | 9972 | 2017-01-09 |  | METC Four Mile Control Relocation Project | Replace METC relaying and controls at Four Mile Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other |  | Other Local Needs | 3520000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9975 | 2017-01-09 |  | METC Verona Control Relocation | Replace METC relaying and controls at Verona Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other |  | Other Local Needs | 2940000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9978 | 2017-01-09 |  | Eureka 138 kV Breaker Replacement | Replace the Eureka 138 kV circuit switcher 256 with a synchronous breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA. | MI | MI | BaseRel |  |  | 510000 | 2018-06-30 | 2018-06-30 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 9984 | 2017-01-09 |  | Tittabawassee 345 kV Breaker 38H9 Replacement | The proposed solution is to replace the Tittabawassee 345 kV breaker 38H9 with a breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA. | MI | MI | BaseRel |  |  | 790000 | 2018-06-30 | 2018-06-30 | 345 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 10286 | 2017-01-09 | METC_12_001 | Campbell 138 kV Remove Circuit Breaker 588 Sparing Capability | Remove the Campbell 508 disconnect switch. Modify the relaying to remove 588 breaker sparing capability. | MI | MI | Other |  | Reliability | 88000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | Coldwater Phase 2 Wagner | Install a new 138 kV, 3 breaker substation (tentatively named Wagner) in a ring bus configuration in Union City, MI. Loop the existing 138 kV Alder Creek-Batavia line into Wagner, and modify relaying at Batavia to accommodate the new substation. Construct an approx. 13 mile, 138 kV line between Wagner and Newton on 138 kV, single circuit, steel poles. | MI | MI | Other |  | Load Growth | 34409000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | East | METC | 11243 | 2018-03-27 | METC_15_019 | Verona - Barnum Creek Jct. 138 kV Rebuild | Rebuild the Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit using 954 ACSR and OGPW on new 230 kV future double circuit structures. Replace PTS 3186. Upgrade terminal equipment at the Verona station. Also reconductor approximately 0.6 miles of the Verona – Foundry 138 kV circuit where it shares common structures with the Verona – Batavia 138 kV circuit. | MI | MI | BaseRel |  |  | 13300000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP16 | A | West | MP | 7910 | 2017-01-09 | 5 Line Upgrade | 5 Line Upgrade | Increase capacity of Brainerd - Mud Lake 115 kV Line | MN | MN | BaseRel |  |  | 2200000 | 2018-12-31 | 2018-12-31 | 115 | 0 | Bottom-Up
A in MTEP16 | A | West | MP | 7996 | 2017-01-09 | 15 Line Upgrade | 15 Line Upgrade | Rebuild & reconductor Fond Du Lac - Hibbard 115 kV Line | MN | MN | BaseRel |  |  | 10000000 | 2019-11-01 | 2019-11-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | West | MP | 7997 | 2017-01-09 | 15th Ave West | 15th Avenue West Modernization | Rebuild & modernize existing 15th Avenue West Substation, including new 14 kV switchgear, one new 115/14 kV transformer, replace 3 115 kV breakers and other 115 kV equipiment, and miscellaneous site improvements | MN | MN | Other |  | Age and Condition | 8875000 | 2017-12-31 | 2018-12-31 | 115 | 13.8 | Bottom-Up
A in MTEP16 | A | West | MP | 9622 | 2017-01-09 | 83 Line Upgrade | 83 Line Upgrade | Replace limiting elements at Boswell & Blackberry to restore 100C rating | MN | MN | Other |  | Reliability | 500000 | 2019-06-01 | 2019-06-01 | 230 | 0 | Bottom-Up
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | Nemadji 115 kV Project | New switching station in Gary - Stinson 115 kV Line near Enbridge's Superior Terminal; 115 kV line development around the Superior Terminal | WI | WI | Other |  | Reliability | 8690000 | 2019-07-01 | 2019-07-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | Laskin-Tac Harbor Voltage Conversion | Convert Laskin - Tac Harbor 138 kV system to 115 kV and add 2x20 MVar capacitor Banks at Hoyt Lakes | MN | MN | Other |  | Age and Condition | 2484000 | 2020-12-31 | 2020-12-31 | 115 | 13.8 | Bottom-Up
A in MTEP16 | A | West | OTP | 9990 | 2017-01-09 |  | Devils Lake East 41.6 kV | Relay upgrades | ND | ND | Other |  | Reliability | 37500 | 2017-12-31 | 2017-12-31 | 41.6 | 0 | Bottom-Up
A in MTEP16 | A | West | OTP | 10007 | 2017-09-26 |  | Max to Ryder 41.6 kV Line Upgrade | The project will start in 2016 and be completed in 2018. The project will replace failing insulation, cross arms and poles identified through patrols and inspections and replace the failing 1/0 ACSR conductor for approximately 34 miles between Max, ND and Ryder, ND. | ND | ND | Other |  | Age and Condition | 2500000 | 2019-12-31 | 2019-12-31 | 41.6 | 0 | Bottom-Up
A in MTEP16 | A | Central | PPI | 9564 | 2017-12-21 | 2016-12,38,39,43 | Turris Tap Breaker Station, Turris-Athens 138 kV, Athens 138/69 kV station | Construct Turris tap 138 kV 4-breaker station, Turris-Athens 138 kV transmission line, Athens 138/69 kV substation, Athens Tap 69 kV switching station | IL | IL | Other |  | Reliability | 12173000 | 2022-12-31 | 2022-12-31 | 138 | 69 | Bottom-Up
A in MTEP16 | A | Central | Vectren | 4393 | 2017-06-30 | 2013SIGE7 | Y67-2 Dubois - Huntingburg Rebuild | Rebuild and Reconductor approx. 3.5 miles of 69 kV | IN | IN | Other |  | Load Growth | 2625000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | Central | Vectren | 9946 | 2017-06-30 | 2016SIGE11 | Adams Substation for Distribution | 69kV/12kV distribution substation to serve customer load (Y65). | IN | IN | Other |  | Load Growth | 4000000 | 2019-12-31 | 2019-12-31 | 138 | 12 | Bottom-Up
A in MTEP16 | A | Central | Vectren | 9952 | 2017-06-30 | 2016SIGE13 | Y43 Berry Plastics Sub Loop Feed | Berry Plastics Substation loop feed (69kV Y43). | IN | IN | Other |  | Load Growth | 1850000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | East | WPSC | 4385 | 2017-01-09 | BP-FV | Burnips to Fairview | Burnips to Fairview Rebuild | MI | MI | Other | Not Shared | Reliability | 3500000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | East | WPSC | 9899 | 2017-01-09 | RW-SV Rebuild | Redwood to Scottville Rebuild | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor | MI | MI | Other |  | Reliability | 10500000 | 2018-12-01 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | East | WPSC | 9915 | 2017-01-09 | OE Relay Upgrade | Oden Relay Upgrade | Upgrade the relaying on the Oden-Emmet terminal | MI | MI | Other |  | Age and Condition | 35000 | 2017-12-31 | 2017-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | East | WPSC | 11023 | 2017-01-09 |  | J392 Generator Interconnection | Upgrades determined in the FEB2015 DPP studies to connect J392. Wolverine to construct the following: -Advance 138kV station and 138/69kV transformer -Gaylord 138kV 4 breaker ring bus to accommodate 3rd line into the station (2016) -Gaylord 138kV 6 breaker ring bus and 2nd 138/69KV transformer (2018) -Upgrades to Elmira, Deer Lake and Alpine distribution subs from 69kV to 138kV operation -Conversion of existing Gaylord - Advance 69kV line to 138kV operation, new lines will be Gaylord - Van Tyle and Van Tyle to Advance -Rebuild of Gaylord - Livingston 138kV line to 795ACSS | MI | MI | GIP |  |  | 24930414.65 | 2016-04-30 | 2018-10-31 | 138 | 13.09 | Externally Driven
A in MTEP16 | A | West | XEL | 4696 | 2017-01-09 |  | Rebuild Prentice-Medford 69 kV | Rebuild this line to 795 ACSR due to age and condition of the line | WI | WI | Other |  | Age and Condition | 4449013 | 2019-05-01 | 2019-05-01 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10045 | 2017-01-09 |  | City of Chaska Interconnection | Build an in-and-out from double circuit 115 kV just south of Bluff Creek. This in-and-out will serve the City of Chaska’s new distribution substation. New line will 1.7 mi following road from POI to potential new sub | MN | MN | Other |  | Reliability | 3200000 | 2018-11-15 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10069 | 2017-01-09 |  | Twin Creek Breaker Station | Install a 2 or 3 position 69 kV breaker station - Breakers to Radisson and Osprey/Big Falls - Possible breaker looking toward the Enbridge loads or just switches - Replaces the planned 3-way tap switch on line W3474 that was part of the Enbridge expansion/DPC N-2 retirement plan | WI | WI | Other |  | Reliability | 2866000 | 2019-12-15 | 2019-12-15 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10074 | 2017-01-09 |  | Airport – Rogers Lake 115 kV Rebuild | This project rebuilds the Airport - Rogers Lake 115 kV line due to age and condition. The new line would be built using 795 ACSS conductor. | MN | MN | Other |  | Age and Condition | 4092000 | 2020-12-15 | 2020-12-15 | 115 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10076 | 2017-01-09 |  | West St Cloud – Millwood Tap Rebuild | Rebuild 24 miles of line from West St. Cloud to Millwood Tap. This new line will be built using 477 ACSR conductor. | MN | MN | Other |  | Age and Condition | 10400000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10288 | 2017-01-09 |  | Osprey 69 kV Expansion | Install 69 kV straight bus with 2 additional 69 kV breakers. Reterminate line from Whitetail Tap and Flambeau into Osprey. Rebuild the last 0.4 mies of 69 kV on the Whitetail Tap line to match the rest of the conductor type | WI | WI | Other |  | Reliability | 2880000 | 2018-12-30 | 2018-12-30 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10289 | 2017-01-09 |  | Elmwood - Eau Galle Rebuild | Rebuild the existing 2/0 conductor to 477 ACSR due to age and condition | WI | WI | Other |  | Age and Condition | 4109095 | 2015-12-01 | 2018-10-15 | 69 | 0 | Bottom-Up
A in MTEP16 | A | West | XEL | 10291 | 2017-01-09 |  | New LCO Hydro Transformer | Install single 34.5/23.9 kV TR to connect the Lac Courte Oreilles (LCO) hydro facility to the NCP system near Radisson | WI | WI | Other |  | Load Growth | 180000 | 2019-12-01 | 2019-12-01 | 34.5 | 23.9 | Bottom-Up
A in MTEP15 | A | South | AECC | 8320 | 2015-12-28 |  | Tap EAI El Dorado - Monticello East 115 kV line: Construct 115 kV line, Hermitage 115/13.2 kV substation | Tap Entergy El Dorado 115 kV line: Construct 1.6 miles 115 kV line and Hermitage 115/13.2 kV substation. | AR | AR | Other |  | Load Growth | 8060000 | 2019-05-15 | 2019-05-15 | 115 | 13.2 | Bottom-Up
A in MTEP15 | A | South | AECC | 8402 | 2018-08-22 |  | Camden South to Camden West 115kV transmission line, 115/13.2kV substation | Construct 7 mile 115kV transmission line from the existing Camden South delivery point to the proposed Camden West substation, construct Camden West 115/13.2kV substation. | AR | AR | Other |  | Load Growth | 3950000 | 2022-12-01 | 2022-12-01 | 115 | 13.2 | Bottom-Up
A in MTEP15 | A | South | AECC | 8420 | 2017-10-25 |  | Ingram 161/25kV Substation | New 161/25kV substation with inital load of 12,000kW. | AR | AR | Other |  | Load Growth | 7611500 | 2018-10-01 | 2019-10-31 | 161 | 24.9 | Bottom-Up
A in MTEP15 | A | South | AECC | 8480 | 2015-12-28 |  | Gainesville 161/13.2kV Substation | New 161/13.2kV substation with initial load of 9,500 KW. | AR | AR | Other |  | Load Growth | 7000000 | 2017-01-01 | 2017-01-01 | 161 | 13.2 | Bottom-Up
A in MTEP15 | A | Central | AmerenIL | 7825 | 2015-12-28 |  | Mascoutah Municipal (Hilgard) 138 kV Breaker Station | Install a 4-breaker 138 kV ring bus (2000 A, 40 kA) at or near the tap to Mascoutah Municipal on the existing Turkey Hill-Ashley 138 kV Line 1482. | IL | IL | Other |  | Reliability | 6700000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | AmerenIL | 8054 | 2018-03-28 |  | Tilden Jct to Sparta 138kv | Tilden Jct to Sparta 138kv - Reconductor approx. 5.7 of 4.77 KCM ACSR | IL | IL | Other |  | Other Local Needs | 2710721 | 2040-12-01 | 2040-12-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | AmerenIL | 8055 | 2018-03-28 |  | Sparta Tap - Steelville - 138kv | Sparta Tap to Steelville 138kv - Reconductor approx. 7.4 of 4.77 KCM ACSR | IL | IL | Other |  | Other Local Needs | 2318247 | 2040-12-01 | 2040-12-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | AmerenIL | 8134 | 2015-12-28 |  | Tilden Jct to Tilden 138kv | Tilden Jct to Tilden 138kv - Reconductor one span of 1113 KCM ACSR | IL | IL | Other |  | Other Local Needs | 175920 | 2015-12-01 | 2015-12-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | AmerenIL | 8581 | 2015-12-28 |  | California Ridge Wind Farm Expansion | Increase of plant output capacity to 250 MW | IL | IL | Other |  | Reliability |  | 2017-03-02 | 2017-03-02 | 138 | 0 | Bottom-Up
A in MTEP15 | A | West | ATC | 4421 | 2015-12-28 | PR06011 | Construct Williams Bay 138 kV Substation | Loop Elkhorn - Brick Church (X-44) 138kV line in and out of Williams Bay, add two 138kV line breakers and addition of a new distribution transformer | WI | WI | Other |  | Load Growth | 4200000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | West | ATC | 4732 | 2015-12-28 | PR06105 | Construct Ogden Street 69 kV T-D | Construct a new 69kV line from Ogden St. - Bayshore, rebuild Bayshore - 2nd St. - Fiber switching structure (N-14) 69kV and install two line breakers at Odgen St. | WI | WI | Other |  | Load Growth | 10400000 | 2021-01-12 | 2021-01-12 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ATC | 7602 | 2015-12-28 | PR05440 | Rerate Bunker Hill - Kelly 115 kV | Rerate Bunker Hill - Kelly 115 kV based on SBRM. This project is a part of PR05440. | WI | WI | BaseRel |  |  | 3100000 | 2019-11-01 | 2019-11-01 | 115 | 0 | Bottom-Up
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | Rebuild Bunker Hill - Blackbrook 115 kV | Rebuild Blackbrook - Bunker Hill portion of M-13. Retire Blackbrook and Bunker Hill stations and build new Roehring Rd ring bus. | WI | WI | BaseRel |  |  | 29724000 | 2019-05-01 | 2019-05-01 | 115 | 0 | Bottom-Up
A in MTEP15 | A | West | ATC | 8660 | 2017-09-15 | PR07030 | Construct Somers 138 kV T-D | Reconfigure Somers substation to add second 138/24.9 kV distribution transformer. | WI | WI | Other |  | Load Growth | 4000000 | 2018-12-14 | 2018-12-14 | 138 | 24.9 | Bottom-Up
A in MTEP15 | A | West | ATC | 9080 | 2016-12-30 | PR07203, F4691, WO601606 | Install W. Marinette 138-69 kV transformer high-side protection | Install high and low side breakers on existing 138/69 kV transformer. | WI | WI | Other |  | Reliability | 2200000 | 2019-03-31 | 2019-03-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC | 3435 | 2015-12-28 | LRP1 | Rome Junction to West Owensboro 69 kV reconductor. | Reconductor 5.8 miles of 3/0 and 267 MCM ACSR with 336 MCM ACSS | KY | KY | Other | Not Shared | Reliability | 440000 | 2017-12-31 | 2017-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC | 3436 | 2015-12-28 | LRP2 | Wilson to Sacremento 69 kV line addition | New 11 mile line and line terminal at Wilson | KY | KY | Other | Not Shared | Reliability | 2100000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC | 3437 | 2015-12-28 | LRP3 | Thruston Junction to East Owensboro reconductor. | Reconductor .4 miles of 3/0 ACSR with 336 MCM ACSR | KY | KY | Other | Not Shared | Reliability | 40000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC | 3438 | 2015-12-28 | LRP4 | Daviess County to Philpot Tap reconductor. | Reconductor 7.7 miles of 267 MCM ACSR with 336 MCM ACSS | KY | KY | Other | Not Shared | Reliability | 580000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC | 3441 | 2015-12-28 | LRP7 | Olivet Church Road to Olivet Church Road Tap 69 kV reconductor. | Reconductor 1.4 miles of 4/0 ACSR with 336 MCM ACSS | KY | KY | Other | Not Shared | Reliability | 150000 | 2015-12-31 | 2015-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC | 3444 | 2015-12-28 | LRP10 | Meade County 161/69 transformer addition | Add a third 56 MVA transformer to the existing Meade County substation. Modified to replace both 56 MVA transformers with two 100 MVA transfomers. | KY | KY | BaseRel | Not Shared |  | 4000000 | 2015-12-31 | 2015-12-31 | 161 | 69 | Bottom-Up
A in MTEP15 | A | Central | BREC | 9420 | 2015-12-28 |  | Aleris Expansion | The proposed service plan for the Aleris load includes construction of a new-terrain 1.7 mile 161 kV radial circuit from Coleman EHV to serve the 28 MW load at the existing 161/13.8 kV delivery point. In addition, the plan includes a new-terrain 2 mile 161 kV circuit to provide service to a new 161/13.8 kV delivery point necessary to serve the expanded load (44 MW at 90% PF maximum contract demand). | KY | KY | Other |  | Reliability | 9550000 | 2017-03-31 | 2017-03-31 | 161 | 0 | Bottom-Up
A in MTEP15 | A | Central | BREC, Vectren | 10142 | 2018-06-22 |  | Duff-Coleman 345 kV | New 28.5 miles of single circuit, single conductor 345 kV transmission from Duff to Coleman, including sub upgrades (MISO) | KY | IN | MEP | Shared |  | 62140798 | 2021-01-01 | 2021-01-01 | 345 | 0 | Top-Down
A in MTEP15 | A | South | CLECO, Entergy-LA | 7988 | 2015-12-28 | 15-ELL-001 | Schriever to Bayou Vista 230 kV line(Entergy and CLECO Joint Project) | Construct approximately 30.44 miles of 230 kV line from Terrebonne 230 kV substation(Entergy owned) to Bayou Vista 230 kV substation (CLECO owned).This is a CLECO and Entergy joint project, Cleco's portion includes 12.1 miles of 230 kV line and expanding Bayou Vista substation to 230 kV and installing 230-138 kV auto transformer at Bayou Vista substation. Entergy's portion includes approx. 18.33 miles of 230 line from Schriever 230 kV substation. | LA | LA | BaseRel |  |  | 141735171 | 2018-05-25 | 2019-06-30 | 230 | 138 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7882 | 2015-12-28 | AMIN1047 | Bloomington Rogers St - Dunn St New 69kV Line | Construct new 69kV line from Bloomington Rogers St. to Bloomington Dunn St. (also includes Dunn St. bus work - AMIN1046) 954ACSR@100C | IN | IN | Other |  | Reliability | 4820000 | 2018-11-07 | 2018-11-07 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7883 | 2015-12-28 | AMIN1093 | Bloomington Downtown 69/12kV Sub | Construct new 22.4MVA - 69/12kV sub near downtown Bloomington in the new line established by project AMIN1047 / 7882. | IN | IN | Other |  | Reliability | 602000 | 2018-12-01 | 2018-12-01 | 69 | 12 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7885 | 2015-12-28 | AMIN1052 | Frankfort Burlington St - Middlefork 69kV Reconductor | Frankfort Burlington St to Middlefork 69kV - 69133 ckt: Reconductor 12.4 miles with 954ACSR@100C | IN | IN | Other |  | Reliability | 6636000 | 2018-10-01 | 2018-10-01 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7903 | 2015-12-28 | AMIN0701 | Martinsville SE - HE Park Ave 69kV Reconductor | Martinsville SE - HE Park Ave 69kV - 6903 ckt: Reconductor 3.4 miles with 954ACSR@100C | IN | IN | Other |  | Reliability | 2102000 | 2024-06-01 | 2024-06-01 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7911 | 2015-12-28 | AMIN1146 | Frankfort 230kV and 69kV Ring Buses | Frankfort 230kV: complete 4-brkr ring bus; 69kV: complete 6-brkr ring bus and retire Jefferson Jct with new line terminal for 69kV line to Frankfort Muni. | IN | IN | Other |  | Reliability | 5109020 | 2018-12-31 | 2018-12-31 | 230 | 69 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7946 | 2015-12-28 | AMIN1070 | Speed - Jeffersonville New 138kV Line | Loop existing 138kV line from Speed to Clark Maritime to Jeffersonville. Add 2.52 mile 138kV line section from Speed to Memphis Jct and tie into existing 13890 circuit. Add .01 mile 138kV line section from Jeffersonville Jct. to Jeffersonville sub. Install 138kV line terminals at Speed and Jeffersonville. | IN | IN | Other |  | Reliability | 5472000 | 2019-03-01 | 2019-03-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7963 | 2015-12-28 | AMIN1291 | New Castle 138kV Breaker Replacements | New Castle 138kV Breaker Replacements: replace OCB 13805, 13835, 13842, 13873, 13869-1, 13869-2, and relays at line terminals 13805, 13835, 13842, 13873, 13843 | IN | IN | Other |  | Age and Condition | 2516322 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7964 | 2015-12-28 | AMIN1292 | Kokomo Highland Park 69kV Breaker Replacements | Kokomo Highland Park Equipment: Replace OCB 69230-4, -5, -6, -7, OCB BK 7 CAP, 69kV primary UG cables, relays at terminals 6910, 6911, 6913, 6928, 6992, 13879, 13887, 138kV TRANSFER | IN | IN | Other |  | Age and Condition | 3351124 | 2018-12-31 | 2018-12-31 | 138 | 69 | Bottom-Up
A in MTEP15 | A | Central | DEI | 7992 | 2015-12-28 | AMIN1281 | Hillenbrand Jct - Andersonville Jct 69kV Rebuild | Hillenbrand Jct - Batesville North - Andersonville Jct 69kV - 6919 ckt: Rebuild 7.93 mile line with 477ACSR@100C - replacing all structures with steel poles. | IN | IN | Other |  | Age and Condition | 6472095 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 9246 | 2015-12-28 | TIN1607 | Lafayette SE to Laf S Jct2 new 138kV line | Lafayette SE to new Lafayette S Jct 2 (in existing 13808 ckt.) - build new 138kV - 1.75 mile - 954acsr@100c - 13899 ckt.; add new breaker in Laf SE ring; add (2) line switches at new jct and operate Laf S Jct to Laf S Jct 2 N.O. | IN | IN | BaseRel |  |  | 3976181 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | DEI | 9247 | 2015-12-28 | TIN1674-AMIN1151 | Lafayette 230 sub - 138Kv bus tie brkr and relays | Lafayette 230 sub - insert a redundant 138kV bus tie breaker in series with existing breaker; add redundant bus differential relays to both 138kV bus 1 and 2. Scope also includes (5) 138Kv antiquated breaker and relay replacements, disconnect switches and misc buswork. | IN | IN | BaseRel |  |  | 3400000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | South | Entergy-AR | 4666 | 2015-12-28 | 12-EAI-014 | Mabelvale-Bryant: Reconductor 115kV line | Identified in MCPS study to relieve congestion on the Mabelvale - Bryant - Bryant South 115 kV line. EAI has agreed to fund the upgrade to reduce congestion for the area. | AR | AR | Other |  | Other Local Needs | 8798431 | 2019-12-01 | 2019-12-01 | 115 | 0 | Bottom-Up
A in MTEP15 | A | South | Entergy-AR | 4669 | 2018-02-15 | 11-EAI-015 | Jim Hill Area Upgrades - Rebuild Jim Hill - Datto line and convert to 161kV | Rebuild the Jim Hill - Datto 115kV line and convert it from 115kV to 161kV operation. Install breakers at Corning. After the completion of the project, remove the mobile temporary capacitor bank at Datto. | AR | AR | BaseRel |  |  | 64418541 | 2019-05-31 | 2019-06-01 | 161 | 0 | Bottom-Up
A in MTEP15 | A | South | Entergy-LA | 4606 | 2017-10-05 | 14-EGL-004 | Fancy Point: Add 2nd 500-230 kV, 1200 MVA transformer | Add a second 500-230 kV, 1200MVA bank (composed of single phase units) at the Fancy Point substation. | LA | LA | BaseRel |  |  | 64346901 | 2019-04-07 | 2019-04-07 | 500 | 230 | Bottom-Up
A in MTEP15 | A | South | Entergy-LA | 7923 | 2015-12-28 | 15-EGL-005 | Lake Charles Bulk to Chlomal 69 kV Line: Reconductor line | Re-conductor Lake Charles Bulk to Chlomal 69 kV line and station equipment at Lake Charles bulk. | LA | LA | BaseRel |  |  | 10201219 | 2018-11-30 | 2018-11-30 | 69 | 0 | Bottom-Up
A in MTEP15 | A | South | Entergy-LA | 9285 | 2015-12-28 | 15-ELL-005 | Waterford - Vacherie 230 kV: Reconductor Line | Reconductor the Waterford to Vacherie 230 kV line. | LA | LA | BaseRel |  |  | 36631106 | 2019-06-01 | 2019-06-01 | 230 | 0 | Bottom-Up
A in MTEP15 | A | South | Entergy-TX | 9280 | 2015-12-28 | 15-ETI-016 | Cypress 500/138 kV: New 2nd Auto | Install second 500/138 kV auto at Cypress. | TX | TX | BaseRel |  |  | 17420213 | 2020-06-01 | 2020-06-01 | 500 | 138 | Bottom-Up
A in MTEP15 | A | South | Entergy-TX | 9482 | 2015-12-28 | 15-ETI-023 | China to Stowell 230 kV: Construct New Line | Construct a new 230 kV line from China to Stowell with a minimum rating of 1950 Amps. Install a 230/138 kV 400 MVA autotransformer at Stowell. | TX | TX | BaseRel |  |  | 66172893 | 2019-05-01 | 2019-05-01 | 230 | 138 | Bottom-Up
A in MTEP15 | A | South | Entergy-TX | 10487 | 2017-10-12 | 15-ETI-024; 15-ETI-025 | Western Region Economic Project(WREP): New Grimes to Lewis Creek 230 kV Line, New Grimes 345/230 kV Auto, & Newton Bulk to Leach 138 kV reconductor | Build a new 230 kV line from Grimes to Lewis Creek and install a second 345/230 kV auto at the Grimes station. Rebuild the ~25 mile long Newton Bulk – Leach 138 kV line. | TX | TX | Other |  | Other Local Needs | 150244892 | 2019-06-01 | 2020-06-01 | 345 | 138 | Bottom-Up
A in MTEP15 | A | South | ETEC | 8208 | 2015-12-28 | PRJ 07 | Luce Bayou 138kV | Cut into Tarkington-Long John 138 kV and install new Luce Bayou 138 kV substation. | TX | TX | Other |  | Load Growth | 16300000 | 2018-11-01 | 2018-11-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | West | GRE | 7912 | 2015-12-28 | 202919 | Lawndale to Bass Lake 2.0 mile 115 kV Rebuild | Construct two miles of 115 kV line with 795 ACSS conductor from Lawndale Tap, which is between Bass Lake and Cedar Island, to the high side structure of new Wright Hennepin Electric Cooperative's Lawndale #2 distribution substation. | MN | MN | Other |  | Load Growth | 2000000 | 2022-10-21 | 2022-10-21 | 115 | 115 | Bottom-Up
A in MTEP15 | A | Central | HE | 10343 | 2015-12-28 |  | Hubbell Primary 138 kV Ring Bus and Transformer Addition | Construct a 138kV ring bus and add a second 138/69kV transformer | IN | IN | Other |  | Load Growth | 10047000 | 2016-06-01 | 2016-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | Central | IPL | 9402 | 2015-12-28 |  | Guion - Westlane Line Upgrade | Upgrade conductor rating to 298 MVA via line clearance. | IN | IN | BaseRel |  |  |  | 2017-07-15 | 2017-07-15 | 138 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8042 | 2015-12-28 | Burl Sourth Sub | ITCM Burlington South Sub Modifications | Alliant Energy will install high side protection at the Burlington South substation. ITC protection equipment will be removed and switches will be replaced. | IA | IA | Other |  | Other Local Needs | 60000 | 2016-12-31 | 2016-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8043 | 2015-12-28 | Cust Interconnet Blanket | ITCM Customer Interconnections with short lead time | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL | IA,MN,IL | Other |  | Load Growth | 4800000 | 2017-12-31 | 2018-12-31 | 345 | 69 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8106 | 2015-12-28 | Hrn Lk Sub & Cap | ITCM Heron Lake Sub Rebuild and 161kV Cap | Install two 21 MVAR banks and rebuild the Heron Lake 161kV sub to a ring bus(designed for future bkr and 1/2). | MN | MN | BaseRel |  |  | 16929252 | 2022-12-31 | 2022-12-31 | 161 | 69 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8125 | 2015-12-28 | Anita-Grand Jct Rblds ph1 | ITCM Anita-Grand Junciton Area Rebuilds Phase 1 | Rebuild the Anita-Anita Muni-Adair-Thompson Junction (17.6 miles) to 69kV construction, continue to operate at 34kV | IA | IA | Other |  | Age and Condition | 11159322 | 2019-02-01 | 2019-02-01 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8128 | 2015-12-28 | Anita-Grand Jct Rblds ph2 | ITCM Anita-Grand Junction Area Rebuilds phase 2 | Add a new Redfield-Panora 69kV line (10 miles) and rebuild Bagley Jct-Bagley REC Tap-Bagley Town-Herndon-Dawson-Perry (19.25 miles) to 69kV construction, continue to operate at 34kV | IA | IA | Other |  | Age and Condition | 20693758.8 | 2018-08-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8129 | 2015-12-28 | Anita-Grand Jct Rblds ph3 | ITCM Anita-Grand Junction Area Rebuilds phase 3 | Rebuild the Jefferson WCC- Scranton line to 69kV(14.5 miles) and rebuild Perry-Madrid North (12.4 miles) to 69kV (continue to operate at 34kV). | IA | IA | Other |  | Age and Condition | 11837228.4 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8132 | 2015-12-28 | Anita-Grand Jct Rblds ph4 | ITCM Anita-Grand Junction Area Rebuilds phase 4 | Rebuild the Bagley Junction-Scranton (16 miles) distribution substation to 69kV (continue to operate at 34kV) | IA | IA | Other |  | Age and Condition | 8104200 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8150 | 2015-12-28 | Belle Plaine Conv | ITCM Belle Plaine Area Conversion | The conversion will need a new 161/69kV 100MVA transformer at Belle Plaine. Four 69kV breakers are needed at Belle Plaine. A three position breaker station will be needed south of Belle Plaine. A three position breaker station is needed west of Chelsea. | IA | IA | Other |  | Age and Condition | 11523054.6 | 2021-06-15 | 2024-12-31 | 161 | 34.5 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8151 | 2015-12-28 | B Plaine-Vinton-Traer | ITCM Belle Plaine-Vinton-Traer Conversion | Two additional 69kV breakers are needed at the Vinton substation. One additional 69kV breaker is needed at the Traer substation. | IA | IA | Other |  | Age and Condition | 1932610.8 | 2025-12-31 | 2025-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8152 | 2015-12-28 | Conroy-Parnell Conv | ITCM Conroy-Parnell Conversion | A new 161/69kV 100MVA transformer and three 69kV breakers are needed at the Parnell Substation. | IA | IA | Other |  | Age and Condition | 3812623.2 | 2025-12-31 | 2025-12-31 | 161 | 69 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8153 | 2015-12-28 | Parnell-Keswick Conv | ITCM Parnell-Keswick Conversion | Add a new Keswick three (3) terminal 69kV switch station | IA | IA | Other |  | Age and Condition | 2931082.8 | 2025-12-31 | 2025-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8154 | 2015-12-28 | Fairfax-Marengo Conv | ITCM Fairfax-Marengo Conversion | Convert the Fairfax-Marengo Area to 69kV. Two 69kV breakers are needed at the Fairfax Substation. Four 69kV breakers are needed at the Marengo Substation. | IA | IA | Other |  | Age and Condition | 6632210.8 | 2017-05-19 | 2023-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8155 | 2015-12-28 | Mtown-Tama-Laurel Conv | ITCM Marshalltown-Tama-Laurel Conversion | Convert the Marshalltown-Tama-Laurel to 69kV. One breaker is needed at the Fletcher 69kV Substation. Four 69kV breakers are needed at the Tama Breaker Substation. Three 69kV breakers are needed at the Laurel breaker substation. | IA | IA | Other |  | Age and Condition | 7128457.6 | 2019-12-31 | 2025-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | ITCM Morgan Valley-Beverly 345kV | The project builds a new 345 kV switching station in the DAEC-Tiffin 345 kV line (Morgan Valley Switch Station), adds a new 6.5 mile 345 kV line from the new Morgan Valley Switchstation to a new 345/161 kV substation adjacent to the existing Beverly 161/69/34.5 kV substation. The new 345 kV portion of the substation connects to the existing Beverly substation via a new 345/161 kV autotransformer. | IA | IA | BaseRel |  |  | 38156592 | 2021-05-01 | 2021-05-01 | 345 | 69 | Bottom-Up
A in MTEP15 | A | East | ITCT | 7892 | 2017-12-21 | ITC_14_028 | Bartlett Substation | Interconnection Request for a new 120 kV, 2 transformer distribution substation | MI | MI | Other |  | Load Growth | 7920000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
A in MTEP15 | A | East | ITCT | 8083 | 2018-06-28 | ITC_14_013 | Cortland Relay Replacement | The proposed solution is to upgrade the limiting relaying on the Cortland - Warren 120 kV line to increase its summer emergency rating. | MI | MI | Other |  | Reliability | 300000 | 2019-12-31 | 2019-12-31 | 120 | 0 | Bottom-Up
A in MTEP15 | A | East | ITCT | 8087 | 2018-03-29 | ITC_14_022 | Stratford 33.3 MVAR Capacitor Bank | Install a 33.3 MVAR capacitor bank on the 120 kV bus 101 at Stratford along with the necessary station equipment. | MI | MI | BaseRel |  |  | 820000 | 2025-12-31 | 2025-12-31 | 120 | 0 | Bottom-Up
A in MTEP15 | A | East | ITCT | 8094 | 2015-12-28 | ITC_14_018 | Fitz 345/120 kV Transformer and 120 kV Station | Install a 345/120 kV transformer and construct a 120 kV, 3 breaker yard (ring bus configuration with space to expand to a breaker and a half configuration) at the existing Fitz substation. The Adams-Bunce Creek 120 kV line, which runs adjacent to the Fitz property, would be looped into the new 120 kV side of the substation. To facilitate looping the line, less than 0.1 miles of new double circuit structures would be constructed with 1431 ACSR being installed on both sides of the new structures. Sag limits on the Bunce-Wabash#2 120 kV line and the Fitz-Bunce Creek 120 kV line will also need to be remediated to accommodate this project | MI | MI | BaseRel |  |  | 13200000 | 2018-12-31 | 2018-12-31 | 345 | 120 | Bottom-Up
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | State (formerly “Maize”) and Apex (formerly “Blue”) Substations | DTE has submitted a load interconnection request for 2 new 120/41.6 kV substations proposing to serve load in the City of Ann Arbor and the University of Michigan Campus. ITCT would Install 2-120 kV line breakers and 1-120 kV section breaker w/ associated disconnects in a straight bus configuration at State (formerly "Maize") and Apex (formerly “Blue”) substations respectively. At, Pioneer substation, ITCT would add 2-120 kV line breaker and create 2 new positions to terminate 2 new lines between Pioneer and State (formerly "Maize"). ITCT would construct approx. 2.6 miles of double circuit 120 kV structures between Pioneer and State (formerly "Maize") , and string 954 ACSR to create the 120 kV State (formerly "Maize")-Pioneer 1 and 2 circuits. At, Phoenix substation, ITCT would add 2-120 kV line breaker, 1-120 kV section breaker, relocate the Phoenix end of the Phoenix-Lark line, and create 2 new positions to terminate 2 new lines between Phoenix and Apex (formerly “Blue”). ITCT would construct 2, approx. 2.7 mile underground lines between Phoenix and Apex (formerly “Blue”) using 2500 CU XLPE cable to create the 120 kV Apex-Phoenix 1 and 2 circuits. | MI | MI | Other |  | Reliability | 97873000 | 2018-12-31 | 2019-05-01 | 120 | 41.6 | Bottom-Up
A in MTEP15 | A | East | ITCT | 9440 | 2017-03-29 | ITC_14_027 | Waterman 120kV Cable Relocation for GICB | Portions of the following ITCT circuits will need to be relocated to accomodate the construction of the Gordie Howe International Bridge (GICB) and the related US customs area: Waterman-Cato 120kV (underground), Waterman-St. Antoine 120kV (underground), Waterman-Frisbie 120kV (underground), Waterman-Zug 120kV (Overhead), and Waterman-DIG-Navarre 230kV (overhead). | MI | MI | Other |  | Reliability | 25000000 | 2016-11-11 | 2020-06-30 | 230 | 0 | Bottom-Up
A in MTEP15 | A | South | LAFA | 8820 | 2018-07-27 |  | Northeast Station | New 230-69 autotransformer to feed new 69kv line to feed new 69kv station to alleviate distribution loading. | LA | LA | Other |  | Load Growth | 10500000 | 2019-06-30 | 2019-06-30 | 230 | 69 | Bottom-Up
A in MTEP15 | A | West | MEC | 8020 | 2015-12-28 |  | Pleasant Corner-Beacon 161 kV Line & Terminal | Construct the new Pleasant Corner-Beacon 161 kV line & install a new 161 kV line terminal at Beacon | IA | IA | BaseRel |  |  | 15630000 | 2019-10-01 | 2019-10-01 | 161 | 0 | Bottom-Up
A in MTEP15 | A | West | MEC | 8028 | 2016-06-30 |  | Hastings Replace 161-69 kV Transformer | Replace the Hastings 89.6 MVA 161-69 kV transformer with a 125 MVA transformer. | IA | IA | Other |  | Reliability | 2600000 | 2023-06-01 | 2023-06-01 | 161 | 69 | Bottom-Up
A in MTEP15 | A | West | MEC | 8030 | 2015-12-28 |  | Clarksville-Waverly West 69 kV Line | Construct three miles of new 69 kV line between Clarksville and Waverly West Substations. | IA | IA | Other |  | Reliability | 2600000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | MEC | 8039 | 2016-09-16 | G7154 | Sub R - GRS Tap 69 kV Rebuild | Rebuild the 69 kV line from Sub R to the three-way GRS tap in Rock Island. Replace underground cable and upgrade overhead section as needed to match cable rating. | IL | IL | Other |  | Reliability | 3325000 | 2020-11-01 | 2020-11-01 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | MEC | 8340 | 2015-12-28 |  | Ashawa-Army Post-Willow Creek-Greenfield Plaza 161 kV line rebuild | Rebuild and reconductor the Ashawa-Army Post-Willow Creek-Greenfield Plaza 161 kV line with T-2 556.5 MC ACSR conductor. | IA | IA | BaseRel |  |  | 4400933 | 2014-06-15 | 2018-12-31 | 161 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 2810 | 2018-06-20 | METC_13_038 | Delhi - Canal Jct 138kV Rebuild | Rebuild 7.2 miles of 4/0 ACSR and 336.4 ACSR utilizing 954 ACSR on new 138 kV structures. Also replace terminal equipment at the Delhi 138 kV station. | MI | MI | Other | Not Shared | Reliability | 7500000 | 2019-09-30 | 2019-09-30 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 3926 | 2018-03-27 | METC_14_016 | Dort to Pasadena (Goss) station equipment replacement | Replace/reset relay equipment and replace trainers in the Dort station | MI | MI | Other |  | Reliability | 225000 | 2018-09-28 | 2018-09-28 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 4506 | 2017-10-10 | METC_14_018 | Four Mile - Wealthy Street 138 kV Rebuild | Rebuild 0.59 miles of 6-wired 266.8 ACSR + 3/0 Cu conductor from the Four Mile - Mullins Jct. section using 954 ACSR and rebuild 0.37 miles of 266.8 ACSR + 3/0 Cu, 6.75 miles of 2-3/0 Cu, and 0.49 miles of 795 ACSR from the Wealthy Street - Mullins Jct 138 kV segment utilizing 954 ACSR on new 138 kV structures. Install OPGW along the entire length of the circuit. Also upgrade terminal equipment at the Four Mile and Wealthy Street 138 kV stations. | MI | MI | BaseRel |  |  | 8600000 | 2020-03-31 | 2020-03-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 4509 | 2018-03-27 | METC_13_043 | Argenta - Battle Creek 345kV Sag Remediation and Station Equipment | Remediate Sag Limit to SEMER 2350 Amps. Upgrade station equipment at Battle Creek 345kV. | MI | MI | Other | Not Shared | Reliability | 2568000 | 2017-05-25 | 2018-06-29 | 345 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8066 | 2017-12-21 | METC_14_022 | Amber - Donaldson Creek 138 kV Rebuild | Rebuild approx. 19.8 miles of the Amber to Donaldson Creek 138 kV circuit using 954 ACSR and OPGW on 138 kV future double circuit structures. | MI | MI | BaseRel |  |  | 23000000 | 2019-06-14 | 2019-06-14 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8072 | 2018-04-27 | METC_14_047 | Riggsville to Port Calcite to Rockport 138 kV Rebuild | Rebuild 69 miles of existing 138 kV wood poles to double circuit capable 138 kV construction steel monopoles and string one side with T2 477 ACSR (or another similar capacity anti-galloping conductor configuration). | MI | MI | Other |  | Age and Condition | 96505000 | 2021-12-31 | 2021-12-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8077 | 2018-06-20 | METC_14_039 | Vestaburg to Alma 138 kV Rebuild | Rebuild the Vestaburg - Alma 138 kV circuit utilizing 138 kV single circuit steel poles and 954 ACSR conductor. Install OPGW along the entire length of the circuit. Also reconductor 2.9 miles of the Eureka – Vestaburg 138 kV circuit using 954 ACSR. | MI | MI | Other |  | Age and Condition | 22900000 | 2020-12-31 | 2020-12-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8078 | 2017-02-23 | METC_14_025 | Donaldson Creek 33.3 MVAR Capacitor | Install a 33.3 MVAR capacitor at Donaldson Creek. | MI | MI | BaseRel |  |  | 1200000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8090 | 2015-12-28 | METC_14_035 | Cornell - Blue Water Jct. 138 kV Sag Remediation | Remediate the sag limit on the Cornell to Blue Water Jct. section of the Cornell - Bingham 138 kV circuit to increase its summer emergency rating to at least 760 A. | MI | MI | Other |  | Reliability | 320000 | 2018-06-01 | 2018-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8091 | 2017-12-05 | METC_14_030 | Donaldson Creek - White Lake 138 kV Sag Remediation | Remediate the sag limit on the Donaldson Creek - White Lake 138 kV line to 160 MVA (670 Amp). | MI | MI | Other |  | Reliability | 360000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8118 | 2018-06-20 | METC_14_040 | Beecher - Samaria 138 kV Rebuild | Rebuild the 636 ACSR portion of the Beecher to Samaria 138 kV circuit utilizing 954 ACSR on 138 kV double circuit steel poles. Relocate the Beecher-Whiting 138 kV line to the open side of the new structures. Replace overloaded terminal equipment at Beecher and upgrade relaying at Morocco. | MI | MI | Other |  | Age and Condition | 25600000 | 2019-09-30 | 2019-09-30 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8121 | 2018-02-01 | METC_14_037 | Hackett Jct. - Laundra Jct. 138 kV Sag Remediation | Remediate the sag limit on the Hackett Jct. - Laundra Jct. section of the Bullock - Saginaw River 138 kV circuit to increase its summer emergency rating to at least 840 A. | MI | MI | Other |  | Reliability | 90000 | 2019-11-01 | 2019-11-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8122 | 2016-08-30 |  | METC Pole Top Switches Additions-Replacement Program - 2018 | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points . | MI | MI | Other |  | Reliability | 3600000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8124 | 2018-06-25 | METC_14_046 | Argenta - Morrow 138 kV Rebuild | Rebuild approximately 10 miles of existing 138 kV steel lattice towers with wood cross arms to double circuit capable 230 kV construction steel monopoles and string one side with 954 ACSR. | MI | MI | Other |  | Age and Condition | 13900000 | 2022-03-31 | 2022-03-31 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8127 | 2016-08-30 | METC_14_024 | Six Ludington 345 kV Circuit Breaker Replacements | Replace the 22H9, 24H9, 25H9, 22F7, 24F7, and 25F7 Ludington 345 kV circuit breakers with the circuit breakers containing 400 ohm pre-insertion resistors. | MI | MI | Other |  | Reliability | 8640000 | 2017-12-31 | 2017-12-31 | 345 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | Meyer (formerly “Hayes Street”) 345/138 kV Station | Construct a new EHV “Meyer” (formerly “Hayes Street”) substation approximately four miles north of the Tallmadge station, loop the existing Ludington - Tallmadge #2, Kenowa - Argenta 345 kV and Cobb - Tallmadge #1 138 kV circuits into the new station and install a new 345/138 kV transformer at Meyer. The solution will also require replacing the limiting terminal equipment at the Tallmadge 345 kV station (pos. 27HR) and remediating the sag limits on the Argenta - Meyer 345 kV circuit (formerly Argenta - Kenowa 345 kV line) to at least 1,524 MVA (2,550 A) and on the Tallmadge - Meyer #1 345 kV circuit (formerly Ludington - Tallmadge #2 345 kV) to 2,007 MVA (3,358 A). | MI | MI | BaseRel |  |  | 31700000 | 2019-12-31 | 2019-12-31 | 345 | 138 | Bottom-Up
A in MTEP15 | A | East | METC | 8171 | 2018-03-27 | METC_13_016 | Croton to Felch Road 138 kV Circuit Dual Pilot Relay Protection Installation and Sparing Removal | 1. Install dual pilot relay protection system on Croton to Felch Road 138 kV circuit so that 3 phase to ground faults on the circuit will be cleared within 7 cycles. 2. Remove the sparing scheme of using Croton 138 kV breaker 500 to spare breaker 388 for Croton to Felch Road 138 kV circuit. 3. Remove Felch Road 138 kV BK 188 Bypassing | MI | MI | Other |  | Reliability | 540000 | 2018-04-02 | 2018-04-02 | 138 | 0 | Bottom-Up
A in MTEP15 | A | East | METC | 8460 | 2018-03-27 | METC_14_045 | Hemphill - Sabine 138 kV Sag Remediation | Remediate the sag limit on the Sabine - Hemphill 138 kV line to increase its summer emergency rating to the 336 ACSR conductor rating of 208 MVA (871 Amps). | MI | MI | Other |  | Reliability | 140000 | 2018-06-01 | 2018-06-01 | 138 | 0 | Bottom-Up
A in MTEP15 | A | West | MP | 8000 | 2015-12-28 | 16 Line Relocation | 16 Line Relocation | Relocate a segment of the existing Arrowhead - 16L Tap 115 kV Line around proposed United Taconite basin expansion | MN | MN | Other |  | Reliability | 3450000 | 2020-05-01 | 2020-05-01 | 115 | 0 | Bottom-Up
A in MTEP15 | A | East | NIPS | 8500 | 2015-12-28 |  | Lagrange 138kV Ring Bus | Create 138kV Ring Bus at lagrange Substation | IN | IN | BaseRel |  |  | 2715000 | 2018-12-31 | 2018-12-31 | 138 | 138 | Bottom-Up
A in MTEP15 | A | East | NIPS | 9405 | 2015-12-28 |  | Kosciusko 13881 Switch | Replace Line Switch and substation Conductor at Kosciusko. | IN | IN | BaseRel |  |  | 147845 | 2019-11-08 | 2019-11-08 | 138 | 0 | Bottom-Up
A in MTEP15 | A | West | OTP | 8281 | 2018-06-29 |  | Donaldson 115 kV Breaker | Add a new 115 kV breaker at Donaldson to the Donaldson to Drayton 115 kV line to improve reliability of area loads. This breaker will reduce fault exposure to Donaldson loads by 17 miles and improve operations, maintenance, and relaying flexibility at Donaldson. | MN | MN | Other |  | Reliability | 370000 | 2019-11-30 | 2019-11-30 | 115 | 0 | Bottom-Up
A in MTEP15 | A | Central | PPI | 7881 | 2018-09-17 | 2015-12 | Fishhook-Pittsfield 138 kV | Construct new 14.5 mile 138 kV line from the new Ameren Fishhook 138 kV switching station on the Meredosia-East Quincy South 138 kV line to the PPI Pittsfield 138/69 kV substation. | IL | IL | Other |  | Reliability | 14430000 | 2021-12-31 | 2021-12-31 | 138 | 69 | Bottom-Up
A in MTEP15 | A | Central | PPI | 7889 | 2018-03-22 | 2015-14,35,37 | Fishhook-Liberty 138 kV, Liberty 138/69 kV, and St. Anthony 138/69 kV | Construct Fishhook-Liberty 138 kV line, Liberty 138/69 kV substation, and replace St. Anthony 138/69 kV transformer. | IL | IL | Other |  | Reliability | 6904800 | 2019-12-31 | 2019-12-31 | 138 | 69 | Bottom-Up
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | SMEPA/SOCO IC (Jasper County) | Tap the Missionary - Waynesboro 161kV line (SMEPA L232) at the intersection with Mississippi Power Company (MPCo?s) Laurel East - Enterprise 230kV line. Add a new 230/161kV autotransformer at the Missionary substation and convert the entire Missionary - Waynesboro line to 230kV operation. Construct a new 161kV line from Homewood - Missionary utilizing existing double circuit lines as well as rebuilding existing 69kV lines to double circuit specifications that currently span from Homewood - Missionary. *Note: L232 was constructed using 230kV insulation, but is currently operated at 161kV | MS | MS | Other |  | Reliability | 16878000 | 2018-08-01 | 2021-09-01 | 230 | 161 | Bottom-Up
A in MTEP15 | A | Central | Vectren | 4391 | 2016-05-19 | 2013SIGE5 | Pigeon Creek Cap Bank Addition | Add a 15.6 MVAR cap bank at the Pigeon Creek Sub | IN | IN | Other |  | Reliability | 770000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | East | WPSC | 3567 | 2015-12-28 | HY-WN | Hersey to Weidman | Hersey to Weidman line rebuild | MI | MI | Other | Not Shared | Reliability | 11500000 | 2017-12-31 | 2017-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | East | WPSC | 4086 | 2015-12-28 | FNX-SV | Fountain Junction to Scottville | Fountain Junction to Scottville Rebuild | MI | MI | Other |  | Reliability | 4650000 | 2016-12-31 | 2016-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | East | WPSC | 4384 | 2015-12-28 | Airport Xmsn | Airport Station Modification | The current configuration of the Airport station is not desirable from a planning or protection standpoint. The transformer protection clears the entire 138kV bus, there is primarily electromechanical relaying in the station and both the 138kV and 69kV the stations have oil circuit breakers. This project will upgrade both busses to ring bus configurations, put the current 138kV and 69kV stations in a common fence, replace oil breakers with SF6 and bring the design up to current Wolverine standards. | MI | MI | Other | Not Shared | Other Local Needs | 4190000 | 2017-01-01 | 2018-12-31 | 138 | 69 | Bottom-Up
A in MTEP15 | A | East | WPSC | 7661 | 2015-12-28 | Vestaburg Transmission | Vestaburg Transmission | Convert transfer bus to straight bus, replace old station swiches and upgrade relaying to add a sparing scheme. | MI | MI | Other |  | Other Local Needs | 170000 | 2017-12-31 | 2017-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | East | WPSC | 8221 | 2015-12-28 | Airport Line Mods | Airport Station Line Modifications | This project will construct the line modifications required to route lines into the new Airport station. | MI | MI | Other |  | Other Local Needs | 1000000 | 2017-12-31 | 2017-12-31 | 138 | 69 | Bottom-Up
A in MTEP15 | A | East | WPSC | 8380 | 2015-12-28 | Advance Line Mods | Advance Line Modifications | Line modifications to support the new Advance Transmission station project. | MI | MI | Other |  | Other Local Needs | 1250000 | 2016-12-31 | 2016-12-31 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | XEL | 8079 | 2015-12-28 |  | Line 0714 Rebuild | Rebuild 3.6 miles of 69 kV line from Madelia Switching Station to Village of Madelia to 336 ACSR | MN | MN | Other |  | Reliability | 1594000 | 2022-12-01 | 2022-12-01 | 69 | 0 | Bottom-Up
A in MTEP15 | A | West | XEL | 8113 | 2015-12-28 |  | Ward County 230 kV | Construct new 230/115 kV substation near Minot, ND construct new 230 kV line from new substation to GRE McHenry substation Joint project with BEPC | ND | ND | BaseRel |  |  | 33000000 | 2018-12-01 | 2018-12-01 | 230 | 115 | Bottom-Up
A in MTEP15 | A | West | XEL | 8117 | 2015-12-28 |  | Ward County - Souris 115 kV Line Rebuild | Rebuild 115 kV lines from Ward County to Souris substation | ND | ND | BaseRel |  |  | 9400000 | 2018-12-01 | 2018-12-01 | 115 | 0 | Bottom-Up
A in MTEP15 | A | West | XEL | 8149 | 2015-12-28 |  | Bayfield Loop 69 kV | This project builds new 69 kV line 20 miles from the existing Stinson - Bayfront 115 kV line to a new substation near Bayfield, WI. New substation at the 115 kV tap location and a new 69/34.5 kV sub near Bayfield. Also included in the project is a rebuild of the existing Iron River - Herbster 34.5 kV line to 69 kV standards. All of the lines in the Bayfield loop will be operated at 34.5 kV for the initial planning horizon and converted when necessary. | WI | WI | Other |  | Reliability | 40000000 | 2020-03-15 | 2022-12-01 | 115 | 34.5 | Bottom-Up
A in MTEP14 | A | Central | AmerenIL | 4471 | 2015-01-09 |  | Cahokia-Dupo Ferry-1 138 kV Line | Replace 6.98 miles of 2-300 kcmil Copper conductor with largest size conductor existing structures will carry. | IL | IL | Other |  | Age and Condition | 5200000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP14 | A | Central | AmerenIL | 4480 | 2017-03-10 |  | Oglesby 138 kV Substation - Rebuild | Rebuild Oglesby Substation. Utilize a breaker-and-a-half arrangement. | IL | IL | Other |  | Reliability | 34600000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
A in MTEP14 | A | Central | AmerenMO | 4723 | 2015-01-09 |  | Kelso-Lutesville-1 345 kV Replace Structures | Replace 50% of structures (17.6 miles) to maintain at least a 100 degree C conductor temperature capability on this line. | MO | MO | Other |  | Age and Condition | 8441336 | 2017-12-01 | 2017-12-01 | 345 | 0 | Bottom-Up
A in MTEP14 | A | West | ATC | 1624 | 2014-12-17 | PR05259, F4004 | Uprate Portage-Trienda 138 kV | Increase clearance and uprate SS equipment | WI | WI | Other | Not Shared | Reliability | 2000000 | 2022-06-01 | 2022-06-01 | 138 | 0 | Bottom-Up
A in MTEP14 | A | West | ATC | 3096 | 2017-11-27 | PR04463, F3735 | Uprate Munising-Blaney Park 69 kV | Increase ground clearance for the Inland line Munising-Blaney Park 69 kV to 167 deg F (37 MVA) clearance | MI | MI | Other | Not Shared | Reliability | 18187669 | 2019-05-01 | 2019-05-01 | 69 | 0 | Bottom-Up
A in MTEP14 | A | West | ATC | 3510 | 2016-09-15 | PR04651, F3421 | Rebuild Mukwonago-St Martins 138 kV | Rebuild Mukwonago-Edgewood-St. Martins 138 kV Line, includes replacing jumpers at Edgewood and Mukwonago | WI | WI | Other | Not Shared | Reliability | 24736000 | 2019-06-15 | 2019-06-15 | 138 | 0 | Bottom-Up
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | Construct Bain-Spring Valley-North Lake Geneva 138 kV | Reconductor Bain-Spring Valley 138; construct a 138/69 kV Geneva substation; construct a new Spring Valley-Geneva 138 kV line; construct a new Geneva-North Lake Geneva 138 kV line; construct Twin Lakes-Geneva 138 kV line; reconductor Katzenberg-Richm | WI | WI | Other | Not Shared | Reliability | 70546000 | 2019-12-31 | 2019-12-31 | 138 | 69 | Bottom-Up
A in MTEP14 | A | Central | DEI | 4411 | 2015-01-09 | AMIN0863&4&5 | Bloomington 6991 Reconductor | Reconductor 13.7 miles of the 6991 ckt from Bloomington Dunn St sub to Bloomington 230 sub with 954ACSR @ 100C | IN | IN | Other |  | Reliability | 10973000 | 2014-07-16 | 2018-10-01 | 69 | 0 | Bottom-Up
A in MTEP14 | A | Central | DEI | 4415 | 2015-01-09 | AMIN0890 | Veedersburg West 230-69kv Bk 2 addition | Veedersburg West: Add 75MVA 230/69 Bk 2 with LTC at Veedersburg West sub; add breaker to 69kV ring bus and tie in new bank; convert 230kV bus into 4-breaker ring | IN | IN | Other |  | Reliability | 3509000 | 2020-06-01 | 2020-06-01 | 230 | 69 | Bottom-Up
A in MTEP14 | A | Central | DEI | 4417 | 2015-01-09 | AMIN0988 | Pumpkin Center 69KV Brk Repl | Pumpkin Center: Replace OCB 6952, OCB 69123, OCB 69230, (1) Ground Switch, (2) 230KV ABS and Motor Mechs, Lighting Arrestors, Line & Bus Pots, (7) 69KV Disconnect Switches and Station Service Transformer. Replace 230/69 Circuit Switcher with a 230KV Gas Circuit Breaker. | IN | IN | Other |  | Reliability | 2424000 | 2018-10-01 | 2018-10-01 | 69 | 0 | Bottom-Up
A in MTEP14 | A | Central | DEM | 3550 | 2016-08-03 | AMIN0499 | Martinsville 69kv Normally Open Loop | Construct approximately 1.5 mi of 69kv line to complete a normally open loop between Martinsville SE and Martinsville East distribution subs. | IN | IN | Other | Not Shared | Reliability | 1434000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-AR | 4751 | 2014-12-17 | 14-EAI-020-8 | EAI Underrated Breaker Project: Jacksonville North 115 kV B3621-CBO | Upgrade breaker to increase short circuit interrupting capability | AR | AR | Other |  | Reliability | 84000 | 2019-06-30 | 2019-06-30 | 115 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-AR | 4757 | 2015-09-10 | 14-EAI-022-4 | EAI SPOF Projects: Modify relaying at El Dorado 500 kV | EAI SPOF Projects: Modify relaying at El Dorado 500 kV | AR | AR | Other |  | Other Local Needs | 4698843 | 2019-06-30 | 2019-06-30 | 500 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-LA | 4761 | 2014-12-17 | 14-EGL-022-1 | EGSL SPOF Projects: Modify relaying at Willow Glen 500 kV | EGSL SPOF Projects: Modify relaying at Willow Glen 500 kV | LA | LA | Other |  | Other Local Needs | 6502968 | 2019-06-01 | 2019-06-01 | 500 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-LA | 4773 | 2014-12-17 | 14-ELL-009-1 | ELL SPOF Projects: Modify relaying at Ninemile 230 kV | ELL SPOF Projects: Modify relaying at Ninemile 230 kV | LA | LA | Other |  | Other Local Needs | 5981188 | 2019-01-31 | 2019-01-31 | 230 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-LA | 4774 | 2014-12-17 | 14-ELL-009-2 | ELL SPOF Projects: Modify relaying at Southport 230 kV | ELL SPOF Projects: Modify relaying at Southport 230 kV | LA | LA | Other |  | Other Local Needs |  | 2018-09-30 | 2018-09-30 | 230 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-LA | 4775 | 2014-12-17 | 14-ELL-009-3 | ELL SPOF Projects: Modify relaying at Labarre 230 kV | ELL SPOF Projects: Modify relaying at Labarre 230 kV | LA | LA | Other |  | Other Local Needs |  | 2018-09-30 | 2018-09-30 | 230 | 0 | Bottom-Up
A in MTEP14 | A | South | Entergy-LA | 4778 | 2014-12-17 | 14-ENO-003-1 | ENOI SPOF Projects: Modify relaying at Market Street 230 kV | ENOI SPOF Projects: Modify relaying at Market Street 230 kV | LA | LA | Other |  | Other Local Needs |  | 2018-11-16 | 2018-11-16 | 230 | 0 | Bottom-Up
A in MTEP14 | A | West | GRE-WMU | 4380 | 2015-01-09 | 202647 | Priam Substation | Move Willmar 115/69 kV transformer to new Priam substation location | MN | MN | Other |  | Reliability | 4000000 | 2019-05-01 | 2019-05-01 | 115 | 69 | Bottom-Up
A in MTEP14 | A | Central | HE | 4714 | 2015-01-09 | 1052 Ratts 138/161 kV Transformer Upgrade | Ratts 138/161 kV Transformer Upgrade | New Transformer | IN | IN | Other |  | Reliability | 3500000 | 2014-05-15 | 2014-05-15 | 161 | 138 | Bottom-Up
A in MTEP14 | A | Central | HE | 4715 | 2015-01-09 | 1052 Ratts 138 kV Transmission Upgrade | Ratts 138 kV Transmission line Upgrade | Upgrade Transmission line | IN | IN | Other |  | Reliability | 200000 | 2014-05-15 | 2014-05-15 | 138 | 0 | Bottom-Up
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | Carrigan 120 kV Switching Station | Reconfigure the Lee - Menlo and Wabash - Yuma 120 kV circuits into a switching station named Carrigan. | MI | MI | BaseRel | Not Shared |  | 7380000 | 2019-05-30 | 2019-05-30 | 120 | 0 | Bottom-Up
A in MTEP14 | A | East | ITC, ITCT | 4567 | 2016-03-23 |  | ITCT Customer Interconnections - Year 2018 | Customer interconnection requests and retirements | MI | MI | Other | Not Shared | Load Growth | 2000000 | 2018-12-31 | 2018-12-31 | 120 | 0 | Bottom-Up
A in MTEP14 | A | West | ITCM | 4456 | 2014-12-17 | East Nevada St | East Nevada Street Expansion | Install 69 kV bus and three breaker positions in the East Nevada St substation. Initially one breaker will be installed with the Timber Creek to East Nevada St line rebuild, and the remaining breakers will be installed closer to the 69 kV conversion | IA | IA | Other | Not Shared | Age and Condition | 2400000 | 2016-05-27 | 2020-12-31 | 34 | 0 | Bottom-Up
A in MTEP14 | A | West | ITCM | 4459 | 2014-12-17 | East IA phase 3 | Eastern Iowa Rebuild & Conversion Plan Phase 3 | ITCM has worked with the stakeholders in the Eastern Iowa Study area to find a solution that is acceptable to everyone. A conversion plan was chosen that maximizes the number of miles of 34.5 kV lines that can be retired and gives the most substations lo | IA | IA | Other | Not Shared | Age and Condition | 4260000 | 2015-08-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP14 | A | West | ITCM | 4462 | 2014-12-17 | Keswick-Victor Conv | Keswick-Victor 69kV Conversion | Convert the Keswick - Victor to 69kV. Build Victor 69kV Switching Station substation and install a 69/34.5kV XFMR to provide back up for the 34.5kV system in the Victor and Brooklyn area until that area is converted to 69kV in 2020. | IA | IA | Other | Not Shared | Age and Condition | 3000000 | 2021-12-30 | 2021-12-30 | 69 | 34 | Bottom-Up
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | Otter Creek-Fletcher 69kV Conversion | Convert the 34kV lines between Otter Creek and Fletcher to 69kV operation. The 34kV terminal at Marshalltown will be retired and a new 69kV source from the new Fletcher sub will feed the new line. | IA | IA | Other | Not Shared | Age and Condition | 240000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP14 | A | West | ITCM | 4467 | 2014-12-17 | Fairbank-Oelwein | Fairbank-Oelwein 5.5 mile 69kV Rebuild | Rebuild 5.5 miles of the Oelwein-Fairbank 69kV line. | IA | IA | Other | Not Shared | Age and Condition | 5492400 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | Marshalltown-Parnell-Cedar Rapids 34kV Rebuild Plan | The project wll rebuild several 34kV lines to 69kV standards to prepare for the future conversion to 69kV. | IA | IA | Other | Not Shared | Age and Condition | 53398912 | 2015-08-17 | 2021-12-31 | 34 | 0 | Bottom-Up
A in MTEP14 | A | East | ITCT | 4518 | 2016-11-07 | ITC_15_004 | Monroe 345/120 kV Transformer 304 Replacement | Replace the 345/120 kV Transformer 304 at Monroe. | MI | MI | Other | Not Shared | Reliability | 3800000 | 2019-12-31 | 2019-12-31 | 345 | 120 | Bottom-Up
A in MTEP14 | A | West | MDU | 3083 | 2015-03-31 | Dickinson Loop | Dickinson 115 kV Loop | Complete 115 kV loop & new 115/41.6 subsation in Dickinson area | ND | ND | Other |  | Reliability | 10533790 | 2014-05-07 | 2019-11-30 | 115 | 41.6 | Bottom-Up
A in MTEP14 | A | East | METC | 4538 | 2016-03-23 | METC-996 | METC Customer Interconnections - Year 2018 | Customer interconnection requests and retirements | MI | MI | Other | Not Shared | Load Growth | 2500000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
A in MTEP14 | A | East | METC | 4539 | 2018-03-27 | METC-995 | METC Hemphill Control Relocation Project - Years 2015, 2016, 2017 | Replace METC relaying and controls at Hemphill Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other | Not Shared | Other Local Needs | 3640000 | 2019-01-24 | 2019-01-24 | 0 | 0 | Bottom-Up
A in MTEP14 | A | East | METC | 4542 | 2018-03-27 | METC-990 | METC Morrow Control Relocation Project - Years 2015, 2016, 2017 | Replace METC relaying and controls at Morrow Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI | MI | Other | Not Shared | Other Local Needs | 3110000 | 2019-12-30 | 2019-12-30 | 0 | 0 | Bottom-Up
A in MTEP14 | A | East | METC | 4555 | 2018-06-20 | METC_13_018 | Tippy to Stronach 138 kV Circuit Dual Pilot Relay Protection Installation | Install a dual pilot relay protection system on the Tippy to Stronach 138 kV circuit so that three (3) phase to ground faults will be cleared within 5 cycles. The Tippy 138 kV BK 177 bypassing will also be removed. | MI | MI | Other | Not Shared | Reliability | 575000 | 2019-04-30 | 2019-04-30 | 138 | 0 | Bottom-Up
A in MTEP14 | A | East | METC | 4556 | 2016-11-10 | METC_13_032 | Blackstone 138 kV Second Bus Protection and Independent Relay Component | Install a second bus relay scheme on Blackstone blue and white busses and install second independent relay components on Blackstone end of the Blackstone-Marshall 138 kV circuit, Blackstone-Tompkins 138 kV ckts #1 and #2 and Blackstone-Leoni 138 kV ckts # | MI | MI | Other | Not Shared | Reliability | 845000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
A in MTEP14 | A | East | METC | 4557 | 2017-02-21 | METC_13_017 | Croton to Four Mile 138 kV Circuit Dual Pilot Relay Protection Installation | Add a dual pilot relay protection system on Croton to Four Mile 138 kV circuit so that 3 phase to ground faults on the circuit will be cleared within 5 cycles. | MI | MI | Other | Not Shared | Reliability | 483000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
A in MTEP14 | A | West | MH, MP | 3831 | 2014-12-17 | GNTL | Great Northern Transmission Line | U.S. portion of new Dorsey - Iron Range 500 kV transmission line, including 500 kV line from border crossing to Iron Range, midpoint series compensation station, new Iron Range 500/230 kV yard adjacent to existing Blackberry 230/115 kV Substation, and interconnection to 230 kV system at Blackberry. | MN | MB | TDSP |  |  | 676242932 | 2020-06-01 | 2020-06-01 | 500 | 230 | Externally Driven
A in MTEP14 | A | West | OTP | 4444 | 2016-12-22 | OTP | NERC Alert Facility Ratings for Low Priority | Verify and remediate facilities as required due to the industry-wide NERC alert | MN,ND,SD | MN,ND,SD | Other |  | Reliability | 7701028 | 2017-01-31 | 2017-01-31 | 115 | 0 | Bottom-Up
A in MTEP13 | A | Central | DEM | 4032 | 2012-09-12 | AMIN0744 | Five Points 230kV Station Upgrade Phase I | Five Points Station Upgrade Phase I ? Install new prefabricated control building. Replace 230kV breakers and relays. Replace 230kV circuit switchers with 230kV breakers. Replace 230-138kV bank protection. Replace 230kV bus protection. | IN | IN | Other | Not Shared | Reliability | 5406000 | 2019-04-01 | 2019-04-01 | 230 | 138 | Bottom-Up
A in MTEP13 | A | Central | DEM | 4033 | 2016-10-04 | AMIN0758 | Camp Atterbury to Edinburg 6950 Rebuild | Camp Atterbury to Edinburg 6950 Reconductor 2/0 Cu (4.0 miles) to 477ACSR and uprate existing 477ACSR 80C to 477ACSR 100C (4.5 miles). | IN | IN | Other | Not Shared | Reliability | 1650765 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP13 | A | Central | DEM | 4037 | 2012-09-12 | AMIN0841 | Lafayette 230kV Ring Bus - Ph. 2 | Lafayette 230kV Sub Ring Bus - Phase 2, install two 230kV 40KIA breakers, support structures, bus and 954KCM jumpers to complete five-breaker - 230kV ring bus. Install three transformer protection schemes. | IN | IN | BaseRel | Not Shared |  | 1618000 | 2019-12-31 | 2019-12-31 | 230 | 0 | Bottom-Up
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | Toll Road + SVC | Relocate all ITCTransmission circuits at the Fermi 120 kV switchyard to a new station nearby (Toll Road station). This station would be configured as a breaker-and-a-half scheme. Create three feeds from Toll Road to the Fermi 120 kV switchyard. Install a 100 MVAR Static VAR Compensator at Toll Road. | MI | MI | BaseRel | Not Shared |  | 40000000 | 2018-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP13 | A | East | ITC, ITCT | 4175 | 2016-08-30 | ITC-015 | ITCT Pole Top Switch Additions/Replacement Program 2014 | Installing, or replacing as appropriate, pole-top switches at tap points of circuits will provide the operational flexibility to sectionalize parts of the line to isolate faults or perform maintenance work on it without having to shut down the entire circuit. | MI | MI | Other | Not Shared | Reliability | 2400000 | 2014-10-15 | 2018-09-30 | 120 | 0 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4099 | 2012-09-14 | AleaW-SBroadway | Albert Lea Westside-South Broadway 69kV Rebuild | Rebuild approximately 2 miles of the Albert Lea Westside-South Broadway 69kV line to T2-4/0 capacity. | MN | MN | Other | Not Shared | Age and Condition | 840000 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4101 | 2012-09-14 | Montgomery-Waseca | Montgomery-Waseca Jct 69kV Rebuild | Rebuild the ~29.5 mile Montgomery-French Lake Tap-Waseca Jct 69kV line to T2-4/0. | MN | MN | Other | Not Shared | Age and Condition | 26137683 | 2016-11-28 | 2020-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4102 | 2012-09-14 | Columbus Jct-Newport | Columbus Jct-Newport 69kV Rebuild | Rebuild the ~19 mile Columbus Jct-IBP Tap-Winfield Tap-Cairo REC-Newport 69kV line to T2-4/0. | IA | IA | Other | Not Shared | Age and Condition | 13798885 | 2023-12-31 | 2023-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4103 | 2018-10-04 | NBurl-Mediapolis | North Burlington-Mediapolis 69kV Rebuild | Rebuild the ~6.4 mile North Burlington-North Burlington Tap 69kV line to T2-4/0. | IA | IA | Other | Not Shared | Reliability | 5760000 | 2018-08-27 | 2018-08-27 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4104 | 2012-09-14 | Lansing-Monona | Lansing-Monona 69kV Rebuild | Rebuild the ~25 mile Lansing-Harper's Ferry Tap-Waterville Tap-Monona 69kV line to T2-4/0. | IA | IA | Other | Not Shared | Age and Condition | 20975036 | 2021-12-31 | 2021-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4105 | 2012-09-14 | Decorah-Waukon | Decorah-Waukon 69kV Rebuild | Rebuild the ~23 mile Decorah-Ludlow Tap-Waukon 69kV line to T2-4/0. | IA | IA | Other | Not Shared | Age and Condition | 9660000 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4106 | 2012-09-14 | Windsor-Richfield | Windsor-Richfield 69kV Rebuild | Rebuild the ~11.2 mile Windsor-Hawk Tap-Richfield 69kV line to T2-4/0. | IA | IA | Other | Not Shared | Age and Condition | 4750000 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4108 | 2012-09-14 | Ellendale-WOwatonna | Ellendale-West Owatonna 69kV Rebuild | Rebuild the ~13 mile Ellendale-West Owatonna 69kV line to T2-4/0. | MN | MN | Other | Not Shared | Age and Condition | 7281277 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4115 | 2012-09-14 | Fletcher Sub | New Fletcher 161/69kV Sub & Line Taps | Construct a new Fletcher 161/69kV sub next ot the Marsahalltown. Fletcher will be served from the new Marshalltown 161kV ring position. | IA | IA | Other | Not Shared | Age and Condition | 7173600 | 2019-12-31 | 2019-12-31 | 161 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM | 4116 | 2012-09-14 | East IA phase 2 | Eastern Iowa Phase 2 Rebuilds | Eastern Iowa Study Rebuild and Conversion Projects (Phase 2) ? Rebuild 34kV single CKT to DBL CKT 69kV for Marion ? Anamosa & Hiawatha ? Coggon ? Mt. Vernon ? Linn TWP REC New Line ? Linn TWP REC ? Cornell New Line ? Springville ? Amber 34kV Rebuild to 69kV ? Lovell REC Tap ? Monticello Industrial 34kV Rebuild to 69kV ? Hiawatha ? Echo Hill REC 69 kV Conversion | IA | IA | Other | Not Shared | Age and Condition | 16718510 | 2014-03-14 | 2018-09-05 | 69 | 69 | Bottom-Up
A in MTEP13 | A | West | ITCM, MEC | 3249 | 2014-03-31 | G5566, 32337 | NE 54th Ave.-Bondurant 161 kV line | New 161 kV line from NE 54th Ave. Substation to Bondurant Substation and associated substation equipment additions. | IA | IA | Other | Not Shared | Load Growth | 11221895 | 2019-12-01 | 2019-12-01 | 161 | 0 | Bottom-Up
A in MTEP13 | A | East | ITCT | 4286 | 2015-04-03 | ITC_12_015 | Henry Ford Substation | Loop in the Frisbie ? Waterman 120 kV underground cable to feed the Henry Ford substation. Splices and terminals will be installed and underground cable run from the existing line to the new substation. The substation is located approximated 150 feet fro | MI | MI | Other | Not Shared | Load Growth | 5000000 | 2018-05-31 | 2018-05-31 | 120 | 0 | Bottom-Up
A in MTEP13 | A | West | MEC | 3248 | 2015-09-15 | G2705, 32335 | Rising Sun - NE 54th Ave. 161 kV Line | New 161 kV line from new Rising Sun Substation on DPS-Reasnor line to NE 54th Ave. and associated substation equipment additions. | IA | IA | Other | Not Shared | Load Growth | 14036000 | 2018-03-01 | 2019-06-01 | 161 | 0 | Bottom-Up
A in MTEP13 | A | East | METC | 4149 | 2017-12-21 | METC_12_026 | Argenta - Tallmadge 345kV Sag Remediation | Remediate sag on the Argenta ? Tallmadge 345kV line to bring its thermal rating up to 2422 Amp (1447 MVA) | MI | MI | BaseRel | Not Shared |  | 1500000 | 2018-09-15 | 2018-09-15 | 345 | 0 | Bottom-Up
A in MTEP13 | A | East | WPSC | 4084 | 2015-04-03 | NS-VB | North Shade to Vestaburg | North Shade to Vestaburg Rebuild | MI | MI | Other | Not Shared | Age and Condition | 10000000 | 2018-12-31 | 2018-12-31 | 69 | 0 | Bottom-Up
A in MTEP13 | A | East | WPSC | 4085 | 2015-04-03 | LC-FNX | Lake County to Fountain Junction | Lake County to Fountain Junction Rebuild | MI | MI | Other | Not Shared | Reliability | 3100000 | 2016-12-31 | 2016-12-31 | 69 | 0 | Bottom-Up
A in MTEP13 | A | West | XEL | 4314 | 2013-01-10 |  | Ashland - Ironwood 88 kV rebuild | Rebuild the 88 kV line between Bay Front - Saxon Pump - Norrie due to age and condition | WI,MI | WI | Other | Not Shared | Age and Condition | 35977500 | 2022-12-01 | 2022-12-01 | 88 | 0 | Bottom-Up
A in MTEP12 | A | Central | AmerenMO | 3366 | 2015-09-11 |  | Wallen Creek Substation High-Side Transfer | Install 2-2000 A,138 kV PCBs | MO | MO | Other | Not Shared | Reliability | 2635000 | 2018-12-01 | 2018-12-01 | 138 | 0 | Bottom-Up
A in MTEP12 | A | West | ATC, ATC LLC | 3679 | 2014-06-13 | NP-Package2_3 F3501 WO069260 | Green Bay to Morgan 345 kV project and Menominee Co to Delta Co 138 kV line | New Green Bay sub to Morgan 345 kV line and new 138 kV line from Holmes to 18th road | WI | MI | BaseRel | Shared |  | 306081000 | 2016-08-13 | 2018-10-25 | 345 | 69 | Bottom-Up
A in MTEP12 | A | West | ATC, ATC LLC | 3952 | 2014-06-13 | NP_GB-M 138, PR05016 F3501 WO069260 | Green Bay - Morgan 138 kV line | Green Bay - Morgan 138 kV line | WI | WI | Other | Not Shared | Reliability | 59269000 | 2017-10-27 | 2018-10-28 | 345 | 138 | Bottom-Up
A in MTEP12 | A | Central | BREC | 3792 | 2012-04-20 | Matanzas | Wilson-Matanzas 161 kV Interconnection | Create a new 161 kV BREC-LG&E/KU interconnection by looping the Wilson-Paradise portion of the three terminal interconnection through a new Matanzas substation (LG&E\KU) The loop will require 600 feet of new 954 MCM ACSS construction and will be located 10.5 miles from Wilson. The new LG&E\KUMatanzas station will include 2 161/138 kV transformers, (2) 161 kV line terminals, (2) 138 kV line terminals, (6) 138 kV breakers, and (6) 161 kV breakers. | KY | KY | Other | Not Shared | Reliability | 0 | 2013-09-01 | 2016-01-01 | 161 | 0 | Bottom-Up
A in MTEP12 | A | Central | DEM | 3542 | 2015-09-15 | AMIN0447 | New Castle Ingersoll 1 Bank 2 Repl | New Castle Ingersoll 1 Bank 2 Repl ? Replace 34/12kV bank w/22MVA 69/12kV Bank. Add 69kV tap line. | IN | IN | Other | Not Shared | Load Growth | 579657 | 2019-12-31 | 2019-12-31 | 69 | 12 | Bottom-Up
A in MTEP12 | A | West | GRE | 11543 | 2016-07-25 | 200497 | G549 - Glacial Ridge | Install new 69kV 3-way switch structure in the GRE AG-WL line. | MN | MN | GIP |  |  | 150000 | 2018-11-01 | 2018-11-01 | 69 | 0 | Externally Driven
A in MTEP12 | A | West | GRE | 11563 | 2016-07-25 | 202038 | G830 - McHenry Substation Upgrade | Install 115 kV ring bus at McHenry substation | ND | ND | GIP |  |  | 4952173 | 2018-09-20 | 2018-09-20 | 115 | 0 | Externally Driven
A in MTEP12 | A | East | ITC, ITCT | 3591 | 2018-03-27 | ITC_13_028 | St. Clair 345 kV Station Equipment Upgrades | Replace 345kV station equipment in the B, C and D rows at St. Clair. | MI | MI | BaseRel | Not Shared |  | 924000 | 2018-06-01 | 2018-06-01 | 345 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3630 | 2011-12-13 | Adams-Stewartville | Adams to Stewartville 69 kV Rebuild | Rebuild the ~35 mile line section due to age & condition. | IA | IA | Other | Not Shared | Reliability | 12200000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3632 | 2011-12-13 | Arnold 161 | Arnold 161kV Bus Upgrades | Move the Arnold-Hiawatha 161 kV line terminal to a new terminal position next to the Arnold-6th Street 161 kV line by adding 2 new 161 kV breakers. | IA | IA | BaseRel | Not Shared |  | 2529402 | 2018-12-30 | 2018-12-30 | 161 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3638 | 2011-12-13 | Corydon Sub Rbld | Corydon 69 kV Sub Rebuild | Complete rebuild of the substation with all new equipment. | IA | IA | Other | Not Shared | Age and Condition | 5129204 | 2019-06-28 | 2019-06-28 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3640 | 2011-12-13 | Belmond-Meservey | Belmond-Meservey | Rebuild the 4.65 mile section old line to new T2-4/0 ACSR. | IA | IA | Other | Not Shared | Age and Condition | 1056316 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3643 | 2011-12-13 | Osceola-Woodburn | Osceola Rec. to Woodburn Jct. 69 kV Rebuild | Rebuild the 5.5 mile section old line to new T2-4/0 ACSR. | IA | IA | Other | Not Shared | Age and Condition | 1950000 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3644 | 2011-12-13 | Knoxville-Lucas | Knoxville to Lucas County 69 kV Rebuild | Rebuild 10.6 miles of old line to new T2-4/0 ASCR. | IA | IA | Other | Not Shared | Age and Condition | 3750000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3645 | 2011-12-13 | Tirboji-Orleans Tap | Triboji 6750 (Oleans Tap) 69 kV Rebuild | Rebuild ~9.5 miles of old line to new T2-4/0 ASCR. | IA | IA | Other | Not Shared | Age and Condition | 3350000 | 2027-12-31 | 2027-12-31 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | Eastern Iowa Project Rebuilds | Rebuild the 34.5 kV line sections to 69 kV construction and operate at 34.5 kV until conversion. | IA | IA | Other | Not Shared | Age and Condition | 43838066 | 2013-06-10 | 2022-05-25 | 34 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3648 | 2011-12-13 | Marshalltown-Grand Jct | Marshalltown-Grand Junction Area Conversion | Rebuild the 34.5 kV line sections to 69 kV construction and operate at 34.5 kV until conversion. | IA | IA | Other | Not Shared | Age and Condition | 34170041 | 2013-07-19 | 2019-12-31 | 34 | 0 | Bottom-Up
A in MTEP12 | A | West | ITCM | 3649 | 2011-12-13 | Plaza LI | Plaza Interconnection | The Marshalltown ? Timber Creek 161 kV line will be tapped in & out of the new Plaza substation, with line terminals including breakers and a bus tie breaker. | IA | IA | Other | Not Shared | Load Growth | 1750000 | 2025-12-31 | 2025-12-31 | 161 | 0 | Bottom-Up
A in MTEP12 | A | West | MEC | 3710 | 2014-03-31 | T3094 | Norwalk 161-33 kV transformer | Add 33 MVA 161-13 kV transformer at existing substation | IA | IA | Other | Not Shared | Load Growth | 886413 | 2019-11-01 | 2019-11-01 | 161 | 13.2 | Bottom-Up
A in MTEP12 | A | East | METC | 3590 | 2015-02-26 |  | SVC at Tippy | Install Static Var Compensator (SVC) at Tippy | MI | MI | BaseRel | Shared |  | 28500000 | 2030-06-01 | 2030-06-01 | 138 | 0 | Bottom-Up
A in MTEP12 | A | East | METC | 3599 | 2014-03-31 |  | Palisades 345 kV Station Equipment Upgrades | Upgrade the station equipment at Palisades in rows 25, 27, and 29. | MI | MI | BaseRel | Not Shared |  | 4000000 | 2018-12-31 | 2018-12-31 | 345 | 0 | Bottom-Up
A in MTEP12 | A | West | XEL | 3769 | 2011-12-13 | Mankato - Twin Cities through flow mitigation | Mankato - Twin Cities through flow mitigation | Re-build 13 miles of 69 kV line from Carver County substation to Arlington to 477 ACSR conductor and Install 5.4 MVAR capacitor at Crystal Foods substation along with Auto transfer switch. | MN | MN | Other | Not Shared | Reliability | 6364887 | 2022-05-31 | 2022-05-31 | 69 | 0 | Bottom-Up
A in MTEP12 | A | West | XEL | 3797 | 2012-01-07 | Maple River - Red River 2nd 115 kV circuit | Maple River - Red River 2nd 115 kV line | build 5 miles of new 115 kV circuit between Maple River and Red River substations | ND | ND | Other | Not Shared | Reliability | 20899014 | 2019-05-31 | 2019-05-31 | 115 | 0 | Bottom-Up
A in MTEP11 | A | Central | AmerenIL, DEI | 2237 | 2011-11-03 | 11 Prop. MVP Port.1 (62) | Proposed MVP Portfolio 1 - Pana - Mt. Zion - Kansas - Sugar Creek 345 kV line | Pana to Mt. Zion to Kansas to Sugar Creek 345 kV line. Install transformers at Mt. Zion and Kansas | IN | IL | MVP | Shared |  | 404079819 | 2015-02-26 | 2019-11-15 | 345 | 138 | Top-Down
A in MTEP11 | A | Central | AmerenMO | 3170 | 2017-10-24 | 08 Prop. MVP Port.1 | Proposed MVP Portfolio 1 - Zachary-Maywood 345 kV Line | Zachary - Maywood 345/161 kV, 64 miles. Establish a new 345 kV substation at Maywood | MO | MO | MVP | Shared |  | 175011053 | 2016-01-10 | 2019-12-15 | 345 | 161 | Top-Down
A in MTEP11 | A | Central, West | AmerenMO, ITCM, MEC | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | Proposed MVP Portfolio 1 - Zachary - Ottumwa 345 | Zachary Substation - New 560 MVA, 345/161 kV Transformer. New 71 mile 345 kV line from Zachary to Ottumwa with 3000 A summer emergency capability | MO | IA | MVP | Shared |  | 222958799 | 2019-05-16 | 2019-05-31 | 345 | 161 | Top-Down
A in MTEP11 | A | West | ATC, ATC LLC, DPC, ITCM, XEL | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | Proposed MVP Portfolio 1: N LaCrosse-N Madison-Cardinal-Hickory Creek 345 kV | Construct N LaCrosse-N Madison-Cardinal 345 kV & Hickory Creek-Cardinal 345 kV line. | WI,IA | IA | MVP | Shared |  | 1033927000 | 2013-06-05 | 2023-12-31 | 345 | 69 | Top-Down
A in MTEP11 | A | Central | DEM | 3386 | 2010-09-15 | AMIN0379 | Carmel Springmill Rd. to Hortonville 69kV Line and Brkrs | Carmel Springmill Rd. Sub - Add 3-69kV breakers in straight bus config and build new .23 mile 69kV 954ACSS@200C line from Springmill Sub to old Springmill Jct. to complete circuit to Hortonville. Change operating mode at Homeplace to close loop from 146th to Springmill. | IN | IN | Other | Not Shared | Reliability | 1866000 | 2019-06-01 | 2019-06-01 | 69 | 0 | Bottom-Up
A in MTEP11 | A | West | GRE | 2679 | 2010-09-15 | 200331 | Ramsey-Grand Forks (81.02 mi.) 230 kV Rebuild | Ramsey-Grand Forks (81.02 mi.) 230 kV Rebuild | MN | MN | Other | Not Shared | Age and Condition | 41496024.63 | 2021-05-31 | 2021-05-31 | 230 | 0 | Bottom-Up
A in MTEP11 | A | West | GRE | 3454 | 2014-09-12 | 201035 | Pomerleau Lake Line Termination | Terminate the Parkers Lake - Elm Creek 115 kV line to the Pomerleau Lake breaker station that Xcel Energy plans to establish in the 2013 timeframe | MN | MN | Other | Not Shared | Reliability | 428949.26 | 2018-12-21 | 2018-12-21 | 115 | 0 | Bottom-Up
A in MTEP11 | A | East | ITC, ITCT | 3285 | 2018-06-27 | ITCT_12_007 | Shoal 120kV Capacitor | 33.3 Mvar Capacitor at Shoal 120kV | MI | MI | BaseRel | Not Shared |  | 4330000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
A in MTEP11 | A | West | ITCM, MEC | 3213 | 2014-03-31 | 04 Prop. MVP Port.1 | Proposed MVP Portfolio 1 - Winco to Hazleton 345 kV line | Winco to Lime Creek to Killdeer to Blackhawk to Hazleton 345 kV line and Lime Creek, Killdeer and Black Hawk transformers | IA | IA | MVP | Shared |  | 564397635.58 | 2015-08-14 | 2019-06-30 | 345 | 161 | Top-Down
A in MTEP11 | A | West | MDU, OTP | 2220 | 2018-07-31 | 06 Prop. MVP Port.1 | MVP Portfolio 1 - Ellendale to Big Stone South | Big Stone to Ellendale 345 kV line | SD,ND | ND | MVP | Shared |  | 274000000 | 2019-06-30 | 2019-06-30 | 345 | 230 | Top-Down
A in MTEP11 | A | East | NIPS | 3203 | 2011-11-03 | 12 Prop. MVP Port.1 | Proposed MVP Portfolio 1 - Reynolds to Burr Oak to Hiple 345 kV | Reynolds to Burr Oak to Hiple 345 kV line and tie in second AEP 345 kV circuits at Reynolds and Hiple | IN | IN | MVP | Shared |  | 404800000 | 2018-09-30 | 2018-09-30 | 345 | 0 | Top-Down
A in MTEP11 | A | East | WPSC | 3335 | 2010-09-15 | Burnips Xmsn | Burnip Transmission Station Upgrade | Upgrade to replace outdated equipment. Bus, breakers, relays, and other equipment as necessary. | MI | MI | Other | Not Shared | Age and Condition | 800000 | 2022-12-31 | 2022-12-31 | 69 | 0 | Bottom-Up
A in MTEP10 | A | Central | DEM | 2143 | 2017-09-27 | 602J3066 | Frances Creek 345/69kV Bank 2 | Add Frances Creek 345/69kV Bank 2 - 200MVA with LTC | IN | IN | Other | Not Shared | Reliability | 6887000 | 2023-06-01 | 2023-06-01 | 345 | 69 | Bottom-Up
A in MTEP10 | A | West | GRE | 2577 | 2016-02-10 | 20312 | Columbus (CE) 69 kV Substation | Columbus (previously Elmcrest) (CE) 69 kV Substation | MN | MN | Other | Not Shared | Load Growth | 140000 | 2021-05-18 | 2021-05-18 | 69 | 0 | Bottom-Up
A in MTEP10 | A | West | GRE | 2579 | 2010-09-15 | 20273 | Foster Lake (WH) 69 kV Substation | Foster Lake (WH) 69 kV Substation | MN | MN | Other | Not Shared | Load Growth | 140000 | 2021-11-01 | 2021-11-01 | 69 | 0 | Bottom-Up
A in MTEP10 | A | West | GRE | 2589 | 2009-11-19 | 20328 | Barnes Grove (DEA) 2.0 mile, 69 kV line | Barnes Grove (DEA) 2.0 mile, 69 kV line | MN | MN | Other | Not Shared | Load Growth | 115001 | 2023-07-20 | 2023-07-20 | 69 | 0 | Bottom-Up
A in MTEP10 | A | West | GRE | 2670 | 2018-09-11 | 20446 | Schuster Lake 115/41.6 Source | Schuster Lake115/41.6 Source | MN | MN | Other | Not Shared | Reliability | 6676163.28 | 2019-11-01 | 2019-11-01 | 115 | 41.6 | Bottom-Up
A in MTEP10 | A | West | ITCM | 3048 | 2009-09-14 | Jeff-Perlee | Jefferson Co-Perlee 69kV Rebuild | Rebuild the Jefferson Co-Perlee 69kV line section. | IA | IA | Other | Not Shared | Age and Condition | 2700000 | 2022-12-31 | 2022-12-31 | 69 | 69 | Bottom-Up
A in MTEP10 | A | West | ITCM | 3053 | 2017-11-09 | Keokuk-Carbide | Keokuk Hydro-Carbide 69kV Dbl Ckt | Build a new 69kV circuit from Keokuk Hydro-Carbide. | IA | IA | Other | Not Shared | Reliability | 20062760 | 2016-08-03 | 2020-06-15 | 69 | 69 | Bottom-Up
A in MTEP10 | A | West | ITCM | 3055 | 2018-05-04 | CR 34kV Plan | Cedar Rapids 34kV Conversion Plan | ITCM, working with IP & L, has formed a plan to better serve Cedar Rapids load with new larger, 2-transformer substations that will allow retirement of the 4kV system along with several other small distribution substations. Most of these new substations will be served from a new 69 kV and 161 kV Cedar Rapids transmission system that will use the existing 34.5 kV system right-of-way. This will allow retirement of several existing 34.5kV lines while shifting distribution load to a higher voltage to allow better normal and contingency performance. | IA | IA | Other | Not Shared | Reliability | 33882151 | 2011-04-29 | 2019-04-01 | 161 | 69 | Bottom-Up
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | West Branch 34kV Load Shift Projects | Construct 69kV taps for the Moscow & New Liberty dist. Subs | IA | IA | Other | Not Shared | Load Growth | 1258000 | 2020-05-12 | 2020-12-31 | 69 | 34 | Bottom-Up
A in MTEP10 | A | West | MP | 2761 | 2009-11-13 | Dunka Rd | Polymet | add new 138/14 kV substaion off MP 138 KV Line #1 | MN | MN | Other | Not Shared | Load Growth | 3242847 | 2020-12-31 | 2020-12-31 | 138 | 14 | Bottom-Up
A in MTEP10 | A | West | NWEC | 3092 | 2009-11-16 | 2012-02 | Webb Lake 69KV line | Rebuild 34.5KV line to Webb Lake at 69KV with horizontal post construction and #4/0 ACSR | WI | WI | Other | Not Shared | Age and Condition | 425000 | 2021-06-01 | 2021-06-01 | 69 | 0 | Bottom-Up
A in MTEP09 | A | Central | AmerenIL | 2273 | 2010-04-05 |  | Supply to LaFarge Customer Substation | Provide 161 kV supply to customer substation | IL | IL | Other | Not Shared | Load Growth | 570000 | 2020-06-01 | 2020-06-01 | 161 | 0 | Bottom-Up
A in MTEP09 | A | Central | DEM | 2154 | 2011-09-27 | AMIN0360 | Carmel Rohrer Rd 69/12kv New Sub | Carmel Rohrer Rd 69/12-22.4MVA sub to looped through the 6989 ckt. at or near the existing Carmel Shell Oil tap | IN | IN | Other | Not Shared | Load Growth | 591143 | 2019-06-01 | 2019-06-01 | 69 | 12 | Bottom-Up
A in MTEP09 | A | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | Anita Area 34kV to 69kV Rebuilds | Rebuild 5 miles from the Anita-Exira REC to 69kV. Also rebuild 4.7 miles of the Anita to th e Anita-Wiota Joint sub. Rebuild 21.9 miles from Thompson- Redfield. These lines will continue to opeate at 34kV. | IA | IA | Other | Not Shared | Age and Condition | 18739439 | 2014-08-27 | 2018-12-31 | 34 | 0 | Bottom-Up
A in MTEP09 | A | East | METC | 2478 | 2017-06-30 |  | Capital Ave | New distribution interconnection served from Battle Creek - Verona #2 138kV (Line connection change to Battle Creek to Island Road) | MI | MI | Other | Not Shared | Load Growth | 178188 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP09 | A | East | METC | 2481 | 2016-06-08 |  | Forrest Grove | New distribution interconnection served from Campbell-Ransom 138kV circuit. | MI | MI | Other | Not Shared | Load Growth | 170000 | 2018-05-31 | 2018-05-31 | 138 | 0 | Bottom-Up
A in MTEP09 | A | East | METC | 2482 | 2018-06-27 |  | Hawthorne | New distribution interconnection served from Four Mile - Blendon 138kV circuit. | MI | MI | Other | Not Shared | Load Growth | 170000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
A in MTEP09 | A | East | METC | 2485 | 2016-06-08 |  | Ironwood | New distribution interconnection served from CE's 138kV spur on the Ransom-Buck Creek 138kV. | MI | MI | Other | Not Shared | Load Growth | 12000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
A in MTEP09 | A | East | METC | 2486 | 2018-03-27 |  | Haakwood | New distribution interconnection served from Riggsville-Livingston 138kV (on the Rondo-Vanderbilt section) | MI | MI | Other | Not Shared | Load Growth | 170000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
A in MTEP09 | A | East | METC | 2501 | 2015-02-26 |  | Northern Reactive | Install 3 capacitors in the northern part of Michigan | MI | MI | BaseRel | Not Shared |  | 2700001 | 2030-06-01 | 2030-06-01 | 0 | 0 | Bottom-Up
A in MTEP09 | A | Central | Vectren | 2466 | 2017-06-30 | SIGE7 | Roesner Rd 138/12kV Substation | New 138/12kV Substation for load growth | IN | IN | Other | Not Shared | Load Growth | 5000000 | 2025-12-31 | 2025-12-31 | 138 | 12.47 | Bottom-Up
A in MTEP09 | A | East | WPSC | 2770 | 2009-02-03 |  | Gilmore | New distribution interconnection served from Hersey to Vestaburg circuit. | MI | MI | Other | Not Shared | Load Growth | 500000 | 2017-06-01 | 2017-12-31 | 69 | 0 | Bottom-Up
A in MTEP08 | A | Central | HE | 1929 | 2008-01-10 | None Yet | Georgetown Primary Ring Bus | 138kV Ring Bus addition / Modification to Georgetown Primary | IN | IN | Other | Not Shared | Reliability | 1250000 | 2012-09-01 | 2012-09-01 | 138 | 0 | Bottom-Up
A in MTEP08 | A | West | ITCM | 1744 | 2009-09-25 | GM-MAQ | Maquoketa-Grand Mound 161kV Reconductor | Reconductor 161kV from Maquoketa to Grand Mound (old East Calamus-Maquoketa 161kV line) | IA | IA | BaseRel | Not Shared |  | 12800161 | 2018-12-31 | 2018-12-31 | 161 | 0 | Bottom-Up
A in MTEP08 | A | East | METC | 1448 | 2018-04-04 | 196 | Simpson | Project to connect a distribution transformer at Simpson | MI | MI | Other | Not Shared | Load Growth | 2200000 | 2019-12-31 | 2019-12-31 | 138 | 12.5 | Bottom-Up
A in MTEP08 | A | West | NWEC | 2016 | 2018-04-04 | 2011-02 | Frederic-Coffee Cup 69KV reconductor | Reconductor 69KV line with 477ACSR | WI | WI | Other | Not Shared | Reliability | 450000 | 2020-06-01 | 2020-06-01 | 69 | 0 | Bottom-Up
A in MTEP08 | A | Central | Vectren | 1784 | 2018-04-04 |  | Jasper#3 Sub Exp-Victory Line | Extend existing Victory line to new term at existing sub | IN | IN | Other | Not Shared | Reliability | 3625000 | 2025-12-31 | 2025-12-31 | 69 | 0 | Bottom-Up
A in MTEP08 | A | Central | Vectren | 1789 | 2018-09-13 |  | Y56 - City of Boonville Loop | New 69kV line from Boonville Sub to Boonville Pioneer Sub | IN | IN | Other | Not Shared | Reliability | 6600000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
A in MTEP06 | A | Central | AmerenIL | 739 | 2018-04-04 |  | Franklin County Power Plant Connection | Franklin County Power Plant Connection - Tap 345 kV Line 4561 Tap, and Install new 345 kV ring bus | IL | IL | Other | Not Shared (Pre-RECB 1) | Reliability | 6410900 | 2020-11-01 | 2020-11-01 | 345 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 13689 | 2018-09-27 |  | Upgrade Louisville South-Newton 138 kV line | Increase ground clearance for 20.49 miles of 954 ACSR rail in order to permit operation at 120 degrees C. Replace 954 ACSR rail bus conductor at both Louisville South and Newton. | IL | IL | BaseRel |  |  |  | 2030-06-01 | 2030-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 13705 | 2017-09-07 |  | North Nashville Substation: Install 138 kV Ring Bus | Install initial 3 position 138 kV ring bus (ultimate 4 position) at North Nashville Substation. | IL | IL |  |  |  | 7810000 | 2021-12-01 | 2021-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 13708 | 2018-10-03 |  | New Athens Dutch Hill 138 kV substation ring bus | Add 138 kV ring Bus. Initial 3-position (ultimate 4-position) | IL | IL |  |  |  | 8376000 | 2021-12-01 | 2021-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 13709 | 2018-10-03 |  | New Putnam breaker-and-a-half 138 kV substation | Build new 138 kV BAAH substation on new site near Hennepin. | IL | IL |  |  |  | 32492000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 13793 | 2018-10-03 |  | New El Paso 138 kV substation ring bus | Install initial 4-postion ring bus at El Paso Substation for in/out supply. | IL | IL |  |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 13797 | 2017-09-08 |  | Albion South-Norris City North-1: Rebuild to double circuit | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. | IL | IL |  |  |  |  | 2020-06-01 | 2020-06-01 | 345 | 138 | Bottom-Up
B in MTEP18 | B | Central | AmerenIL | 14062 | 2018-10-03 |  | New Hutsonville-Robinson-Marathon 138 kV line No. 2 | Install 2nd line between Hutsonville and Robinson Marathon. | IL | IL |  |  |  |  | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | Central | AmerenMO | 4075 | 2017-10-03 |  | Reconductor Sioux-Huster 138 kV line | Reconductor 5.9 miles of 954 kcmil ACSR with conductor capable of carrying 1600 A under summer emergency conditions. Replace 1200 A terminal equpment (dixconnect switches, CT's, bus conductor) at Huster with equipment capable of carrying 1600 A or better. | MO | MO |  |  |  | 5900000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | West | ATC | 13739 | 2018-02-05 | F4580 | S. Fond Du Lac - Spring Brook 69 kV (Y-133) Rebuild | Y133 SFDL SPB 69kV Rebuild | WI | WI |  |  |  | 31000000 | 2029-12-31 | 2029-12-31 | 69 | 0 | Bottom-Up
B in MTEP18 | B | West | ATC | 14187 | 2018-02-05 | PR07829 | Arnold SS, New 345 kV Inductor Bank | This project consists of installing a new 345 kV, 80 MVAR, oil-filled inductor bank at the Arnold substation to an open 345 kV bay position. | MI | MI | Other |  | Reliability | 5000000 | 2019-06-01 | 2019-06-01 | 345 | 0 | Bottom-Up
B in MTEP18 | B | West | ATC | 14907 | 2018-05-23 |  | Load Interconnection 2021 | These Distribution load Interconnections are customer need driven and typically require limited infrastructure modifications and additions with shorter project life cycles. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI |  |  |  | 7350000 | 2024-06-30 | 2024-06-30 | 138 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14909 | 2018-05-23 |  | Small Capital Project and Asset Renewal 2021 | Asset replacements and upgrades with short project life cycles not compatible with the MTEP 18-month review cycle. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI |  |  |  | 32969227 | 2024-06-30 | 2024-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14911 | 2018-05-30 |  | Communication Reliability Upgrades 2021 | Communications network system upgrades with short project life cycles not compatible with the MTEP 18-month review process. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI |  |  |  | 1741667 | 2024-06-30 | 2024-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14913 | 2018-05-23 |  | Line Clearance Mitigation Projects 2021 | Line Clearance Mitigation Project life cycles are not compatible with the MTEP 18-month review cycle. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI |  |  |  | 14000000 | 2024-06-30 | 2024-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14915 | 2018-05-30 |  | Physical Security 2021 | Physical Security Project life cycles are not compatible with the MTEP 18-month review cycle. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2021. | WI,MI | WI,MI |  |  |  | 9629152 | 2024-06-30 | 2024-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14964 | 2018-05-23 |  | Small Capital Project and Asset Renewal 2022 | Asset replacements and upgrades with short project life cycles not compatible with the MTEP 18-month review cycle. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI |  |  |  | 30489835 | 2025-06-30 | 2025-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14965 | 2018-05-30 |  | Communication Reliability Upgrades 2022 | Communications network system upgrades with short project life cycles not compatible with the MTEP 18-month review process. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI |  |  |  | 8851667 | 2025-06-30 | 2025-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14966 | 2018-05-23 |  | Line Clearance Mitigation Projects 2022 | Line Clearance Mitigation Project life cycles are not compatible with the MTEP 18-month review cycle. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI |  |  |  | 7100000 | 2025-06-30 | 2025-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14967 | 2018-05-30 |  | Physical Security 2022 | Physical Security Project life cycles are not compatible with the MTEP 18-month review cycle. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI |  |  |  | 9165536 | 2025-06-30 | 2025-06-30 | 345 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 14968 | 2018-05-30 |  | Load Interconnection 2022 | These Distribution load Interconnections are customer need driven and typically require limited infrastructure modifications and additions with shorter project life cycles. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | WI,MI | WI,MI |  |  |  | 38475000 | 2025-06-30 | 2025-06-30 | 138 | 69 | Bottom-Up
B in MTEP18 | B | West | ATC | 15125 | 2018-05-24 |  | Marquette County, new DIC | Load addition in Marquette County, MI | MI | MI |  |  |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | CLECO | 13874 | 2017-12-05 |  | Flagon Substation | Build a new 230 kV substation Tapped into the Donahue to Sherwood 230 kV line. Use the distribution in the area to move 16 MW from Beaver Creek substation. | LA | LA |  |  |  | 8130000 | 2020-05-01 | 2020-05-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | CLECO | 13875 | 2017-09-25 |  | North Bend Double Circuit | This project will eliminate Bayou Sale 138 kV substation bypassing it and going straight from Teche to North Bend. It will also build a new 3.85 mile 138 kV line from North Bend to the Bayou Sale to Wax lake 138 kV line. This will create the new 138 kV transmission path Teche to North Bend to Wax lake. The current 19.2 MVAR cap bank at Bayou Sale will be moved to North Bend. Also the 34.5 low side of north bend will be reconfigured due to the the substation no longer being served from a radial transmission feed. | LA | LA | BaseRel |  |  | 14461000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | CLECO | 13876 | 2017-09-25 |  | Madisonville-Mandeville 230 kV Reconductor | Reconductor Madisonville to Mandeville 230 kV line with 1-ACSS/TW/HS285 Cardinal. | LA | LA | BaseRel |  |  | 15803000 | 2025-05-01 | 2025-05-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | CLECO | 14404 | 2018-08-20 |  | Rork-Oakdale 230kV line | Build a new 57.5 mile 230 kV line from Rork to Oakdale add a new 138/230 kV 500 MVA Auto at Oakdale. | LA | LA |  |  |  | 87690000 | 2026-05-01 | 2026-05-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 12670 | 2018-08-07 | 17-EAI-015 | Hall 115kV: Construct new Substation and Line | Extend transmission line 5.5 miles from Mt Ida substation to east of Hall Street. Build a new substation with one 40 MVA 115/34.5kV LTC transformer, one main breaker, three feeder breakers, and one bus tie breaker. | AR | AR | Other |  | Load Growth | 38093408 | 2025-06-01 | 2025-06-01 | 115 | 34.5 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13605 | 2017-09-13 | 18-EAI-025 | Carmel 115kV: Install Transmission Breakers | Build a 115kV breaker station at the Carmel Switching Station. | AR | AR |  |  |  | 10493407 | 2025-12-01 | 2025-12-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13606 | 2017-09-13 | 18-EAI-032 | Maumelle East 115kV: Install Transmission Breakers | Build a 115kV breaker station at the Maumelle East tap station. Build a transmission line between structures 91 and 79 on Line #944 to ensure looped service to Maumelle East substation. | AR | AR |  |  |  | 11499529 | 2024-06-01 | 2024-06-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13607 | 2017-09-21 | 18-EAI-034-6 | Little Rock Enhanced Reliability Project Phase 6 | Upgrade all station equipment along the Little Rock South - Little Rock West 115kV line to provide full conductor capacity. | AR | AR |  |  |  | 5356512 | 2023-12-01 | 2023-12-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13609 | 2017-09-21 | 18-EAI-034-5 | Little Rock Enhanced Reliability Project Phase 5 | Rebuild 5.3 miles of the LR Pinnacle - LR Walton Heights 115kV line to a minimum of 1950 Amps. | AR | AR |  |  |  | 7796854 | 2022-12-01 | 2022-12-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13610 | 2017-09-21 | 18-EAI-034-4 | Little Rock Enhanced Reliability Project Phase 4 | Rebuild 0.7 mile of the LR Gaines - NLR Westgate 115kV line to a minimum of 1950 Amps. | AR | AR |  |  |  | 3921272 | 2022-12-01 | 2022-12-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13616 | 2017-09-13 | 18-EAI-022 | Walnut Ridge - Black Rock 161kV: Upgrade line bay bus | Upgrade the line bay bus and all station equipment at Walnut Ridge to a minimum of 800 Amps. | AR | AR |  |  |  | 710127 | 2027-12-01 | 2027-12-01 | 161 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13627 | 2018-05-23 | 18-EAI-004 | El Dorado 115kV: Reliability Improvement Project | Tap the El Dorado Lion - El Dorado Parker's Chapel 115kV line into El Dorado West 115kV station. Convert the El Dorado West 115kV station to a breaker station. Construct a new 10 mile El Dorado EHV - El Dorado West 115kV line. | AR | AR | BaseRel |  |  | 41226266 | 2025-06-01 | 2025-06-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-AR | 13633 | 2018-05-22 | 18-EAI-009 | Quitman - AECC Bee Branch 161kV: Rebuild line | Rebuild the ~8.8 mile line segment along with any other station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | AR | BaseRel |  |  | 11901686 | 2023-06-01 | 2023-06-01 | 161 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13894 | 2017-09-25 | 18-ELB-002 | Addis to Tiger 230 kV: New 2nd line | Construct a new Addis to Tiger 2nd 230 kV line to a minimum of 1600 Amps. The construction will include 5 miles of new 230 kV line on separate structures and additional 1 mile of river crossing. Addis 230 kV expansion 1) Expand Addis 230 kV to a breaker and half scheme .This can be achieved by installing (3) breakers in an existing bay, between 230-115 kV auto and the existing Tiger 230 kV Line-782. 2) The new second Tiger line will require additional bay at Addis with (2) breakers protection. Tiger 230 kV expansion 3) The second 230 kV line from Addis terminates into Tiger Bus #1 with (1) 230 kV line breaker. | LA | LA | BaseRel |  |  | 63530000 | 2027-06-01 | 2027-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13904 | 2017-09-25 | 18-ELS-002 | Valentine to Golden Meadow 115 kV 2nd line | 1) Construct a new ~22 mile long 230 kV line from Valentine to Golden Meadow. 2) Rebuild the existing Clovelly to Golden Meadow 115 kV line to double circuit 230 kV and 115 kV, ~7.2 miles. Operate the line at 115 kV initially and tie both circuits together at Clovelly and Golden Meadow. 3) At Valentine 115 kV station, extend the bus work to the east and add two new breakers. 4) Reconfigure the Golden Meadow 115 kV station into a ring bus with the ability to expand to breaker and a half. | LA | LA | BaseRel |  |  | 82800000 | 2026-06-01 | 2026-06-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13905 | 2017-09-25 | 18-ELS-003 | Burnside 230-115 kV Autotransformer | 1) Construct a 3 breaker 230 kV ring bus at Burnside, Minimum of 2000 Amp equipment. 2) Cut in and out the Conway to Panama 230 kV line. 3) Install 230-115 kV Autotransformer 4) Install 115 kV low side breaker at Burnside. | LA | LA | BaseRel |  |  | 17000000 | 2024-06-01 | 2024-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13907 | 2018-08-30 | 18-ELS-004 | Re-terminate North Slidell to Bogalusa 230 kV at Adams Creek 230 kV | Move the terminal point of the North Slidell to Bogalusa 230 kV line from Bogalusa 230 kV substation to the Adams Creek 230 kV substation, creating the North Slidell to Adams Creek 230 kV line (in place of the current North Slidell – Bogalusa 230 kV line). Install three new breakers at the empty line bay in breaker and half configuration, such that Adams Creek – North Slidell 230 kV and Adams Creek – Bogalusa 230 kV line B are accommodated in the same bay. | LA | LA | BaseRel |  |  | 5200000 | 2023-06-01 | 2023-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13910 | 2018-08-06 | 18-ELN-002 | Calhoun: New distribution substation | Construct a 230 kV distribution substation named Calhoun in western Ouachita parish near the town of Calhoun and construct a 230 kV transmission line from the new substation that terminates into the Choudrant substation (MISO Project ID 13925). | LA | LA | Other |  | Load Growth | 38330000 | 2026-06-01 | 2026-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13925 | 2018-08-06 | 18-ELN-004 | Choudrant: New distribution substation | Construct a 230 kV distribution substation named Choudrant in southern Lincoln parish near the town of Choudrant and construct a 230 kV transmission line from the new substation that terminates into the existing Mt Olive substation. | LA | LA | Other |  | Load Growth | 47500000 | 2023-06-01 | 2023-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13927 | 2017-09-25 | 18-ELN-003 | Calhoun - Cadeville 230 kV: new line | Construct a 230 kV transmission line from the Calhoun substation (MISO ID 13910) to the Cadeville substation (MISO ID 9684). Convert the Rilla - Cotton - Cadeville line sections to 230 kV operation. | LA | LA | BaseRel |  |  | 20700000 | 2026-06-01 | 2026-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13936 | 2018-08-06 | 18-ELN-007 | Dubach: New distribution substation | Construct a new distribution substation near the town of Dubach, LA that cuts into the Vienna - Bernice 115 kV line section. | LA | LA | Other |  | Load Growth | 12100000 | 2025-06-01 | 2025-06-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13937 | 2018-08-06 | 18-ELN-008 | Homer: New distribution substation | Construct a new distribution substation near the town of Homer, LA that cuts into the Haynesville - Minden East 115 kV line (MISO ID 12068). | LA | LA | Other |  | Load Growth | 27100000 | 2027-06-01 | 2027-06-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13938 | 2017-09-25 | 18-ELN-005 | Cheniere 115 kV: Install transmission breakers | Install transmission breakers at the existing Cheniere 115 kV substation, which is located on the Frostkraft - Sterlington 115 kV transmission circuit. | LA | LA | Other |  | Reliability | 3400000 | 2023-12-01 | 2023-12-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13954 | 2018-08-06 | 18-ELB-004 | Cohen Area 230 kV: Construct New Substation | Cohen Area (Northline) substation will cut in between Addis and Cohen 230 kV stations. | LA | LA | Other |  | Load Growth | 14500000 | 2024-06-01 | 2024-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13969 | 2018-08-06 | 18-ELC-004 | Pine Hill Rd 138 kV: New Substation | Pine Hill substation will cut in on the Lowe Grout to Jennings 138 kV line section near Pine Hill Road. | LA | LA | Other |  | Load Growth | 10800000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13970 | 2018-08-06 | 18-ELC-005 | Vinton 138 kV: New Substation | Vinton substation will cut in on the Marshall to Toomey 138 kV line section. Depending on the location of the station, ~three miles of transmission may need to be constructed to the new station. | LA | LA | Other |  | Load Growth | 11500000 | 2026-12-01 | 2026-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13971 | 2018-08-06 | 18-ELB-005 | South Baton Rouge Area 230 kV: New Substation | The station may be cut in between the Tiger and Willow Glen 230 kV stations and will include ~8 miles of new 230 kV line. Mileage and exact location of the station is still TBD. | LA | LA | Other |  | Load Growth | 14650000 | 2025-12-01 | 2025-12-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13984 | 2017-09-25 | 18-ELF-001 | Labit Rd 230 kV: New Substation | Labit Road 230 kV substation will cut in on the Cecelia to Lake Peigneur 230 kV line section. | LA | LA | Other |  | Reliability | 12000000 | 2024-06-01 | 2024-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13986 | 2018-08-06 | 18-ELF-003 | Milton 230 kV: New Substation | Milton 230 kV substation may be cut in on the Segura to Sellers Road 230 kV CLECO line section. | LA | LA | Other |  | Load Growth | 13400000 | 2027-06-01 | 2027-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13988 | 2018-08-06 | 18-ELF-005 | Ambassador 230 kV: New Substation | Ambassador 230 kV substation may be served on a radial out of Labit Road 230 kV station. Approximately 6 miles of 230 kV line will need to be constructed from Labit Road to the new station. | LA | LA | Other |  | Load Growth | 19600000 | 2025-12-01 | 2025-12-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13989 | 2017-09-25 | 18-ELF-004 | Sugar 230 kV: New Substation | Sugar 230 kV substation will be cut in on the Cecelia to Labit Road 230 kV line section. | LA | LA | Other |  | Reliability | 5500000 | 2025-12-01 | 2025-12-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-LA | 13991 | 2018-08-30 | 18-ELS-005 | Ascension 230 kV: New Substation | Gonzales Area 230 kV substation will be cut in on the Sorrento to Demco Airline 230 kV line section. | LA | LA | Other |  | Load Growth | 8600000 | 2023-06-01 | 2023-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-MS | 13892 | 2018-09-13 | 18-EMI-004 | Moon Lake 230 kV: Cut-in Ritchie - Tunica 230 kV line | Cut in the Ritchie to Tunica 230 kV line into the Moon Lake substation. | MS | MS |  |  |  | 8600000 | 2027-06-01 | 2027-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-MS | 13906 | 2017-09-15 | 18-EMI-012 | Cockrum 230kV Substation | Construct new 230kV load serving substation near Cockrum, MS. Construct a new 230kV line from Byhalia to the new Cockrum substation. | MS | MS |  |  |  | 14000000 | 2027-06-01 | 2027-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-MS | 13951 | 2017-09-15 | 18-EMI-007 | Franklin to Wynndale 230kV Line | Construct a 230 kV line from Franklin to Wynndale. Construct 230 kV yards at the existing Wynndale and Franklin substations. Convert the Ray Braswell - Wynndale line to 230 kV operation. Install a 230-115 kV autotransformer at Wynndale. Install a 500-230 kV autotransformer at Franklin. | MS | MS |  |  |  | 99000000 | 2026-06-01 | 2026-06-01 | 500 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-MS | 13987 | 2017-09-15 | 18-EMI-014 | East Metro 230kV Substation | Tap Rankin to S. Jackson 230kV line and Brandon to Whitfield 115kV line to construct a new Substation with a 230-115kV autotransformer. | MS | MS |  |  |  | 19300000 | 2022-12-01 | 2022-12-01 | 230 | 115 | Bottom-Up
B in MTEP18 | B | South | Entergy-MS | 13994 | 2017-10-04 | 18-EMI-017 | Mitchell 115kV Substation | Construct new 115kV substation tapping the S. Jackson to Georgetown 115kV line. | MS | MS |  |  |  | 7600000 | 2022-06-01 | 2022-06-01 | 115 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-MS | 13995 | 2017-09-14 | 18-EMI-017 | Mannsdale 230kV Substation | Construct new 230kV substation cutting in on the Tinnin to Bozeman 230kV line | MS | MS |  |  |  | 8700000 | 2025-06-01 | 2025-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13930 | 2017-09-13 | 18-ETI-003 | Knatson 138 kV: New Substation | Knatson substation will cut into L825 between Stilson and Gordon. | TX | TX |  |  |  | 12800000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13931 | 2017-09-13 | 18-ETI-004 | Bolivar Peninsula T-Line & Substation Phase 1: Crenshaw 138 kV: New Substation | Construct a 138 kV line from Himex to Crenshaw and convert Blue Water to Crenshaw 138 kV substation. | TX | TX |  |  |  | 65300000 | 2024-06-01 | 2024-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13933 | 2017-09-13 | 18-ETI-005 | Bolivar Peninsula T-Line & Substation Phase 2: Brownwater 138 kV: New Substation | Convert Sandy Shores to Brownwater 138 kV and cut in and out of Himex to Crenshaw line. | TX | TX |  |  |  | 22000000 | 2024-06-01 | 2024-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13939 | 2017-09-13 | 18-ETI-006 | Hatcherville 138 kV: New Substation | Construct a new Hatcherville 138 kV substation and feed radial from Knatson substation. | TX | TX |  |  |  | 22200000 | 2024-06-01 | 2024-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13940 | 2017-09-13 | 18-ETI-007 | Wolf Island 138 kV: New Substation | Construct a new Wolf Island 138 kV substation that cuts into emergency Dayton - Crosby 138 kV tie. Operate Wolf Island - Crosby as normally open emergency tie. | TX | TX |  |  |  | 12300000 | 2025-06-01 | 2025-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13943 | 2017-09-13 | 18-ETI-010 | Southern Point 138 kV: New Substation | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | TX | TX |  |  |  | 11900000 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13945 | 2018-08-16 | 18-ETI-014 | Fairview 138 kV: Construct New Substation | Construct a new 138 kV substation on the Dayton Bulk to New Caney 139 kV line near Road 624. | TX | TX |  |  |  | 14400000 | 2024-12-01 | 2024-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13946 | 2017-09-13 | 18-ETI-015 | Intersection 138 kV: Construct New Substation | Construct a new Intersection 138 kV substation and feed radial (3.5 miles) from Wolf Island 138 kV substation. | TX | TX |  |  |  | 19000000 | 2026-06-01 | 2026-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 13947 | 2017-09-13 | 18-ETI-016 | Texaco Rd 138 kV: Construct New Substation | Construct a new 138 kV substation on the Colony to Eastgate 138 kV line near Texaco Road. | TX | TX |  |  |  | 12800000 | 2027-12-01 | 2027-12-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 14944 | 2018-04-05 | 17-ETI-016 | Tuscany 230 kV: New Substation | Tuscany substation will cut in on the China to Porter 230 kV line. | TX | TX |  |  |  | 36990000 | 2023-06-01 | 2023-06-01 | 230 | 0 | Bottom-Up
B in MTEP18 | B | South | Entergy-TX | 15104 | 2018-05-10 | 18-ETI-020 | Dobbin 138 kV: Install capacitor bank | Install a 25.1 MVAR capacitor bank with a breaker at the Dobbin 138 kV substation by the summer of 2024. | TX | TX |  |  |  | 730000 | 2024-06-01 | 2024-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | South | LAFA | 14105 | 2018-07-27 |  | Bonin 69kV Reconfiguration | A reconfiguration of the Bonin 69kV station. | LA | LA |  |  |  | 6400000 | 2019-12-31 | 2019-12-31 | 69 | 0 | Bottom-Up
B in MTEP18 | B | West | MDU | 14106 | 2018-07-10 |  | Heskett Tie Breaker | Add 115 kV bus tie breaker to the Heskett Swtichyard | ND | ND |  |  |  | 500000 | 2019-03-31 | 2019-03-31 | 115 | 0 | Bottom-Up
B in MTEP18 | B | West | MEC | 2938 | 2018-08-31 | G0104 | Uprate Sub 39 - Cordova 345 kV Line | Change out a limited number of existing 345 kV line structures to increase rating. | IL | IL | Other |  | Reliability | 325000 | 2023-12-01 | 2023-12-01 | 345 | 0 | Bottom-Up
B in MTEP18 | B | East | METC | 14050 | 2017-09-18 |  | Gallagher Fault Termination | Implement standard relaying scheme at Gallagher 345 kV to isolate the faulted line or transformer elements. | MI | MI | [6 empty] | 345 | 0 | Bottom-Up
B in MTEP18 | B | West | MP | 16069 | 2018-09-18 |  | Dunka - Babbitt 115 kV Project | Build Dunka switching station & extend existing Embarrass - Babbitt 115 kV Line to switching station. Rebuild Embarrass - Babbitt 115 kV line back to Embarrass. Includes 2x20 MVAR cap banks at Dunka. | MN | MN |  |  |  |  | 2021-12-31 | 2021-12-31 | 115 | 0 | Bottom-Up
B in MTEP18 | B | West | MP | 16070 | 2018-09-18 |  | Hoyt Lakes - Babbitt 115 kV Project | Build Hoyt Lakes switching station & extend existing Embarrass - Babbitt 115 kV Line to switching station. Rebuild Embarrass - Babbitt 115 kV line back to Embarrass. Includes 2x20 MVAR cap banks at Hoyt Lakes. | MN | MN |  |  |  |  | 2021-12-31 | 2021-12-31 | 115 | 0 | Bottom-Up
B in MTEP18 | B | West | MPC, OTP | 4232 | 2018-08-29 | OTP | Winger-Thief River Falls 230 kV Line | Winger Sub Expansion, Thief River Sub Expansion, New 47 mile 230kV Transmission Line Between Winger & Thief River, Thief River 230/115 Transformer | MN | MN | BaseRel |  |  | 30000000 | 2024-11-15 | 2024-11-15 | 230 | 115 | Bottom-Up
B in MTEP18 | B | West | MPC, OTP | 971 | 2018-07-18 | OTP1 | Winger 230/115 kV Transformer Upgrade | Winger 230/115 kV Transformer upgrade | MN | MN | BaseRel | Not Shared |  | 4458420 | 2022-10-01 | 2022-10-01 | 230 | 115 | Bottom-Up
B in MTEP18 | B | East | WPSC | 9916 | 2017-09-14 | Fairview Station Upgrade | Fairview Station Upgrade | Replace Fairview station with 138kV ring bus configuration station. | MI | MI |  |  |  | 4000000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP18 | B | East | WPSC | 14004 | 2017-09-14 |  | Haggensville Interconnection Line | Construct approximately 0.25 miles of new 138kV transmission line to connect the Grand Lake Distribution Station to METC’s 138 kV Port Calcite to Rockport transmission line. | MI | MI |  |  |  | 260000 | 2022-12-31 | 2022-12-31 | 138 | 0 | Bottom-Up
B in MTEP18 | B | East | WPSC | 14005 | 2017-09-14 |  | Hammond Bay Interconnection Line | Construct approximately 2 miles of new transmission line to connect the Hammond Bay Distribution Station to METC’s 138 kV transmission line. | MI | MI |  |  |  | 900000 | 2022-12-31 | 2022-12-31 | 138 | 0 | Bottom-Up
B in MTEP18 | B | East | WPSC | 14328 | 2017-10-13 |  | 2022 Fiber Retrofit | Installation of fiber on recently rebuilt (post 2006) 138kV structures utilizing ADSS (All Dielectric Self Supporting) and OPGW (Optical Ground Wire). Install approximately 100 miles per year for four years, starting in 2019 | MI | MI |  |  |  | 6000000 | 2022-12-22 | 2022-12-22 | 69 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 11925 | 2018-09-07 |  | New Massac Substation - Convert Joppa 230 kV substation to 345 kV substation | Install 345/161 kV, 560 MVA transformer, remove 230/161 kV equipment. Rebuild Joppa-West Frankfort 230 kV for 345 kV use (Massac-Jordan). | IL | IL |  |  |  |  | 2023-06-01 | 2023-06-01 | 345 | 161 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 11926 | 2017-03-10 |  | New Jordan Substation - Convert West Frankfort 230 kV substation to 345 kV substation | Install 345/138 kV, 560 MVA transformer. Rebuild/reinsulate 19.9 miles of existing 230 kV line between West Frankfort and St. Johns for use at 345 kV. | IL | IL |  |  |  |  | 2023-12-01 | 2023-12-01 | 345 | 138 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 11927 | 2017-08-23 |  | Convert Derby 230 kV substation to 345 kV substation | Install 345/138 kV, 560 MVA transformer. Extend 138 kV line to existing Derby Substation from new 345 kV substation. Replace 230/69 kV transformer with similarly rated 138/69 kV transformer. Rebuild/reinsulate 230 kV line between Commodore and Derby for 345 kV use. | IL | IL |  |  |  |  | 2022-12-01 | 2022-12-01 | 345 | 69 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 11969 | 2017-01-18 |  | New Miles-Misissippi 138 kV line | Construct new 138 kV line | IL | IL |  |  |  |  | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 12172 | 2017-01-18 |  | New Miles 138 kV capacitor bank w/ 120 Mvar capacity | Install a 120 Mvar, 138 kV capacitor bank (relocated from Mississippi) | IL | IL |  |  |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 12176 | 2017-01-18 |  | New West Frankfort East 345 kV reactor w/ 50 Mvar capacity | Install 345 kV, 50 Mvar shunt reactor and PCB. | IL | IL |  |  |  |  | 2020-12-01 | 2020-12-01 | 345 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenIL | 12179 | 2017-03-10 |  | New Massac 345 kV shunt reactor w/ 50 Mvar capacity | Install 345 kV, 50 Mvar shunt reactor and PCB. | IL | IL |  |  |  |  | 2020-12-01 | 2020-12-01 | 345 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenMO | 11905 | 2017-01-18 |  | Replace Watson 138 kV bus-tie 2-3 position | Replace terminal equipment in 138 kV Bus-Tie 2-3 position. | MO | MO |  |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenMO | 12173 | 2017-02-23 |  | New Gasco 138 kV capacitor bank | Gasco Area 138 kV Capacitor Bank (size TBD) | MO | MO |  |  |  |  | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenMO | 12181 | 2017-02-23 |  | New Bland-Gasco 138 kV line | Bland-Gasco 138 kV Line - Establish a new 8-mile 138 kV line with 1200 A summer emergency capability. | MO | MO |  |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenMO | 12426 | 2017-12-19 |  | Replace Meramec 138 kV breakers | Replace 1-138 kV Breaker | MO | MO |  |  |  |  | 2030-12-01 | 2030-12-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | Central | AmerenMO | 12428 | 2017-01-18 |  | Replace Stoddard 161 kV breakers | Replace 1-161 kV breaker at Stoddard | MO | MO |  |  |  |  | 2021-12-01 | 2021-12-01 | 161 | 0 | Bottom-Up
B in MTEP17 | B | West | ATC | 12143 | 2018-03-26 | PR05000 | Rebuild Sobieski - Bayport 69kV (T-98) | Rebuild Sobieski - Bayport 69kV (T-98) | WI | WI |  |  |  | 14990000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
B in MTEP17 | B | West | ATC | 12144 | 2018-03-26 | PR05000 | Rebuild Pioneer - Sobieski 69kV (E-83) | Rebuild Pioneer - Sobieski 69kV (E-83) | WI | WI |  |  |  | 14390000 | 2021-12-31 | 2021-12-31 | 69 | 0 | Bottom-Up
B in MTEP17 | B | West | ATC | 12175 | 2016-09-15 | PR07213, F4738, WO601705 | Rebuild West Middleton - Stagecoach 69KV | Rebuild 69 kV line from West Middleton to Stagecoach | WI | WI |  |  |  | 3754320 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
B in MTEP17 | B | Central | BREC | 12703 | 2016-12-15 |  | Bryan Rd-McCracken 161 kV Reconductor | The project involves replacing 15.6 miles of 795 MCM ACSR conductor on an existing 161 kV circuit with 795 MCM ACSS conductor. The improvement is expected to be completed in 2019. No additional land or right-of-way will be acquired as part of this project. It is expected that this project will be completed within an existing easement with minimal disturbance. As a result, this project is expected to have no significant environmental impact. It is expected that this project description and work plan report provide adequate information to classify the project as a categorical exclusion pursuant to 7 CFR 1794.21. | KY | KY | [6 empty] | 161 | 0 | Bottom-Up
B in MTEP17 | B | South | CLECO | 12984 | 2017-09-18 | CLEC | Beaver Creek Double Circuit Rebuild | Rebuild the Double Circuit portions of Beaver Creek to Donahue 138 kV line 1 and 2 so that their are no more Common structures between the two lines. | LA | LA |  |  |  | 3700000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-AR | 12026 | 2017-09-13 | 17-EAI-009 | Pine Bluff Enhanced Reliability Improvement Project | Cut the Woodward - Pinebergen 115kV line section into the Pine Bluff South 115kV station and operate to 230kV. Install a 230/115kV auto transformer at Pine Bluff South. Build Pine Bluff South - AECC Pinebergen to 230kV standards but only operate it at 115kV. | AR | AR |  |  |  | 30582348 | 2025-06-01 | 2025-06-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-AR | 12055 | 2017-09-13 | 17-EAI-008 | Gum Springs 115kV: Add transmission breakers | Create a new substation by tapping the Arkadelphia North – Richwood 115kV and the Arkadelphia West – Dalark 115kV line sections. | AR | AR |  |  |  | 10513196 | 2024-06-01 | 2024-06-01 | 115 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-AR | 12671 | 2018-08-01 | 17-EAI-021 | Timbo 161kV: Construct new Substation and Line | Construct a new substation on Highway 66 east of Timbo, AR. Install one 40 MVA 161/13.8 kV LTC transformer and four feeder breakers. Build 6 miles of transmission line from the Mt. View station to the new Timbo station. | AR | AR |  |  |  | 41213740 | 2026-12-01 | 2026-12-01 | 161 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-LA | 12068 | 2017-09-15 | 17-ELN-007 | Haynesville - Minden East 115 kV: Construct new line | Construct a switching substation (named Minden East) just east of the existing Minden REA substation that cuts into the Minden REA - Arcadia 115 kV line. Construct a 115 kV line from Haynesville to the new Minden East substation. | LA | LA |  |  |  | 39900000 | 2026-06-01 | 2026-06-01 | 115 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-LA | 12084 | 2016-09-14 | 17-ELB-003 | Dixie Baker to Zachary 69 kV: Upgrade Line | The ~3.3 mile long line should be upgraded to a minimum rating of 143 MVA. If any station equipment is rated lower than 143 MVA (1200 Amps), it should be upgraded as well. | LA | LA |  |  |  | 4700000 | 2027-06-01 | 2027-06-01 | 69 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-LA | 12088 | 2018-09-04 | 17-ELB-005 | Big Cajun to Coly 500 kV: New Line | Build a new 500 kV station near Big Cajun or expand LaGN owned Big Cajun 500 kV substation to connect new 500 kV line. Similarly, expand at the existing Coly 500 kV station to a 5 breaker ring bus configuration to terminate the other end of the 500 kV line with an ongoing project to install second Coly 500-230 kV, 1200 MVA auto. Installation of 2nd 500-230 kV auto at Coly is a MTEP Appendix A project 14-EGL-026. Construct approx. 37 miles of new Big Cajun to Coly 500 kV line. The new 500 kV line will be constructed to a minimum of 3000 A using a triple bundled conductor. | LA | LA |  |  |  | 129850000 | 2027-06-01 | 2027-06-01 | 500 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-LA | 12098 | 2017-09-12 | 17-ELB-007 | Delmont to Hazel 230 kV: Upgrade Line | Upgrade the Delmont to Hazel 230 kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. | LA | LA |  |  |  | 3900000 | 2026-06-01 | 2026-06-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-LA | 12771 | 2017-01-05 |  | Arnaudville 230 kV: New Substation | Build new distribution substation. | LA | LA |  |  |  | 9850000 | 2023-06-01 | 2023-06-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-MS | 4613 | 2017-05-17 | 11-EMI-007 | Breakers at Hollandale and Belzoni (close normally-open point) | Install breakers in the Hollandale substation and build a new breaker switching station at or near the Belzoni Tap switch or Midnight substation such that the normally open line segment between the Belzoni Tap Switch and the Murphy switching station can be closed in without creating a four-terminal line | MS | MS | BaseRel |  |  | 12235047 | 2022-12-01 | 2022-12-01 | 115 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-MS | 12218 | 2017-05-04 |  | Install Breakers at Whitfield SS | Add (3) 115kV breakers to the EMI Whitfield switching station. | MS | MS | Other |  | Reliability | 2200000 |  |  | 115 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-TX | 12069 | 2018-09-04 | 17-ETI-012 | War Eagle 138 kV: Construct New Substation and Lines | Construct a new War Eagle 138 kV (4) breaker ring bus substation approximately 0.3 miles north of the Oak Ridge 138 kV substation that cuts into the Oak Ridge – Metro 138 kV L-169. Construct a new 138 kV line from Porter to the new War Eagle substation using a conductor rated a minimum of 1950 A and a line route approximately 8 miles. Energize the abandoned 138 kV L-403 by terminating into the War Eagle and Forest 138 kV substations and rebuilding to a minimum of 1950 A. | TX | TX |  |  |  | 32600000 | 2025-06-01 | 2025-06-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-TX | 12086 | 2016-09-14 | 17-ETI-001 | Bryan to Caldwell Area 69 kV Station: Construct New Line and Substation | Construct a new (4) breaker 69 kV ring bus substation named Caldwell just East of the existing Caldwell Industrial 69 kV substation. Construct an approximately 24 mile line to 161 kV specifications from Bryan to the new 69 kV substation and operate to 69 kV. Move the City of Caldwell 69-13.8 kV distribution transformer to the new substation. | TX | TX |  |  |  | 32900000 | 2023-06-01 | 2023-06-01 | 69 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-TX | 12087 | 2017-05-17 | 17-ETI-002 | Magnolia Hebert 69 kV: Close Normally Open; Recondutor portion of line 114 | Rebuild the portion of 69 kV L114 between Texas Eastern Spindletop – Gulf Lucas – Gladys to achieve a minimum through path rating of 880 A. Install (2) breakers at Gladys 69 kV substation. | TX | TX | BaseRel |  |  | 5900000 | 2024-06-01 | 2024-06-01 | 69 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-TX | 12089 | 2018-09-04 | 17-ETI-004 | Pony 230-138 kV: Construct New Substation | Construct a new 230-138 kV substation named “Pony” adjacent to the existing Dayton 138 kV substation. The 138 kV bus should be constructed as a (4) bay breaker-and-a-half configuration (8 line bays). The 230 kV bus should be constructed as a (4) breaker ring bus with the ability to expand to a breaker-and-a-half. Move the Parkway, Long John, Petry Woods, Liberty and Rolke Road 138 kV lines to the new Pony substation. Construct two 138 kV lines between the existing Dayton substation and the new Pony substation. Install a 230-138 kV, 400 MVA autotransformer at the new Pony substation. | TX | TX |  |  |  | 17000000 | 2026-06-01 | 2026-06-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-TX | 12765 | 2017-05-17 | 17-ETI-018 | Double Bayou 138 kV: New Substation | Build new distribution substation. | TX | TX |  |  |  | 30200000 | 2024-06-01 | 2024-06-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | South | Entergy-TX | 12766 | 2017-01-05 | 17-ETI-015 | Junction 230 kV: New Substation | Build new distribution substation. | TX | TX |  |  |  | 13200000 | 2023-05-01 | 2023-05-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | South | ETEC | 8202 | 2016-09-12 | SHECO_02_MTEP17 | Fork Creek - Fred 138kV | Construct new Fred 138 kV substation and new Fred-Fork Creek 138 kV line | TX | TX | Other |  | Reliability | 27700000 | 2020-08-01 | 2020-08-01 | 138 | 0 | Bottom-Up
B in MTEP17 | B | South | ETEC | 12225 | 2017-06-01 | ETEC_01_MTEP17 | Lewis Creek - Ponderosa 230kV | Construct Lewis Creek - Ponderosa 230kV line, upgrade substations to accommodate new transmission line | TX | TX | Other |  | Reliability | 24000000 | 2021-08-01 | 2021-08-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | Lewis Creek - Ponderosa 230kV, Quarry - Rivtrin 345kV | Construct Lewis Creek - Ponderosa 230kV line, upgrade substations to accommodate new transmission line. Construct Quarry 345kV switching station, cut-in the 345kV Crocket - Grimes line. Construct Rivtrin 345kV switching station, install 345/138kV AT transformer. Construct Quarry - Rivtrin 345kV transmission line. | TX | TX | Other |  | Reliability | 62500000 | 2021-08-01 | 2021-08-01 | 345 | 138 | Bottom-Up
B in MTEP17 | B | East | ITC, ITCT | 2933 | 2017-09-14 | ITC_16_023 | Superior - Wayne 120 kV Reconductor | Re-conductor approximately 10.5 miles of 477 ACSR conductor of the Superior ? Wayne 120 kV circuit to 795 ACSR. | MI | MI | BaseRel | Not Shared |  | 6500000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
B in MTEP17 | B | East | ITC, ITCT | 4501 | 2017-09-14 | ITC_16_019 | Bunce Creek - Menlo 120 kV Rebuild | Rebuild the Bunce Creek - Menlo 120 kV circuit (8.6 miles) using 954 ACSR and OPGW on new 120 kV single circuit structures. Also replace limiting terminal equipment at both Bunce Creek and Menlo 120 kV stations. | MI | MI | BaseRel |  |  | 9800000 | 2020-12-31 | 2020-12-31 | 120 | 0 | Bottom-Up
B in MTEP17 | B | West | ITCM | 10784 | 2016-10-12 |  | Dubuque 8th Street 69kV 10MVAR | test | IA | IA | Other |  | Reliability |  | 2018-12-31 | 2018-12-31 | 69 | 69 | Bottom-Up
B in MTEP17 | B | West | ITCM | 13712 | 2017-09-27 | BvrChnl T3 TEQ | ITCM Beaver Channel T3 Terminal Upgrades | Upgrade the terminal equipment on the Beaver Channel 161/69kV T3 transformer. | IA | IA |  |  |  |  | 2026-12-31 | 2026-12-31 | 161 | 69 | Bottom-Up
B in MTEP17 | B | West | MEC | 10002 | 2017-05-25 |  | Sub 39 second 161-69 kV transformer | Install a second 125 MVA 161-69 kV transformer at Sub 39. | IA | IA | Other |  | Reliability | 960000 | 2022-06-01 | 2022-06-01 | 161 | 69 | Bottom-Up
B in MTEP17 | B | West | MP | 12564 | 2016-11-17 | 51 Line Upgrade | 51 Line Upgrade | Increase rating on 51 Line. | MN | MN | [6 empty] | 115 | 0 | Bottom-Up
B in MTEP17 | B | West | MP | 12684 | 2016-12-09 | Boswell 230 Fast-Switched Cap Bank | Boswell 230 Fast-Switched Cap Bank | Add fast-switched capacitor bank at Boswell 230 kV Substation (size TBD) | MN | MN |  |  |  | 1000000 | 2020-07-01 | 2020-07-01 | 230 | 0 | Bottom-Up
B in MTEP17 | B | West | OTP | 4813 | 2018-06-29 | OTP | Clearbrook 115 kV-Bagley West 230 kV | Clearbrook 115 kV to Bagley West 230 kV - new 115 kV transmission line (22 miles) 795 ACSR conductor. Bagley West 230/115 kV new substation. Add 230/115 kV Breakers 140 MVA Transformer & new line termination. Bagley West 230 kV tap. Project taps proposed Clearbrook to Clearbrook West 115 kV radial line. | MN | MN | BaseRel | Not Shared |  | 12300000 | 2026-01-01 | 2026-01-01 | 230 | 115 | Bottom-Up
B in MTEP17 | B | South | SMEPA | 12210 | 2016-09-15 |  | South Hattiesburg Delivery Point | In order to serve the South Hattiesburg delivery point economically and reliably, service will be established by rebuilding SMEPA’s exiting 69kV Line 87 (South Hattiesburg GOAB - South Hattiesburg Sub) with 795 ACSR conductor and installing a new 3-way remote controlled GOAB north of Purvis on Line 39B (Purvis – Okahola GOAB). A new 69/26.4kV, 15/20/25 MVA transformer will be installed at the South Hattiesburg substation to accommodate the 69 kV service feed. | MS | MS |  |  |  | 3090000 | 2020-12-01 | 2020-12-01 | 69 | 0 | Bottom-Up
B in MTEP17 | B | South | SMEPA | 12212 | 2016-09-15 |  | Oak Grove Delivery Point | In order to serve the Oak Grove delivery point economically and reliably, SMEPA’s Line 91 (Okahola GOAB – Oak Grove) will be rebuilt with 795 ACSR conductor and extended 0.5 miles to the proposed Oak Grove 161/69kV substation. A new 69/26.4kV, 15/20/25 MVA transformer will be installed at the Oak Grove substation to accommodate the 69kV service. | MS | MS |  |  |  | 2323000 | 2021-12-01 | 2021-12-01 | 69 | 0 | Bottom-Up
B in MTEP17 | B | South | SMEPA | 12222 | 2016-09-15 |  | Maxie Delivery Point | In order to serve the Maxie delivery point economically and reliably from SMEPA’s transmission, a short 161kV looped service feed consisting of 795 ACSR conductor will connect the Maxie substation with SMEPA Lines 37 and 38. A 161kV breaker and a dual voltage high side 69-161/26.4kV, 15/20/25 MVA transformer will complete the substation upgrades. | MS | MS |  |  |  | 1135000 | 2022-09-01 | 2022-09-01 | 69 | 0 | Bottom-Up
B in MTEP17 | B | South |  | 13023 | 2017-03-30 |  | Pocahontas Ind New Load | A new prospective 50MW, 21.3MVAR load is being added to the Pocahontas Industrial Park bus. | [8 empty] | 0 | 0 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9723 | 2015-12-14 |  | Fishhook Breaker Station | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV line. | IL | IL |  |  |  |  | 2018-12-31 | 2018-12-31 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9734 | 2017-12-19 |  | North Utica Substation | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | IL | IL |  |  |  |  | 2022-12-01 | 2022-12-01 | 138 | 34.5 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9738 | 2016-09-16 |  | Grand Tower-Carbondale Reconductoring | Reconductor to 1200 A summer emergency capability | IL | IL |  |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9739 | 2016-09-16 |  | Carbondale, Northwest-West Frankfort Reconductoring | Reconductor 3.18 miles conductor in the Carbondale-Reeds section with conductor capable of carrying 1200 A under summer emergency conditions. | IL | IL |  |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9740 | 2016-09-16 |  | Grand Tower-Campbell Hill Reconductoring | Reconductor to 1200 A summer emergency capability | IL | IL |  |  |  |  | 2025-06-01 | 2025-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9743 | 2015-09-11 |  | Pana, North-Route 51D Reconductoring | Reconductor to 2000 A summer emergency capability | IL | IL |  |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9832 | 2015-09-14 |  | Casey-Kansas Reconductoring | Reconductor to 3000 A summer emergency capability | IL | IL |  |  |  |  | 2027-06-01 | 2027-06-01 | 345 | 345 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9838 | 2017-09-15 |  | Kincaid Terminal Upgrade | Upgrade terminal equipment on Kincaid-Austin 345 kV position. | IL | IL |  |  |  |  | 2020-06-01 | 2020-06-01 | 345 | 345 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9840 | 2015-09-14 |  | Washington Street Ring Bus | Install 138 kV Ring Bus | IL | IL |  |  |  |  | 2020-05-01 | 2020-05-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenIL | 9844 | 2017-03-10 |  | Hershey-McLean 138 kV Line | Construct 138 kV line | IL | IL |  |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9717 | 2016-05-23 |  | Moberly Terminal Upgrade | Upgrade terminal equipment on Thomas Hill-Moberly-1 161 kV line position. | MO | MO |  |  |  |  | 2040-06-01 | 2040-06-01 | 161 | 161 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9721 | 2015-10-14 | AMRN46 | Bland-Tegeler 138 kV Reconductoring | Reconductor line to 1200 A summer emergency capability | MO | MO |  |  |  |  | 2020-06-01 | 2020-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9730 | 2016-02-29 |  | Gray Summit Breaker Replacement | Replace overstressed 138 kV breakers. | MO | MO |  |  |  |  | 2019-12-01 | 2019-12-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9732 | 2016-05-20 |  | Mason Breaker Replacment | Replace overstressed Bus-Tie 1-2 138 kV breaker. | MO | MO |  |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9733 | 2016-05-23 | AMRN47 | Page Breaker Replacment | Replace overstressed 138 kV breakers | MO | MO |  |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9735 | 2016-05-23 | AMRN48 | Tyson Breaker Replacement | Replace overstressed 138 kV breakers | MO | MO |  |  |  |  | 2021-12-01 | 2021-12-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9825 | 2015-09-14 |  | Osage Terminal Upgrade | Upgrade terminal equipment on Tegeler-Osage-1 position. | MO | MO |  |  |  |  | 2021-06-01 | 2021-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | Central | AmerenMO | 9830 | 2016-05-23 |  | Meramec-Joachim-2 Reconductoring | Reconductor to 1600 A summer emergency capability | MO | MO |  |  |  |  | 2022-06-01 | 2022-06-01 | 138 | 138 | Bottom-Up
B in MTEP16 | B | West | ATC | 9925 | 2018-03-26 | MTEP ID 10183 | Tap Stone Lake - Gardner Park 345-kV line | Loop Stone Lake - Gardner Park 345-kV line into new Pershing 345-kV Substation. | WI | WI | BaseRel |  |  | 15000000 | 2018-06-01 | 2018-06-01 | 345 | 0 | Bottom-Up
B in MTEP16 | B | West | ATC | 10590 | 2018-03-26 | PR06462, F4830 | Rebuild Academy - Columbus 69kV | Rebuild Academy - Columbus (Y-21) 69kV | WI | WI |  |  |  | 3000000 | 2023-12-31 | 2023-12-31 | 69 | 0 | Bottom-Up
B in MTEP16 | B | West | ATC, XEL | 10183 | 2016-08-18 |  | Pershing 345 kV Substation | New 345/115 kV substation located near Sheldon Pump on the Stone Lake to Gardner Park 345 kV line. This is a joint Xcel Energy/ATC project with ATC owning the 345 kV yard at Pershing and Xcel Energy owning the rest of the substation. | WI | WI | BaseRel |  |  | 14500000 | 2018-06-01 | 2018-06-01 | 345 | 115 | Bottom-Up
B in MTEP16 | B | East | CETO | 9879 | 2015-09-14 |  | Moore Road-Vrooman 138 kV Line | Construct a new approximately 22 mile 138 kV line between Moore Road and Vrooman Substations, adding 138 kV circuit breakers to each station. | MI | MI |  |  |  | 22000000 | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
B in MTEP16 | B | South | Entergy-LA | 9764 | 2015-09-13 | 16-EGL-005 | Dixie Baker to Baker 69 kV: Reconductor Line | Upgrade the Dixie Baker to Baker 69 kV line section. This includes a reconductor and upgrading substation equipment. | LA | LA |  |  |  | 3200000 | 2026-06-01 | 2026-06-01 | 69 | 0 | Bottom-Up
B in MTEP16 | B | South | Entergy-TX | 9821 | 2018-09-04 | 16-ETI-020 | Bryan to College Station Area 138 kV: Construct New Line | Build a new 138 kV line from the Bryan substation to a new substation in the College Station Area. | TX | TX |  |  |  | 31500000 | 2024-06-01 | 2024-06-01 | 138 | 0 | Bottom-Up
B in MTEP16 | B | South | ETEC | 10081 | 2015-09-18 | SHECO_01_MTEP16 | Fred 138kV Loop Project | Construct new Fred switching station on Dogwood-Warren 138 kV line, construct new 138kV Fred substation, construct new 138 kV line from Fred switching station to new Fred substation, construct new 138kV line from Fred substation to North Buna substation. | TX | TX | [6 empty] | 138 | 0 | Bottom-Up
B in MTEP16 | B | South | ETEC | 10082 | 2015-09-18 | SHECO_02_MTEP16 | Fred 138kV Loop Project Alt_01 | Construct new 138kV Fred substation, construct new 138kV line from Fred substation to the existing North Buna substation, construct new 138kV line from Fred substation to the existing Fork Creek substation | TX | TX | [6 empty] | 138 | 0 | Bottom-Up
B in MTEP16 | B | South | ETEC, Entergy-TX | 10080 | 2016-05-12 | HCEC_01_MTEP16 | Weldon 138kV Tie Line | Construct 138 kV line from existing Mustang Prairie station in AEP-Texas to a new Weldon station to existing Magnolia Groveton station in Entergy-Texas. | TX | TX | Other |  | Load Growth |  |  |  | 138 | 0 | Bottom-Up
B in MTEP16 | B | Central | IPL | 10786 | 2016-02-18 |  | Stout BESS - DPP J401 | New ±20 MVA battery energy storage system at existing Stout substation | IN | IN |  |  |  | 4000 | 2017-12-31 | 2017-12-31 | 138 | 13.8 | Bottom-Up
B in MTEP16 | B | West | ITCM | 9100 | 2015-05-28 | Burlington Area 69kV | Burlington Terminal & 4th St-Agency 69kV | Upgrade the Burlington 69kV terminal so the Burlington-South Burlington line is conductor limited. Rebuild the Burlington 4th Street-Agency 69kV line to T2-477 (140MVA). | IA | IA |  |  |  |  | 2019-12-19 | 2019-12-31 | 69 | 0 | Bottom-Up
B in MTEP16 | B | East | ITCT | 9885 | 2016-09-30 | ITC_15_017 | Jewell - St. Clair #1 345 kV Sag Remediation | Raise the Sag Limit on Jewell-St.Clair 345 kV to 1965 MVA (3288 Amp) | MI | MI | BaseRel |  |  | 5380000 | 2019-12-31 | 2019-12-31 | 345 | 0 | Bottom-Up
B in MTEP16 | B | West | MDU | 9122 | 2015-06-10 |  | East Bismarck-Expressway 115 Upgrade | Replace switches and line jumpers at East Bismarck Jct. on the 115 kV line to Expressway Sub. | ND | ND |  |  |  | 125000 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
B in MTEP16 | B | West | MDU | 9140 | 2015-06-12 |  | Coyote-NACO Sub 115 Upgrade | Reconductor Coyote Jct-NACO sub 115 kV line with 477 ACSS | ND | ND |  |  |  | 1270000 | 2020-09-01 | 2020-09-01 | 115 | 0 | Bottom-Up
B in MTEP16 | B | West | MDU | 9180 | 2015-06-16 |  | Green River Capacitors | Increase Green River Jct. 15 Mvar capacitors to 20 Mvar | ND | ND |  |  |  | 400000 | 2020-10-01 | 2020-10-01 | 115 | 0 | Bottom-Up
B in MTEP16 | B | East | METC | 9880 | 2016-09-30 | METC_15_025 | Claremont - Manning #1 138 kV Sag Remediation | Remediate the sag limit on the Portsmouth Tap – Manning 138 kV section of the Claremont – Manning 1 138 kV line to a minimum of 378 MVA / 1581 Amps, remediate the sag limit on the Claremont – Portsmouth Tap 138 kV section of the Claremont – Manning 1 138 kV line to a minimum of 362 MVA / 1514 Amps, and upgrade terminal equipment at Claremont | MI | MI | BaseRel |  |  | 330000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
B in MTEP16 | B | East | METC | 9929 | 2016-09-30 | METC_15_29 | Donaldson Creek - Pere Marquette 138 kV | Build new ~21 mile circuit from Donaldson Creek to Pere Marquette using 954 ACSR and OPGW. Replace equipment at Donaldson Creek, Pere Marquette, and White Lake Stations | MI | MI | BaseRel |  |  | 8700000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
B in MTEP16 | B | West | MP | 9643 | 2015-09-11 | Little Falls Tie Breaker | Little Falls 115 kV Tie Breaker Addition | Add a tie breaker in the Little Falls 115 kV bus. Bus 1 to consist of 163 Line (Little Falls - CWP Little Falls), 46 Line (Little Falls - Mud Lake), and 1TR (115/34 kV). Bus 2 to consist of 868 Line (Little Falls - West St Cloud), 49 Line (Little Falls - Blanchard), 10K Cap Bank, and 2TR (115/34 kV). Line-connected transformer 2TR will need to be reconfigured to connect to Bus 2. | MN | MN |  |  |  | 1000000 | 2017-06-01 | 2017-06-01 | 115 | 0 | Bottom-Up
B in MTEP16 | B | West | OTP | 9997 | 2018-08-21 |  | Rolette 230/69/41.6 kV Substation | Tap Xcel's 230 kV line between Rugby and Glenboro and install 230/69/41.6 kV Transformer - Install three 230 kV Breakers, one 69 kV Breaker, one 41.6 kV Breaker and install one 230/69/41.6 kV Transformer (60 MVA). Construct 12 miles of 41.6 kV line and 6 miles of 69 kV line. | ND | ND | Other |  | Reliability | 9000000 | 2021-12-31 | 2021-12-31 | 230 | 41.6 | Bottom-Up
B in MTEP16 | B | West | OTP | 10001 | 2018-08-21 |  | Voltaire 115/41.6 kV Substation | Build a new 115/41.6 kV substation in the Voltaire area. Install one 56 MVA Transformer 115/41.6 kV. Install four 41.6 kV Breakers. | ND | ND | Other |  | Reliability | 5000000 | 2021-12-31 | 2021-12-31 | 115 | 41.6 | Bottom-Up
B in MTEP16 | B | West | OTP | 10043 | 2015-09-17 |  | Jamestown 345 Breaker Addition | Install an additional 345 kV breaker to meet TPL-001-4 Compliance Standard. | ND | ND |  |  |  | 2000000 | 2020-12-31 | 2020-12-31 | 345 | 0 | Bottom-Up
B in MTEP16 | B | West | OTP | 10903 | 2018-08-21 |  | Rugby 115 kV Breaker/Line Addition | Rugby 115 kV Breaker/Line Addition - Install a new 115 kV Breaker and 2 miles of line to Rugby-Harvey line. | ND | ND | Other |  | Reliability | 1500000 | 2021-12-31 | 2021-12-31 | 115 | 0 | Bottom-Up
B in MTEP16 | B | Central | PPI | 9563 | 2017-06-02 | 2016-13 | Cronus 138 kV Transmission Lines | Construct two new 138 kV transmission lines from Ameren Illinois's West Tuscola substation to serve new Cronus Fertilizer Plant | IL | IL | Other |  | Reliability | 3600000 | 2017-12-01 | 2017-12-01 | 138 | 0 | Bottom-Up
B in MTEP16 | B | Central | Vectren | 9943 | 2016-05-18 | 2016SIGE14 | Leonard Road 138/69 kV Transformer Addition and Z94 138 kV Line Loop | Leonard Road 138kV/69kV transformer addition and 138kV line Z94 loop. | IN | IN |  |  |  | 3100000 | 2023-12-31 | 2023-12-31 | 138 | 69 | Bottom-Up
B in MTEP16 | B | East | WPSC | 10264 | 2015-10-28 | Pellston to Cross Village | Pellston to Cross Village Rebuild | Rebuild the Pellston to Cross Village 69kV line, install new poles and hardware with 336ACSR conductor | MI | MI |  |  |  | 3600000 | 2022-12-31 | 2022-12-31 | 138 | 0 | Bottom-Up
B in MTEP16 | B | East | WPSC | 10265 | 2015-10-28 |  | Gaylord Relay Replacement | Gaylord relay replacement - 138kV Livingston line | MI | MI |  |  |  | 35000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
B in MTEP16 | B | West |  | 10102 | 2016-04-13 |  | Owatonna Area Project | Construct a 33 mile 161 kV line from Freeborn/Hayward to West Owatonna. | [8 empty] | 0 | 0 | Bottom-Up
B in MTEP15 | B | Central | AmerenIL | 3010 | 2015-03-19 | AMRN13 | Baldwin-Grand Tower-N.W. Cape (Heritage) 345 kV Line | New 69 mile, single-circuit line (possible double circuit), 3000 A SE capability (Baldwin-Grand Tower - 45 miles; Grand Tower-N.W. Cape - 24 miles). Grand Tower 345/138 kV Substation - 1-560 MVA transformer, 345 kV Ring bus | IL | IL | Other |  | Reliability | 5000000 | 2030-06-01 | 2030-06-01 | 345 | 138 | Bottom-Up
B in MTEP15 | B | Central | AmerenIL | 7802 | 2015-11-24 |  | West Frankfort, East-West-Frankfort-1 138 kV Reconductoring | Reconductor 5.25 miles of 1272 kcmil ACSR conductor with conductor capable of carrying 1600 A under summer emergency conditions. Replace bus conductor at West Frankfort, East with conductor having capability equal to or greater than the new line conductor. | IL | IL | BaseRel |  |  |  | 2026-06-01 | 2026-06-01 | 138 | 0 | Bottom-Up
B in MTEP15 | B | Central | AmerenIL | 7821 | 2016-06-02 |  | Kickapoo Capacitor Bank Addition | Install --2-7.2 Mvar, 34.5 kV capacitor banks and PCBs. | IL | IL | BaseRel |  |  |  | 2020-06-01 | 2020-06-01 | 34.5 | 0 | Bottom-Up
B in MTEP15 | B | Central | AmerenIL | 7861 | 2015-03-19 |  | Effingham Northwest Breaker Additions | Install 2-138 kV, 2000 A, 40 kA PCBs, one on each 138 kV line position. Upgrade bus conductor to 2000 A continuous capability. | IL | IL | Other |  | Reliability |  | 2019-06-01 | 2019-06-01 | 138 | 0 | Bottom-Up
B in MTEP15 | B | Central | AmerenMO | 7862 | 2014-12-05 |  | Buick Smelter Substation Relocation | Relocate substation. Remove existing substation, install 2 motor-operated 161 kV switches and 2 customer owned and installed 161 kV circuit switchers. Make provisions for the addition of a third 161-4 kV transformer. | MO | MO | Other |  | Age and Condition |  | 2020-12-01 | 2020-12-01 | 161 | 4 | Bottom-Up
B in MTEP15 | B | West | ATC | 8082 | 2018-04-24 | PR07197, F5291 | Highway V – Preble 138 kV, rebuild | Highway V - Preble 138 kV line reconductor | WI | WI |  |  |  | 6000000 | 2020-12-01 | 2020-12-01 | 138 | 0 | Bottom-Up
B in MTEP15 | B | Central | BREC | 3440 | 2014-09-16 | LRP6 | Reid EHV 161/69 kV transformer | Add a 56 MVA transformer to the existing Reid EHV substation. | KY | KY | BaseRel | Not Shared |  | 5000000 | 2024-12-31 | 2024-12-31 | 161 | 69 | Bottom-Up
B in MTEP15 | B | South | CLECO | 7993 | 2015-04-01 |  | Rodemacher to East Leesville(reconductor) | Reconductor Rodemacher to East Leesville 230 kv line. | LA | LA | BaseRel |  |  | 10000000 | 2024-05-01 | 2024-05-01 | 230 | 0 | Bottom-Up
B in MTEP15 | B | South | Entergy-TX | 4799 | 2017-09-13 | 13-ETI-021 | Dishman: Construct new substation | Construct new 230kV substation on the Amelia to Helbig 230kV line | TX | TX | Other |  | Load Growth | 10500000 | 2023-05-01 | 2023-05-01 | 230 | 0 | Bottom-Up
B in MTEP15 | B | West | GRE | 2632 | 2014-12-19 | 20385 | Onigum 115 kV Conversion | Onigum 115 kV Conversion | MN | MN | Other | Not Shared | Load Growth | 5300000 | 2022-11-30 | 2022-11-30 | 115 | 0 | Bottom-Up
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | Mortar Creek (formerly Hull Road) Station | Build Mortar Creek 345 kV station and reconfigure the Bayshore to Monroe 345 kV, Lemoyne to Majestic 345 kV, and Morocco to Milan to Monroe 345 kV lines into it in a breaker-and-a-half scheme configuration. | MI | MI | Other |  | Reliability | 23950000 | 2020-12-31 | 2020-12-31 | 345 | 0 | Bottom-Up
B in MTEP15 | B | West | ITCM | 8842 | 2015-03-19 | Quad-Rock Ck 345 | Quad Cities-Rock Creek 345kV Dbl Ckt | Rebuild the Quad Cities to Rock Creek 345kV line to double circuit and add 345kV terminals at both substations. | IA,IL | IA,IL | BaseRel |  |  |  | 2024-12-31 | 2024-12-31 | 345 | 0 | Bottom-Up
B in MTEP15 | B | West | ITCM | 8843 | 2015-03-19 | Rock Creek 2nd 345/161kV | Rock Creek 2nd 345/161kV Transformer | Add a 2nd 345/161kV 450MVA transformer at the Rock Creek substation. | IA | IA | BaseRel |  |  |  | 2024-12-31 | 2024-12-31 | 345 | 161 | Bottom-Up
B in MTEP15 | B | West | ITCM | 8844 | 2015-03-19 | Albany-Galena 161kV Rebuild | Albany-Galena 161kV Rebuild | Rebuild the Albany-York-Savanna-Galena 161kV line. | IL | IL | BaseRel |  |  |  | 2024-12-31 | 2024-12-31 | 161 | 0 | Bottom-Up
B in MTEP15 | B | East | ITCT | 3943 | 2014-12-02 |  | Navarre 230/120 kV Transformer #201 | Increase the CT ratio on the low-side breaker of the Navarre 230/120 kV Transformer #201. | MI | MI |  |  |  |  | 2018-12-31 | 2018-12-31 | 230 | 120 | Bottom-Up
B in MTEP15 | B | East | ITCT | 8068 | 2015-04-22 | ITC_13_061 | Brownstown - Monroe #2 345 kV Sag Remediation | Remediate the sag limit on the Brownstown to Monroe #2 345 kV line | MI | MI | Other |  | Reliability | 1200000 | 2017-12-31 | 2017-12-31 | 345 | 0 | Bottom-Up
B in MTEP15 | B | East | ITCT | 8069 | 2015-04-22 | ITC_13_056 | Lemoyne - Majestic 345 kV Sag Remediation | Remediate the sag limit on the Lemoyne - Majestic 345 kV line to increase its summer emergency rating to a minimum rating of 1822 MVA / 3049 Amps. | MI | MI | Other |  | Reliability | 2500000 | 2018-12-31 | 2018-12-31 | 345 | 0 | Bottom-Up
B in MTEP15 | B | East | ITCT | 8099 | 2015-04-22 | ITC_14_014 | Lincoln to Northeast/Northwest 120 kV Rebuild | Rebuild about 2.95 miles of 477 ACSR on the Lincoln section of the Lincoln/Northeast/Northwest circuit to 1431 ACSR on new 120 kV double circuit towers. The other side of these towers supports a portion of the Lincoln to Northeast 120 kV circuit which will also be upgraded to 1431 ACSR. Upgrades or replacement of any limiting equipment at Lincoln, Hilton Road (formerly Ferndale), and Northeast substations will also be necessary. | MI | MI | Other |  | Reliability | 4200000 | 2018-12-31 | 2018-12-31 | 120 | 0 | Bottom-Up
B in MTEP15 | B | West | MEC | 8023 | 2015-04-09 |  | Hills - Sub E 161 kV Reconductor | Reconductor the Hills - Sub E 161 kV line in Iowa City to increase the line rating. | IA | IA | BaseRel |  |  | 4000000 |  |  | 161 | 0 | Bottom-Up
B in MTEP15 | B | West | MEC | 8114 | 2015-04-09 |  | Sub A - Sub 84 69 kV Line Uprate | Replace structures to allow a higher conductor operating temperature. | IA | IA | Other |  | Reliability | 225000 | 2018-06-01 | 2018-06-01 | 69 | 0 | Bottom-Up
B in MTEP15 | B | East | METC | 1804 | 2014-12-02 |  | Marquette - Easton Jct. 138kV | Replace limiting equipment at the Marquette 138 kV station | MI | MI |  |  |  |  | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
B in MTEP15 | B | East | METC | 3927 | 2015-07-22 | METC_14_026 | Saginaw River 138 kV Station Equipment Replacement | Replace limiting equipment from the Saginaw River 138 kV station. | MI | MI | Other |  | Reliability | 2800000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
B in MTEP15 | B | East | METC | 4525 | 2017-05-22 | METC_14_015 | Goss 345/138 kV Transformer #2 | Install a second 345/138 kV transformer and install/upgrade station equipment at Goss. | MI | MI | Other |  | Reliability | 9300000 | 2021-12-31 | 2021-12-31 | 345 | 138 | Bottom-Up
B in MTEP15 | B | East | METC | 8123 | 2015-04-22 | METC_14_028 | Weeds Lake Transformer #2 and Looping in Argenta to Twin Branch 345 kV | Install a second 345/138 kV transformer at the Weeds Lake Substation and loop in the Argenta to Twin Branch 345 kV line. This creates a Weeds Lake - Twin Branch 345 kV line and a 2nd Argenta - Weeds Lake 345 kV circuit | MI | MI | Other |  | Reliability | 17500000 | 2018-12-31 | 2018-12-31 | 345 | 138 | Bottom-Up
B in MTEP15 | B | East | METC | 8130 | 2016-11-10 | METC_13_049 | Pere Marquette to Keystone 230 kV | Construct a new 75 mile, 230 kV circuit between Keystone and Pere Marquette Substation. Approx. 20 miles of the new line will be on new double circuit steel pole structures, 30 miles from rebuiding existing 138 kV structures to 230 kV double circuit steel poles, and 25 miles on existing DCTs with a vacant side of the structures. Install a 345/230 kV transformer and associated terminal equipment at Pere Marquette substation. Add a 230/138 kV transformer and associated terminal equipment at Keystone substation. Project will also swap the line positions of the Keystone-Wexford 138 kV and the 138 kV side of the Keystone 345/138 kV transformer at Keystone substation. | MI | MI | BaseRel |  |  | 90198000 | 2020-12-31 | 2020-12-31 | 345 | 138 | Bottom-Up
B in MTEP15 | B | East | NIPS | 8026 | 2014-12-01 |  | Dekalb Transformer | Upgrade Dekalb 138/69kV Transformer. This will also increase ratings of the Dekalb to Auburn 138kV Line | IN | IN |  |  |  | 2700000 | 2017-12-31 | 2017-12-31 | 138 | 69 | Bottom-Up
B in MTEP15 | B | West | OTP | 8085 | 2016-09-14 |  | Kerkhoven Town Conversion to 115 kV Service - 115/12.5 kV | Build a new, approximately, one mile 115 kV line from the GRE Kerkhoven 115/41.6 kV sub to the new OTP Kerkhoven Town substation. Also convert the Kerkhoven town delivery substation from 41.6 kV to 115 kV through the installation of a new 10 MVA 115/12.5 kV transformer. This project will consist of two facilities: 1. New 115/12.5 kV Substation at Kerkhoven Town with a new (1) 115 kV breaker and a new 10 MVA 115/12.5 kV transformer. 2. Approxmetely 1 mile of115 kV transmission line from the GRE Kerkhoven 115 kV Substation to the New Kerkhoven Town 115/12.5 kV substation. The total estimated cost of this project is $ 1.7 million. The expected in service date for this project is November 15, 2020. | MN | MN | Other |  | Reliability | 1700000 | 2020-11-15 | 2020-11-15 | 115 | 12.5 | Bottom-Up
B in MTEP15 | B | Central | PPI | 7888 | 2017-09-22 | 2015-19,20,41 | New Sub 39 to Ladwig 69 kV line | Project Modified from original submittal and moved to Appendix B. Tyson substation is no longer part of this project. 69 kV terminal addition at MidAmerican Sub 39. Construct new 11 mile 69 kV line from MidAmerican Sub 39 to PPI/Jo-Carroll Energy Ladwig Substation. Construct 0.2 mile 69 kV line from the City of Geneseo plant to Jo-Carroll Energy Geneseo Substation. | IL | IL | Other |  | Reliability | 289300 | 2016-12-31 | 2016-12-31 | 69 | 69 | Bottom-Up
B in MTEP15 | B | South | SMEPA | 8141 | 2015-04-03 |  | Rebuild L16 (Hoy - Sharon GOAB) 69kV Line | Rebuild the existing Hoy - Sharon GOAB 69kV line using 161kV double circuit specifications and 795 ACSR conductor. | MS | MS | BaseRel |  |  | 1273600 | 2026-06-01 | 2026-06-01 | 69 | 0 | Bottom-Up
B in MTEP15 | B | South | SMEPA | 8143 | 2015-04-03 |  | Rebuild L45A (Foxworth - Pickwick GOAB) 69kV Line | Rebuild the existing Foxworth - Pickwick GOAB 69kV line using 161kV specifications and 795 ACSR conductor. | MS | MS | BaseRel |  |  | 2050300 | 2026-06-01 | 2026-06-01 | 69 | 0 | Bottom-Up
B in MTEP15 | B | Central | Vectren | 4397 | 2014-10-06 | 2013SIGE11 | Y31 Leonard Rd. - Z93 Rebuild | Rebuild approx. 6.8 miles of 69 kV | IN | IN |  |  |  | 5100000 | 2020-12-31 | 2020-12-31 | 69 | 0 | Bottom-Up
B in MTEP15 | B | Central | Vectren | 4399 | 2016-05-19 | 2013SIGE13 | Newtonville 161 kV ring bus conversion | Convert existing 161 kV bus to a ring bus configuration | IN | IN |  |  |  | 1000000 | 2023-12-31 | 2023-12-31 | 161 | 0 | Bottom-Up
B in MTEP15 | B | East | WPSC | 8360 | 2015-03-30 | Alba New Station | Alba New Station | The Alba transmission tie station represents the oldest tie on the Wolverine system. It is located on a small parcel of leased property with limited expansion capability. The existing station shall be replaced with a new in/out transmission line design, three (3) breaker substation, modern control house, metering, protection relaying and a 50 or 90MVA, 138/69kV tie transformer, dependent upon load requirements. | MI | MI | Other |  | Age and Condition | 4000000 | 2022-12-31 | 2022-12-31 | 138 | 69 | Bottom-Up
B in MTEP15 | B | East | WPSC | 8361 | 2015-03-30 | Alba Line Mods | Alba Line Mods | This project will address 138kV transmission line and structure reconfiguration costs associated with construction of the new Alba transmission substation, so that the 138kV ITC/METC looped transmission line segments can successfully enter and leave the substation | MI | MI | Other |  | Other Local Needs | 1000000 | 2022-12-31 | 2022-12-31 | 138 | 69 | Bottom-Up
B in MTEP14 | B | Central | AmerenMO | 4498 | 2014-12-17 | AMRN45 | Berntie-Jim Hill 161 kV Line | Construct approximately 20 miles of 161 kV line between Jim Hill Plant and Berntie Substation in southeast, Missouri. The new line should have a 2000 A summer emergency rating. Construct 161 kV ring bus at Berntie Substation. Install 161 kV breaker at Jim Hill. | MO | MO |  |  |  | 30500000 | 2020-06-01 | 2020-06-01 | 161 | 0 | Bottom-Up
B in MTEP14 | B | West | ATC, MP | 3832 | 2015-05-07 | Iron Range - Arrowhead 345 kV | Iron Range - Arrowhead 345 kV Line | Blackberry-Arrowhead 345kV double circuit | MN | MN |  |  |  | 220481656.22 | 2025-12-31 | 2025-12-31 | 500 | 345 | Bottom-Up
B in MTEP14 | B | West | GRE | 4376 | 2016-06-30 | 202496 | Parkwood-Crooked Lake 115 kV Reconductor | Reconductor the existing conductor to 795 ACSS | MN | MN |  |  |  | 500000 | 2020-04-29 | 2020-04-29 | 115 | 0 | Bottom-Up
B in MTEP14 | B | West | MDU | 3082 | 2017-01-16 | NW Bism | NW Bismarck Ring Bus | Install 115kV ring bus at the NW Bismarck substation | ND | ND | TBD |  |  | 3050000 | 2020-06-01 | 2020-06-01 | 115 | 0 | Bottom-Up
B in MTEP14 | B | East | METC | 1795 | 2016-12-20 | METC_13_037 | David Jct. - Bingham 138kV | Rebuild approximately 19 miles of 336.4 ACSR utilizing 954 ACSR on new 138 kV future double circuit structures. | MI | MI | BaseRel | Not Shared |  | 19000000 | 2023-12-31 | 2023-12-31 | 138 | 0 | Bottom-Up
B in MTEP14 | B | East | METC | 3922 | 2016-11-10 | METC_13_039 | Alpine J - Rogue River J - Cannon J 138kV Rebuild | Rebuild 8.4 miles of 336 ACSR utilizing 954 ACSR on new 138 kV structures. | MI | MI | BaseRel | Not Shared |  | 8200000 | 2023-12-31 | 2023-12-31 | 138 | 0 | Bottom-Up
B in MTEP14 | B | East | METC | 4510 | 2014-12-17 | METC_13_044 | Morrow - Battle Creek 138kV #1 Rebuild | Rebuild approximately 22 miles of Morrow to Battle Creek 138kV #1 to 954 ACSR. Upgrade station equipment at Morrow. | MI | MI | BaseRel | Not Shared |  | 24640000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
B in MTEP14 | B | East | METC | 4511 | 2016-07-05 | METC_13_046 | Verona-Foundry 138 kV Rebuild | Rebuild approximately 21 miles of Verona to Foundry 138kV to 1431 ACSR. Upgrade station equipment at Verona. | MI | MI | BaseRel | Not Shared |  | 16021000 | 2019-12-31 | 2019-12-31 | 138 | 0 | Bottom-Up
B in MTEP14 | B | West | MP | 2548 | 2014-12-17 | Duluth 230 kV Project | Duluth 230 kV Project | Add a second 230/115 kV transformer and upgrade an existing line to 230 kV | MN | MN |  |  |  | 6000000 | 2026-12-31 | 2026-12-31 | 230 | 115 | Bottom-Up
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | HVDC 750 MW Upgrade | Upgrade existing HVDC line & terminal from Square Butte-Arrowhead to 750MW | ND,MN | MN |  |  |  | 200000000 | 2020-12-31 | 2020-12-31 | 250 | 230 | Bottom-Up
B in MTEP14 | B | South | SMEPA | 4439 | 2015-04-03 | LRTPS11-RP2102 | Plant Morrow to Purvis Bulk 161kV Line | Tap existing Purvis to Lumberton 161kV line. Construct a 161kV switching station with 3 breakers at Tap Point (new). Construct a 3 mile 161kV line from the Tap point to Morrow (new). Uprate existing line section from Purvis to Tap Point to Lumberton to 296 MVA. Add 161kV breaker at Morrow (new) | MS | MS | Other |  | Reliability | 3498200 | 2021-06-01 | 2021-06-01 | 161 | 0 | Bottom-Up
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | Lumberton-Wiggins-Benndale 161kV Conversion | Rebuild line 35A, 37A, 37B and 37C @ 161kV insulation (new). Add 161kV breaker at Lumberton and Benndale 161kV stations (new). Construct a new Stillmore and Big Level switching station with 3 breakers (new). Construct a 8 mile line to Stillmore (new). Convert Stillmore and Big Level distribution stations to 161kV | MS | MS | BaseRel |  |  | 15755800 | 2021-06-01 | 2021-06-01 | 161 | 0 | Bottom-Up
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | State Line 161kV Source Project | Tap existing Waynesboro to Hintonville 161kV line. Construct a 161kV switching station with 3 breakers at Tap Point (new). Construct a 161kV switch yard at State Line with breakers (new). Construct a 19 mile 161kV line from Tap point to State Line 161kV station (new). Add a 161/69kV 100MVA transformer at State Line (new). Add 69kV bay and breaker at State Line 69kV station (new). | MS | MS | BaseRel |  |  | 14250000 | 2026-06-01 | 2026-06-01 | 161 | 69 | Bottom-Up
B in MTEP13 | B | Central | AmerenIL | 4071 | 2014-11-17 | AMRN31 | Wood River-Stallings 138 kV Line Upgrade | Wood River-Stallings 138 kV Line 1456 - Increase clearances to ground on 5.63 miles of 477 kcmil ACSR between Cottage Hills and Wanda to permit operation at 120 degrees C. Reconductor 6.01 miles of 477 kcmil ACSR in the Stallings-Wanda section with conductor capable of carrying 1600 A under summer emergency conditions. Replace or reconnect 600 A CTs and replace an 800 A PCB at Cottage Hills with equipment capable of carrying 1200 A continuously. | IL | IL | BaseRel | Not Shared |  | 11004000 | 2025-06-01 | 2025-06-01 | 138 | 0 | Bottom-Up
B in MTEP13 | B | West | GRE | 4012 | 2016-06-30 | 20326 | Hardy Lake Substation (CWP) 115 kV | GRE will build new Crow Wing Power 115 KV Hardy Lake Substation | MN | MN | Other | Not Shared | Load Growth | 207500 | 2020-12-31 | 2020-12-31 | 115 | 0 | Bottom-Up
B in MTEP13 | B | West | GRE | 4013 | 2012-09-11 | 20334 | Air Lake (DEA) 115 kV Substation | GRE will build new Dakota Electric 115 kv South Air Lake substation. | MN | MN | Other | Not Shared | Load Growth | 864000 | 2026-05-02 | 2026-05-02 | 115 | 0 | Bottom-Up
B in MTEP13 | B | West | GRE | 4016 | 2016-06-30 | 20507 | Cashel 115 kV conversion | GRE will convert Agralite Cashel 41.6 kV distribution sub to 115 kV | MN | MN | Other | Not Shared | Load Growth | 625000 | 2022-05-31 | 2022-05-31 | 115 | 0 | Bottom-Up
B in MTEP13 | B | West | MEC | 4252 | 2012-09-15 | G4083 | Neal North:161 kV Breaker Replacements | Replace 161 kV oil circuit breaker 9680 at the Neal North Substation | IA | IA | BaseRel | Not Shared |  | 325000 | 2015-06-30 | 2015-06-30 | 161 | 0 | Bottom-Up
B in MTEP13 | B | East | METC | 4346 | 2015-11-13 |  | Karn-Garfield 138kV Rebuild | Rebuild the 33.5 mile copper portion of the Karn to Garfield circuit using single circuit 138kV structures and 954 ACSR conductor. Mitigate several additional points of interest on the remaining portions (795 and 1431 ACSR). Replace station equipment at | MI | MI |  |  |  | 39500000 | 2018-12-31 | 2018-12-31 | 138 | 0 | Bottom-Up
B in MTEP13 | B | West | MP | 3756 | 2015-05-07 | Wrenshall | Wrenshall | Add Transformer and breakers at Wrenshall | MN | MN | TBD |  |  | 3000000 | 2020-12-31 | 2020-12-31 | 115 | 69 | Bottom-Up
B in MTEP13 | B | West | MP | 4295 | 2015-06-10 | HVDC Valve Hall Replacement | HVDC Valve Hall Replacement | Modernization of HVDC terminals at Arrowhead & Square Butte | ND | MN | Other | Not Shared | Age and Condition | 75000000 | 2020-12-31 | 2020-12-31 | 250 | 0 | Bottom-Up
B in MTEP12 | B | Central | AmerenIL | 2290 | 2015-09-11 |  | Joppa 345 kV Switching Station 2nd. Xfmr | Add 2nd. 345/161 kV, 560 MVA Transformer | IL | IL | Other | Not Shared | Reliability |  | 2023-06-01 | 2023-06-01 | 345 | 161 | Bottom-Up
B in MTEP12 | B | Central | AmerenIL | 3336 | 2012-03-06 |  | Gilman-Watseka Reconductoring | Reconductor to 1600 A summer emergency capability | IL | IL | BaseRel |  |  | 4763000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP12 | B | Central | AmerenIL | 3342 | 2017-09-15 |  | Diamond Star-McClean County Sw. Station - Increase Ground Clearance | Increase ground clearance on 2.4 miles of 477 kcmil ACSR conductor | IL | IL | BaseRel |  |  | 240000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP12 | B | Central | AmerenIL | 3703 | 2016-08-15 |  | New Berlin 138-69 kV Sub | New Berlin 138-69 kV Substation - Install new 112 MVA, 138-69 kV Substation. Connect to Auburn, North-Jacksonville Industrial 138 kV Line 1306. | IL | IL | Other |  | Load Growth |  | 2022-12-01 | 2022-12-01 | 138 | 69 | Bottom-Up
B in MTEP12 | B | Central | AmerenMO | 3701 | 2012-03-06 | AMRN25 | Cotter Creek 138-34.5 kV Substation Supplies | Cotter Creek 138-34.5 kV Substation - Provide 138 kV supplies to new Cotter Creek Substation. This will consist of installing a 2000 A, 138 kV PCB at Joachim Substation, and extending new 138 kV line from Joachim to Cotter Creek Substation. Also, for the second 138 kV supply to Cotter Creek, a new 3-2000 A breaker 138 kV switching station (Olympian Village) will be established in the Joachim-St. Francois-2 138 kV line, with a 138 kV line extended from Olympian Village Switching Station to Cotter Creek Substation. | MO | MO | Other |  | Load Growth | 31230640 | 2023-06-01 | 2023-06-01 | 138 | 0 | Bottom-Up
B in MTEP12 | B | Central | AmerenMO | 3708 | 2017-12-19 |  | Fountain Lake 2nd. Transformer | Install 2nd. 138-12.5 kV Transformer | MO | MO | Other |  | Load Growth |  | 2030-06-01 | 2030-06-01 | 138 | 12.5 | Bottom-Up
B in MTEP12 | B | East | ITC, ITCT | 1295 | 2014-01-31 |  | Quaker to Southfield #2 120 kV | Rebuild the existing Quaker to Drexel to Southfield circuit utilizing 1431 ACSR conductor on double circuit 230 kV towers and add a second Quaker to Southfield circuit on this new tower line | MI | MI | BaseRel | Shared |  | 51050000 | 2018-06-01 | 2018-06-01 | 120 | 0 | Bottom-Up
B in MTEP12 | B | East | ITC, ITCT | 3589 | 2014-01-31 |  | Lee - Menlo 120 kV Rebuild | Rebuild approximately 5.4 miles of 267 ACSR conductor to 954 ACSR between Lee and the Lake Huron Pumping Tap and approximately 6.4 miles of 267 ACSR conductor to 954 ACSR between Menlo and the Lake Huron Pumping Tap and replace station equipment Lee and M | MI | MI | BaseRel | Shared |  | 11200000 | 2018-06-01 | 2018-06-01 | 120 | 0 | Bottom-Up
B in MTEP12 | B | East | METC | 3137 | 2014-01-31 |  | Warren - Bard Road 138 kV Rebuild | Rebuild approximately 19.6 miles of the Warren to Bard Road 138 kV circuit to 230 kV double circuit construction using 954 ACSR. One side would be energized at 138kV, with the other side left vacant for future use. Also replace terminal equipment at Bard Road. | MI | MI | BaseRel | Shared |  | 27800000 | 2017-12-31 | 2017-12-31 | 138 | 0 | Bottom-Up
B in MTEP12 | B | East | METC | 3582 | 2014-01-31 |  | Bullock - Summerton 138 kV Rebuild | Rebuild the entire circuit between Bullock and Summerton to 954 ACSR on single-circuit, 138 kV steel pole structures and replace the terminal equipment at Bullock | MI | MI | BaseRel | Shared |  | 20000000 | 2017-06-01 | 2017-06-01 | 138 | 0 | Bottom-Up
B in MTEP12 | B | East | METC | 3594 | 2014-11-04 |  | Tittabawassee 345 kV Station Equipment Upgrades | Replace 345kV station equipment in rows 34 and 36 at Tittabawassee. | MI | MI | BaseRel | Not Shared |  | 3500000 | 2018-12-31 | 2018-12-31 | 345 | 0 | Bottom-Up
B in MTEP11 | B | Central | AmerenMO | 2973 | 2014-11-17 |  | Howard Bend Substation Connection | Howard Bend 138-12 kV Substation - Provide 138 kV ring bus connection from Mason-Carrollton-8 138 kV line to new Howard Bend Substation. Install 1-138 kV, 2000 A PCB at Carrollton Substation as a bus-tie. | MO | MO | Other | Not Shared | Load Growth | 1371000 | 2022-12-01 | 2022-12-01 | 138 | 0 | Bottom-Up
B in MTEP11 | B | West | MEC | 3215 | 2016-09-14 | T6242 | Sub 49 161 kV Capacitor | Add 50 MVAr 161 kV capacitor | IL | IL | BaseRel | Not Shared |  | 840000 | 2030-06-01 | 2030-06-01 | 161 | 0 | Bottom-Up
B in MTEP11 | B | West | MEC | 3266 | 2013-09-15 | T6164 | Sub 56-89 161 Line Uprate | Increase 161 kV line rating. | IA | IA | BaseRel | TBD |  | 680000 | 2024-06-01 | 2024-06-01 | 161 | 0 | Bottom-Up
B in MTEP11 | B | East | METC | 1815 | 2014-01-31 |  | Chase - Mecosta 138kV Rebuild | Rebuild 7.2 miles of 138kV 110 and 115 CU to 954 ACSR. Prebuild to 230kV construction. | MI | MI | BaseRel | Shared |  | 8900000 | 2020-06-01 | 2020-06-01 | 138 | 0 | Bottom-Up
B in MTEP10 | B | East | ITC, ITCT | 1856 | 2014-01-31 |  | Belle River - Greenwood - Pontiac 345kV cut into Jewell | Cut the Pontiac section of the Belle River-Greenwood-Pontiac 345kV circuit into and out of Jewell station. Utilize an existing unused side of 345kV tower for one of the circuits into Jewell, and relocate the Jewell-Spokane 230kV circuit | MI | MI | BaseRel | Shared |  | 5200000 | 2030-12-31 | 2030-12-31 | 345 | 0 | Bottom-Up
B in MTEP10 | B | East | ITC, ITCT | 2932 | 2015-03-25 |  | St Antoine-Essex #2 120 kV | Construct 2nd underground cable from St Antoine to Essex (5.1 miles). | MI | MI | BaseRel | Shared |  | 54800000 | 2020-06-01 | 2020-06-01 | 120 | 0 | Bottom-Up
B in MTEP10 | B | West | ITCM | 1746 | 2011-12-13 |  | Lakefield-Adams 161 kV Rebuild | Rebuild Lakefield-Fox Lake-Rutland-Winnebago-Hayward-Adams 161 kV line to double circuit 345 & 161 kV. Allow for a 345 kV line position for future use. | MN | MN | BaseRel |  |  | 97580000 | 2014-12-31 | 2018-12-31 | 161 | 0 | Bottom-Up
B in MTEP10 | B | East | METC | 3210 | 2014-01-31 |  | Vanderbilt - Riggsville 138 kV Rebuild | Rebuild 30.3 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. | MI | MI |  |  |  | 33254000 | 2016-06-01 | 2016-06-01 | 138 | 0 | Bottom-Up
A in MTEP18 | B | South | AXLA | 14524 | 2018-08-20 |  | Downtown - Willow Glen 138 kV Reconductor | Replace 4.8 miles of conductor from Willow Glen to Downtown substations | LA | LA | Other |  | Age and Condition | 2500000 | 2020-02-01 | 2020-02-01 | 138 | 0 | Bottom-Up
Note on O3: Estimated costs do not reflect facilties that are in service or withdrawn prior to MTEP17.

## Fac Legend
MTEP Database Export
Facility Table Field Legend
Project table has blue highlighted header. A project may have multiple facilties.
Facility table has beige highlighted header. A project's facilities may have different in service dates.
Facilty Table Field Legend
Field | Description
Target Appendix | Target appendix for the MTEPyy planning cycle. Example: "A in MTEP15" projects were reviewed in MTEP15.
App AB | Appendix the project is in. B>A for projects moving during this planning cycle.
Region | MISO Planning Region: Central, East, West or South
Geographic Location by TO Member System | Project geographic location by Transmission Owner member systems
PrjID | Indicates the Facility's Project. Projects may have multiple facilities.
Facility ID | Facility ID: MISO facility identifier
Expected ISD | Expected In Service Date for this facility
From Sub | From substation for transmission line or location of transformer or other equipment
To Sub | To substation for transmission line or transformer designation
Ckt | Circuit identifier
Max kV | Maximum voltage of this facility
Min kV | Minumum voltage of this facility (transformer low-side voltage)
Facility Rating | Rating of the facility in applicable units. Typically Summer rate
Facility Description | Brief description of transmission facility
State | State the facility is located in
Miles Upg. | Transmission line miles on existing rights of way (ROW)
Miles New | Transmission line miles on new rights of way (ROW)
Plan Status | Indicates status of project in planning or implementation. Conceptual, Proposed, Planned, Last Milestone Achieved, Under Construction and In Service
Estimated Cost | Total estimated facility cost
Cost Shared | Y if facility is cost shared per Attachment FF
Postage Stamp | Y if facility has postage stamp cost allocation per Attachment FF
MISO Facility | Y for facilities under MISO functional control. NT for non-transferred facilities under Agency Agreements

## MTEP18_AppAB_Facilities
MTEP18 MISO Transmission Expansion Plan 2018 | [26 empty] | Appendices A, B
Appendices A, B: Project Facility Table 12/07/2018
Target Appendix | App ABC | Planning Region | Geographic Location by TO Member System | PrjID | Prj Rec Date | Owner PrjID | Facility ID | Record Date | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Facility Rating | Description | State | Miles Upgrade | Miles New | Plan Status | Estimated Cost | Estimate Type | Gen Int Upgrade Type | TSR Cond Upg | Cost Shared | Postage Stamp | MISO Facility
A in MTEP18 | A | South | AECC | 10203 | 2018-08-22 |  | 21489 | 2018-08-22 | SwSta | 2023-06-01 | AECC Vimy Ridge |  |  | 115 |  |  | 4 position ring bus | AR |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | AECC | 10203 | 2018-08-22 |  | 21490 | 2018-08-22 | LN | 2023-12-01 | AECC Shaw | Proposed AECC Vimy Ridge SS |  | 115 |  |  | 15 mile 115kV transmission line | AR |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | AECC | 13993 | 2018-08-06 |  | 23103 | 2017-10-09 | SwSta | 2020-12-31 | Dry Creek |  |  | 161 |  |  | 161 kV switching station on the Entergy Harrison East to Osage Creek 161 kV transmission line. | AR |  |  | Planned | 4000000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | South | AECC | 13993 | 2018-08-06 |  | 23105 | 2018-08-22 | SUB | 2023-02-01 | Smyrna |  |  | 161 |  |  | 161/69 kV substation to constructed on the south end of the existing Osage Creek 69 kV system. | AR |  |  | Planned | 4000000 | Planning |  | N | N | N
A in MTEP18 | A | South | AECC | 13993 | 2018-08-06 |  | 23104 | 2018-08-22 | SUB | 2021-06-01 | Long Creek |  |  | 161 |  |  | 161/69 kV substation to constructed on the north end of the existing Osage Creek 69 kV system. | MO |  |  | Planned | 4000000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | South | AECC | 14384 | 2018-08-22 |  | 23318 | 2018-08-22 | Dist | 2020-04-01 | Brazil Road |  |  | 115 |  |  | 115/13.2kV 20MVA distribution substation | AR |  |  | Planned | 3000000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | South | AECC | 14444 | 2018-08-22 |  | 23324 | 2018-08-22 | LNcnv | 2023-12-01 | Zion Hill | Mountain Springs | 1 | 115 |  |  | Convert from 69kV to 115kV | AR | 6.5 |  | Planned | 4900000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | South | AECC | 14445 | 2018-08-22 |  | 23325 | 2018-08-22 | LNcnv | 2023-12-01 | Mountain Springs | Ward |  | 115 |  |  | Convert Mountain Springs to Ward 69kV line to 115kV | AR | 4.6 |  | Planned | 3450000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | South | AECC | 14446 | 2018-08-22 |  | 23326 | 2018-08-22 | Dist | 2023-06-01 | Sardis South |  |  | 115 |  |  | 115/13.2kV 20MVA substation | AR |  |  | Planned | 2500000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 3033 | 2018-10-03 | AMRN18 | 5247 | 2017-11-15 | SUB | 2022-12-01 | Beehive | New 345/138 kV Substation | 1 | 345 | 138 | 560 | Beehive 345/138 kV Substation - 2-700 MVA Transformer, 345 kV ring bus, 138kV BAAH. | IL |  |  | Proposed | 0 | Planning |  | N | N | N | Y
A in MTEP18 | A | Central | AmerenIL | 3033 | 2018-10-03 | AMRN18 | 5249 | 2017-11-15 | LN | 2022-12-01 | Cahokia | Meramec | 1 & 2 | 138 |  | 411 | New in/out 138 kV outlet from Cahokia-Meramec 1&2 to the new Beehive Substation. Re-conductor/Rebuild the Mississippi river crossing and Beehive – Watson – 1351 138 kV line and Beehive – Mackenzie section of Beehive – Lakeshire – 1468 138 kV line with conductor having a minimum summer emergency capability of 2000 Amps. | IL |  | 0.5 | Proposed | 0 | Planning |  | N | N | N | Y
A in MTEP18 | A | Central | AmerenIL | 3033 | 2018-10-03 | AMRN18 | 5248 | 2017-11-15 | LN | 2022-12-01 | Cahokia | Baldwin | 4511 | 345 |  | 1793 | Install in/out 345 kV supply from C-BLWN-4511 line into new Beehive substation. | IL |  | 8 | Proposed | 0 | Planning |  | N | N | N | Y
A in MTEP18 | A | Central | AmerenIL | 4068 | 2017-12-13 |  | 7715 | 2018-09-27 | LN | 2018-12-01 | South Bloomington | Clinton Route 54 | 1 | 138 |  | 141 | Increase clearances to ground on 17 miles of 336 kcmil ACSR conductor between South Bloomington Substation and the L1372 Tap to permit operation at 120 degrees C., and reconductor 5.41 miles of 336 kcmil ACSR conductor between North Decatur and County Hwy | IL | 22.4 |  | Planned | 28800000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | Central | AmerenIL | 4069 | 2017-12-04 |  | 7716 | 2018-09-27 | SUB | 2020-12-01 | Stallings Sub | Install Breaker-and-a-half arrangement |  | 138 |  |  | Re-configure the existing Stallings Substation to accommodate an initial 7-position Breaker-and-a-half arrangement with an ultimate of 10 positions. | IL |  |  | Planned | 18600000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | Central | AmerenIL | 11954 | 2017-10-27 |  | 21915 | 2018-09-28 | SUB | 2018-05-11 | Tabor |  |  | 138 |  | 478 | Establish 138 kV ring bus | IL |  |  | M5_In Service | 8100000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13544 | 2017-08-28 |  | 22638 | 2018-09-28 | SwSta | 2021-12-01 | Tibbs | 138 kV Breaker Station |  | 138 |  |  | Install initial 3-position (ultimate 4-position) ring bus at the Sparta Tap location in the Prest-Steeleville-1476 138 kV line | IL |  |  | Planned | 7300000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13546 | 2018-10-03 |  | 22640 | 2018-09-28 | SUB | 2020-12-01 | County Highway 20 | 138 kV ring bus |  | 138 |  |  | Install new 3-position (ultimate 4-position) ring bus at the existing County Highway 20 substation location. | IL |  |  | Planned | 8900000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13548 | 2018-10-03 |  | 22642 | 2018-09-28 | SwSta | 2020-12-01 | McLean County | 138 kV ring bus |  | 138 |  |  | Re-configure the existing McLean County 138 kV Switching Station to accommodate a 3-position (ultimate 4-position) ring bus. | IL |  |  | Planned | 10000000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13549 | 2017-09-06 |  | 22643 | 2018-09-28 | LNrc | 2017-12-07 | West Frankfort | Ina |  | 138 |  |  | Rebuild the Benton NW-Ina-1 and Benton NW-West Frankfort-1 138 kV lines using conductor capable of carrying 2000A under summer emergency conditions. Install OPGW. | IL |  |  | M5_In Service | 14000000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13550 | 2017-08-28 |  | 22644 | 2018-09-28 | CAP | 2018-12-01 | ADM North | 138 kV cap bank |  | 138 |  |  | Upgrade the existing 50 Mvar, 138 kV capacitor bank in the ADM North Substation to a 120 Mvar capacitor bank. Remove the existing 14.4 Mvar and 18.0 Mvar capacitor banks at the Faries Parkway Substation on the 34.5 kV bus. | IL |  |  | Planned | 600000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13551 | 2018-08-24 |  | 22645 | 2018-09-28 | SwSta | 2022-12-01 | Shockey | 138 kV breaker station |  | 138 |  |  | Construct a 5-position (ultimate 6-position) 138 kV switching station at structure 380 of the San Jose Rail-Interstate-1318 138 kV line to tie the Havana-East Springfield-1422 and San Jose Rail-Interstate-1318 138 kV lines together. | IL |  |  | Planned | 13100000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13564 | 2018-08-24 |  | 22647 | 2018-09-28 | SwSta | 2023-06-01 | Docket | 138 kV braker Station |  | 138 |  |  | Construct a 3-position (ultimate 4-position) ring bus breaker station near structure 423 on the N. Decatur-Latham-1342 138 kV line. | IL |  |  | Planned | 7200000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13565 | 2018-01-08 |  | 22648 | 2018-09-28 | TX | 2018-12-01 | Mount Vernon West |  |  | 345 | 138 |  | Replace existing 450 MVA 345-138 kV transformer with 560 MVA unit. | IL |  |  | Planned | 4300000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13566 | 2017-09-14 |  | 22649 | 2018-09-28 | LNrc | 2018-05-05 | Ina | Mt. Vernon 42nd Street | 1322 | 138 |  |  | Rebuild the INA-MTVS-1322 138 kV line from Ina to Mt. Vernon 42nd Street using conductor capable of 2000A under summer emergency conditions. Install OPGW. | IL |  |  | M5_In Service | 8800000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13567 | 2017-08-30 |  | 22650 | 2018-09-28 | LNup | 2017-12-12 | Elkhart Switching Station | Turris Coal Tap |  | 138 |  |  | Upgrade the clearance from 93°C to 120°C on the 138 kV HAV-SPFL-1422A line from Elkhart Switching Station to Turris Coal Tap. | IL |  |  | M5_In Service | 1900000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13569 | 2018-10-03 |  | 22652 | 2018-09-28 | SUB | 2021-12-01 | Roodhouse West | 138 kV ring bus substation |  | 138 |  |  | Re-configure the existing Roodhouse West Substation to accommodate an initial 3-position ring bus with an ultimate of 6 positions. | IL |  |  | Planned | 7800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13570 | 2018-01-08 |  | 22653 | 2018-09-28 | LNrc | 2019-10-01 | Cahokia | Baldwin | 4511 | 345 |  |  | In Cahokia-Baldwin 345 kV line 4511, reconductor 0.83 miles of 1113 kcmil ACSR/T2 Finch conductor from structures 148 to 153 with conductor capable of carrying 3000 A under summer emergency conditions. | IL |  |  | Planned | 1100000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13571 | 2018-10-03 |  | 22654 | 2018-09-27 | SwSta | 2019-12-01 | South Clinton | 138 kV ring bus substation |  | 138 |  |  | Construct a 138 kV, 6-position Ring Bus at the current site of the South Clinton Tap utilizing bus conductors of at least 3000 Amps continuous capability. Install 4 new breakers, and associated switches of at least 3000 Amps continuous capability. Install 3 motorized line disconnect switches of at least 2000 Amps continuous capability. Install 1 circuit switcher for high-side transformer protection of at least 2000 Amps continuous capability and 40k Amps fault interrupting capability. | IL |  |  | Planned | 6700000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13585 | 2018-10-03 |  | 22692 | 2018-09-27 | SwSta | 2023-12-01 | Gillett | 138 kV breaker station |  | 138 |  |  | Install new 3-position (ultimate 4-position) ring bus at tap to Turris Coal. | IL |  |  | Planned | 8100000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13619 | 2018-10-03 |  | 22709 | 2018-09-27 | SwSta | 2019-10-01 | Ruby | 345 kV Breaker Station |  | 345 |  |  | Construct a 3-position initial (6-position ultimate), 3000 A 345 kV switching station in a ring bus configuration at structure 100 in the Kansas-Sidney 345 kV line 4560 for the interconnection of Broadlands Wind Farm. | IL |  |  | Planned | 7533136 | Budgetary |  | N | Y | Y
A in MTEP18 | A | Central | AmerenIL | 13619 | 2018-10-03 |  | 24209 | 2018-09-27 | INT | 2019-10-01 | Ruby |  |  | 345 |  |  | TOIFs for J468 | IL |  |  | Planned | 892305 | Budgetary |  | N | N | N | Y
A in MTEP18 | A | Central | AmerenIL | 13664 | 2017-09-06 |  | 22741 | 2018-09-27 | LNrc | 2017-12-05 | Pana North | Moweaqua | 1462 | 138 |  |  | In Pana – Route 51 Decatur 138 kV line 1462, rebuild the backbone (Pana North to the Moweaqua tap), from 1272 kcmil ACSR to conductor capable of carrying 2000 A under summer emergency conditions. | IL |  |  | M5_In Service | 7800000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13665 | 2017-09-12 |  | 22742 | 2018-09-27 | CAP | 2019-11-15 | Tazewell | 120 Mvar cap bank |  | 138 |  |  | Install 120 Mvar Cap Bank at Tazewell Substation | IL |  |  | Planned | 3800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13666 | 2018-10-03 |  | 22743 | 2018-09-27 | TX | 2019-06-01 | Sidney | 345-138 kV Transformer |  | 345 |  |  | Replace transformer #1 345-138 kV 560 MVA due to age and condition | IL |  |  | Planned | 4800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13668 | 2017-09-12 |  | 22745 | 2018-09-27 | LNrc | 2018-06-04 | Crab Orchard | Herrin East | 1 | 138 |  |  | Upgrade the section of Crab Orchard-Herrin East-1 going from Crab Orchard to Marion North from 100C MOT to 110C MOT. | IL |  |  | M5_In Service | 3200000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13669 | 2017-09-12 |  | 22746 | 2018-09-27 | LNrc | 2017-12-23 | West Frankfort East | West Frankfort | 1 | 138 |  |  | Replace 10 wood-pole H-Frame structures to raise conductor clearance from 100C-capable to 120C-capable. ( Line to be operated at 110 degrees C pending future project.) | IL |  |  | M5_In Service | 3300000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13670 | 2017-09-12 |  | 22747 | 2018-09-27 | LNrc | 2019-12-01 | Fargo | Pioneer | 1347 | 138 |  |  | Upgrade line to 100 degrees C and add OPGW. | IL |  |  | Planned | 3100000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13671 | 2017-09-12 |  | 22748 | 2018-09-27 | LNrc | 2018-11-11 | Muddy | Norris City North | 1 | 138 |  |  | Rebuild to 2000A capability | IL |  |  | Planned | 10800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13675 | 2017-09-12 |  | 22752 | 2018-09-27 | LNrc | 2018-05-25 | Moweaqua Tap | Blue Mound.Mount Auburn Tap | 1462 | 138 |  |  | Rebuild to 2000A. Replace 7 structures. | IL |  |  | M5_In Service | 5700000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13677 | 2017-09-12 |  | 22754 | 2018-09-27 | CAP | 2018-12-01 | Edwards | 120 Mvar Cap Bank |  | 138 |  |  | Install 120 Mvar cap bank | IL |  |  | Planned | 2200000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13691 | 2017-09-12 |  | 22765 | 2018-09-27 | CAP | 2019-06-01 | Albion South | Install Cap Bank |  | 138 |  |  | Install capacitor bank on 138 kV North Bus. | IL |  |  | Planned | 1000000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13695 | 2017-09-14 |  | 22769 | 2018-09-27 | LNrc | 2019-06-01 | Brokaw | Mahomet | 1376 | 138 |  |  | Rebuild to 1800A (795 ACSR T2). Upgrade the Mahomet bus-tie to 2000A. Rebuild the 1.55 mile Mahomet-Mahomet Tap section of RISN-NCMP-1592 with conductor capable of a minimum of 1200A. | IL |  |  | Planned | 18800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13696 | 2017-09-14 |  | 22770 | 2018-09-27 | SUB | 2020-12-01 | Jerseyville Northwest | 138 kV ring bus |  | 138 |  |  | Construct initial 4-position (ultimate 6-position) Ring bus. | IL |  |  | Planned | 8000000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13710 | 2018-10-03 |  | 22778 | 2018-09-27 | DVAR | 2019-06-01 | Stallings | Install 138 kV FACTS Device |  | 138 |  |  | Install +250/-100 Mvar FACTS device | IL |  |  | Planned | 28900000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 13794 | 2017-09-29 |  | 22856 | 2018-09-27 | LNup | 2018-06-15 | Hennepin | Woodhall | 1512 | 138 |  |  | Rebuild 636 ACSR Rook to 795 ACSR T2 capability. | IL |  |  | M5_In Service | 13400000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 14061 | 2017-12-19 |  | 23193 | 2018-09-27 | LNrc | 2019-12-01 | Towerline | Tazewell |  | 138 |  |  | Rebuild 6.19 miles 477 ACSR to 2000A. | IL |  |  | Planned | 8800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 15225 | 2018-08-08 |  | 23492 | 2018-09-27 | LNrc | 2018-12-01 | Lawrenceville South | Olney North | 1 | 138 |  |  | Rebuild line to 2000A capability | IL |  |  | Planned | 11600000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 15226 | 2018-08-08 |  | 23493 | 2018-09-27 | LNrb | 2018-12-31 | Jerseyville NW | Roodhouse West |  | 138 |  |  | Rebuild 28.3 miles of the Jerseyville NW – Roodhouse West portion of the Jerseyville NW – Ballard 1561 line. | IL | 28.3 |  | Planned | 21700000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenIL | 16227 | 2018-10-05 |  | 24244 | 2018-10-05 | TEQ | 2021-06-01 | Marblehead |  |  | 161 | 138 |  | Disconnect Switch and Bus Conductor |  | IL |  | Planned | 175000 |  |  | N | Y | N | Y
A in MTEP18 | A | Central | AmerenMO | 9828 | 2017-10-13 | AMRN50 | 21202 | 2017-09-15 | LNup | 2018-06-01 | Joachim | St. Francois | 2 | 138 | 138 | 210 | Increase ground clearance | MO | 18.79 |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 9828 | 2017-10-13 | AMRN50 | 21203 | 2017-09-15 | LNup | 2018-06-01 | Boyd Branch | St. Francois | 1 | 138 | 138 | 212 | Increase ground clearance | MO | 7.07 |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 13547 | 2018-10-03 |  | 22641 | 2018-09-28 | LNrb | 2018-06-08 | Lutesville | St. Francois | 1 | 345 |  |  | Replace 55 structures in the Letesvillde-St. Francois-1 345 kV line to achieve a conductor MOT of 120 degrees C | MO |  |  | M5_In Service | 9600000 | Actual |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 13568 | 2018-10-03 |  | 22651 | 2018-09-28 | LNup | 2018-10-01 | Eldon | Overton |  | 161 |  |  | Replace structures on portions of 53.5 miles of 161kV line to provide ground clearance for a future maximum conductor operating temperature of 120 degrees C. Replace bus conductor at California substation with a minimum rating of 1200 amps. | MO |  |  | Proposed | 4800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 13672 | 2018-03-20 |  | 22749 | 2018-09-27 | SUB | 2018-12-01 | Lakeshire Substation |  |  | 138 |  |  | Install 2 new breakers and replace position G breaker in order to accommodate an in/out of MER-WAT-2 into Lakeshire Substation | MO |  |  | Planned | 1800000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 13672 | 2018-03-20 |  | 23283 | 2018-09-27 | LNrb | 2018-12-01 | Cahokia | Meramec | 1-2 | 138 |  |  | Cahokia-Meramec-1&2 line work | MO |  |  | Planned | 1400000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 13673 | 2017-09-12 |  | 22750 | 2018-09-27 | LNrc | 2018-12-01 | Bland | Osage | 6030 | 138 |  |  | Upgrade conductor to 120 degrees MOT. Install OPGW. | MO |  |  | Planned | 21950000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | AmerenMO | 13676 | 2017-09-12 |  | 22753 | 2018-09-27 | LNrb | 2018-07-17 | Overton | Sedalia | 1 | 161 |  |  | Upgrade line to 120 degrees C MOT - Replace 22 wood pole H-frame structures. Install 2 mid-span structures. | MO |  |  | M5_In Service | 2000000 | Actual |  | N | N | N
A in MTEP18 | A | West | ATC | 4726 | 2018-08-13 | PR04983, F3600, F3601 | 8955 | 2018-08-13 | LNrb | 2025-12-31 | Hillman | Dalington | 1 | 138 |  |  | Transmission Line Work - Hillman to Falcon | WI | 18.73 |  | Proposed | 20480000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 7584 | 2018-08-13 | PR04986, F3632 | 20018 | 2018-08-13 | LNrb | 2025-12-31 | New Holstein | Custer | 1 | 69 |  |  | Rebuild P-68 | WI | 21.55 |  | Proposed | 27000000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 7763 | 2018-08-13 | PR06467, F4847, F5141 | 20079 | 2018-08-13 | LNrb | 2025-12-31 | McKenna | Castle Rock | 1 | 69 |  | 69 | Rebuild Y-47 | WI | 8.52 |  | Proposed | 12050000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 7764 | 2018-08-13 | PR06465, F4475 | 20081 | 2018-08-13 | LNrb | 2023-12-31 | Wautoma | WC5 (ACEC Richford) | 1 | 69 |  | 79 | Rebuild Y-49 Wautoma - ACEC Richford | WI | 8.25 |  | Proposed | 14500000 | Engineering |  | N | N | N
A in MTEP18 | A | West | ATC | 7764 | 2018-08-13 | PR06465, F4475 | 20082 | 2018-08-13 | LNrb | 2023-12-31 | WC5 (ACEC Richford) | Chaffee Creek | 1 | 69 |  | 64 | Rebuild Y-49 ACEC Richford - Chaffee Creek | WI | 4.78 |  | Proposed |  | Engineering |  | N | N | N
A in MTEP18 | A | West | ATC | 7765 | 2018-08-13 | PR06467, F4847, F5141, | 20083 | 2018-08-13 | LNrb | 2025-12-31 | Lincoln Pumping Station | McKenna | 1 | 69 |  | 69 | Rebuild Y-145 | WI | 12.06 |  | Proposed | 9000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 8444 | 2018-08-13 | PR07820, PR07950, F5348 | 20672 | 2018-08-22 | LNrb | 2020-12-31 | First Ave | Sawyer | 1 | 69 | 69 | 360 | Replace UG Cable from 1st Ave-Sawyer 69 kV line | WI | 0.3 | 0.4 | Proposed | 11200000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 8444 | 2018-08-13 | PR07820, PR07950, F5348 | 23425 | 2018-08-13 | LNrb | 2020-12-31 | Sawyer Sw St | First Ave SS | 1 | 69 | 69 | 360 | awyer Sw St - First Avenue SS 69kV (T-46), overhead transmission clearance resolution | WI | 0.1 | 0.1 | Proposed | 100000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 10486 | 2018-08-13 | PR06461, F4829 | 21594 | 2018-08-13 | LNrb | 2023-12-31 | Chafee Creek | ACEC Colma Tap | 1 | 69 |  | 526 | Rebuild line Y-18 Chaffee Creek - Lincoln Pump Station. | WI |  |  | Proposed | 9600000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 10486 | 2018-08-13 | PR06461, F4829 | 21595 | 2018-08-13 | LNrb | 2023-12-31 | ACEC Coloma Tap | Lincoln Pump Station | 1 | 69 |  | 526 | Rebuild Chaffee Creek - Lincoln Pump Station 69 kV. | WI |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | West | ATC | 12134 | 2018-08-13 | PR06458, F4445 | 22254 | 2018-08-13 | LNrb | 2023-12-31 | Finger Rd SW Station | Wesmark |  | 69 |  | 79 | Rebuild Finger Rd SW Station - Wesmark 69KV (FIRY11) | WI | 10.98 |  | Proposed | 14400000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 12135 | 2018-08-13 | PR04987, F3626 | 22256 | 2018-08-13 | LNrb | 2024-12-21 | Manrap | Wesmark |  | 69 |  | 79 | Rebuild Manrap - Wesmark 69KV (R-44) | WI | 19.8 |  | Proposed | 21500000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 12137 | 2018-08-13 | F3622 | 22260 | 2018-08-13 | LNrb | 2025-12-21 | Hwy V | Oak St |  | 69 |  | 42 | Rebuild Hwy V - Oak St 69KV (Z-26) | WI | 5.9 |  | Proposed | 9000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 12140 | 2018-08-13 | F3622 | 22262 | 2017-09-15 | LNrb | 2022-12-31 | Finger Rd | Hwy V |  | 69 |  | 79 | Rebuild Finger Rd - Hwy V 69 KV (U-47) | WI | 0.81 |  | Proposed | 1520000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 12141 | 2018-08-13 | PR0499, F3621,F3622 | 22265 | 2017-09-15 | LNrb | 2022-12-31 | Danz | Finger Rd |  | 69 |  | 60 | Rebuild Danz - Finger Rd 68KV (L64) | WI | 2.8 |  | Proposed | 4230000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 12147 | 2018-08-13 | PR06460, F4828 | 22273 | 2018-05-23 | LNrb | 2020-12-31 | Wild Rose | Harrison |  | 69 |  | 79 | Rebuild Wild Rose Pumping Station - Harrison 69kV (Y19) | WI | 26.36 |  | Proposed | 14400000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 13104 | 2018-08-17 | PR07720 | 22575 | 2018-01-31 | SUB | 2020-12-31 | TBD |  |  | 138 |  |  | 138 kV GIS Substation | WI |  |  | Proposed | 34600000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 13104 | 2018-08-17 | PR07720 | 22576 | 2018-01-31 | LNug | 2020-12-31 | Haymarket | Harbor |  | 138 |  | 282 | 138 kV Underground Lines. | WI | 1 | 1 | Proposed |  |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13243 | 2018-08-17 | PR07735 | 22598 | 2017-12-08 | CB | 2019-12-01 | Winneconne |  |  | 69 |  | 3000 | Replace 69KV Breakers Winneconne SS | WI |  |  | Proposed | 2150000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 13713 | 2018-08-17 | F5007 | 22781 | 2017-09-22 | TEQ | 2017-07-19 | Liberty St |  |  | 138 |  |  | Liberty St DIC - Jumpers-Insulators | WI |  |  | Proposed | 30777 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13715 | 2018-08-17 | F4996 | 22783 | 2017-09-22 | LN | 2017-09-30 | Westfield |  |  | 69 |  |  | Westfield DIC Install GOAB New Line | WI |  |  | Proposed | 428782 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13717 | 2018-08-17 | F5043 | 22785 | 2017-09-22 | CB | 2018-12-15 | Husikamp |  |  | 69 |  |  | Huiskamp SS Asset Renewal | WI |  |  | Proposed | 506490 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13718 | 2018-08-17 | F5239 | 22786 | 2018-01-31 | TEQ | 2018-02-25 | Hooterville |  |  | 69 |  |  | Hooterville SS DIC New Jumps Insul | WI |  |  | Proposed | 338663 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13719 | 2018-08-17 | F4982 | 22787 | 2017-09-22 | TEQ | 2017-11-01 | Cooney |  |  | 138 |  |  | Cooney DIC D-T Jumper Insulator Rep | WI |  |  | Proposed | 35096 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13720 | 2018-08-17 | F5237 | 22788 | 2017-09-22 | TAP | 2018-07-01 | Velp Ave |  |  | 138 |  |  | Velp-DIC | WI |  |  | Proposed | 225050 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13721 | 2018-08-17 | F5253 | 22790 | 2017-09-22 | BUS | 2018-07-01 | Sherman |  |  | 115 |  |  | Sherman St-DIC | WI |  |  | Proposed | 68962 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13722 | 2018-08-17 | F4970 | 22789 | 2017-09-22 | SUBmisc | 2018-12-31 | Eastom |  |  | 115 |  |  | Eastom SS-Equip Replmnts-Upgrades | WI |  |  | Proposed | 1033443 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13723 | 2018-08-17 | F5235 | 22791 | 2018-05-25 | TAP | 2017-09-08 | Perch Lake |  |  | 138 |  |  | Perch Lake-DIC | MI |  |  | Proposed | 85000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13724 | 2018-08-17 | F4722 | 22796 | 2017-09-22 | TX | 2017-08-05 | Walworth |  |  | 69 |  |  | Walworth T-D Xfmr Replacements | WI |  |  | Proposed | 33481 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13725 | 2018-08-17 | F4947 | 22792 | 2017-09-22 | TAP | 2017-04-18 | Three Lakes |  |  | 115 |  |  | Three Lakes SS-DIC | WI |  |  | Proposed | 603151 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13726 | 2018-08-17 | F5211 | 22793 | 2017-09-22 | TAP | 2019-06-30 | Plover |  |  | 115 |  |  | Plover-DIC | WI |  |  | Proposed | 1770286 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13727 | 2018-08-17 | F4942 | 22794 | 2017-09-22 | RLY | 2019-12-31 | Pulliam |  |  | 138 |  |  | Pulliam SS-Add Bus Differentials | WI |  |  | Proposed | 1873282 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13728 | 2018-08-17 | F5205 | 22795 | 2017-09-22 | TEQ | 2019-12-01 | Cloverleaf |  |  | 138 |  |  | Cloverleaf SS-Repl DeadEnd-Switches | WI |  |  | Proposed | 1062784 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13731 | 2018-08-17 | F5031 | 22800 | 2017-09-22 | SUBmisc | 2017-10-01 | Juneau |  |  | 69 |  |  | Juneau Northside SS - DIC | WI |  |  | Proposed | 137387 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13732 | 2018-08-13 | F5195 | 22799 | 2017-09-22 | LNrb | 2021-12-31 | Paris |  |  | 138 |  |  | 8962 Paris - Burlington Rebuild | WI |  |  | Proposed | 12560000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13733 | 2018-08-17 | F4650 | 22801 | 2017-09-22 | RLY | 2018-04-15 | N Monroe |  |  | 138 |  |  | N Monroe OCB and Relay Upg | WI |  |  | Proposed | 1623849 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13734 | 2018-08-17 | F5252 | 22804 | 2017-09-22 | SUBmisc | 2018-06-01 | Berryville |  |  | 138 |  |  | Berryville SS DIC | WI |  |  | Proposed | 528612 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13735 | 2018-08-13 | F5194 | 22802 | 2018-08-13 | LNrb | 2023-12-31 | St. Lawrence |  |  | 138 |  |  | 8032 St Lawrence-Barton Rebuild | WI |  |  | Proposed | 8400000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 13736 | 2018-08-17 | F4874 | 22803 | 2017-09-22 | TAP | 2018-06-01 | Hillman |  |  | 138 |  |  | Hillman DIC Transformer Add and Bus | WI |  |  | Proposed | 2324874 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13737 | 2018-08-17 | F4608 | 22805 | 2018-05-25 | RLY | 2017-12-01 | Victoria |  |  | 69 |  |  | Victoria SS-Equip Replmnt-RTU Upgrd | MI |  |  | Proposed | 1770698 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13738 | 2018-08-17 | F5246 | 22806 | 2018-08-22 | SUB | 2019-12-01 | Lincoln |  |  | 138 |  |  | Lincoln SS Breaker Renewals and Bus Reconfiguration | WI |  |  | Proposed | 4100000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13740 | 2018-08-17 | F4708 | 22808 | 2017-09-22 | CB | 2018-10-31 | Darlington |  |  | 138 |  |  | Darlington | WI |  |  | Proposed | 1882294 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13742 | 2018-08-17 | PR07733, F5245 | 22811 | 2017-09-22 | CB | 2019-12-01 | Waukesha |  |  | 138 |  |  | Waukesha SS Breaker Renewals | WI |  |  | Proposed | 836447 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13743 | 2018-08-13 | F5192 | 22810 | 2018-08-13 | LNrb | 2024-12-31 | Auburn |  |  | 138 |  |  | 9752 Barton-Auburn Rebuild | WI |  |  | Proposed | 7050000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 13746 | 2018-08-17 | F5244 | 22814 | 2017-09-22 | CB | 2018-07-31 | St Lawrence |  |  | 138 |  |  | St Lawrence SS Breaker Renewals | WI |  |  | Proposed | 219619 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13747 | 2018-08-17 | F5176 | 22815 | 2017-09-22 | RLY | 2019-04-12 | Wesmark |  |  | 69 |  |  | Wesmark SS-Repl RTU CPU-Brkrs-SW-R Replace: RTU/Breakers | WI |  |  | Proposed | 811572 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13749 | 2018-08-17 | F5170 | 22818 | 2017-09-22 | SUB | 2019-12-31 | West Towne |  |  | 69 |  |  | West Towne House and Asset Renewal | WI |  |  | Proposed | 3185723 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13754 | 2018-08-17 | F4388 | 22822 | 2017-09-22 | TAP | 2017-04-30 | Colley Road |  |  | 69 |  |  | Y32 Bio Enzyme 2nd GOAB DuPont DIC | WI |  |  | Proposed | 988101 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13755 | 2018-08-17 | F5165 | 22823 | 2018-05-25 | CB | 2019-12-01 | Osceola |  |  | 69 |  |  | Osceola SS - Repl 69kV Breaker | MI |  |  | Proposed | 348998 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13756 | 2018-08-17 | F5302 | 22824 | 2018-05-16 | SUB | 2020-12-01 | Edgewater |  |  | 345 |  |  | Edgewater 345kV Breaker replacement, Breaker retirement and Bus reconfiguration | WI |  |  | Proposed | 10400000 | Engineering Preliminary |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 13758 | 2018-08-17 | F5164 | 22826 | 2018-05-25 | CB | 2019-12-01 | Straits |  |  | 138 |  |  | Straits SS-Repl 3 Breakers-138kV | MI |  |  | Proposed | 1086498 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13760 | 2018-08-17 | F4338 | 22827 | 2017-09-22 | CB | 2017-10-31 | Lone Rock |  |  | 69 |  |  | Lone Rock SS Replace OCBs | WI |  |  | Proposed | 1939148 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13761 | 2018-08-17 | F4804 | 22829 | 2017-09-22 | TAP | 2018-06-01 | Okray |  |  | 115 |  |  | Okray DIC | WI |  |  | Proposed | 1812667 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13762 | 2018-08-17 | F5161 | 22830 | 2017-09-22 | CB | 2019-10-11 | Dyckesville |  |  | 138 |  |  | Dyckesville SS-Brkr-Switches-Relays | WI |  |  | Proposed | 599728 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13766 | 2018-08-17 | F4787 | 22834 | 2017-09-22 | TEQ | 2018-10-31 | Baraboo |  |  | 69 |  |  | Baraboo SS Reconductor Bus Jumpers | WI |  |  | Proposed | 1799436 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13768 | 2018-08-17 | F4767 | 22836 | 2018-05-23 | RLY | 2025-12-01 | Pflaum |  |  | 69 |  |  | Pflaum SS RTU Upgr & Asset Renewals | WI |  |  | Proposed | 2075688 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 13769 | 2018-08-23 | PR08006, F5132, F5135 | 22838 | 2018-05-16 | SUB | 2019-01-31 | Silver River |  |  | 138 |  |  | J704 GIC- Interconnection and Network Upgrades | MI |  |  | Proposed | 19700000 | Planning |  | N | Y | N | Y
A in MTEP18 | A | West | ATC | 13770 | 2018-08-13 | F4828 | 22837 | 2017-09-22 | LNrb | 2020-12-31 | Wautoma | Wild Rose |  | 69 |  |  | Partial Rebuild 69kV Y-180 Wautoma - Wild Rose. | WI |  |  | Proposed | 5500000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13773 | 2018-08-13 | PR04980, F3666 | 22841 | 2018-08-22 | LNrb | 2020-03-01 | Hiawatha | Pine River |  | 69 |  |  | 69kV ESE_6908 (Hiawatha - Pine River) Partial Rebuild | MI |  |  | Proposed | 7200000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13774 | 2018-08-17 | PR05842, F4131 | 22842 | 2017-09-22 | CB | 2019-12-31 | Hancock |  |  | 69 |  |  | Hancock DIC – Alliant and ACEC joint rebuild Hancock Substation, ATC add line breakers to sectionalize 69 kV line Y-90 (Chaffee Creek - Sand Lake), relocate cap banks, and add sync close breakers. | WI |  |  | Proposed | 4721140 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13784 | 2018-08-17 | PR08005, F5134 | 22844 | 2018-05-16 | SUB | 2019-01-23 | Huron SS |  |  | 138 | 138 |  | J703 GIC- Huron SS, Interconnection and Network Upgrades | MI |  |  | Proposed | 17100000 | Planning |  | N | Y | N | Y
A in MTEP18 | A | West | ATC | 13786 | 2018-08-17 | F4750 | 22846 | 2017-09-22 | TAP | 2017-07-13 | Richland Center |  |  | 69 |  |  | Richland Center DIC SS Transformer | WI |  |  | Proposed | 203040 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13787 | 2018-08-17 | F5124 | 22847 | 2017-09-22 | TAP | 2018-06-01 | Wittenberg |  |  | 69 |  |  | Wittenberg SS-DIC | WI |  |  | Proposed | 123085 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13788 | 2018-08-17 | F5284 | 22848 | 2018-05-25 | RLY | 2019-12-01 | Nine Mile |  |  | 115 |  |  | Nine Mile-MODs- Relay-CtrlHouse | MI |  |  | Proposed | 3443060 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13789 | 2018-08-17 | F4734 | 22849 | 2018-08-22 | RLY | 2019-12-01 | Kilbourn |  |  | 138 |  |  | Kilbourn SS Upgrade Relay | WI |  |  | Proposed | 6900000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13790 | 2018-08-17 | F5091 | 22850 | 2017-09-22 | TAP | 2018-10-01 | Oak St |  |  | 69 |  |  | Oak St-DIC | WI |  |  | Proposed | 879600 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13791 | 2018-08-17 | F5267 | 22853 | 2017-09-22 | CB | 2019-12-01 | New Holstein |  |  | 69 |  |  | New Holstein SS Install 69kV Brkr | WI |  |  | Proposed | 784901 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13792 | 2018-08-17 | PR04698, F3699 | 22854 | 2018-05-21 | SUB | 2022-06-01 | Keel Ridge |  |  | 69 | 69 |  | Keel Ridge D-T New SS | MI |  |  | Proposed | 2600000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 13802 | 2018-08-17 | PR07730, F5171 | 22864 | 2017-09-22 | CB | 2019-12-01 | Hillside |  |  | 69 |  |  | At Hillside Substation, replace 69kV breaker and replace line and bus disconnect switches. | WI |  |  | Proposed | 670000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13821 | 2018-08-17 |  | 22890 | 2018-08-22 | SUB | 2021-06-30 | NA |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal Current Cycle | WI,MI |  |  | Proposed | 38457451 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 13822 | 2018-08-17 |  | 22892 | 2018-08-22 | SUB | 2022-06-30 | NA |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal 2019 | WI,MI |  |  | Proposed | 8007814 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13823 | 2018-08-17 |  | 22893 | 2018-08-22 | COM | 2021-06-30 | NA |  |  | 345 | 69 |  | Communication Reliability Upgrades Current Cycle | WI,MI |  |  | Proposed | 34461836 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 13824 | 2018-08-17 |  | 22894 | 2018-08-22 | LNup | 2021-06-30 | NA |  |  | 345 | 69 |  | Line Clearance Mitigation Projects Current Cycle | WI,MI |  |  | Proposed | 18718669 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13825 | 2018-08-17 |  | 22895 | 2018-08-22 | LNup | 2022-06-30 | NA |  |  | 345 | 69 |  | Line Clearance Mitigation Projects 2019 | WI,MI |  |  | Proposed | 5832204 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 13826 | 2018-08-17 |  | 22896 | 2018-08-22 | SUB | 2021-06-30 | NA |  |  | 345 | 69 |  | Physical Security Current Cycle | WI,MI |  |  | Proposed | 67198396 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13828 | 2018-08-17 |  | 22897 | 2018-08-22 | SUB | 2022-06-30 | NA |  |  | 345 | 69 |  | Physical Security 2019 | WI,MI |  |  | Proposed | 3000000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 13829 | 2018-08-17 |  | 22899 | 2018-08-22 | COM | 2022-06-30 | NA |  |  | 345 | 69 |  | Communication Reliability Upgrades 2019 | WI,MI |  |  | Proposed | 1422500 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 13831 | 2018-08-17 | PR07800 | 22901 | 2018-03-30 | SUB | 2020-12-31 | Petenwell |  |  | 138 | 69 |  | Petenwell Substation | WI |  |  | Proposed |  | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 13831 | 2018-08-17 | PR07800 | 22903 | 2018-03-30 | LN | 2020-12-31 | Dellwood | Petenwell |  | 69 |  | 581 | Y-146 69 kV Line | WI |  |  | Proposed |  | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 13831 | 2018-08-17 | PR07800 | 22902 | 2018-03-30 | SUB | 2020-12-31 | Big Pond |  |  | 69 |  |  | Big Pond Substation | WI |  |  | Proposed | 454000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 13832 | 2018-05-24 | PR07779 | 22904 | 2017-09-08 | TEQ | 2022-01-01 | NA |  |  | 69 | 69 | 80 | Y-55: Re-rate Edgewater-Riverside 69 kV line | WI |  |  | Proposed | 80000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 13832 | 2018-05-24 | PR07779 | 22905 | 2017-12-08 | TEQ | 2022-01-01 | NA |  |  | 69 |  | 103 | Y-82: Re-rate Erdman-Riverside 69 kV line | WI |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | West | ATC | 14039 | 2018-08-13 | F5122 | 23180 | 2017-09-22 | LNug | 2019-12-31 | Walker Tap |  |  | 138 |  |  | De-energize, isolate and ground the 96SG41 underground (UG) pipe-type cable. | WI |  |  | Proposed | 700000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 14073 | 2018-08-17 | PR07814 | 23211 | 2018-02-01 | SUB | 2019-12-31 | NA |  |  | 345 | 138 |  | Details to be determined | WI |  |  | Proposed | 140000000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 14184 | 2018-08-17 | PR07832 | 23278 | 2018-02-19 | IND | 2019-06-01 | Cranberry |  |  | 115 |  |  | This project consists of removing the existing 115 kV, 14.4 MVAR capacitor bank at the Cranberry substation and installing a new 115 kV, 10.4 MVAR oil-filled inductor bank to the vacated bay position. | WI |  |  | Proposed | 1700000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14185 | 2018-08-17 | PR07831; PR07998 | 23279 | 2018-02-19 | IND | 2019-06-01 | M-38 |  |  | 138 |  |  | This project consists of installing a new 138 kV, 15 MVAR oil-filled inductor bank at the M-38 substation in one of bay positions that has been vacated due to the removal of several 138 kV line terminals. | MI |  |  | Proposed | 2100000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14185 | 2018-08-17 | PR07831; PR07998 | 23388 | 2018-02-19 | IND | 2019-06-01 | Silver River |  |  | 138 |  |  | The inductor bank is a 8 MVAR size to provide acceptable voltage step-change levels under certain system conditions. | MI |  |  | Proposed | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14186 | 2018-08-17 | PR07830, F5398 | 23280 | 2018-02-19 | IND | 2019-06-01 | Iron Grove |  |  | 138 |  |  | This project consists of installing a new 138 kV, 15 MVAR, oil-filled inductor bank at the Iron Grove substation to the 138 kV straight bus. | MI |  |  | Proposed | 1900000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14204 | 2018-08-23 | PR08007, F5338 | 23289 | 2018-08-23 | LNup | 2020-09-23 | Silver River | North Lake |  | 138 |  |  | Silver River to North Lake 138-kV Line | MI |  |  | Proposed | 18200000 | Planning |  | N | Y | N | Y
A in MTEP18 | A | West | ATC | 14204 | 2018-08-23 | PR08007, F5338 | 23409 | 2018-08-23 | LNug | 2020-09-23 | Silver River | Perch Lake | 1 | 138 |  | 463 | Silver River to Perch Lake 138-kV Line | MI |  |  | Proposed | 500000 | Planning |  | N | Y | N | Y
A in MTEP18 | A | West | ATC | 14604 | 2018-08-17 | PR07959 | 23338 | 2018-08-17 | CAP | 2019-12-01 | Balsam |  |  | 138 |  |  | Balsam Cap Banks. 2 x 16.3 Mvar Cap Banks. State Line Cap Banks. 2 x 16.3 Mvar Cap Banks. | WI |  |  | Proposed | 8200000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14604 | 2018-08-17 | PR07959 | 23339 | 2017-12-22 | SUB | 2019-12-01 | State Line |  |  | 138 |  |  | New loop through State Line Substation | WI |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | 23357 | 2018-03-29 | LNcnv | 2022-06-30 | Bayport | Pioneer |  | 138 |  | 294 | E83 and T98 69kV Rebuild to 138kV | WI |  |  | Proposed | 41100000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | 23407 | 2018-03-29 | SUB | 2022-06-30 | Suamico |  |  | 138 |  |  | Suamico SS - Remote End Work | WI |  |  | Proposed | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | 23406 | 2018-03-29 | SUB | 2022-06-30 | Sobieski |  |  | 138 |  |  | Sobieski SS - Remote End Work | WI |  |  | Proposed | 3600000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | 23405 | 2018-03-29 | SUB | 2022-06-30 | Pulliam |  |  | 138 |  |  | Pulliam SS - Remote End Work | WI |  |  | Proposed | 100000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | 23404 | 2018-03-29 | SUB | 2022-06-30 | Pioneer |  |  | 138 |  |  | Pioneer SS Remote End Work | WI |  |  | Proposed | 3400000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14706 | 2018-08-13 | PR07854 | 23403 | 2018-03-29 | SUB | 2022-06-30 | Bayport |  |  | 138 |  |  | Remote End Work | WI |  |  | Proposed | 1500000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14805 | 2018-08-17 | PR07999 | 23387 | 2018-02-19 | IND | 2019-06-01 | Winona |  |  | 138 |  |  | The inductor bank is a 8 MVAR size to provide acceptable voltage step-change levels under certain system conditions. | MI |  |  | Proposed | 1900000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14806 | 2018-08-17 | PR07942, F5036 | 23389 | 2018-02-19 | CAP | 2020-06-01 | Venus |  |  | 115 | 115 |  | Remove Capacitor bank from Venus substation | WI |  |  | Proposed | 140000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14904 | 2018-08-17 |  | 23475 | 2018-08-22 | SUB | 2021-06-30 | NA |  |  | 138 | 69 |  | Distribution Interconnection Current Cycle | WI,MI |  |  | Proposed | 6436258 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 14905 | 2018-08-17 |  | 23476 | 2018-08-22 | SUB | 2022-06-30 | NA |  |  | 138 | 69 |  | Distribution Interconnection 2019 | WI,MI |  |  | Proposed | 10570000 |  |  | N | N | N
A in MTEP18 | A | West | ATC | 14925 | 2018-08-17 | PR07995, F5438, F5437 | 23408 | 2018-03-30 | SUB | 2021-01-28 | Apollo |  |  | 138 | 138 |  | Construct new Apollo substation adjacent to the existing Kewaunee-Shoto line. Loop the Kewaunee-Shoto line into the new station. | WI |  |  | Proposed | 8300000 | Planning |  | N | Y | N | Y
A in MTEP18 | A | West | ATC | 14926 | 2018-08-13 | PR08029, F5468, F5469 | 23410 | 2018-04-17 | LINE | 2022-12-01 | Pioneer | Crivitz |  | 138 | 69 |  | Pioneer-Crivitz, retire double-circuit 69 kV | WI |  |  | Proposed | 20400000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 14986 | 2018-08-17 | PR08084 | 23416 | 2018-04-17 | SUB | 2021-12-01 | Caroline SS |  |  | 115 |  |  | 115-69kV substation work | WI |  |  | Proposed | 4500000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14987 | 2018-08-17 | PR07558, PR07877 | 23417 | 2018-04-17 | SUB | 2021-12-01 | Whitcomb SS |  |  | 115 |  |  | (4) new 69kV, 3000A GCB, (1) power transformer | WI |  |  | Proposed | 5500000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 14988 | 2018-08-17 | PR08036 | 23418 | 2018-04-17 | SUB | 2021-12-01 | Shoto SS |  |  | 138 |  |  | New transformer, breakers and other substation work. | WI |  |  | Proposed | 5700000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15044 | 2018-08-17 | PR08039 | 23427 | 2018-04-27 | SUB | 2019-12-01 | Stratford |  |  | 115 |  |  | ATC work includes loop through bus, (2) MODs, cap bank replacement and upgrade of high side circuit breakers | WI |  |  | Proposed | 3700000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 15045 | 2018-08-17 | PR08025 | 23428 | 2018-04-27 | SUB | 2020-06-01 | Dam Heights |  |  | 69 |  |  | Reconfigure, expand bus no. 2 and add new line terminal at Dam Heights SS | WI |  |  | Proposed | 3300000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 15045 | 2018-08-17 | PR08025 | 23429 | 2018-04-27 | LN | 2020-06-01 | Dam Heights | Prairie du Sac Tower SS |  | 69 | 69 | 33 | Build half mile of new 69 kV single circuit along HWY 78 and build quarter mile partially double circuit with Y-75 | WI |  |  | Proposed |  |  |  | N | N | N | Y
A in MTEP18 | A | West | ATC | 15124 | 2018-08-17 |  | 23447 | 2018-05-14 | Dist | 2020-06-30 | Muscoda SS |  |  | 69 |  |  | ATC will loop through 69 kV line Y-124 with line breakers | WI |  |  | Proposed | 3290000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15126 | 2018-08-17 |  | 23449 | 2018-05-14 | Dist | 2023-12-31 | Edgewater SS |  |  | 138 |  |  | Loop through the 138 kV line X-37 with line breakers | WI |  |  | Proposed | 3000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15127 | 2018-08-17 |  | 23450 | 2018-05-14 | Dist | 2021-06-01 | Portage Industrial Park SS |  |  | 138 |  |  | ATC will loop through 138 kV line X-67 with line switches | WI |  |  | Proposed | 3000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15128 | 2018-08-17 |  | 23451 | 2018-05-14 | Dist | 2021-06-01 | New Switching Station |  |  | 69 |  |  | ATC to build a new switching station near Birnamwood tap to loop through the 69 kV line Y-86 with line breakers | WI |  |  | Proposed | 4500000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15129 | 2018-08-17 |  | 23452 | 2018-05-14 | Dist | 2021-05-15 | New Sub |  |  | 69 |  |  | New substation in Green County, WI | WI |  |  | Proposed | 4500000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15130 | 2018-08-17 | PR07436, F5025 | 23453 | 2018-05-14 | Dist | 2021-03-01 | New Sub |  |  | 69 |  |  | Load addition in Eastern UP, MI | MI |  |  | Proposed | 12593000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15131 | 2018-08-17 | PR08126 | 23454 | 2018-05-14 | Dist | 2020-06-01 | Milton Lawn SS |  |  | 69 |  |  | ATC work includes loop through bus and two line breakers. | WI |  |  | Proposed | 3000000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15132 | 2018-08-17 | PR08136 | 23455 | 2018-08-17 | Dist | 2020-07-01 | New Sub |  |  | 138 |  |  | Quincy Street Substation to support Green Bay Packaging's expansion. | WI |  |  | Proposed | 6466513 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15133 | 2018-08-17 | PR07793, F5293 | 23456 | 2018-05-14 | Dist | 2019-07-01 | New Sub |  |  | 138 |  |  | Load addition in Central UP, MI | MI |  |  | Proposed | 6200000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 15145 | 2018-08-22 | PR 08090, F5479 | 23462 | 2018-08-14 | LNrb | 2021-12-31 | Mackinac SS | Mc Gulpin SS |  | 138 |  |  | Replace one damaged and one operating fluid dielectric 138 kV insulated submarine cable circuits with two solid dielectric insulated 138 kV submarine circuits | MI | 4 | 0 | Proposed | 105000000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | ATC | 15284 | 2018-08-13 | PR08113, F5518 | 23508 | 2018-06-28 | LNrb | 2020-12-30 | North Lake SS | M-38 SS |  | 138 | 138 |  | NLKG31 Asset Renewal, select rebuild | MI |  |  | Proposed | 8500000 | Planning |  | N | N | N
A in MTEP18 | A | West | ATC | 16164 | 2018-10-01 |  | 24228 | 2018-10-01 | SUB | 2022-12-31 | Elkhart Lake |  |  | 138 |  |  | Configure station to eliminate market congestion | WI |  |  | Planned | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | South | AXLA | 14524 | 2018-08-20 |  | 23334 | 2018-08-09 | LNrc | 2020-02-01 | Downtown | Willow Glen | 1 | 138 |  |  | Reconductor of Downtown - Willow Glen 138 kV transmission line | LA | 4.8 |  | Proposed | 2500000 |  | Generator | N | N | N | Y
A in MTEP18 | A | Central | BREC | 16204 | 2018-10-04 | BREC | 24230 | 2018-10-04 | TEQ | 2023-01-01 | Wilson |  |  | 161 |  | 837 MVA | Terminate new 161 kV circuit at Wilson | KY |  |  | Proposed | 1000000 | Planning |  | N | N | N
A in MTEP18 | A | Central | BREC | 16204 | 2018-10-04 | BREC | 24234 | 2018-10-04 | TEQ | 2023-05-30 | Matanzas |  |  | 161 |  | 529 MVA | KU upgrade included in LG&E/KU transmission expansion plan. | KY |  |  | Proposed | 500000 | Planning |  | N | N | N
A in MTEP18 | A | Central | BREC | 16204 | 2018-10-04 | BREC | 24233 | 2018-10-04 | TEQ | 2023-01-01 | Paradise |  |  | 161 |  | 837 MVA | Paradise (TVA) 161 kV line terminal upgrade | KY |  |  | Proposed | 2500000 | Planning |  | N | N | N
A in MTEP18 | A | Central | BREC | 16204 | 2018-10-04 | BREC | 24232 | 2018-10-04 | LNrc | 2023-01-01 | BR Tap | Paradise (TVA) |  | 161 |  | 837 MVA | Remove BR Tap and reconductor 7.7 mile line to Paradise (TVA) with (2) bundled 954 ACSS (includes 0.4 mile TVA portion). | KY | 7.7 |  | Proposed | 4100000 | Planning |  | N | N | N
A in MTEP18 | A | Central | BREC | 16204 | 2018-10-04 | BREC | 24231 | 2018-10-04 | LNrb | 2023-01-01 | Wilson | BR Tap |  | 161 |  | 837 MVA | Add 13.2 mile circuit on existing Wilson to BR Tap route. | KY | 13.2 |  | Proposed | 7920000 | Planning |  | N | N | N
A in MTEP18 | A | East | CETO | 13962 | 2017-09-13 |  | 23073 | 2017-09-13 | RLY | 2019-12-31 | CE Relay Replacement Program - 2019 |  |  | 138 |  |  | Replace relays to coordinate with protective system changes by adjacent Transmission Owners. | MI |  |  | Proposed | 640000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 13963 | 2017-09-13 |  | 23074 | 2017-09-13 | CB | 2020-12-31 | CE Breaker Replacement Program - 2020 |  |  | 138 |  |  | Replace damaged or defective circuit breakers across the system. | MI |  |  | Proposed | 1170000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 13965 | 2017-09-13 |  | 23075 | 2017-09-13 | TEQ | 2020-12-31 | CE Substation Equipment Replacements - 2020 |  |  | 138 |  |  | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI |  |  | Proposed | 1410000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 13966 | 2017-09-13 |  | 23076 | 2017-09-13 | LNup | 2020-12-31 | CE Pole & Line Equipment Replacement Program - 2020 |  |  | 138 |  |  | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI |  |  | Proposed | 840000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 13967 | 2017-09-13 |  | 23078 | 2017-09-13 | LNrb | 2019-12-31 | Muskegon Heights | Cobb | 2 | 138 |  |  | Rebuild the portion of the Muskegon Heights #2 138 kV Line, presently on KK71 towers, approximately 2 miles in length, utilizing 138 kV single circuit construction | MI | 2 |  | Proposed | 800000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 14164 | 2017-09-21 |  | 23276 | 2017-11-15 | LNup | 2020-06-01 | Boardman | Grand Traverse Jct | 1 | 138 |  |  | Add fiber optic cable to the line to maintain protective system coordination of the line. | MI | 0.2 |  | Proposed | 100000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 14164 | 2017-09-21 |  | 23277 | 2017-11-15 | LNup | 2020-06-01 | Boardman | Grand Traverse Jct | 2 | 138 |  |  | Add fiber optic cable to the line to maintain protective system coordination of the line. | MI | 0.2 |  | Proposed | 100000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | East | CETO | 14725 | 2018-05-16 |  | 23364 | 2018-01-26 | RLY | 2018-12-10 | Summerton |  |  | 138 |  |  | Replace existing relaying at Summerton Substaion on the Luce (J589) line exit with dual pilot schemes; Route OPGW fiber into control house; Terminate the new OPGW fiber installed by METC; Install new OPGW fiber patch panel; Install an anti-islanding scheme; Upgrade the 288 line switch with auxiliary contacts and integrate into protective schemes. | MI |  |  | Planned | 371500 | Facility Study |  | N | N | N
A in MTEP18 | A | East | CETO | 14864 | 2018-03-19 |  | 23397 | 2018-03-15 | LN | 2020-03-01 | Polkton | Polkton Jct | 1 | 138 |  |  | Approximately 0.3 miles of 138 kV line from the Cobb-Tallmadge #2 138 kV Line to the new Polkton 138/46 kV distribution substation. | MI |  | 0.3 | Proposed | 200000 | Planning |  | N | N | N
A in MTEP18 | A | South | CLECO | 9716 | 2017-09-25 |  | 21095 | 2017-10-04 | LNcnv | 2020-06-01 | Coughlin | Plaisance | 1 | 138 |  |  | Reconductor Coughlin to Plaisance with 2 -954 ACSS conductor | LA | 17 |  | Proposed | 12320000 | Planning |  | N | N | N
A in MTEP18 | A | Central | DEI | 13750 | 2017-09-07 | TIN1863 | 22817 | 2017-09-07 | LNrb | 2019-12-31 | Greenfield 69 | Fountaintown 69 | 1 | 69 |  | 153 | Greenfield (actually pole 811-7903) to Westland Jct to Fountaintown 69166 (Pt1) 69kV Rebuild w/ 954ACSR; Replace Westland Jct #1 and #2 switches | IN | 5.6 |  | Proposed | 7478000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13759 | 2017-09-07 | TIN1862 | 22828 | 2017-09-07 | LNrb | 2019-12-31 | HE Raysville 69 | Knightstown 69 | 1 | 69 |  | 153 | HE Raysville to Knightstown 69140 (Part 1) 69kV Rebuild w/ 954ACSR; Replace Raysville #1 and #2 switches | IN | 3.6 |  | Proposed | 4732000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13765 | 2017-09-07 | TIN1857 | 22833 | 2017-09-07 | LNrb | 2019-12-31 | Metea 69 | Lucerne 69 | 1 | 69 |  | 100 | Metea to Lucerne 6926 (Part 1) 69kV Rebuild w/ 477ACSR | IN | 7.1 |  | Proposed | 7078000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13772 | 2017-09-07 | TIN1840 | 22840 | 2017-09-07 | SUB | 2019-12-31 | Seymour 138 |  |  | 138 | 69 |  | Seymour 138 Reliability Upgrades: Replace (3) 138kV circuit switchers – 13869-1, 13869-2; (12) 138kV line CCVTs; 13829 and 13830 wave traps; 13830 & 13851 MOLB Sw's; 13880 switch 2000 amp load break; Add new ctrl bldg; Misc relay upgrades; Replace (3) 69kv breakers and main bus (954acsr); | IN |  |  | Proposed | 4508000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13775 | 2017-09-07 | AMIN1741 | 22843 | 2018-09-27 | SUB | 2018-12-31 | Gallagher Station |  |  | 230 | 138 |  | Gallagher 230 Reliability Upgrades: Replace misc. relays; (4) 230kV breakers – 23004, 23005, 230138-10, 230kV TR; (11) misc. 230kV switches; (4) 138kV breakers – 13827, 13885, 13822, 138TR; (3) wave traps - 13852, 23004, 23005 | IN |  |  | Under Construction | 4072000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13796 | 2018-08-10 | TIN1897 | 22858 | 2018-08-10 | INT | 2019-06-01 | Cayuga CT 345 | 400MW wind farm |  | 345 |  | 400 | Cayuga CT 345kV Ring Bus Expansion - to accommodate wind farm connection - J515 | IN |  |  | Planned | 3237942 | GIA |  | N | Y | Y
A in MTEP18 | A | Central | DEI | 13796 | 2018-08-10 | TIN1897 | 23533 | 2018-08-10 | INT | 2019-06-01 | Cayuga CT 345 |  |  | 345 |  |  | TOIF for J515 | IN |  |  | Planned | 273440 |  |  | N | N | N | Y
A in MTEP18 | A | Central | DEI | 13808 | 2017-09-27 | M17SG0009 | 22871 | 2018-09-27 | Dist | 2019-06-01 | McCordsville (WVPA) |  |  | 69 | 12 |  | McCordsville (WVPA) New 69-12kV Sub: DEI to provide PM support, system protection engineering, metering, substation testing, for new WVPA-owned sub | IN |  |  | M4_Pre-Construction | 100000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | Central | DEI | 13812 | 2018-07-10 | M180405 | 22876 | 2017-09-08 | Dist | 2019-12-31 | Intelliplex (HE) |  |  | 138 | 12 |  | Intelliplex (HE) New 138-12kV Sub: DEI to provide PM support, system protection engineering, metering, substation testing, for new HE-owned sub in the 13803 ckt. | IN |  |  | Proposed | 300000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | Central | DEI | 13820 | 2017-09-08 | DIN1773 | 22891 | 2017-09-08 | Dist | 2019-12-31 | Galveston |  |  | 69 | 12 |  | Galveston New 69-12kV Sub: loop 69173 ckt thru with (3) 1200A switches and 954AAC bus; 22.4MVA NLTC xfmr | IN |  |  | Proposed | 1702880 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13827 | 2017-09-08 | DIN1697 | 22898 | 2017-09-08 | Dist | 2019-06-01 | Westfield Dunbar Rd. |  |  | 69 | 12 |  | Westfield Dunbar Rd. New 69-12kV Sub: loop 6917 ckt thru; 22.4MVA xfmr - near str. 935-1083 | IN |  |  | Proposed | 1609000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13830 | 2017-09-08 | DIN1719 | 22900 | 2017-09-08 | Dist | 2019-06-01 | Westfield Casey Rd. |  |  | 69 | 12 |  | Westfield Casey Rd. New 69-12kV Sub: loop 69142 ckt thru; 22.4MVA xfmr - near str. 838-8345 | IN |  |  | Proposed | 1544000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13844 | 2017-09-11 | TIN1822 | 22914 | 2017-09-11 | SUB | 2019-12-31 | Washington Muni. 10th St. |  |  | 138 |  |  | Washington Muni. 138kV Ring Bus: add 2 breakers and replace 1; relocate metering; add control building; install wave traps on the 13825 and 13856 line terminals | IN |  |  | Proposed | 3882000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13845 | 2018-07-12 | M170016 | 22915 | 2018-07-12 | SUB | 2019-12-31 | Crawfordsville Jct 69 |  |  | 69 |  |  | Crawfordsville Jct 69kV Ring Bus Switching Station: build 3 breaker ring at existing junction in the 6935 ckt and close in Crawfordsville 69 #1 switch. | IN |  |  | Proposed | 6420000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 13849 | 2017-09-11 | DIN1666 | 22919 | 2017-09-11 | LN | 2019-12-31 | Brazil 69 | Carbon 69 |  | 69 |  | 100 | Brazil to Carbon - New 69kV Ckt. to remove Carbon loads from the 6938 ckt. | IN |  | 1.1 | Proposed | 4353000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | Central | DEI | 14624 | 2018-01-02 | M170127 | 23340 | 2018-01-02 | LNrb | 2018-12-31 | Andersonville 69 | Andersonville Jct. | 1 | 69 |  | 100 | Rebuild 6919 from Andersonville 69 sub (pole # 840-1272) to Andersonville Jct (pole # 840-1175) using light-duty steel poles, 477ACSR conductor and OPGW static | IN | 7 |  | Proposed | 14093000 | Engineering w/AFUDC |  | N | N | N
A in MTEP18 | A | West | DPC | 16184 | 2018-10-03 |  | 24229 | 2018-10-03 | LNrb | 2023-12-31 | Wabaco 161 kV | Rochester 161 kV |  | 161 |  |  | Rebuild existing ~13.1 miles Wabaco to Rochester 161kV line by using 795kcmil Drake ACSS conductor. No substation work is needed. No additional ROW required. Some terrain work is needed as well as one OPGW and one steel shieldwire. | MN | 13.1 |  | Proposed | 11000000 |  |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-AR | 9694 | 2017-08-29 | 16-EAI-003 | 21018 | 2018-08-02 | LNrb | 2021-06-01 | Camden Maguire 115kV | Smackover 115kV |  | 115 |  |  | The 14.32 mile long line will be upgraded to a minimum rating of 176 MVA (882 Amps). | AR | 14.32 |  | Proposed | 16418417 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 12663 | 2018-08-06 | 17-EAI-016 | 22461 | 2018-08-02 | SUB | 2023-06-01 | Palestine 161kV |  |  | 161 | 13.8 |  | New 161/13.8kV Substation that will include one 2000 AMP main breaker and three 1200 AMP feeder breakers. | AR |  |  | Proposed | 12484101 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 12664 | 2018-08-06 | 17-EAI-011 | 22462 | 2018-06-01 | SUB | 2021-06-01 | Skunk Hollow 161kV |  | 1 | 161 | 13.8 |  | Construct a new substation with a new 40 MVA 161/13.8kV LTC and four feeder breaker bays. | AR |  |  | Proposed | 7351525 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 12668 | 2018-08-07 | 17-EAI-025 | 22465 | 2018-08-02 | SUB | 2020-05-01 | Hot Springs Village 115kV |  |  | 115 |  |  | Install one 40 MVA LTC transformer, replace T2 with a 40 MVA LTC, and install high side breakers. | AR |  |  | Proposed | 15015860 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13604 | 2018-08-06 | 18-EAI-033 | 22693 | 2018-08-02 | SUB | 2021-06-01 | Social Hill 115kV |  |  | 115 | 13.8 |  | Build a new 115kV distribution substation on the Hot Springs EHV - Gurdon 115kV line. | AR |  |  | Proposed | 11607797 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13621 | 2017-09-26 | 18-EAI-015 | 22711 | 2018-06-28 | LNrb | 2027-12-01 | Norfork | Southland |  | 161 |  |  | Rebuild this line and upgrade all station equipment to a minimum of 1300 Amps. | AR | 9 |  | Proposed | 14434622 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13622 | 2018-09-04 | 18-EAI-017 | 22712 | 2018-09-13 | LNrb | 2023-06-01 | Southland | Mt. Home |  | 161 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amps. | AR | 1.4 |  | Proposed | 4239252 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13624 | 2017-09-26 | 18-EAI-014 | 22714 | 2018-06-28 | LNrb | 2025-12-01 | Everton Road | Harrison East |  | 161 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amps. | AR | 8.3 |  | Proposed | 14890896 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13625 | 2017-09-26 | 18-EAI-013 | 22715 | 2018-06-28 | LNrb | 2024-12-01 | St. Joe | Everton Road |  | 161 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amp. | AR | 13.5 |  | Proposed | 18582810 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13626 | 2017-09-26 | 18-EAI-012 | 22716 | 2018-08-03 | LNrb | 2023-06-01 | Hilltop | St. Joe |  | 161 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amps. | AR | 3.9 |  | Proposed | 6535668 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13630 | 2018-05-22 | 18-EAI-024 | 22723 | 2018-09-13 | LNrb | 2021-06-01 | LR Fourche | LR East |  | 115 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1492 Amps. | AR | 1.4 |  | Proposed | 2674070 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13632 | 2017-09-26 | 18-EAI-029 | 22725 | 2018-08-02 | LNrb | 2020-12-01 | Conway South | Conway Industrial |  | 161 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1950 Amps. | AR | 1 |  | Proposed | 2087033 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13635 | 2017-09-26 | 18-EAI-002 | 22728 | 2018-08-02 | LNrb | 2020-12-01 | Cheetah | Hot Springs Village |  | 115 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amps. | AR | 2.85 |  | Proposed | 4424101 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13636 | 2017-09-26 | 18-EAI-005 | 22729 | 2018-09-13 | SUBmisc | 2021-12-01 | Paragould |  |  | 161 | 115 |  | Install station services to run fans and pump on the autotransformer. | AR |  |  | Proposed | 532374 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 13637 | 2017-09-26 | 18-EAI-001 | 22730 | 2018-06-28 | LNup | 2019-12-01 | Jacksonville North | Holland Bottom |  | 115 |  |  | Upgrade structures and distribution lines necessary to operate the line at 100C rating. | AR |  |  | Proposed | 164409 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-AR | 14984 | 2018-06-05 | 18-EAI-036 | 23414 | 2018-08-02 | SwSta | 2019-06-01 | Moses 161kV |  |  | 161 |  |  | A new 4 breaker ring bus will be installed adjacent to the existing Moses 161kV switchyard. | AR |  |  | Planned | 7438862 | Planning |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-AR | 15107 | 2018-05-14 | 18-EAI-035 | 23446 | 2018-05-10 | TEQ | 2018-12-01 | Mabelvale 500kV |  |  | 500 |  |  | Upgrade switch B8859 to a 3000 A switch | AR |  |  | Proposed | 285025 | Planning w/AFUDC |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 9793 | 2017-09-25 | 16-EGL-031 | 21167 | 2018-09-26 | LNrc | 2021-06-01 | Esso | Delmont | 1 | 230 |  |  | Reconductor line | LA |  |  | Proposed | 2322052 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 9797 | 2018-08-17 | 16-EGL-036 | 21171 | 2018-09-26 | LNup | 2019-08-01 | Nelson | Lake Charles | 1 | 138 |  |  | Change multiple structures to achieve full rating of conductor | LA |  |  | Proposed | 8682037 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 12101 | 2018-09-26 | 17-ELF-001 | 22205 | 2018-09-26 | LN | 2022-06-01 | Cecelia | Conrad | 1 | 230 |  |  | Construct new line from Cecelia to Conrad | LA |  |  | Proposed | 105479468 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 12101 | 2018-09-26 | 17-ELF-001 | 22208 | 2018-09-26 | SUB | 2022-06-01 | Conrad |  |  | 230 | 138 |  | Build new Conrad 230 kV substation | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 12101 | 2018-09-26 | 17-ELF-001 | 22207 | 2018-09-26 | TX | 2022-06-01 | Conrad |  |  | 230 | 138 |  | Install 230-138 kV auto at Conrad | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 12105 | 2017-09-25 | 17-ELB-010 | 22210 | 2018-09-26 | LN | 2021-12-01 | Fancy Point | Horseshoe |  | 230 |  |  | Construct approx. 7 miles of 2nd Fancy to Horseshoe 230 kV line. The new line will be constructed to a minimum of 1900 amps. This line should not share structures with any other line. | LA |  | 7 | Proposed | 24610733 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 12769 | 2018-08-15 | 17-ELC-009 | 22516 | 2018-09-26 | Dist | 2025-06-01 | Goosport |  |  | 138 |  |  | New Distribution | LA |  |  | Proposed | 12893410 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 12773 | 2018-08-06 | 17-ELS-012 | 22520 | 2018-09-26 | Dist | 2021-06-01 | Chackbay |  |  | 230 |  |  | New Substation | LA |  |  | Proposed | 19500747 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13867 | 2017-09-25 | 18-EMI-003 | 22932 | 2018-09-26 | LNrb | 2021-04-01 | Natchez SES | Red Gum | 1 | 115 |  | 259 | Upgrade the line to a minimum of 1300 Amps or 259 MVA. | LA | 6.13 |  | Planned | 24184715 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13867 | 2017-09-25 | 18-EMI-003 | 22934 | 2017-09-12 | RLY | 2021-04-01 | Red Gum |  |  | 115 |  | 259 | Upgrade relays and settings to a minimum of 1300 Amps or 259 MVA. | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13867 | 2017-09-25 | 18-EMI-003 | 22933 | 2017-09-12 | TEQ | 2021-04-01 | Red Gum |  |  | 115 |  | 259 | Upgrade terminal equipment to a minimum of 1300 Amps or 259 MVA. | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13890 | 2017-09-25 | 18-ELB-001 | 22962 | 2018-09-26 | CB | 2020-04-01 | Conway |  |  | 138 |  |  | Replace all 138 kV Conway Oil circuit breakers to a minimum of 2000 Amp GCBs. Also replace all 138 kV switches to a minimum of 2000 Amps. Replace any additional equipment to achieve a final rating of 2000 Amps on the Conway 230-138 kV transformer. | LA |  |  | Proposed | 2359929 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13890 | 2017-09-25 | 18-ELB-001 | 22963 | 2017-09-12 | BUS | 2020-04-01 | Conway |  |  | 138 |  |  | Upgrade the bus work on 138 kV Conway substation to a minimum of 2000 Amp. | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13895 | 2018-08-06 | 18-ELB-003 | 22966 | 2018-09-26 | SUB | 2018-10-01 | Mt. Houmas |  |  | 230 |  |  | New 230 kV 3 breaker ring bus customer station to replace the Licar substation cut in between the AAC Corp and Belle Helene 230 kV stations. Install 60 MVA 230-34.5 kV transfomer. | LA |  |  | Proposed | 10168815 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13902 | 2018-05-10 | 18-ELC-002 | 22972 | 2018-09-26 | LNrb | 2020-06-01 | Mossville | Lockmoor |  | 69 |  |  | Rebuild or re-conductor the approximately 2.10 mile long Mossville to Lockmoor 69 kV transmission circuit to a minimum of 1200 A, 143 MVA. | LA | 2.1 |  | Proposed | 2968717 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 13909 | 2017-09-25 | 18-ENO-001 | 22993 | 2018-09-26 | CB | 2020-06-01 | Curran |  |  | 230 |  |  | Install breakers at Curran 230 kV | LA |  |  | Proposed | 3725376 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | 23365 | 2018-09-26 | LNrc | 2020-02-28 | Nelson | Spanish Trail to Mossville | 1 | 138 |  |  | • Reconductor / Rebuild the Nelson – Spanish Trail – Mossville 138 kV line sections (approximately 3.35 miles) using 1272 ACSS conductor and upgrade substation equipment to achieve a through path rating of 1958 A. | LA |  |  | Planned | 8182426 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | 23370 | 2018-08-03 | CB | 2020-02-28 | Conoco |  |  | 138 |  |  | • Replace the following breakers at Alfol 69 kV and Conoco 138 kV with breakers having interrupting capability of at least 22 kA and 23 kA respectively Substation Breaker Conoco 138 kV 18035 | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | 23369 | 2018-08-03 | CB | 2020-02-28 | Alfol |  |  | 69 |  |  | • Replace the following breakers at Alfol 69 kV and Conoco 138 kV with breakers having interrupting capability of at least 22 kA and 23 kA respectively Substation Breaker Alfol 69 kV 17695 | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | 23368 | 2018-09-26 | CB | 2020-02-28 | Nelson |  |  | 230 | 138 |  | • Replace the following breakers at Nelson with 80 kA IPO breakers Substation Breaker Substation Breaker Nelson 138 kV 7925 Nelson 230 kV 13025 Nelson 138 kV 7930 Nelson 230 kV 13030 Nelson 138 kV 7935 Nelson 230 kV 13035 Nelson 138 kV 7940 Nelson 230 kV 13040 Nelson 138 kV 7945 Nelson 230 kV 13140 Nelson 138 kV 7965 Nelson 230 kV 18145 Nelson 138 kV 7980 Nelson 230 kV 18155 Nelson 138 kV 7985 Nelson 230 kV 18160 Nelson 138 kV 7990 Nelson 230 kV 18165 Nelson 138 kV 18640 Nelson 230 kV 18170 Nelson 138 kV 18645 Nelson 230 kV 18175 Nelson 138 kV 18590 Nelson 230 kV 18185 Nelson 138 kV 18595 Nelson 230 kV 18190 Nelson 138 kV 18600 Nelson 230 kV 18210 Nelson 138 kV 18605 Nelson 230 kV 27105 Nelson 138 kV 7900 Nelson 230 kV 37455 Nelson 138 kV 7905 Nelson 230 kV 37460 Nelson 138 kV 7910 Nelson 138 kV 7915 Nelson 138 kV 7920 | LA |  |  | Planned | 42498733 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | 23367 | 2018-08-03 | INT | 2020-02-28 | Nelson |  |  | 230 | 138 |  | Work related to Substation Interconnection for new units at existing Nelson 230 and 138 kV stations | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 14744 | 2018-05-30 | 18-ELC-006 | 23366 | 2018-08-03 | LNrc | 2020-02-28 | Nelson | Mossville | 1 | 138 |  |  | • Reconductor / Rebuild the Nelson – Mossville 138 kV line section (approximately 3.56 miles) using 1272 ACSS conductor and upgrade substation equipment to achieve a through path rating of 1958 A. | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 15270 | 2018-08-09 | 18-ELS-009 | 23501 | 2018-09-26 | SUB | 2019-09-01 | Clovelly |  |  | 115 |  |  | The new 115 kV station will be located east of Highway 308 and will be served on an existing radial 115 kV line from the Clovelly 115 kV station. | LA |  |  | Proposed | 1916583 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-LA | 15271 | 2018-08-09 | 18-ELB-006 | 23502 | 2018-09-26 | SUB | 2020-06-01 | Luce |  |  | 230 |  |  | The new substation will be located southwest of Geismar near Old Jefferson Highway. The interconnection will cut in and out of the existing 230 kV line between AAC Corp and Licar (Mt. Houmas), at approximately 2.5 miles from AAC Corp 230 kV station. | LA |  |  | Proposed | 17932040 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 9829 | 2017-09-12 | 16-EMI-004 | 21205 | 2018-09-26 | CB | 2019-06-01 | Ray Braswell |  |  | 115 |  |  | Replace 2-115 kV breakers | MS |  |  | Proposed | 1552276 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13865 | 2017-09-15 | 18-EMI-001 | 22926 | 2018-09-26 | LNrb | 2020-06-01 | Star | Mendenhall | 1 | 115 |  | 259 | Rebuild the ~15 mile Star to Mendenhall 115 kV line to a minimum of 1300 Amps or 259 MVA | MS | 15.12 |  | Planned | 15500045 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13865 | 2017-09-15 | 18-EMI-001 | 22952 | 2017-09-12 | TEQ | 2020-06-01 | Mendenhall |  |  | 115 |  |  | Upgrade terminal equipment to a minimum of 1300 Amps or 259 MVA. | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13865 | 2017-09-15 | 18-EMI-001 | 22951 | 2017-09-12 | TEQ | 2020-06-01 | Star |  |  | 115 |  |  | Upgrade terminal equipment to a minimum of 1300 Amps or 359 MVA | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13866 | 2017-09-15 | 18-EMI-002 | 22927 | 2018-09-26 | LNrb | 2020-12-01 | Mendenhall | Magee | 1 | 115 |  | 259 | Upgrade facility to a minimum 259 MVA. | MS | 9.67 |  | Planned | 11485197 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13866 | 2017-09-15 | 18-EMI-002 | 22954 | 2018-08-07 | RLY | 2020-12-01 | Magee |  |  | 115 |  |  | Upgrade relaying and settings to a minimum of 1300 Amps or 259 MVA | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13866 | 2017-09-15 | 18-EMI-002 | 22928 | 2018-08-07 | TEQ | 2020-12-01 | Magee |  |  | 115 |  | 259 | Upgrade terminal equipment at Magee substation to a minimum of 259 MVA. | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13867 | 2017-09-25 | 18-EMI-003 | 22929 | 2018-09-26 | LNrb | 2021-04-01 | Natchez SES | Red Gum | 1 | 115 |  | 259 | Upgrade the line to a minimum of 1300 Amps or 259 MVA. | MS | 5.28 |  | Planned | 21828991 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13867 | 2017-09-25 | 18-EMI-003 | 22931 | 2017-09-12 | RLY | 2021-04-01 | Natchez SES |  |  | 115 |  | 259 | Upgrade relays and settings to a minimum of 1300 Amps or 259 MVA. | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13867 | 2017-09-25 | 18-EMI-003 | 22930 | 2017-09-12 | TEQ | 2021-04-01 | Natchez SES |  |  | 115 |  | 259 | Upgrade terminal equipment to a minimum of 1300 Amps or 259 MVA. | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13899 | 2018-08-27 |  | 22971 | 2018-08-27 | SwSta | 2019-12-01 | Redwood Switching Station |  |  | 115 |  |  | Construct a new switching station with breakers at Redwood to increase reliability of the IP Redwood member delivery point and relocate a member communication tower impacted by station construction. | MS |  |  | Planned | 3700000 |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13900 | 2018-04-11 | 18-EMI-005 | 22973 | 2018-09-13 | LN | 2020-12-01 | Openwood | Flowers | 1 | 115 |  | 261 | Construct a new 115kV line from Bovina to Flowers utilizing the existing Bovina to Flowers SS line. Create a new 115 kV line section from Openwood to Flowers by utilizing the existing Openwood - Bovina 115 kV line section and extending a new section of line from the Bovina area to Flowers. | MS |  | 7 | Conceptual | 21900000 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13900 | 2018-04-11 | 18-EMI-005 | 22977 | 2018-08-07 | SwSta | 2020-12-01 | Flowers |  |  | 115 |  |  | Construct a new 115 kV switching substation adjacent to the existing Flowers substation. | MS |  |  | Conceptual |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13900 | 2018-04-11 | 18-EMI-005 | 22975 | 2018-08-07 | TEQ | 2020-12-01 | Bovina |  |  | 115 |  |  | Upgrade terminal equipment to a minimum of 261 MVA. | MS |  |  | Conceptual |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13900 | 2018-04-11 | 18-EMI-005 | 22974 | 2018-08-07 | LNrb | 2020-12-01 | Bovina | Flowers | 1 | 115 |  | 261 | Rebuild the existing 115 kV line sections between Bovina and Flowers to a minimum of 261 MVA. | MS | 7 |  | Conceptual |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13908 | 2017-09-15 | 18-EMI-013 | 22994 | 2018-09-26 | TAP | 2023-06-01 | Greenbrook-Plum Point |  |  | 115 |  |  | Tap Greenbrook to Plum Point 115kV line with 3.5mi of in and out 115kV line to Snowden Park. In and out 115kV line rated at least 200MVA | MS |  | 3.5 | Planned | 15527746 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13908 | 2017-09-15 | 18-EMI-013 | 22995 | 2017-09-12 | SUB | 2023-06-01 | Snowden Park |  |  | 115 |  |  | Construct 115k substation to serve load in the Southaven, MS area | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13992 | 2017-09-15 | 18-EMI-015 | 23099 | 2018-09-26 | SUB | 2023-06-01 | Hernando |  |  | 115 |  |  | Construct 4 mile 115kV line out of Hernando 115kV sub to new Pine Tree 115kV Sub. | MS |  |  | Planned | 15678288 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 13992 | 2017-09-15 | 18-EMI-015 | 23100 | 2017-09-14 | LN | 2023-06-01 | Hernando | Pine Tree |  | 115 |  |  | 4mi 115kV line from Hernando to PineTree | MS |  | 4 | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-MS | 15084 | 2018-05-08 | 17-EMI-014 | 23438 | 2018-08-07 | LNrb | 2022-12-01 | Horn Lake | Allen | 1 | 161 |  |  | Upgrade the existing 161 kV transmission line from Horn Lake Substation toward Allen SES to a new rating of 430 MVA stopping at the TN/MS state line | MS | 6 |  | Planned |  |  |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-MS | 15084 | 2018-05-08 | 17-EMI-014 | 23439 | 2018-08-07 | RLY | 2022-12-01 | Horn Lake |  |  | 161 |  |  | Upgrade relays at Horn Lake to take into account the Freeport cut in. | MS |  |  | Planned |  |  |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-TX | 12066 | 2018-09-04 | 17-ETI-013 | 22146 | 2018-09-26 | BUS | 2021-06-01 | Lewis Creek |  |  | 138 |  |  | Install a 138 kV breaker and construct bus work required to include the Lewis Creek to Alden 138 kV line in a double-bus-double-breaker configuration at Lewis Creek 138 kV. | TX |  |  | Proposed | 1574517 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 12090 | 2018-08-15 | 17-ETI-006 | 22181 | 2018-09-26 | LNrb | 2021-06-01 | Longmire | Ponderosa | 1 | 138 |  |  | Rebuild the Longmire – Ponderosa 138 kV using approximately 3.13 miles of conductor rated a minimum of 1950 A. | TX |  |  | Proposed | 6446221 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 12090 | 2018-08-15 | 17-ETI-006 | 22183 | 2017-09-13 | TEQ | 2021-06-01 | Ponderosa |  |  | 138 |  |  | Upgrade line bay riser at Ponderosa to a minimum of 2000 A. | TX |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 12090 | 2018-08-15 | 17-ETI-006 | 22182 | 2017-09-13 | TEQ | 2021-06-01 | Longmire |  |  | 138 |  |  | Upgrade CTs at Longmire to a minimum of 2000 A. | TX |  |  | Proposed |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 12767 | 2018-08-03 | 17-ETI-017 | 22514 | 2018-09-26 | Dist | 2021-12-01 | Timberland |  |  | 230 |  |  | New Substation | TX |  |  | Proposed | 56123385 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 13926 | 2017-09-13 | 18-ETI-001 | 23002 | 2018-09-26 | LNrb | 2019-06-01 | South Beaumont | Virginia |  | 69 |  |  | Rebuild approximately 2.77 miles of 69kV line between South Beaumont and Virginia substations. The new line should be rated at least 880A. | TX | 2.77 |  | Proposed | 1292701 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 13929 | 2018-08-16 | 18-ETI-002 | 23004 | 2018-09-26 | SUB | 2019-12-01 | Hankamer |  |  | 138 |  |  | Install 2nd transformer at Hankamer and reconfigure into a 138 kV ring bus | TX |  |  | Proposed | 7410604 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23371 | 2018-09-26 | LN | 2021-06-01 | Lewis Creek | Porter | 1 | 230 |  |  | • Construct new 230 kV line from Lewis Creek to Porter with a minimum through path rating of 1956 Amps. Construct a 230 kV ring bus at Porter | TX |  |  | Planned | 79561523 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23378 | 2018-09-26 | CB | 2021-05-30 | Lewis Creek |  |  | 138 |  |  | Replace the following breakers at Lewis Creek with 63 kA IPO breakers. All breakers at Lewis Creek 138 kV and 230 kV must be 63 kA, IPO breakers. Substation Breaker Lewis Creek 138 kV 1600 Lewis Creek 138 kV 1605 Lewis Creek 138 kV 1615 Lewis Creek 138 kV 1625 Lewis Creek 138 kV 1630 Lewis Creek 138 kV 1635 Lewis Creek 138 kV 1640 Lewis Creek 138 kV 1645 Lewis Creek 138 kV 1650 Lewis Creek 138 kV 1655 Lewis Creek 138 kV 1660 Lewis Creek 138 kV 1665 Lewis Creek 138 kV 26225 | TX |  |  | Planned | 19408367 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23377 | 2018-10-03 | INT | 2021-06-01 | Lewis Creek |  | 1 | 230 | 138 |  | Generator Interconnection on 230 and 138 kV busses | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23376 | 2018-03-20 | LNrb | 2021-06-01 | Longmire | Ponderosa |  | 138 |  |  | Accounted for in MTEP project 12090 | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23375 | 2018-01-30 | LNrc | 2021-06-01 | Lewis Creek | Sheawill to Ft Worth Pipe | 1 | 138 |  |  | • Reconductor/Rebuild Lewis Creek – Sheawill – Fort Worth Pipe 138 kV and upgrade terminal equipment to achieve a minimum through path rating of 1300 Amps | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23374 | 2018-01-30 | LNrb | 2021-06-01 | Goree | Rivtrin | 1 | 138 |  |  | • Rebuild Goree - Rivtrin 138 kV line section and upgrade terminal equipment to achieve a minimum through path rating of 1200 Amps | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23373 | 2018-01-30 | LNrb | 2021-06-01 | Lewis Creek | Goree | 1 | 138 |  |  | • Rebuild Lewis Creek – Goree 138 kV line section and upgrade terminal equipment to achieve a minimum through path rating of 1300 Amps | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 14745 | 2018-10-03 | 18-ETI-018 | 23372 | 2018-01-30 | BUS | 2021-06-01 | Porter |  |  | 230 |  |  | Construct a 230 kV ring bus at Porter | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 15025 | 2018-05-22 |  | 23422 | 2018-04-25 | SwSta | 2019-04-15 | Gibbs |  |  | 138 |  |  | Main and Transfer Bus | TX |  |  | Planned | 5000000 | Budgetary |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-TX | 15025 | 2018-05-22 |  | 23424 | 2018-04-25 | SUB | 2019-01-15 | Gibbs |  | 1 | 138 | 26.4 |  | New distribution station | TX |  |  | Planned | 2750500 | Budgetary |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-TX | 15025 | 2018-05-22 |  | 23423 | 2018-04-25 | LN | 2019-04-15 | Gibbs |  | 1 | 138 |  |  | New (In and Out) transmission line between the new Gibbs Switching Station to Bishop - Cedar Entergy transmission line. | TX |  | 0.28 | Planned | 600000 | Budgetary |  | N | N | N | Y
A in MTEP18 | A | South | Entergy-TX | 15105 | 2018-05-10 | 18-ETI-021 | 23444 | 2018-09-26 | CB | 2020-06-01 | Dobbin |  |  | 138 |  |  | Install 2 138kV line breakers at the Dobbin 138 kV substation by the summer of 2020. | TX |  |  | Proposed | 1700136 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 15106 | 2018-05-10 | 18-ETI-019 | 23445 | 2018-09-26 | LNrc | 2020-06-01 | Fish Creek | Ponderosa |  | 138 |  |  | Reconductor the Fish Creek to Ponderosa 138kV transmission line using a minimum of 882 Amperes conductor. Upgrade all equipment to achieve a minimum through path rating of 882A on the Fish Creek to Ponderosa 138 kV line section. | TX |  |  | Proposed | 5549331 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 15331 | 2018-07-23 |  | 23523 | 2018-08-17 | LN | 2019-10-31 | STRYKER |  |  | 138 |  |  | New (In and Out) transmission line between the new Stryker Substation to L-93 Corrigan and Camden | TX |  | 0.4 | Planned | 580800 | Planning |  | N | N | N
A in MTEP18 | A | South | Entergy-TX | 15331 | 2018-07-23 |  | 23524 | 2018-08-17 | SUB | 2019-10-31 | STRYKER |  | 1 | 138 | 6.9 |  | 138kV in/out substation with one 138-6.9kV, 25 MVA SHECO step down transformer for TransCanada Pipeline’s pumping station. | TX |  |  | Planned | 2980000 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 8920 | 2017-09-12 | 20477 | 20786 | 2018-08-22 | SUB | 2020-10-31 | Elisha |  |  | 115 | 34.5 |  | New Elisha 115/34.5 kV substation using Hubbard transformer | MN |  |  | Proposed | 3252035 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | GRE | 8920 | 2017-09-12 | 20477 | 20789 | 2018-08-22 | LN | 2020-10-31 | Elisha | Potato Lake Tap | 1 | 115 |  |  | Build new 2 mile 115 kV line from Elisha to Potato Lake Tap 115 kV line | MN |  | 2 | Proposed | 1310000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | GRE | 8920 | 2017-09-12 | 20477 | 20788 | 2018-08-22 | LN | 2020-10-31 | Elisha | Pine Point | 1 | 34.5 | 34.5 | 190 | Build 69 kV line operated at 34.5 kV from Elisha to Pine Point | MN |  | 12 | Proposed | 4870001 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | GRE | 9200 | 2018-05-24 | 203613 | 20831 | 2018-08-22 | LN | 2019-10-19 | Potato Lake Tap | Arago | 1 | 115 |  |  | Build ~5.5 miles of 115 kV transmission line from Potato Lake tap to Arago distribution substation. | MN |  | 5.5 | Proposed | 5800000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | GRE | 9201 | 2018-05-24 | 203610 | 20832 | 2018-08-22 | LN | 2019-10-01 | Bull Moose tap | Backus Pumping Station | 1 | 115 |  |  | Build 115 kV line from a new interconnection to the MP's 115 kV #142 line (Badoura - Pine River) to the Backus Pump Station. | MN |  | 2.4 | Proposed | 2600000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | GRE | 9202 | 2018-08-22 | 203611 | 23526 | 2018-09-14 | Dist | 2019-10-01 | Swatara |  |  | 230 |  |  | The Swatara 230 kV (X3A) Project includes the development of a new, 230 kV tap substation to be called Swatara, interconnecting to the existing Minnesota Power (MP) Riverton – Blackberry 230 kV Line (92 Line). The Swatara tap will source an Enbridge pumping station via 230/6.6 kV transformer as part of their Line 3 Replacement Project and will be located at the intersection of the 92 Line and MP’s +/- 250 kV DC Line. As part of the project, an additional 230 kV “92L” breaker will be required at the Riverton Substation to facilitate operation of the Swatara tap switches. | MN |  |  | Proposed | 1399370 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 9203 | 2018-09-13 | 203612 | 20834 | 2018-09-14 | LN | 2019-10-01 | Gowan Pumping Station | Gowan Pumping Station Tap | 1 | 115 |  |  | Build 0.2 miles of 115 kV transmission line to the Gowan Pumping Station. | MN |  | 0.2 | Proposed | 943332 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | GRE | 12206 | 2018-05-28 | 205965 | 22592 | 2018-05-30 | CAP | 2018-01-23 | Benson |  |  | 115 |  |  | The Benson 14.4 MVAr capacitor bank is needed to provide voltage support to the 115 kV system for a P3 scenario, i.e. when Benson Power generation is unavailable during a contingency in the 115 kV system between Morris and Hancock. | MN |  |  | M5_In Service | 582643.02 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 12211 | 2018-04-03 | 204611 | 23112 | 2018-05-29 | LNrb | 2020-05-01 | Lebanon Hills | Lebanon Hills Tap | 1 | 115 |  |  | Construct a new 1.3 mile 115 kV double circuit line from Lebanon Hills Tap to Lebanon Hills distribution substation on existing ROW. | MN |  | 1.3 | Planned | 2900274.96 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 13464 | 2017-09-12 | 203796 | 22625 | 2018-08-22 | Dist | 2019-12-19 | Brooks Lake |  |  | 115 |  |  | Construct 0.2 mile, in/out, 115 kV line from NSP’s Big Swan to Crow River 115 kV line with 795 ACSS conductor to interconnect WHECA’s Brooks Lake distribution substation. GRE will construct the high side, and install two 2000A, 115 kV load break switches and metering equipment at WHECAA’s Brooks Lake substation. | MN |  | 0.2 | Proposed | 650000 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 13484 | 2017-08-17 | Two Harbors 115 kV Project | 23754 | 2018-09-11 | LN | 2019-10-31 | Big Rock | Waldo | 1 | 115 |  |  | Build a new 115 kV line from the MP Big Rock substation to the GRE Waldo substation | MN | 0 | 0.1 | Planned | 413616 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 13851 | 2018-08-22 | 206050 | 23066 | 2018-08-22 | LN | 2022-12-31 | Hawick | Prairie Woods | 1 | 69 |  |  | Build 4 miles of 69 kV transmission line from Prairie Woods distribution substation to the HE line road move project. Retire 7 miles of existing 69 kV 1/0 conductor transmission line from the Prairie Woods tap to the HE line road move project. Project schedule determined by MNDOT road move schedule. | MN |  | 4 | Planned | 2832190 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 13851 | 2018-08-22 | 206050 | 23068 | 2018-08-22 | LNrl | 2022-12-31 | Hawick | Prairie Woods | 1 | 69 |  |  | Relocate 2.5 miles of 69 kV transmission line to accommodate the Highway 23 road move. Project schedule determined by MNDOT road move schedule. | MN | 2 |  | Planned | 437526.97 | Planning |  | N | N | N
A in MTEP18 | A | West | GRE | 16304 | 2018-10-18 |  | 24286 | 2018-10-18 | CAP | 2019-06-30 | Winnebago |  |  | 69 |  |  | 8 Mvar shunt reactive device | MN |  |  | Planned | 1400000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | Central | IPL | 13608 | 2017-08-29 |  | 22998 | 2017-09-13 | CB | 2020-12-31 | Southeast |  | 19 | 138 |  |  | 138kV breaker | IN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | Central | IPL | 13924 | 2017-09-13 |  | 22999 | 2017-09-13 | LINE | 2019-01-01 | East | Ford |  | 138 |  |  | Line retirement | IN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | Central | IPL | 16228 | 2018-10-05 |  | 24245 | 2018-10-05 | TEQ | 2021-06-01 | Gibson | Petersburg |  | 345 |  |  | Terminal equipment (switches, breakers, relays, bus work) |  | IN |  | Planned | 4300000 |  |  | N | Y | N | Y
A in MTEP18 | A | West | ITCM | 13752 | 2017-12-04 | SndSpring-Hopkinton Retire | 22821 | 2017-09-07 | Remove | 2020-12-01 | Sand Springs | Hopkinton | 1 | 34 | 34 | N/A | Retire the 34kV line that is no longer needed. | IA |  |  | Planned | 780000 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 13877 | 2017-12-04 | Cust Interconnect Blanket | 22941 | 2017-09-12 | LN | 2021-12-31 | Blanket for Customer Interconnections under $1 million for 2021 | Throughout system |  | 345 | 69 |  | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL |  |  | Planned | 2400000 | Planning |  | N | N | N
A in MTEP18 | A | West | ITCM | 13879 | 2017-12-04 | ITCM Asset Blanket | 22942 | 2017-09-12 | LN | 2021-12-31 | ITCM Asset Blanket for 2021 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL |  |  | Planned | 37080000 | Planning |  | N | N | N
A in MTEP18 | A | West | ITCM | 13889 | 2017-12-04 | Ottumwa East Substation | 22959 | 2017-11-17 | SUB | 2019-12-31 | Ottumwa East | Substation |  | 161 | 161 |  | Construct a new Ottumwa East 161/25kV substation. | IA |  |  | Planned | 968183 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 13889 | 2017-12-04 | Ottumwa East Substation | 23330 | 2017-11-17 | LN | 2019-12-31 | Ottumwa East | Woody | 2 | 161 | 161 |  | Line taps for new Ottumwa East substation. | IA |  |  | Planned | 459600 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 13889 | 2017-12-04 | Ottumwa East Substation | 22960 | 2017-11-17 | LN | 2019-12-31 | Ottumwa East | Woody | 1 | 161 | 161 |  | Construct 161kV line taps to feed the new Ottumwa East substation from the Woody breaker and a half substation. | IA |  |  | Planned | 458400 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 13891 | 2017-12-04 | Columbus Junction 14MVAR Cap | 22961 | 2018-08-21 | CAP | 2019-05-01 | Columbus Junction | Substation |  | 69 | 69 | 14 MVAR | Install a new 14MVAR capacitor with synchronous breaker at the Columbus Junction substation. This will require rebuilding the single box structure to two single box structures and a new control building and expanding the substation. The two single box structures will allow for future expansion of the substation to allow for two distribution transformers. | IA |  |  | Planned | 2542407 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | ITCM | 13893 | 2017-12-04 | Osage Junction 69kV 7MVAR Capacitor | 22964 | 2017-11-17 | CAP | 2019-05-01 | Osage Junction | Substation |  | 69 | 69 | 7 MVAR | Install a 7MVAR capacitor and synchronous breaker at the Osage Junction substation. | IA |  |  | Planned | 654900 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14024 | 2017-12-04 | J041 | 23126 | 2017-09-15 | SUB | 2019-09-01 | Wellsburg | Substation |  | 161 | 161 |  | Rebuild Wellsburg to a breaker and one-half configuration | IA |  |  | Planned | 6806020 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14024 | 2017-12-04 | J041 | 23129 | 2017-09-15 | TEQ | 2019-09-01 | Newton | Maytag | 1 | 69 | 69 | 86 MVA | 69 kV terminal Upgrade at Newton - replace switches and bus conductor | IA |  |  | Planned | 56100 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14024 | 2017-12-04 | J041 | 23128 | 2017-09-15 | LN | 2019-09-01 | Wellsburg | Iowa Falls Industrial & Marshalltown |  | 161 | 161 |  | Relocate 161 kV double circuited line south of Wellsburg to allow for construction of the breaker and 1/2 station | IA |  |  | Planned | 420000 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14024 | 2017-12-04 | J041 | 23127 | 2017-09-15 | SUB | 2019-09-01 | Wellsburg | Substation |  | 161 | 161 |  | Equipment dedicated to J041 terminal at Wellsburg - deadend, CCVTs etc (TOIF) | IA |  |  | Planned | 469504 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14025 | 2017-12-04 | J438 FCA | 23130 | 2017-09-15 | TX | 2018-12-14 | Powesheik | Transformer |  | 161 | 69 | 96 MVA | Replace Poweshiek 161/69 kV transformer with 150 MVA unit | IA |  |  | Planned | 2386020 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14030 | 2017-12-04 | J407 | 23145 | 2017-09-15 | SUB | 2020-08-07 | Glenworth | Substation |  | 161 | 161 |  | Expand 161 kV bus at Glenworth by adding a breaker to the ring bus | MN |  |  | Planned | 477461 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14030 | 2017-12-04 | J407 | 23147 | 2017-09-15 | TX | 2020-08-07 | Glenworth | Transformer | 1 | 161 | 69 | 150 MVA | Replace the Glenworth 161/69 kV transformer with a 150 MVA unit | MN |  |  | Planned | 2518350 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14030 | 2017-12-04 | J407 | 23146 | 2018-08-21 | SUB | 2020-08-07 | Glenworth | Substation |  | 161 | 161 |  | Equipment dedicated to J407 terminal at Glenworth - deadend, CCVTs etc (TOIF) | MN |  |  | Planned | 387904 | Engineering |  | N | N | N
A in MTEP18 | A | West | ITCM | 14032 | 2018-10-03 | J449 | 23150 | 2018-10-03 | TEQ | 2018-09-01 | Mitchell County | Substation |  | 345 | 345 |  | Change relay settings at Mitchell County to allow for a 345 kV interconnection through common, existing TOIF of project G172. A 3 breaker ring will connect J449 and G172 to Mitchell County | IA |  |  | Planned | 60000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 4515 | 2018-04-30 | ITC_14_021 | 8646 | 2017-11-28 | LNrb | 2020-12-31 | Quaker | Sunset | 1 | 120 |  |  | Rebuild the 1431 ACSR sections (approximately 0.265 mile) to 1431 ACSR X2. | MI | 0.27 |  | Proposed | 1212000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | East | ITCT | 4515 | 2018-04-30 | ITC_14_021 | 22889 | 2017-11-28 | TEQ | 2020-12-31 | Sunset |  |  | 120 |  |  | Upgrade station equipment at Sunset 120 kV position "HN" to at least 560 MVA (2694 Amp) summer emergency. | MI |  |  | Proposed | 109000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 4515 | 2018-04-30 | ITC_14_021 | 22888 | 2017-11-28 | TEQ | 2020-12-31 | Quaker |  |  | 120 |  |  | Upgrade station equipment at Quaker 120 kV position "HD" to at least 560 MVA (2694 Amp) summer emergency. | MI |  |  | Proposed | 169000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13326 | 2018-08-03 |  | 22604 | 2017-06-27 | RLY | 2020-12-31 | Waterman |  |  | 230 | 120 |  | Replace ITCT relaying and controls at Waterman Substation. Locate the new relaying and controls in a new dedicated ITCT control center. Install dedicated ITCT AC and DC systems. | MI |  |  | Proposed | 3300000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13646 | 2018-08-07 |  | 22735 | 2017-11-01 | SUB | 2019-12-20 | MIDAS |  |  | 120 |  |  | Construct new 120kV Midas station. Station will be an in and out station with 2 line breakers and a section breaker fed. Station will serve 11.1 MW of relocated from DTE Almont station. | MI |  |  | Planned | 2900000 | Planning |  | N | N | N
A in MTEP18 | A | East | ITCT | 13646 | 2018-08-07 |  | 22738 | 2017-11-01 | SUBmisc | 2019-12-20 | Wabash |  |  | 120 |  |  | Replace Relays, CCVTs, and wavetraps at Wabash position HG. | MI |  |  | Planned | 350000 | Planning |  | N | N | N
A in MTEP18 | A | East | ITCT | 13646 | 2018-08-07 |  | 22737 | 2017-11-01 | SUBmisc | 2019-12-20 | Robin |  |  | 120 |  |  | Replace Relays, CCVTs, and Wavetraps at Robin position HD | MI |  |  | Planned | 350000 | Planning |  | N | N | N
A in MTEP18 | A | East | ITCT | 13646 | 2018-08-07 |  | 22736 | 2018-05-09 | LN | 2019-12-20 | Robin | Wabash | 1 | 120 |  |  | Cut in the Robin - Wabash 120kV line to fed Midas Station | MI |  | 0.25 | Planned | 980000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13804 | 2018-04-30 | ITC_17_019 | 22866 | 2017-11-21 | LNup | 2020-06-01 | Adams | Burns2 Tap | 1 | 120 |  |  | Remediate the sag limit on the Adams – Burns2 120 kV section to the conductor summer emergency rating of 314 MVA (1512 Amp). | MI |  |  | Proposed | 222000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13805 | 2018-04-30 | ITC_17_030 | 22867 | 2017-11-21 | TEQ | 2020-06-01 | St. Clair |  |  | 345 |  |  | Upgrade the station equipment at St. Clair to a minimum rating of 2200 MVA (3682 Amp) summer emergency. | MI |  |  | Proposed | 274000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13806 | 2018-04-30 | ITC_17_020 | 22868 | 2017-11-28 | LNup | 2020-06-01 | Bismarck | Jewell | 1 | 345 |  |  | Raise the sag limit on the Bismarck – Jewell 345 kV line to at least 1661 MVA (2780 Amp). | MI |  |  | Proposed | 340000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13807 | 2018-04-30 | ITC_17_021 | 22870 | 2017-11-28 | LNup | 2020-06-01 | Northeast | Stephens | 1 | 230 |  |  | Raise the Sag Limit on the Northeast – Stephens 230 kV line to at least 700 MVA (1757 Amp) summer emergency. | MI |  |  | Proposed | 370000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13809 | 2018-04-30 | ITC_17_022 | 22872 | 2017-11-21 | TEQ | 2020-06-01 | Stephens |  |  | 345 |  |  | Upgrade station equipment at Stephens 345 kV position DM and DT to at least 1540 MVA (2577 Amp) summer emergency. | MI |  |  | Proposed | 845000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13810 | 2018-04-30 | ITC_17_023 | 22873 | 2017-11-21 | TEQ | 2020-06-01 | Elm |  |  | 120 |  |  | Upgrade station equipment at Elm’s position “HF” to at least 314 MVA (1511 Amp) summer emergency. | MI |  |  | Proposed | 73000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13811 | 2018-04-30 | ITC_17_024 | 22874 | 2017-10-19 | TEQ | 2020-06-01 | Brownstown |  |  | 345 |  |  | Upgrade station equipment at Brownstown 345 kV positions “ET” and “EM” to a minimum of 2000 MVA (3347 Amp) for summer emergency. | MI |  |  | Proposed | 524000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13811 | 2018-04-30 | ITC_17_024 | 22875 | 2017-10-19 | TEQ | 2020-06-01 | Monroe |  |  | 345 |  |  | Upgrade station equipment at Monroe positions “BF” and “BM” to a minimum of 2000 MVA (3347 Amp) for summer emergency. | MI |  |  | Proposed | 552000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13813 | 2018-04-30 | ITC_17_025 | 22877 | 2017-11-21 | TEQ | 2020-06-01 | Monroe |  |  | 345 |  |  | Upgrade station equipment at positions “CT” and “CM” to meet or exceed 1714 MVA (2868 Amp) summer emergency. | MI |  |  | Proposed | 571000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13813 | 2018-04-30 | ITC_17_025 | 22878 | 2017-11-21 | TEQ | 2020-06-01 | Wayne |  |  | 345 |  |  | Upgrade station equipment at positions “EF” and “EM” to meet or exceed 1714 MVA (2868 Amp) summer emergency. | MI |  |  | Proposed | 9000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13814 | 2018-06-20 | ITC_17_026 | 22879 | 2018-06-27 | TEQ | 2018-12-31 | Monroe |  |  | 345 |  |  | Upgrade Monroe 345 kV station equipment so that the summer emergency rating meets or exceeds 2000 MVA (3347 Amp). | MI |  |  | M3_Long Lead Materials | 763000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13815 | 2018-04-30 | ITC_17_027 | 22880 | 2017-11-21 | TEQ | 2020-06-01 | Riverview |  |  | 345 |  |  | Upgrade 120 kV station equipment at Riverview position “HB” to meet or exceed 424 MVA (2040 Amp) summer emergency. | MI |  |  | Proposed | 191000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13816 | 2018-04-30 | ITC_17_028 | 22881 | 2017-10-19 | LNrb | 2020-12-31 | Pioneer | Superior | 1 | 120 |  |  | Rebuild approximately 3.16 miles of 477 ACSR to 954 ACSR from Pioneer to McAuley to Superior utlizing double-circuit, 120 kV towers. Install OPGW on the rebuilt section. | MI | 3.2 |  | Proposed | 4905000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13816 | 2018-04-30 | ITC_17_028 | 23124 | 2017-10-19 | LNrb | 2020-12-31 | Noble | Superior | 1 | 120 |  |  | Rebuild 3.16 miles of 477 ACSR conductor from Noble to Superior 120 kV where the line is on common structures with the Pioneer – Superior 120 kV circuit. Install OPGW on the rebuilt section. | MI | 3.2 |  | Proposed | 0 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13816 | 2018-04-30 | ITC_17_028 | 22882 | 2017-10-19 | TEQ | 2020-12-31 | Superior |  |  | 120 |  |  | Upgrade terminal equipment at Superior to 954 ACSR. | MI |  |  | Proposed | 35000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13817 | 2018-04-30 | ITC_17_029 | 22883 | 2017-11-21 | LNrb | 2020-12-31 | River Rouge | Zug | 1 | 120 |  |  | Rebuild approximately 0.5 mile of 795 ACSR to 954 ACSR on the River Rouge - Zug 120 kV line. | MI | 0.5 |  | Proposed | 468000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13817 | 2018-04-30 | ITC_17_029 | 22884 | 2017-11-21 | TEQ | 2020-12-31 | River Rouge |  |  | 120 |  |  | Upgrade station equipment at River Rouge position JB to at least 371 MVA (1785 Amp). | MI |  |  | Proposed | 113000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13818 | 2018-04-30 | ITC_17_031 | 22885 | 2017-11-21 | TEQ | 2020-06-01 | St. Clair |  |  | 345 |  |  | The proposed solution is to upgrade station equipment at St. Clair 345 kV position “CM” to at least 2000 MVA (3347 Amp) summer emergency. | MI |  |  | Proposed | 360000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13819 | 2018-04-30 | ITC_17_032 | 22886 | 2017-11-21 | TEQ | 2020-06-01 | St. Clair |  |  | 345 |  |  | Upgrade station equipment at St. Clair to at least 1786 MVA (2989 Amp) summer emergency. | MI |  |  | Proposed | 357000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 13819 | 2018-04-30 | ITC_17_032 | 22887 | 2017-11-21 | TEQ | 2020-06-01 | Stephens |  |  | 345 |  |  | Upgrade station equipment at Stephens 345 kV to at least 1786 MVA (2989 Amp) summer emergency. | MI |  |  | Proposed | 357000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14007 | 2018-08-03 | ITC-17-040 | 23123 | 2017-12-04 | LNrb | 2020-06-01 | Enrico Fermi | Toll Road | 1 | 120 |  |  | Rebuild 1.3 miles wood pole circuit from Enrico Fermi to Toll Road 120kV utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on the circuit and replace line entrance at Enrico Fermi. | MI | 1.3 |  | Proposed | 1050000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14007 | 2018-08-03 | ITC-17-040 | 23306 | 2017-12-04 | TEQ | 2020-06-01 | Enrico Fermi |  |  | 120 |  |  | Replace line entrance at Enrico Fermi | MI |  |  | Proposed | 35909 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14007 | 2018-08-03 | ITC-17-040 | 23292 | 2017-12-04 | LNrb | 2020-06-01 | Toll Road | Shoal |  | 120 |  |  | Rebuild 3.7 miles wood pole section of the Toll Road - Shoal 120kV circuit utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on the circuit. | MI | 3.7 |  | Proposed | 4000000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | East | ITCT | 14027 | 2018-08-03 |  | 23134 | 2017-09-15 | Dist | 2021-12-31 | Blanket for Customer Interconnections | Throughout System |  | 120 |  |  | Blanket for customer interconnections and retirements less than $1 million with in service date in the year 2021 | MI |  |  | Proposed | 2000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | ITCT | 14064 | 2018-08-03 |  | 23198 | 2017-09-15 | SUB | 2021-12-31 | 2021 ITCT Asset Replacement Program |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | Planned | 49000000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14068 | 2018-04-30 | ITC_17_036 | 23207 | 2017-10-19 | TEQ | 2020-06-01 | St. Clair |  |  | 120 |  |  | Upgrade station equipment at St. Clair 120 kV position “JE” to at least 314 MVA (1512 Amp) summer emergency. | MI |  |  | Proposed | 123000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14069 | 2018-04-30 | ITC_17_037 | 23208 | 2017-11-21 | TEQ | 2020-06-01 | St. Clair |  |  | 120 |  |  | Upgrade station equipment at position “HF” to at least 417 MVA (2004 Amp). Upgrade station equipment at position “GU” to at least 557 MVA (2680 Amp). Upgrade station equipment at position “JD” to at least 450 MVA (2165 Amp). | MI |  |  | Proposed | 835000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14071 | 2018-04-30 | ITC_17_039 | 23210 | 2017-11-29 | TEQ | 2020-06-01 | Trenton Channel |  |  | 120 |  |  | Upgrade station equipment at positions “HJ”, “IM”, and “IQ” to at least 747 MVA (3594 Amp). | MI |  |  | Proposed | 986000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14284 | 2018-08-03 | ITC_17_044 | 23304 | 2017-12-04 | Remove | 2019-12-31 | Lee |  |  | 120 |  |  | Decommission and remove DVAR capacitor and all related equipment at Lee 120 kV position HJ | MI |  |  | Planned | 360000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14804 | 2018-08-03 | ITC_18_005 | 23385 | 2018-04-05 | LNrl | 2019-09-15 | Waterman | Cato | 1 | 120 |  |  | Relocate ~0.5 mile portions of the Waterman-Cato underground 120kV cable to allow for MDOT installation of sewer drains under I-75. | MI | 0.5 |  | Proposed | 7500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | ITCT | 14804 | 2018-08-03 | ITC_18_005 | 23386 | 2018-04-05 | LNrl | 2019-09-15 | Waterman | St. Antoine | 1 | 120 |  |  | Relocate ~0.5 mile portions of the Waterman St. Antoine underground 120kV cable to allow for MDOT installation of sewer drains under I-75. | MI | 0.5 |  | Proposed | 7500000 |  |  | N | N | N
A in MTEP18 | A | East | ITCT | 15064 | 2018-08-03 | ITC_18_003 | 23430 | 2018-04-27 | SUB | 2019-06-01 | Magneto |  |  | 120 |  |  | Install a new 120 kV Station with 3 breakers | MI |  |  | Planned | 3630000 |  |  | N | N | N
A in MTEP18 | A | East | ITCT | 15064 | 2018-08-03 | ITC_18_003 | 23434 | 2018-04-27 | LINE | 2019-06-01 | Magneto | Southfield |  | 120 |  |  | Cut Quaker - Southfield in to Magneto and install Fiber | MI |  |  | Planned | 830000 |  |  | N | N | N
A in MTEP18 | A | East | ITCT | 15064 | 2018-08-03 | ITC_18_003 | 23433 | 2018-04-27 | LINE | 2019-06-01 | Magneto | Quaker |  | 120 |  |  | Cut in Quaker - Southfield to Magneto and add Fiber | MI |  |  | Planned | 830000 |  |  | N | N | N
A in MTEP18 | A | East | ITCT | 15064 | 2018-08-03 | ITC_18_003 | 23432 | 2018-04-27 | RLY | 2019-06-01 | Southfield |  |  | 120 |  |  | Install relay upgrades at Southfield Substation | MI |  |  | Planned | 170000 |  |  | N | N | N
A in MTEP18 | A | East | ITCT | 15064 | 2018-08-03 | ITC_18_003 | 23431 | 2018-04-27 | RLY | 2019-06-01 | Quaker |  |  | 120 |  |  | Install relay upgrades at Quaker 120 kV Substation | MI |  |  | Planned | 200000 |  |  | N | N | N
A in MTEP18 | A | South | LAFA | 13445 | 2017-12-04 |  | 22622 | 2017-11-15 | RLY | 2018-12-31 | Bonin 138 kV |  |  | 138 |  |  | Addition of redundant relays for bus differential protection to the Bonin 138 kV station. | LA |  |  | Proposed | 83333 |  |  | N | N | N
A in MTEP18 | A | South | LAFA | 13445 | 2017-12-04 |  | 22624 | 2017-11-15 | RLY | 2018-12-31 | Labbe 230 kV |  |  | 230 |  |  | Addition of redundant relays for bus differential protection to the Labbe 230 kV station. | LA |  |  | Proposed | 83333 |  |  | N | N | N
A in MTEP18 | A | South | LAFA | 13445 | 2017-12-04 |  | 22623 | 2017-11-15 | RLY | 2018-12-31 | Bonin 230 kV |  |  | 230 |  |  | Addition of redundant relays for bus differential protection to the Bonin 230 kV station. | LA |  |  | Proposed | 83333 |  |  | N | N | N
A in MTEP18 | A | West | MDU | 13869 | 2018-03-28 |  | 22936 | 2017-09-12 | SUB | 2019-12-31 | Stanley |  |  | 115 | 69 |  | 115 kV three breaker ring bus and 115/69 kV transformer | ND |  |  | Planned | 4720000 | Budgetary |  | N | N | N
A in MTEP18 | A | West | MEC | 2937 | 2017-09-12 | G0103 | 5112 | 2017-12-06 | TX | 2019-12-01 | Sub 39 | Transformer | 2 | 345 | 161 | 560 | Add 2nd 345-161 kV xfmr | IL |  |  | Proposed | 11600000 | Planning |  | N | N | N | Y
A in MTEP18 | A | West | MEC | 2937 | 2017-09-12 | G0103 | 23494 | 2018-06-18 | LNrl | 2018-12-01 | Sub 39 | MEC Cordova | 1 | 345 | 345 | 1471 | Re-route a portion of the existing Sub 39-Cordova 345 kV line going into Sub 39 to connect to a new substation terminal position, associated with the addition of the second 345-161 kV transformer at Sub 39. | IL |  | 0.1 | Proposed | 975000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13833 | 2018-01-23 | T90E1 | 22906 | 2018-01-23 | IND | 2018-03-31 | Council Bluffs Energy Center |  |  | 13.8 |  | 50 MVAr total | Remove/retire two 25 MVAr 13 kV reactors | IA |  |  | Planned | 100000 | Budgetary |  | N | N | N
A in MTEP18 | A | West | MEC | 13834 | 2017-12-04 |  | 22907 | 2017-09-08 | CB | 2018-12-31 | Sycamore |  |  | 69 |  |  | Replace six circuit breakers with breakers having higher fault current interrupting capability. | IA |  |  | Planned | 1936000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13835 | 2017-12-04 |  | 22908 | 2017-09-08 | TEQ | 2019-12-31 | 109th & Clark |  |  | 161 |  |  | Replace existing 161 kV transformer high side circuit switcher with a 40 kA circuit switcher. | IA |  |  | Planned | 452000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13836 | 2017-10-31 |  | 22909 | 2017-12-06 | CB | 2018-12-31 | Sub K Tiffin |  |  | 345 |  |  | Add a new 345 kV circuit breaker on the terminal for the line to Duane Arnold Energy Center. | IA |  |  | Planned | 1800000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13837 | 2017-12-04 |  | 22910 | 2017-09-12 | LN | 2020-06-01 | Sub A | Sub 39 | 2 | 161 |  | 410 | Construct a second 161 kV line from Sub A to Sub 39. | IL,IA |  | 5.8 | Planned | 3700000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13838 | 2017-12-04 |  | 22911 | 2017-09-12 | CB | 2019-06-01 | Sub 18 |  |  | 161 |  |  | 161 kV network additions required to accommodate a third 161-69 kV transformer at Sub 18. | IL |  |  | Planned | 500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13839 | 2017-12-04 |  | 22912 | 2017-09-08 | CB | 2018-12-01 | Sub 18 |  |  | 69 |  | 40 kA | Replace Sub 18 69 kV circuit breaker with a breaker having a 40 kA interrupting rating. | IL |  |  | Planned | 220000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13840 | 2017-12-04 |  | 22913 | 2018-08-20 | CAP | 2019-06-01 | Sub 18 |  |  | 69 |  | 20 MVAr | Add a new 69 kV capacitor bank. | IL |  |  | Planned | 950000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13901 | 2018-08-20 |  | 22978 | 2018-01-26 | SUB | 2020-03-01 | Raccoon Trail |  |  | 345 | 25 |  | 345-25 kV distribution substation | IA |  |  | Planned | 47000000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 13901 | 2018-08-20 |  | 22979 | 2017-09-15 | TAP | 2020-03-01 | Raccoon Trail |  |  | 345 |  |  | Four new 345 kV line taps into the Raccoon Valley Substation from the existing Booneville-Grimes and Fallow Avenue-Grimes lines. | IA |  |  | Planned | 2620000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14108 | 2017-12-04 |  | 23259 | 2017-09-18 | SUB | 2020-06-01 | Lehman Avenue |  |  | 161 | 13.8 | 33 | 161-13 kV distribution substation with 33 MVA transformer and line circuit breakers. | IA |  |  | Planned | 1900000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14625 | 2018-08-15 |  | 23341 | 2018-08-15 | BUS | 2018-07-01 | Montezuma |  |  | 345 |  |  | Expand 345 kV ring bus at Montezuma Substation for J475/J555. | IA |  |  | Planned | 2750000 | GIA |  | N | Y | Y
A in MTEP18 | A | West | MEC | 14626 | 2018-08-15 |  | 23342 | 2018-08-15 | SwSta | 2018-12-15 | Deep River |  |  | 161 |  |  | 161 kV, three breaker ring bus substation tapped off the Parnell-Poweshiek 161 kV line called Deep River Sub for J438 | IA |  |  | Planned | 4400000 | GIA |  | N | N | N
A in MTEP18 | A | West | MEC | 14626 | 2018-08-15 |  | 23343 | 2018-01-02 | TAP | 2018-12-15 | Deep River |  |  | 161 |  |  | 161 kV line taps for Deep River Sub for J438 | IA |  |  | Planned | 400000 | GIA |  | N | N | N
A in MTEP18 | A | West | MEC | 14664 | 2018-08-15 |  | 23345 | 2018-02-06 | LNrb | 2018-12-01 | Clarksville | Waverly West Tap | 1 | 69 |  | 87 | Replace existing conductor with T-2 4/0 ACSR and replace existing poles. | IA | 7.4 |  | Planned | 3477000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23346 | 2018-09-07 | CB | 2018-06-01 | Montezuma |  |  | 345 |  | 3,000 A | Replace existing circuit breakers DBM901 and DBM903 due to age and condition issues, add motor-operated disconnect switches, replace lightning surge arresters and upgrade security fencing. | IA |  |  | Planned | 1870000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23681 | 2018-09-07 | CB | 2019-12-01 | Madison County |  |  | 345 |  | 3000 | Add two new 345 kV circuit breakers and complete a 345 kV ring bus. Eliminates three-terminal line from Booneville – Norwalk – Rolling Hills/Orient to prevent relay mis-operations | IA |  |  | Planned | 5400000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23352 | 2018-09-07 | CB | 2020-12-01 | Various |  |  | 345 | 161 |  | Add and/or replace 345 kV and 161 kV circuit breakers at various locations to increase reliability and operational flexibility. | IA |  |  | Planned | 3100000 | Budgetary |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23351 | 2018-09-07 | CB | 2019-12-01 | Various |  |  | 345 |  |  | Add and/or replace 345 kV and 161 kV circuit breakers at various locations to increase reliability and operational flexibility. Projects to be completed in 2019. | IA |  |  | Planned | 3100000 | Budgetary |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23350 | 2018-09-07 | CB | 2018-12-01 | Waterloo West |  |  | 161 |  | 2,000A | Add one new 161 kV circuit breaker at Waterloo West Substation facing Deere Foundry Substation. | IA |  |  | Planned | 1000000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23349 | 2018-09-07 | CB | 2018-12-01 | Sub J |  |  | 161 |  | 2000A | Add two new 161 kV circuit breakers on the 161 kV line terminals at Sub J to provide increased system reliability and operational flexibility. | IA |  |  | Planned | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23348 | 2018-09-07 | CB | 2018-12-01 | Greenfield Plaza |  |  | 161 |  |  | Add two new 161 kV circuit breakers at Greenfield Plaza Substation to protect the two existing 161-13 kV transformers from line faults. | IA |  |  | Planned | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14665 | 2018-09-07 |  | 23347 | 2018-09-07 | CB | 2018-12-01 | Bondurant |  |  | 345 |  | 3000 | Add three new 345 kV circuit breakers at the Bondurant Substation to eliminate the existing 3-terminal line from Sycamore to Bondurant to Greater Des Moines Energy Center. This will create a four-breaker ring bus. | IA |  |  | Planned | 3500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14666 | 2018-08-15 |  | 23353 | 2018-01-17 | SUB | 2018-12-01 | Ackley |  |  | 161 | 12.5 |  | New Ackley 161-12.5 kV distribution substation with two new 161 kV line circuit breakers. | IA |  |  | Planned | 2114000 | Planning |  | N | N | N
A in MTEP18 | A | West | MEC | 14985 | 2018-05-29 |  | 23415 | 2018-04-18 | TEQ | 2016-04-08 | Franklin |  |  | 161 |  | 2000 | Replace 800A 161 kV switches 9910L and 9210L at Franklin Substation with 2,000 Amp switches. | IA |  |  | M5_In Service | 75293 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | MEC | 15404 | 2018-08-13 |  | 23531 | 2018-08-07 | TX | 2018-08-22 | Sub 91 |  |  | 345 | 161 | 500 | Replace the failed 500 MVA 345/161 kV transformer with a 560 MVA spare unit. | IA |  |  | Planned | 4500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 3135 | 2017-09-14 | METC_17_046 | 5512 | 2017-12-01 | LN | 2021-12-31 | Airport | Long Rapids | 2 | 138 |  |  | From Long Rapids to Str. #103G100 (~6.3 miles), replace the existing single-circuit structures with new double-circuit structures and install new conductor on one side which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). Reinstall the existing 477 ACSR conductor of the Airport - Long Rapids 1 138 kV line on the other side of the new double-circuit structures. Utilize the existing assets of the Airport – Mio 138 kV line from Str. #103A7743 to the Airport station’s new location in the construction of the new Airport – Long Rapids 2 138 kV line. Install new OPGW as well. | MI |  | 6.3 | Proposed | 12000000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | East | METC | 3135 | 2017-09-14 | METC_17_046 | 23089 | 2017-12-01 | TEQ | 2021-12-31 | Long Rapids |  |  | 138 |  |  | Install the station equipment necessary to terminate the new Airport - Long Rapids 2 138 kV line at the new Long Rapids station. | MI |  |  | Proposed | 1500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 3135 | 2017-09-14 | METC_17_046 | 23088 | 2017-12-01 | LN | 2021-12-31 | Airport | Mio | 1 | 138 |  |  | Acquire new ROW and construct new transmission assets for the Airport – Mio 138 kV line utilizing single-circuit structures heading north from Str. #103A7707 to the Airport station’s new location (~2.6 miles). Install new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). | MI |  | 2.6 | Proposed | 4000000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 3921 | 2018-06-11 | METC-17-054 | 7482 | 2018-05-17 | LN | 2021-12-31 | Campbell | Tyler | 1 | 345 |  |  | Build a new 4-mile, 345 kV line from Campbell to Tyler substation. | MI |  | 4 | Proposed | 9617000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | East | METC | 3921 | 2018-06-11 | METC-17-054 | 7483 | 2018-05-17 | SUB | 2021-12-31 | Tyler |  | 1 | 345 | 138 |  | Install a new 345/138 kV transformer at Tyler and new line terminating equipment and protection devices at both Campbell and Tyler stations. | MI |  |  | Proposed | 12911000 | Engineering |  | N | N | N | Y
A in MTEP18 | A | East | METC | 13324 | 2017-06-27 |  | 22602 | 2017-06-27 | RLY | 2019-12-31 | Claremont |  |  | 138 |  |  | Replace Claremont Controls and Relaying | MI |  |  | Proposed | 3300000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13325 | 2017-06-27 |  | 22603 | 2017-06-27 | RLY | 2019-12-31 | Dort |  |  | 138 |  |  | Replace METC relaying and controls at Dort Substation. Locate the new relaying and controls in a single dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | Proposed | 3300000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13327 | 2017-06-27 |  | 22605 | 2017-06-27 | RLY | 2020-12-31 | Beecher |  |  | 138 |  |  | Replace METC relaying and controls at Beecher Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | Proposed | 3300000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13329 | 2017-09-22 |  | 22607 | 2017-06-27 | RLY | 2021-12-31 | Wealthy |  |  | 138 |  |  | Replace METC relaying and controls at Wealthy Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | Proposed | 3300000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13685 | 2017-09-12 | METC-17-031 | 22756 | 2017-11-03 | CB | 2020-06-01 | Gaines |  |  | 138 |  |  | The proposed solution is to replace breakers at the Gaines 138kV station (pos. 9M9 and 13B7). | MI |  |  | Proposed | 700000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13685 | 2017-09-12 | METC-17-031 | 22757 | 2017-12-04 | TEQ | 2020-06-01 | Gaines |  |  | 138 |  |  | Increase CTs ratio so that the CTs have a minimum summer emergency rating of 647 MVA/2706 Amps (summer emergency). | MI |  |  | Proposed | 18000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13687 | 2017-09-12 | METC-17-033 | 22760 | 2017-12-04 | RLY | 2020-06-01 | Morrow |  |  | 138 |  |  | The proposed solution is to upgrade the relay equipment at Morrow position “500” to meet or exceed 338 MVA/1413 Amps (summer emergency). | MI |  |  | Proposed | 15500 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13687 | 2017-09-12 | METC-17-033 | 22761 | 2017-12-04 | TEQ | 2020-06-01 | Morrow |  |  | 138 |  |  | The proposed solution is to upgrade the terminal equipment at Morrow position “500” to meet or exceed 338 MVA/1413 Amps (summer emergency). | MI |  |  | Proposed | 15500 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13688 | 2017-09-15 | METC-17-034 | 22762 | 2017-12-04 | LNrb | 2020-06-01 | Battle Creek | Verona | 1 | 138 |  |  | Rebuild approximately 3.35 miles of 795 ACSR from Battle Creek-Verona #1 138kV circuit using 1431 ACSR on new future double circuit structures constructed to 230kV standards operated at 138kV. The remaining 0.74 miles of the 4.09 mile circuit already has 1431 ACSR installed and does not need replacement. The other side from structure #088X22006 to Verona will be left vacant and available for a potential future circuit. No changes on the remaining 0.74 mile section that currently has another 138kV circuit on it. Install OPGW along the entire length of the line (~4.09 miles) from Battle Creek to Verona. | MI | 4.09 |  | Proposed | 6554000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13870 | 2018-01-08 | METC_17_035 | 22937 | 2017-11-28 | LNup | 2020-12-31 | Bauer | Hampton | 1 | 345 |  |  | Remediate the sag limit on the Bauer - Hampton 1 345 kV line to a minimum of 1179 MVA/1973 Amps. | MI |  |  | Proposed | 365000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13871 | 2017-09-13 | METC_17_042 | 22938 | 2017-11-01 | LNup | 2021-12-31 | Alpena | Rockport | 1 | 138 |  |  | Remediate the sag limit on the Alpena - Rockport 138 kV line to a minimum of 145 MVA/607 Amps. | MI |  |  | Proposed | 250000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13872 | 2017-09-12 | METC_17_038 | 22939 | 2017-11-01 | LNrb | 2021-12-31 | Vanderbilt | Riggsville | 1 | 138 |  |  | Rebuild the Riggsville – Vanderbilt 138 kV portion (~30.4 miles) of the Livingston – Riggsville 138 kV line (~40.1 miles) utilizing 230 kV double circuit construction. Replace the existing assets (all structures, 266 ACSR conductor, and 266 ACSR line entrances at Rondo and Riggsville) with new double-circuit structures that are designed for 954 ACSR conductor on each side and install this conductor along with OPGW for the existing line only. | MI | 30.4 |  | Proposed | 41979000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13872 | 2017-09-12 | METC_17_038 | 23323 | 2017-11-01 | TEQ | 2021-12-31 | Riggsville |  |  | 138 |  |  | At Riggsville, replace the Livingston line entrance conductor. | MI |  |  | Proposed | 21000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13873 | 2018-01-08 | METC_17_036 | 22940 | 2017-11-01 | TEQ | 2020-12-31 | MCV |  |  | 345 |  |  | Replace station equipment at MCV to increase the line's summer emergency rating to 1687 MVA (2823 Amps). | MI |  |  | Proposed | 50000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13873 | 2018-01-08 | METC_17_036 | 22946 | 2017-11-01 | TEQ | 2020-12-31 | Tittabawassee |  |  | 345 |  |  | Replace station equipment at Tittabawassee to increase the line's summer emergency rating to 1687 MVA (2823 Amps). | MI |  |  | Proposed | 800000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13878 | 2018-01-08 | METC_17_037 | 22943 | 2017-11-29 | LNup | 2020-12-31 | MCV | Tittabawassee | 2 | 345 |  |  | Remediate the sag limit on the entire ~2.4 mile-long length of 2156 ACSR conductor of the MCV – Tittabawassee 2 345 kV line to at least the planned target summer emergency rating of 1687 MVA (2823 Amps). | MI |  |  | Proposed | 30000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13878 | 2018-01-08 | METC_17_037 | 22945 | 2017-11-29 | TEQ | 2020-12-31 | Tittabawassee |  |  | 345 |  |  | Replace station equipment at Tittabawassee to achieve at least the planned target summer emergency rating of 1687 MVA (2823 Amps). | MI |  |  | Proposed | 810000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13878 | 2018-01-08 | METC_17_037 | 22944 | 2017-11-29 | TEQ | 2020-12-31 | MCV |  |  | 345 |  |  | Replace station equipment at MCV to achieve at least the planned target summer emergency rating of 1687 MVA (2823 Amps). | MI |  |  | Proposed | 60000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13934 | 2018-01-08 | METC_17_048 | 23013 | 2017-12-04 | SUB | 2021-12-31 | Pere Marquette |  |  | 345 | 138 |  | Construct a 345 kV switchyard at Pere Marquette and terminate the following facilities at it: the Ludington - Pere Marquette 345 kV line, the existing 345/138 kV Transformer #2, and the new 345/138 kV Transformer #1. | MI |  |  | Proposed | 14400000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13934 | 2018-01-08 | METC_17_048 | 23333 | 2017-12-04 | RLY | 2021-12-31 | Ludington |  |  | 345 |  |  | Replace Relaying at Ludington 345 kV station | MI |  |  | Proposed | 400000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13934 | 2018-01-08 | METC_17_048 | 23020 | 2017-12-04 | LNrl | 2021-12-31 | Pere Marquette | Ludington | 1 | 345 |  |  | Cut-in the existing Pere Marquette - Ludington 345 kV line to reterminate it and the existing 345/138 kV Transformer #2 at the new 345 kV switchyard. | MI |  |  | Proposed | 1670000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13934 | 2018-01-08 | METC_17_048 | 23018 | 2017-12-04 | TX | 2021-12-31 | Pere Marquette |  | 1 | 345 | 138 |  | Install a new 345/138 kV transformer at Pere Marquette. | MI |  |  | Proposed | 6120000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13948 | 2018-04-06 | METC_18_011 | 23036 | 2018-05-03 | SwSta | 2020-06-01 | Stronach |  |  | 138 |  |  | Expand Stronach station to a 4 (future 5) breaker ring bus | MI |  |  | Proposed | 9320000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13948 | 2018-04-06 | METC_18_011 | 23437 | 2018-07-09 | LNrl | 2020-06-01 | Stronach | Tippy | 1 | 138 |  |  | Relocate Stronach end of Stronach to Tippy 138kV line into new Stronach station | MI |  |  | Proposed | 320000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13948 | 2018-04-06 | METC_18_011 | 23436 | 2018-07-09 | LNrl | 2020-06-01 | Stronach | Filer City | 1 | 138 |  |  | Relocate Stronach end of Stronach to Filer City 138kV line into new Stronach station | MI |  |  | Proposed | 925000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13948 | 2018-04-06 | METC_18_011 | 23435 | 2018-07-09 | LNrl | 2020-06-01 | Stronach | Pere Marquette | 1 | 138 |  |  | Relocate Stronach end of Stronach - Pere Marquette 138kV line into new Stronach station | MI |  |  | Proposed | 330000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13949 | 2017-09-13 | METC_17_008 | 23039 | 2017-09-13 | SwSta | 2020-06-01 | Long Rapids |  |  | 138 |  |  | Construct a Long Rapids breaker and half 138 kV station. | MI |  |  | Proposed | 10624000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13949 | 2017-09-13 | METC_17_008 | 23045 | 2017-09-13 | LN | 2020-06-01 | Airport | Long Rapids | 1 | 138 |  |  | Re-terminate Alpena - Airport 138 kV circuit from Alpena to Long Rapids. | MI |  |  | Proposed | 847000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13949 | 2017-09-13 | METC_17_008 | 23043 | 2017-09-13 | LN | 2020-06-01 | Iosco | Long Rapids | 1 | 138 |  |  | Re-terminate Alpena - Iosco 138 kV circuit from Alpena to Long Rapids. | MI |  |  | Proposed | 847000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13949 | 2017-09-13 | METC_17_008 | 23040 | 2017-09-13 | LN | 2020-06-01 | Rockport | Long Rapids | 1 | 138 |  |  | Re-terminate Alpena-Rockport 138kV circuit from Alpena to Long Rapids. | MI |  |  | Proposed | 847000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13953 | 2018-03-27 | METC_17_064 | 23058 | 2018-03-27 | SwSta | 2019-12-31 | Donaldson Creek |  |  | 138 |  |  | Add a 3rd 138kV row to Donaldson Creek, add breakers to terminate two new WPSC 138kV circuits. | MI |  |  | Planned | 2000000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 13997 | 2017-11-09 | METC-17-053 | 23308 | 2017-12-04 | RLY | 2020-06-01 | Argenta |  |  | 138 |  |  | Upgrade relay at Argenta 138kV to meet or exceed summer emergency rating of 602 MVA/2520 Amps | MI |  |  | Proposed | 126000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14031 | 2017-09-15 | METC_17_043 | 23149 | 2017-10-31 | SUB | 2020-12-31 | Ransom |  |  | 138 |  |  | The proposed solution is to install two 138 kV breakers and create a ring bus at Ransom station. This will increase reliability and operability of the Ransom 138 kV station and surrounding area | MI |  |  | Planned | 2500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14040 | 2018-01-08 | METC_17_057 | 23162 | 2017-11-01 | TX | 2020-12-31 | Keystone |  | 2 | 345 | 138 |  | Replace the Keystone 345/138 kV Transformer #2 to increase the facility’s summer emergency rating to 478 MVA/2000 Amps. | MI |  |  | Proposed | 3700000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14042 | 2017-10-18 | METC_17_059 | 23170 | 2017-11-28 | TEQ | 2020-12-31 | Goss |  | 1 | 138 |  |  | Upgrade station equipment at Positions 11W8 and 13W8 at Goss to increase the open breaker summer emergency rating to 585 MVA/2447 Amps and account for open breaker scenarios at each position. | MI |  |  | Proposed | 475000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14060 | 2018-06-20 | METC_17_072 | 23187 | 2018-06-20 | LNrl | 2020-02-01 | Blendon | Four Mile | 1 | 138 |  |  | Re-terminate the Four Mile - Blendon 138kV circuit to WPSC's new Blendon 138kV station | MI |  |  | Proposed | 210000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14060 | 2018-06-20 | METC_17_072 | 23426 | 2018-06-20 | SwSta | 2020-02-01 | Blendon |  |  | 138 |  |  | Demolish METC Blendon 138kV switchyard and convert existing WPSC Blendon 69kV station to 138kV | MI |  |  | Proposed | 4300000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14060 | 2018-06-20 | METC_17_072 | 23188 | 2018-06-20 | LNrl | 2020-02-01 | Campbell | Blendon | 1 | 138 |  |  | Re-terminate the Campbell - Blendon 138kV line into WPSC's new Blendon 138kV station | MI |  |  | Proposed | 220000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14065 | 2018-01-08 |  | 23201 | 2017-09-15 | SUB | 2021-12-31 | 2021 METC Asset Replacement Program |  |  | 345 | 138 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life | MI |  |  | Planned | 43500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14067 | 2018-05-31 |  | 23205 | 2018-04-30 | LN | 2020-06-01 | Gaines | Bradley | 1 | 138 |  |  | Extend existing 138kV line 0.25 miles into the new WPSC Bradley 138kV station | MI |  | 0.1 | Proposed | 253000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14067 | 2018-05-31 |  | 23206 | 2018-04-30 | LN | 2020-06-01 | WARNER | BRADLEY | ! | 138 |  |  | Extend METC's Warner - Bradley 138kV line 0.25 into WPSC's new Bradley Sub | MI |  | 0.1 | Proposed | 253000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14072 | 2017-09-15 |  | 23212 | 2017-11-30 | Dist | 2021-12-31 | Blanket for Customer Interconnections | Throughout System |  | 138 |  |  | Blanket for customer interconnections and retirements less than $1 million with in service dates in the year 2021. | MI |  |  | Proposed | 2500000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | METC | 14107 | 2018-01-08 | METC_15_039 | 23258 | 2017-09-18 | RLY | 2019-12-31 | Weeds Lake | Hiple | 1 | 345 |  |  | Replace Wave Traps and modify relaying | MI |  |  | Planned | 150000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14244 | 2017-10-30 | METC_17_017 | 23294 | 2017-10-02 | SwSta | 2019-06-01 | Orr Rd |  |  | 138 |  |  | Decommission and remove 75 MVAR capacitor with adjacent breaker and switch at Orr Road 138 kV station. | MI |  |  | Planned | 95000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14344 | 2017-10-31 | METC_17_066 | 23317 | 2017-11-28 | LNup | 2021-12-31 | Airport | Hillman Tap | 1 | 138 |  |  | Remediate the sag limit on ~17.0 miles of 266 ACSR conductor of the ~21.3 mile-long Airport - Hillman Tap 138 kV section of the Airport - Mio 138 kV line to at least the planned target summer normal/summer emergency rating of 133 MVA/556 Amps. | MI |  |  | Proposed | 400000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14424 | 2017-10-31 |  | 23321 | 2018-01-26 | LNup | 2020-06-01 | Cobb | Meyer |  | 138 |  |  | Remediate the sag limit on the Cobb – Meyer 138kV line to the full conductor summer emergency limit of 260 MVA (1088 A) | MI |  |  | Proposed | 2500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 14464 | 2017-11-30 | METC-17-070 | 23327 | 2017-12-05 | RLY | 2020-06-01 | Battle Creek |  |  | 138 |  |  | Upgrade relaying at Battle Creek Positions 9MB and 9M9 to meet or exceed 574 MVA/2400 Amps | MI |  |  | Proposed | 32000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 15364 | 2018-08-16 |  | 23527 | 2018-07-31 | SUB | 2020-03-01 | Wilson Street |  |  | 138 |  |  | Construct Wilson Street 138kV station. The station will be a ring bus station with three breakers. | MI |  |  | Proposed | 3870000 | Planning |  | N | N | N
A in MTEP18 | A | East | METC | 15364 | 2018-08-16 |  | 23528 | 2018-07-31 | LN | 2020-03-01 | Cobb | Tallmadge | #2 | 138 |  |  | Cut in the Cobb - Tallmadge #2 138kV line near tower 1762 about 15 miles from Tallmadge 138kV to serve new Wilson Street 138kV station. | MI |  | 0.1 | Proposed | 330000 | Planning |  | N | N | N
A in MTEP18 | A | East | METC | 15464 | 2018-10-03 | METC-18-022 | 23557 | 2018-08-17 | LN | 2020-11-01 | Morenci | Morenci Tap | 1 | 138 |  |  | Tap the METC’s Moore Road- Beecher 138kV circuit. Install a Tap Pole and three 1-Way pole top switches. Build 12 miles of a new 138kV transmission circuit. | MI |  | 12 | Proposed | 20703000 | Engineering |  | N | N | N
A in MTEP18 | A | East | METC | 15493 | 2018-10-03 |  | 23576 | 2018-08-22 | SUB | 2020-10-01 | Knowles |  |  | 138 |  |  | Construct a new 138 kV 3 breaker ring station | MI |  |  | Planned | 5079000 | GIA |  | N | Y | N
A in MTEP18 | A | East | METC | 15493 | 2018-10-03 |  | 23578 | 2018-08-22 | LINE | 2020-10-01 | Beecher | Moore Rd |  | 138 |  |  | Cut the Beecher Moore Rd 138 kV circuit into the new Knowles interconnection station. Install OPGW from Moore Rd to Knowles. | MI |  |  | Planned | 1841000 | GIA |  | N | Y | N
A in MTEP18 | A | East | METC | 15496 | 2018-10-03 |  | 23579 | 2018-08-22 | SUB | 2019-10-01 | Slate |  |  | 345 |  |  | Install a 345 kV breaker and two disconnects to complete the row at the Slate 345 kV station. | MI |  |  | Planned | 1456000 | GIA |  | N | Y | Y
A in MTEP18 | A | West | MP | 9202 | 2018-08-22 | 203611 | 23644 | 2018-09-05 | TAP | 2019-10-01 | Swatara |  |  | 230 |  |  | Swatara Tap in Blackberry – Riverton 230 kV Line | MN |  |  | Proposed | 1300000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 9202 | 2018-08-22 | 203611 | 23645 | 2018-09-05 | CB | 2019-10-01 | Riverton |  |  | 230 |  |  | Add 92L breaker at Riverton Sub | MN |  |  | Proposed | 500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 9646 | 2017-08-22 | Nashwauk 14 Line Upgrade | 20959 | 2018-01-25 | LNup | 2020-05-01 | Nashwauk | 14 Line Tap | 1 | 115 |  |  | Upgrade existing 636 ACSR to 100C | MN | 4.9 | 0 | Proposed | 600000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 9646 | 2017-08-22 | Nashwauk 14 Line Upgrade | 23360 | 2018-01-25 | TEQ | 2020-06-01 | Naswauk |  |  | 115 |  |  | Replace limiting substation bus and conductors. | MN |  |  | Planned | 220000 | Scoping |  | N | N | N
A in MTEP18 | A | West | MP | 9647 | 2017-09-18 | 53 Line Upgrade | 20960 | 2018-01-25 | LNup | 2020-06-01 | Nashwauk | National | 1 | 115 |  |  | Upgrade existing 636 ACSR to 100C | MN | 6.2 | 0 | Proposed | 330000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 9647 | 2017-09-18 | 53 Line Upgrade | 23362 | 2018-01-25 | TEQ | 2020-06-01 | National Taconite |  |  | 115 |  |  | Replace limiting Substation conductors and bus. | MN |  |  | Planned | 250000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 9647 | 2017-09-18 | 53 Line Upgrade | 23361 | 2018-01-25 | TEQ | 2020-06-01 | Naswauk |  |  | 115 |  |  | Replace limiting substation conductors and bus. | MN |  |  | Planned | 220000 | Scoping |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22626 | 2017-08-17 | LNup | 2019-12-31 | Arrowhead | Colbyvile |  | 115 |  | 182/214 | Increase operating temperature to 100C | MN |  |  | Planned | 1680000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22633 | 2017-08-17 | TEQ | 2019-12-31 | Two Harbors Switching Station |  |  | 115 |  |  | Replace wave trap and limiting substation conductor. | MN |  |  | Planned | 40000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22632 | 2017-08-17 | TEQ | 2019-12-31 | Haines Road |  |  | 115 |  |  | Remove wave trap and replace limiting substation conductor. | MN |  |  | Planned | 75000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22630 | 2017-08-17 | TEQ | 2019-12-31 | Colbyville |  |  | 115 |  |  | Replace wave trap & substation conductors on 145 Line (Two Harbors - Colbyville). Replace switches & substation conductors on 56 Line (Ridgeview - Colbyville). | MN |  |  | Planned | 750000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22629 | 2017-08-17 | LNrc | 2019-12-31 | Colbyville | Two Harbors Switching Station |  | 115 |  | 175/208 | Reconductoring 2 miles of transmission line with 636 ACSR. | MN |  |  | Planned | 1270000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22628 | 2017-08-17 | LNup | 2019-12-31 | Arrowhead | Haines Road |  | 115 |  | 182/214 | Increase operating temperature to 100C | MN |  |  | Planned | 720000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13364 | 2017-07-25 | North Shore Transmission Lines | 22627 | 2017-08-17 | TEQ | 2019-12-31 | Arrowhead |  |  | 115 |  |  | Replacing Wave Trap & Substation Conductors for 57 Line (Arrowhead - Colbyville). Removing wave trap and replacing substation conductor for 58 Line (Arrowhead - Haines Road). | MN |  |  | Planned | 100000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MP | 13484 | 2017-08-17 | Two Harbors 115 kV Project | 23284 | 2017-09-22 | LNup | 2019-12-31 | Two Harbors | Silver Bay |  | 115 |  | 122 | Increase operating temp to 100C | MN | 30 | 0 | Planned | 4500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13484 | 2017-08-17 | Two Harbors 115 kV Project | 23287 | 2017-09-22 | SUB | 2019-12-31 | Two Harbors | (Big Rock) |  | 115 |  |  | Add a breaker at the existing Two Harbors Switching Station, and other modifications to accommodate line relocations. Station to be rename "Big Rock" to eliminate naming redundancy | MN | 0 | 0 | Planned | 1500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13484 | 2017-08-17 | Two Harbors 115 kV Project | 23285 | 2017-09-22 | LN | 2019-12-31 | Two Harbors | Colbyville |  | 115 |  |  | Relocate existing line termination to a new line position in substation | MN | 0 | 0.25 | Planned | 500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13485 | 2017-12-05 | Hoyt Lakes 115 kV Project | 23270 | 2018-04-03 | LN | 2020-12-31 | Forbes | Hoyt Lakes | 1 | 115 |  | 113 | Extend existing Forbes - Laskin 115 kV Line (38 Line) up to Hoyt Lakes, removing connection to Laskin | MN | 0 | 7 | Proposed | 7000000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13504 | 2018-04-03 |  | 23267 | 2018-04-03 | LNup | 2020-12-31 | Laskin | Hoyt Lakes | 1 | 115 |  | 182 | 43 Line Upgrade | MN | 7 | 0 | Proposed | 500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13504 | 2018-04-03 |  | 23413 | 2018-04-03 | TEQ | 2019-12-31 | Hoyt Lakes |  |  | 138 |  |  | Switches, wave traps, substation conductors | MN |  |  | Planned | 400000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13504 | 2018-04-03 |  | 23412 | 2018-04-03 | TEQ | 2019-12-31 | Laskin |  |  | 138 |  |  | Switches, wave trap & substation conductor | MN | 0 | 0 | Planned | 200000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13504 | 2018-04-03 |  | 23269 | 2018-04-03 | LNup | 2020-12-31 | Hoyt Lakes | Taconite Harbor | 2 | 115 |  | 123 | 2 Line (modify one insulator string following conversion to 115 kV) | MN | 61 | 0 | Proposed | 50000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13504 | 2018-04-03 |  | 23268 | 2018-04-03 | LNup | 2020-12-31 | Hoyt Lakes | Taconite Harbor | 1 | 115 |  | 123 | 1 Line (modify one insulator string following conversion to 115 kV) | MN | 61 | 0 | Proposed | 50000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13526 | 2018-08-16 | Tioga | 22636 | 2017-08-22 | SUB | 2018-12-31 | Tioga |  |  | 115 | 23 | 50 | New 115/23 kV Substation | MN | 0 | 0 | Planned | 1500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13526 | 2018-08-16 | Tioga | 22637 | 2017-08-22 | LN | 2018-12-31 | Tioga | 27 Line Tap | 1 | 115 |  | 50 | Extend existing 115 kV tap a handful of spans to new Tioga Substation | MN | 0 | 0.1 | Planned | 500000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23261 | 2018-05-09 | CB | 2019-12-31 | Blackberry | 20L Breaker |  | 115 |  |  | Replace existing breaker | MN | 0 | 0 | Planned | 160000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23442 | 2018-05-10 | TEQ | 2019-12-31 | Blackberry | 98 Line Tap |  | 230 |  | 470 | Replace limiting substation conductors | MN | 0 | 0 | Planned | 10000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23441 | 2018-05-10 | TEQ | 2019-12-31 | Blackberry | 9 Line Tap |  | 115 |  | 182 | Replace limiting wave trap and substation conductors | MN | 0 | 0 | Planned | 20000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23440 | 2018-05-10 | TEQ | 2019-12-31 | Blackberry | 20 Line Tap |  | 115 |  | 182 | Replace limiting wave trap and conductors | MN | 0 | 0 | Planned | 20000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23266 | 2018-05-09 | CB | 2019-12-31 | Blackberry | 95L Breaker |  | 230 |  |  | Replace existing breaker | MN | 0 | 0 | Planned | 200000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23265 | 2018-05-09 | CB | 2019-12-31 | Blackberry | 98-FUT1LW Breaker |  | 230 |  |  | Replace existing breaker | MN | 0 | 0 | Planned | 200000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23264 | 2018-05-09 | CB | 2019-12-31 | Blackberry | 98L Breaker |  | 230 |  |  | Replace existing breaker | MN | 0 | 0 | Planned | 200000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23263 | 2018-05-09 | CB | 2019-12-31 | Blackberry | 63L Breaker |  | 115 |  |  | Replace existing breaker | MN |  |  | Planned | 160000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 13527 | 2018-05-09 | Blackberry Breakers | 23262 | 2018-05-09 | CB | 2019-12-31 | Blackberry | 62L Breaker |  | 115 |  |  | Replace existing breaker | MN |  |  | Planned | 160000 | Planning |  | N | N | N
A in MTEP18 | A | West | MP | 15144 | 2018-05-25 |  | 23461 | 2018-05-24 | CAP | 2018-08-24 | Square Butte East |  |  | 230 |  | 40 | Existing cap bank relocated from Bison to Square Butte East | ND |  |  | Planned | 150000 | Planning |  | N | N | N
A in MTEP18 | A | East | MPPA | 14124 | 2017-09-21 |  | 23271 | 2017-09-22 | SUB | 2018-12-31 | Riley |  |  | 138 |  |  | This project will provide additional 138/69kV transformer capacity at the Riley Station. | MI |  |  | Under Construction | 2450000 | Construction |  | N | N | N
A in MTEP18 | A | East | MPPA | 14188 | 2018-05-25 |  | 23286 | 2017-09-22 | BUS | 2022-12-31 | Riley | Faiview |  | 138 |  |  | Relocation of the second Riley 138/69kV transformer and associated switching to the Zeeland Fairview station. | MI |  |  | Proposed | 550000 | Construction |  | N | N | N
A in MTEP18 | A | East | MPPA | 14724 | 2018-03-06 |  | 23363 | 2018-01-26 | LINE |  | Riley | Blendon |  | 138 |  |  | 138 kv line from Riley to Blendon | MI |  |  | Proposed | 300000 | Construction |  | N | N | N
A in MTEP18 | A | West | MRES | 13647 | 2018-03-27 | DLIndReconfig | 23136 | 2017-11-22 | SwSta | 2020-12-01 | DL Industrial 115 kV |  |  | 115 |  |  | Convert the high-side of Detroit Lakes Industrial Substation from a line breaker configuration to a ring bus configuration. | MN |  |  | Planned | 2208000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MRES | 13648 | 2018-06-20 | AuduCBReplace | 22739 | 2017-08-30 | CB | 2019-05-01 | Audubon 115 kV |  |  | 115 |  |  | Replace the 115 kV circuit breakers at Audubon substation (CBs 1415 and 1435). | MN |  |  | Planned | 300000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MRES | 13648 | 2018-06-20 | AuduCBReplace | 22740 | 2017-08-30 | RLY | 2019-05-01 | Audubon 115 kV |  |  | 115 |  |  | Upgrade some outdated RTU equipment. | MN |  |  | Planned | 200000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | MRES | 13852 | 2017-09-11 | DLSthIntrcnct | 23328 | 2017-11-15 | TEQ | 2019-10-01 | DL South Tap 115 kV |  |  | 115 |  |  | Three-way load break switch for interconnecting with GRE's Cormorant Jct. to Frazee 115 kV line. The approximate point of interconnection is 7.09 miles from Frazee on the Cormorant Jct. to Frazee 115 kV line (7.95 miles from Cormorant Jct.). The Detroit Lakes South Substation, the radial tap line (~2.5 miles), and a portion of the switch is radial at the point of interconnection. | MN |  |  | Planned | 266667 | Planning |  | N | N | N
A in MTEP18 | A | East | NIPS | 15384 | 2018-08-02 |  | 23529 | 2018-08-08 | BUS | 2019-12-31 | Maple | LNG | 1 | 138 |  |  | Replacement of substation bus conductor | IN |  |  | Proposed | 140181 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | East | NIPS | 15385 | 2018-08-02 |  | 23530 | 2018-08-08 | CB | 2021-12-31 | Dune Acres |  |  | 138 |  |  | Replacement of 13806 Breaker at Dune Acres | IN |  |  | Proposed | 310234 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 14056 | 2018-09-21 |  | 23181 | 2018-09-21 | TAP | 2021-11-30 | Parkers Prairie 115 kV |  |  | 115 | 12.5 |  | Parkers Prairie existing 41.6 kV load will be moved to a Parkers Prairie 115/12.5 kV Tap | MN |  |  | Planned | 224400 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 14057 | 2018-09-28 |  | 23182 | 2018-09-28 | RLY | 2019-09-01 | Veblen 41.6 kV |  |  | 41.6 |  |  | Replace all relays and associated equipment at the Veblen Switching Station. | SD |  |  | Planned | 110000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 14057 | 2018-09-28 |  | 23509 | 2018-09-28 | SUB | 2019-09-01 | Veblen 41.6 kV |  |  | 41.6 |  |  | 2 stages of 1.35 MVAR cap banks, substation work including a new control house, an additional 41.6 kV breaker and site expansion. | SD |  |  | Planned | 990000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 14059 | 2018-05-29 |  | 23184 | 2017-12-06 | SwSta | 2019-01-31 | Bagley 115 kV |  |  | 115 |  |  | Bagley North 115 kV Switching Substation - Add 115 kV 3 Circuit Breaker Ring Bus | MN |  |  | Planned | 2500000 | Planning |  | N | N | N
A in MTEP18 | A | West | OTP | 15164 | 2018-09-28 | OTP 15164 | 23480 | 2018-09-28 | TX | 2018-11-30 | Cass Lake 230/115 |  |  | 115 | 12.5 | 10 MVA | New 10 MVA 115/12.5 kV transformer | MN |  |  | Planned | 243000 | Planning |  | N | N | N
A in MTEP18 | A | West | OTP | 15164 | 2018-09-28 | OTP 15164 | 23481 | 2018-09-28 | SUB | 2018-11-30 | Cass Lake 230/115 |  |  | 230 | 115 |  | Modifications to the Cass Lake 230/115 kV substation- The transformer will be utilizing the existing open 115 kV breaker at Cass Lake. | MN |  |  | Planned | 1150000 | Planning |  | N | N | N
A in MTEP18 | A | West | OTP | 15165 | 2018-05-24 | OTP 15165 | 23482 | 2018-05-24 | TX | 2018-07-15 | Mapleton 115/41.6 kV |  |  | 115 | 12.5 | 10 MVA | New 10 MVA 115/12.5 kV transformer | ND |  |  | Planned | 243000 | Planning |  | N | N | N
A in MTEP18 | A | West | OTP | 15165 | 2018-05-24 | OTP 15165 | 23483 | 2018-07-09 | SUB | 2018-07-15 | Mapleton 115/41.6 kV |  |  | 115 | 12.5 |  | Modifications to the Mapleton 115/41.6 kV substation | ND |  |  | Planned | 955700 | Planning |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23558 | 2018-08-17 | LN | 2019-03-01 | Hetland 115 kV | Lake Norden 115 kV |  | 115 |  | 98 | Build 115 kV radial from Hetland to Lake Norden, 13 miles 1/0 T2 conductor. | SD |  | 13 | Planned | 7225000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23565 | 2018-08-17 | BUS | 2020-12-31 | Lake Norden 115 kV |  |  | 115 | 12.5 |  | Substation upgrades for phase 2 transmission lines. | SD |  |  | Planned | 494625 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23564 | 2018-08-17 | SUB | 2020-12-31 | Astoria 345 kV |  |  | 345 | 41.6 | 112 | Adding spare 345/115/41.6 kV transformer and a single 115 kV breaker. | SD |  |  | Planned | 1500000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23563 | 2018-08-17 | LN | 2020-12-31 | Astoria 345 kV | Toronto 115 kV |  | 345 | 115 | 192 | New 115 kV transmission line (6.6 miles) between Astoria 345 kV to Toronto 115 kV. 266 T2 conductor. | SD |  | 6.6 | Planned | 3810000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23562 | 2018-08-17 | LN | 2020-12-31 | Toronto 115 kV | Lake Norden 115 kV |  | 115 |  | 98 | New 115 kV transmission line (29 miles) from Toronto 115 kV to Lake Norden 115 kV. Conductor size 1/0 T2. | SD |  | 29 | Planned | 15950000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23561 | 2018-08-17 | BUS | 2020-12-31 | Toronto 115 kV |  |  | 115 | 41.6 |  | New 5 breaker 115 kV ring bus to replace existing Toronto substation, and accommodate 2 115 kV transmission lines. | SD |  |  | Planned | 3000000 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23560 | 2018-08-17 | BUS | 2019-03-01 | Hetland 115 kV |  |  | 115 |  |  | New breakers to accommodate the new 115 kV line from Lake Norden to Hetland. | SD |  |  | Planned | 2040930 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | West | OTP | 15465 | 2018-10-03 | 15465 | 23559 | 2018-08-17 | SUB | 2019-03-01 | Lake Norden 115 kV |  |  | 115 | 12.5 |  | New substation will consist of 115 kV 5 breaker ring bus, 3 x 5.4 MVAR capacitors, 2 distribution transformers (28 MVA) and distribution breakers. | SD |  |  | Planned | 4031935 | Planning Preliminary |  | N | N | N
A in MTEP18 | A | Central | PPI | 13950 | 2018-09-17 |  | 23041 | 2018-09-17 | SUB | 2020-12-31 | Oxville |  |  | 138 |  |  | New 138 kV 4 breaker ring bus and 2 distribution transformers. | IL |  |  | Proposed | 6500000 | Planning |  | N | N | N
A in MTEP18 | A | Central | PPI | 13950 | 2018-09-17 |  | 23048 | 2018-09-17 | LN | 2020-12-31 | Ballard-Oxville | Oxville-Pittsfield |  | 138 |  | 229 | The Ballard to Pittsfield 138 kV line will be split into Ballard-Oxville and Oxville-Pittsfield segments by constructing a new 10 mile double circuit line from the original Ballard to Pittsfield line to the Oxville industrial plant. | IL |  | 20 | Proposed | 6000000 | Planning |  | N | N | N
A in MTEP18 | A | Central | PPI | 13952 | 2018-08-06 |  | 23057 | 2017-09-14 | SUB | 2021-12-31 | PPI Meppen |  |  | 138 | 69 | 84 | New 138/69 kV substation with an 84 MVA transformer. | IL |  |  | Planned | 3500000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | PPI | 13952 | 2018-08-06 |  | 23065 | 2017-09-13 | LN | 2021-12-31 | Hardin | Eldred |  | 69 |  | 50 | New 15 mile 69 kV line including Illinois River crossing. | IL |  | 15 | Planned | 8500000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | PPI | 13960 | 2018-09-17 |  | 23070 | 2018-09-17 | Dist | 2022-12-31 | Rattlesnake |  |  | 69 | 12.47 | 7 | New Rattlesnake distribution with a 5/7 MVA transformer | IL |  |  | Proposed | 1200000 | Planning |  | N | N | N
A in MTEP18 | A | Central | PPI | 13960 | 2018-09-17 |  | 23071 | 2018-09-17 | LN | 2022-12-31 | Liberty | Rattlesnake |  | 69 |  | 50 | New 9 mile 69 kV line with 336.4 MCM ACSR conductor. | IL |  | 9 | Proposed | 4500000 | Planning |  | N | N | N
A in MTEP18 | A | Central | PPI | 13964 | 2018-09-17 |  | 23077 | 2018-09-13 | CAP | 2019-12-31 | Naples Breaker Station |  |  | 69 |  |  | New 4.8 MVAR capacitor bank | IL |  |  | Planned | 300000 | Planning |  | N | N | N
A in MTEP18 | A | Central | PPI | 14006 | 2018-08-06 |  | 23122 | 2017-09-14 | SwSta | 2021-12-31 | Walkerville |  |  | 69 |  |  | New 69 kV Walkerville three breaker switching station. | IL |  |  | Planned | 2100000 | Planning |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14074 | 2017-09-15 | 2018SIGE1 | 23213 | 2017-09-15 | TX | 2018-12-31 | Green Oaks |  |  | 69 |  |  | Green Oaks Dist XFMR (253561 - 10GRNOAK) | IN |  |  | M2a_Pre-Project Approval | 1677000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14075 | 2017-09-15 | 2018SIGE2 | 23214 | 2017-09-15 | TX | 2018-12-31 | Ft. Branch |  |  | 69 | 12 |  | Dist. XFMR T2 at Ft. Branch (253560 - 10FTBRAN) | IN |  |  | M2a_Pre-Project Approval | 1293500 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14076 | 2017-09-15 | 2018SIGE3 | 23215 | 2018-09-13 | TX | 2018-12-31 | St. Meinrad |  |  | 69 | 12 |  | Replace 69/12 kV dist. trans. T1 at St. Meinrad (253576 - 10STMEIN) | IN |  |  | M2a_Pre-Project Approval | 1272795 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14077 | 2017-09-15 | 2018SIGE4 | 23216 | 2017-09-15 | LNrb | 2019-12-31 | Lynnville | Liberty Metering | 68 | 69 |  |  | Rebuild ~12.3 miles of Y68 from Lynnville (253563 - 10LYNV69) to Liberty Metering (253588 - 10VIGO_T) | IN | 12.3 |  | M2a_Pre-Project Approval | 8195000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14078 | 2018-09-13 | 2018SIGE5 | 23217 | 2018-09-13 | CB | 2020-12-31 | Boonville Pioneer |  |  | 69 |  |  | 69 kV breaker 199 at Boonville Pioneer | IN |  |  | M2a_Pre-Project Approval | 13700 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14079 | 2017-09-15 | 2018SIGE6 | 23218 | 2017-09-15 | TX | 2019-12-31 | Broadview |  |  | 69 |  |  | Replace 69/12 kV T1 at Broadview (253556 - 10BRDVW) | IN |  |  | M2a_Pre-Project Approval | 1108400 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14080 | 2017-09-15 | 2018SIGE7 | 23219 | 2017-09-15 | CB | 2019-12-31 | Lynnville |  |  | 69 |  |  | Replace OCB 377 at Lynnville (253563 - 10LYNV69) | IN |  |  | M2a_Pre-Project Approval | 137000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14080 | 2017-09-15 | 2018SIGE7 | 23220 | 2017-09-15 | CB | 2019-12-31 | Lynnville |  |  | 69 |  |  | Replace OCB 477 at Lynnville (253563 - 10LYNV69) | IN |  |  | M2a_Pre-Project Approval | 137000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14081 | 2017-09-15 | 2018SIGE8 | 23221 | 2017-09-15 | LNrb | 2019-12-31 | Heidelbach | Angel Mounds | 85 | 138 |  |  | Rebuild ~6.7 miles of 138 kV line between Heidelbach (253530 - 10HEID13) and Angel Mounds (253524 - 10ANGD13) | IN | 6.7 |  | M2a_Pre-Project Approval | 6263500 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14082 | 2017-09-15 | 2018SIGE9 | 23222 | 2017-09-15 | TX | 2019-12-31 | Modification |  |  | 69 |  |  | Replace 69/12 kV dist. xfmr at Modification station | IN |  |  | M2a_Pre-Project Approval | 981000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14083 | 2017-09-15 | 2018SIGE10 | 23223 | 2017-09-15 | TX | 2019-12-31 | Slaughter |  |  | 69 |  |  | Replace 69/12 kV T1 at Slaughter (253572 - 10SLAUTR) | IN |  |  | M2a_Pre-Project Approval | 1108400 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14083 | 2017-09-15 | 2018SIGE10 | 23225 | 2017-09-15 | CB | 2019-12-31 | Slaughter |  |  | 69 |  |  | Replace tie breaker OCB 500 at Slaughter (253572 - 10SLAUTR) | IN |  |  | M2a_Pre-Project Approval | 151000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14083 | 2017-09-15 | 2018SIGE10 | 23224 | 2017-09-15 | TX | 2019-12-31 | Slaughter |  |  | 69 |  |  | Replace 69/12 kV T2 at Slaughter (253572 - 10SLAUTR) | IN |  |  | M2a_Pre-Project Approval | 981000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14084 | 2017-09-15 | 2018SIGE11 | 23226 | 2017-09-15 | TX | 2019-12-31 | Smythe |  |  | 69 |  |  | Replace 69/12 kV T1 at Smythe (253573 - 10SMYTHE) | IN |  |  | M2a_Pre-Project Approval | 1108400 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14084 | 2017-09-15 | 2018SIGE11 | 23227 | 2017-09-15 | TX | 2019-12-31 | Smythe |  |  | 69 |  |  | Replace 69/12 kV T2 at Smythe (253573 - 10SMYTHE) | IN |  |  | M2a_Pre-Project Approval | 1108400 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14085 | 2017-09-15 | 2018SIGE12 | 23228 | 2017-09-15 | TX | 2020-12-31 | Rolling Hills |  |  | 69 |  |  | Replace 69/12 kV T1 at Rolling Hills | IN |  |  | M2a_Pre-Project Approval | 1138300 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14086 | 2017-09-15 | 2018SIGE13 | 23229 | 2017-09-15 | CB | 2020-12-31 | Angel Mounds |  |  | 69 |  |  | Replace GCB 188 at Angel Mounds (253525 - 10ANGD69) | IN |  |  | M2a_Pre-Project Approval | 215000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14086 | 2017-09-15 | 2018SIGE13 | 23233 | 2017-09-15 | CB | 2020-12-31 | Angel Mounds |  |  | 69 |  |  | Replace 69 kV GCB 100 at Angel Mounds (253525 - 10ANGD69) | IN |  |  | M2a_Pre-Project Approval | 203000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14086 | 2017-09-15 | 2018SIGE13 | 23232 | 2017-09-15 | CB | 2020-12-31 | Angel Mounds |  |  | 69 |  |  | Replace 69 kV GCB 177 at Angel Mounds (253525 - 10ANGD69) | IN |  |  | M2a_Pre-Project Approval | 209000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14086 | 2017-09-15 | 2018SIGE13 | 23231 | 2017-09-15 | CB | 2020-12-31 | Angel Mounds |  |  | 69 |  |  | Replace 69 kV GCB 200 at Angel Mounds (253525 - 10ANGD69) | IN |  |  | M2a_Pre-Project Approval | 210000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14086 | 2017-09-15 | 2018SIGE13 | 23230 | 2017-09-15 | CB | 2020-12-31 | Angel Mounds |  |  | 69 |  |  | Replace 69 kV GCB 288 at Angel Mounds (253525 - 10ANGD69) | IN |  |  | M2a_Pre-Project Approval | 212000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14087 | 2017-09-15 | 2018SIGE14 | 23234 | 2017-09-15 | LN | 2020-12-31 | Paradise | Paradise Tap | 58 | 69 |  |  | Build a new 69 kV loop on Y58 to Paradise sub | IN |  | 1.8 | M2a_Pre-Project Approval | 3119500 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14088 | 2018-09-13 | 2018SIGE15 | 23235 | 2018-09-13 | LNrb | 2021-12-31 | Culley | Boonville | 68 | 69 |  |  | Rebuild ~0.6 miles of 69 kV line from Culley (253501 - 10CULY69) to Boonville (253604 - 10BNVL) | IN |  |  | M2a_Pre-Project Approval | 973700 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14089 | 2017-09-15 | 2018SIGE16 | 23236 | 2017-09-15 | TX | 2020-12-31 | Buckwood |  |  | 69 |  |  | Replace 69/12 kV T1 at Buckwood (253557 - 10BUCK58) | IN |  |  | M2a_Pre-Project Approval | 1138300 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14089 | 2017-09-15 | 2018SIGE16 | 23237 | 2017-09-15 | TX | 2020-12-31 | Buckwood |  |  | 69 |  |  | Replace 69/12 kV T2 at Buckwood (253557 - 10BUCK58) | IN |  |  | M2a_Pre-Project Approval | 1138300 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14090 | 2017-09-15 | 2018SIGE17 | 23238 | 2017-09-15 | TX | 2020-12-31 | Civic Center |  |  | 69 |  |  | Replace 69/12 kV T1 and associated UG exit at Civic Center | IN |  |  | M2a_Pre-Project Approval | 2950000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14091 | 2018-09-13 | 2018SIGE18 | 23239 | 2018-09-13 | LN | 2019-12-31 | Garvin | Garvin Tap | 43 | 69 |  |  | Build new 69 kV loop for radial Garvin sub | IN |  | 0.5 | M2a_Pre-Project Approval | 1742300 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14092 | 2017-09-15 | 2018SIGE20 | 23240 | 2017-09-15 | TX | 2020-12-31 | Grimm Rd. |  |  | 138 |  |  | Replace 138/12 kV dist. transformer at Grimm Rd. (253546 - 10GRIMM) | IN |  |  | M2a_Pre-Project Approval | 1138300 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14093 | 2017-09-15 | 2018SIGE21 | 23241 | 2017-09-15 | TX | 2020-12-31 | Mulberry |  |  | 69 |  |  | Replace dist. trans. T3 at Mulberry | IN |  |  | M2a_Pre-Project Approval | 1607350 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14093 | 2017-09-15 | 2018SIGE21 | 23242 | 2017-09-15 | TX | 2020-12-31 | Mulberry |  | T4 | 69 |  |  | Replace dist. trans. T4 at Mulberry | IN |  |  | M2a_Pre-Project Approval | 1607350 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14094 | 2017-09-15 | 2018SIGE22 | 23243 | 2017-09-15 | CB | 2020-12-31 | Mt. Vernon |  |  | 69 |  |  | Replace OCB 177 at Mt. Vernon (253533 - 10MTVN69) | IN |  |  | M2a_Pre-Project Approval | 160000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14094 | 2017-09-15 | 2018SIGE22 | 23244 | 2017-09-15 | CB | 2020-12-31 | Mt. Vernon |  |  | 69 |  |  | Replace OCB 277 at Mt. Vernon (253533 - 10MTVN69) | IN |  |  | M2a_Pre-Project Approval | 160000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14095 | 2017-09-15 | 2018SIGE24 | 23245 | 2017-09-15 | CB | 2020-12-31 | New Harmony |  |  | 69 |  |  | Replace OCB 277 at New Harmony (253607 - 10NEWHRM) | IN |  |  | M2a_Pre-Project Approval | 160000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14096 | 2018-09-13 | 2018SIGE25 | 23246 | 2018-09-13 | LNrb | 2019-06-01 | Leonard Rd. | St. Phillips | 31 | 69 |  |  | Rebuild 6.8 miles of 69 kV line from Leonard Rd. (253700 - 10LEONRD) to St. Phillips (253577 - 10STPHIL) | IN |  |  | M2a_Pre-Project Approval | 3528600 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14097 | 2017-09-15 | 2018SIGE26 | 23247 | 2017-09-15 | CB | 2020-12-31 | Dubois |  |  | 138 |  |  | Replace 138 kV OCB 2000 at Dubois (253522 - 10DUBS13) | IN |  |  | M2a_Pre-Project Approval | 291000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 14097 | 2017-09-15 | 2018SIGE26 | 23248 | 2017-09-15 | CB | 2020-12-31 | Dubois |  |  | 138 |  |  | Replace 138 kV OCB 3000 at Dubois (253522 - 10DUBS13) | IN |  |  | M2a_Pre-Project Approval | 291000 | Engineering |  | N | N | N
A in MTEP18 | A | Central | SIGE | 15819 | 2018-10-03 | SIGE19-1 | 23861 | 2018-09-13 | LNrb | 2019-12-31 | Lynnville | Winslow | 36 | 69 |  |  | Rebuild 4.98 miles of 69 kV line due to aging infrastructure. | IN | 4.98 | 0 | Planned | 2950000 | Engineering Preliminary |  | N | N | N
A in MTEP18 | A | South | SMEPA | 12215 | 2018-08-27 |  | 22349 | 2018-08-27 | Dist | 2019-01-01 | West Hattiesburg SS | West Hattiesburg |  | 69 |  |  | In order to serve the West Hattiesburg delivery point reliably and more economically , service will be established through Cooperative Energy's existing 69 kV Line 97 (West Hattiesburg SS - West Hattiesburg) by closing in the switch at the West Hattiesburg Substation. | MS |  |  | Planned | 0 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13881 | 2017-09-12 |  | 22947 | 2017-09-19 | LNrb | 2019-06-01 | Magee | Maddox |  | 69 |  |  | Abandon 2 mi. of Line 59 (Magee - Maddox, 6.63 mi.) in the city of Magee and reroute as double circuit along Line 163A. | MS |  |  | Planned | 1156000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13882 | 2017-09-12 |  | 22948 | 2017-09-19 | LNrb | 2019-06-01 | Rocky Creek | Agricola |  | 69 |  |  | Completely rebuild Line 73 (Rocky Creek - Agricola, 8.2 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 2460000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13883 | 2017-09-12 |  | 22949 | 2017-09-19 | LNrb | 2020-06-01 | Benndale | Basin |  | 69 |  |  | Completely rebuild Line 71 (Benndale - Basin, 12.14 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 3642000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13884 | 2017-09-12 |  | 22950 | 2017-09-19 | LNrb | 2020-06-01 | Columbia | Goss GOAB |  | 69 |  |  | Completely rebuild Line 53 (Columbia - Goss GOAB, 9.04 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 2712000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13885 | 2017-09-12 |  | 22953 | 2017-09-19 | LNrb | 2021-06-01 | Wiggins GOAB | Stillmore |  | 69 |  |  | Completely rebuild Line 37C (Wiggins GOAB - Stillmore, 7.22 mi.) at 161kV construction with more reliable concrete structures. | MS |  |  | Planned | 3104600 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13886 | 2017-09-12 |  | 22955 | 2017-09-19 | LNrb | 2021-06-01 | Goss GOAB | Hathorn |  | 69 |  |  | Completely rebuild Line 53A (Goss GOAB - Hathorn, 3.53 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 1059000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13887 | 2017-09-12 |  | 22956 | 2017-09-19 | LNrb | 2021-06-01 | Basin | Agricola |  | 69 |  |  | Completely rebuild Line 72 (Basin - Agricola, 9.15 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 2745000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13896 | 2017-09-12 |  | 22967 | 2017-09-19 | LNrb | 2022-06-01 | Rocky Creek | Sawmill Road |  | 69 |  |  | Completely rebuild Line 33B (Rocky Creek - Sawmill Road, 5.54 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 1662000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13897 | 2017-09-12 |  | 22969 | 2017-09-19 | LNrb | 2022-09-01 | Sawmill Road | SE Greene |  | 69 |  |  | Completely rebuild Line 33D (Sawmill Road - SE Greene, 1.39 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS |  |  | Planned | 417000 |  |  | N | N | N
A in MTEP18 | A | South | SMEPA | 13898 | 2017-09-12 |  | 22970 | 2017-09-19 | LNrb | 2022-06-01 | Hathorn | Oakvale |  | 69 |  |  | Close a fiber path from Columbia to Oakvale by a complete rebuild of Line 53B (Hathorn - Oakvale, 5.33 mi.) with 795 ACSR and OPGW. | MS |  |  | Planned | 1599000 |  |  | N | N | N
A in MTEP18 | A | West | SMPA | 14484 | 2018-08-16 |  | 23331 | 2017-12-04 | BUS | 2018-12-05 | Rutland |  |  | 161 |  |  | Install a ring bus on the existing 161kV bus at SMMPA's Rutland 161/69kV substation. | MN |  |  | Proposed | 2750000 | Planning Preliminary |  | N | N | N | Y
A in MTEP18 | A | West | SMPA | 16065 | 2018-10-03 |  | 24190 | 2018-09-18 | SUB | 2019-09-01 | West Owatonna |  |  | 161 |  |  | 161kV Ring bus upgrade | MN |  |  | Planned | 1500000 | Budgetary |  | N | N | N
A in MTEP18 | A | Central | Vectren | 9953 | 2018-10-03 | SIGE19-17 | 21404 | 2018-09-14 | Dist | 2019-04-01 | FRANCISCO | TOYOTA | Z76 | 138 | 12 |  | New 138kV/12kV distribution substation | IN |  |  | Planned | 11500000 | Engineering |  | N | N | N
A in MTEP18 | A | East | WPSC | 4383 | 2018-02-22 | Bradley Xmsn | 8398 | 2018-02-22 | SUB | 2020-06-01 | Bradley | Substation Upgrade |  | 138 | 69 |  | 138kV Breaker Replacement and Protective Equipment Upgrade | MI |  |  | Proposed | 7400000 | Planning |  | N | N | N | Y
A in MTEP18 | A | East | WPSC | 4383 | 2018-02-22 | Bradley Xmsn | 21506 | 2018-02-22 | SUB | 2020-06-01 | Bradley |  |  | 138 |  |  | NOTHING | MI |  |  | Planned | 0 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 4383 | 2018-02-22 | Bradley Xmsn | 21505 | 2018-02-22 | SUB | 2020-06-01 | Bradley |  |  | 138 |  |  | Bradley Land, zoning, landscaping | MI |  |  | Planned | 1000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 8222 | 2018-03-06 | Bradley line mods | 20610 | 2018-06-11 | LN | 2022-12-31 | Bradley 138kV & 69kV |  |  | 138 | 69 |  | Construction to support the upgrade of the Bradley 138kV and 69kV station. | MI |  |  | Proposed | 1000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 9920 | 2017-08-25 | GRX Station Upgrade | 21333 | 2015-09-15 | SwSta | 2020-12-31 | Gravese Crossing |  |  | 69 |  |  | Upgrade the Graves Crossing station | MI |  |  | Proposed | 500000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 12199 | 2017-09-15 | Grand Traverse Station Upgrade | 22323 | 2018-01-18 | SUB | 2020-12-31 | Grand Traverse |  |  | 138 |  |  | Upgrade bus, protection and control and switching equipment at the station | MI |  |  | Proposed | 2150000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 12243 | 2017-08-25 | 2020 Battery Bank Replacement Project | 22374 | 2017-08-25 | SwSta | 2020-12-31 | Unknown |  |  | 69 |  |  | Replace one battery bank that has reached the end of life | MI |  |  | Proposed | 35000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 13575 | 2017-08-25 |  | 22677 | 2017-08-25 | LNrb | 2019-12-31 | Crawford | Weidman |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 17 |  | Planned | 9000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13576 | 2017-08-25 |  | 22678 | 2017-11-29 | LNrb | 2021-12-31 | Airport | Hillman |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 9 |  | Planned | 4500000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13577 | 2017-08-25 |  | 22679 | 2017-08-25 | LNrb | 2021-12-31 | Atlanta | Hillman |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 22 |  | Planned | 11000000 |  |  | N | N | N
A in MTEP18 | A | East | WPSC | 13578 | 2017-08-25 |  | 22680 | 2018-06-08 | LNrb | 2021-12-31 | Gun Lake Junction | Otsego |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 336ACSR conductor and OPGW | MI | 8 |  | Planned | 4000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13579 | 2017-08-25 |  | 22681 | 2017-08-25 | SwSta | 2021-12-31 | South Boardman |  |  | 69 |  |  | The control house and controls will be upgraded to include Wolverine’s standard protection and control system. The existing 69 kV switches limit facility ratings to sub-standard capacity and will be replaced. Additionally, the existing bus configuration will be upgraded to a ring bus and will be built to 138 kV design. | MI |  |  | Planned | 3000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13580 | 2017-08-25 |  | 22682 | 2017-08-25 | SwSta | 2021-12-31 | Unknown |  |  | 138 |  |  | This project will replace one battery bank at a Transmission Station. | MI |  |  | Planned | 35000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | 22683 | 2017-08-25 | LNrb | 2020-12-31 | Airport | Posen |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 16 |  | Planned | 8000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | 22688 | 2017-08-25 | LNrb | 2021-12-31 | Atlanta | Tower |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 28 |  | Planned | 14000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | 22687 | 2017-08-25 | LNrb | 2020-12-31 | Pellston | Oden |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 11 |  | Planned | 5500000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | 22686 | 2017-08-25 | LNrb | 2020-12-31 | Cheboygan | Pellston |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 19 |  | Planned | 9500000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | 22685 | 2017-08-25 | LNrb | 2020-12-31 | Cheboygan | Tower |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 22 |  | Planned | 11000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13581 | 2017-08-25 |  | 22684 | 2017-08-25 | LNrb | 2020-12-31 | Posen | Tower |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | 36 |  | Planned | 18000000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 13667 | 2017-09-01 |  | 22744 | 2017-09-01 | LNrb | 2019-12-31 | Hersey | Leroy |  | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW. | MI | 15 |  | Planned | 7500000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 14000 | 2018-02-22 |  | 23111 | 2017-09-14 | LNrb | 2022-12-31 | Burnips | Portland |  | 69 |  |  | Line Rebuild | MI | 59 |  | Proposed | 29700000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23113 | 2018-02-22 | LNcnv | 2020-06-01 | Goodwin Junction | Goodwin |  | 138 |  |  | Upgrade equipment to 138kV operation | MI |  |  | Proposed | 900000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23391 | 2018-02-22 | LNcnv | 2020-06-01 | Monterey Junction |  |  | 138 |  |  | Upgrade equipment to 138kV operation | MI |  |  | Proposed | 200000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23390 | 2018-02-22 | LNcnv | 2020-06-01 | Burnips Junction | Burnips |  | 138 |  |  | Upgrade equipment to 138kV operation | MI |  |  | Proposed | 900000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23260 | 2018-02-22 | SUB | 2020-06-01 | Burnips |  |  | 138 | 69 |  | Substation rebuild - Cost adder to existing MTEP project #3335 138/69kV transformer will be installed on this project and re-located to Portland in 2024. | MI |  |  | Proposed | 4800000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23118 | 2018-02-22 | LNcnv | 2020-06-01 | Drenth Junction | Drenth |  | 138 |  |  | Upgrade line to 138kV construction | MI | 0.25 |  | Proposed | 950000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23116 | 2018-02-22 | SUB | 2024-12-31 | Portland |  |  | 138 | 69 |  | Add 138kV facility to tie into the existing Portland 69kV station through a 138/69kV transformer. | MI |  |  | Proposed | 3250000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14001 | 2018-02-22 |  | 23114 | 2018-02-22 | LNrl | 2020-06-01 | Blendon |  |  | 138 |  |  | Line Modifications for Blendon Station reconfiguration | MI |  |  | Proposed | 1000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14003 | 2017-09-14 |  | 23119 | 2017-09-14 | LN | 2019-12-31 | Grande Lake Junction | Grand Lake |  | 138 |  |  | New 138KV line | MI |  | 0.5 | Planned | 400000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14144 | 2017-09-20 |  | 23274 | 2017-09-20 | SUB | 2021-12-31 | Airport |  |  | 138 |  |  | Station Terminal Addition | MI |  |  | Planned | 600000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 14304 | 2017-10-13 |  | 23305 | 2017-10-12 | LINE | 2019-12-31 | TBD |  |  | 69 |  |  | Install approximately 100 miles of fiber | MI | 100 |  | Proposed | 6000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14326 | 2017-10-13 |  | 23314 | 2017-10-12 | LINE | 2020-12-31 | TBD |  |  | 69 |  |  | Install approximately 100 miles of fiber on existing structuresa | MI | 100 |  | Proposed | 6000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14327 | 2017-10-13 |  | 23315 | 2017-10-12 | LINE | 2021-12-31 | TBD |  |  | 69 |  |  | Install approximately 100 miles of fiber | MI | 100 |  | Proposed | 6000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14584 | 2018-01-18 |  | 23337 | 2017-12-19 | LNrl | 2021-12-31 | Lake County | Pere Marquette |  | 138 |  |  | Relocate line into Pere Marquette Station | MI |  |  | Proposed | 250000 | Planning |  | N | N | N
A in MTEP18 | A | East | WPSC | 14644 | 2018-01-16 |  | 23344 | 2018-01-16 | LNrb | 2020-12-31 | Gaylord OCB | Lewiston | 1 | 69 |  |  | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW. | MI | 18 |  | Proposed | 9000000 | Budgetary |  | N | N | N
A in MTEP18 | A | East | WPSC | 14704 | 2018-02-02 |  | 23356 | 2018-01-25 | TAP | 2019-05-01 | Richland | Cadillac | 1 | 69 |  |  | Install tap pole and 2 switches at Stoney Corners road on Richland to Cadillac line section to allow Consumers to interconnect service for new Stoney Corners substation. | MI |  |  | Proposed | 200000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 12011 | 2018-04-13 |  | 22083 | 2017-05-26 | BUS | 2020-12-31 | Goodview |  |  | 69 |  |  | Upgrade bus at Goodview substation to allow normally open from Merrick to Goodview to be closed permanently. | WI |  |  | Proposed | 1250000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 12011 | 2018-04-13 |  | 22597 | 2017-05-26 | BUS | 2020-12-31 | Winona |  |  | 69 |  |  | Upgrade bus at Winona substation to allow normally open from Merrick to Goodview to be closed permanently. | WI |  |  | Proposed | 1250000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14028 | 2018-04-13 |  | 23139 | 2017-11-29 | SUB | 2019-07-01 | Stanley |  |  | 69 |  |  | Replace the existing TR1 with a new 28 MVA unit with Load Tap Changers (LTC) | WI |  |  | Planned | 1836000 |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14029 | 2018-04-13 |  | 23143 | 2017-11-15 | SUB | 2019-06-01 | Cable |  |  | 69 |  |  | Replace the existing transformer with a new 7 MVA unit | WI |  |  | Planned | 800000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14033 | 2018-04-13 |  | 23148 | 2017-11-15 | SUB | 2018-12-31 | Coulee Ave |  |  | 69 | 13.8 |  | Replace the aging units at Coulee Ave with 2 new 50 MVA LTC unit | WI |  |  | Planned | 3200000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14034 | 2018-04-13 |  | 23152 | 2017-09-21 | SUB | 2018-01-31 | Gateway |  |  | 69 |  |  | Install a bus tie breaker to reduce the loss of both Transformers at Gateway. Also install revenue metering | ND |  |  | Planned | 470000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14035 | 2018-04-13 |  | 23153 | 2017-09-15 | SUB | 2018-12-01 | Aldrich |  |  | 115 |  |  | Open 2x115 kV breakers at Aldrich to create a bypass from St Louis Park to Medicine Lake. | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14035 | 2018-04-13 |  | 23155 | 2017-09-15 | TEQ | 2018-12-01 | Edina |  |  | 115 |  |  | Replace the switch at Edina to increase capacity | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14035 | 2018-04-13 |  | 23154 | 2017-09-21 | LNup | 2018-12-01 | St Louis Park | Edina | 1 | 115 |  |  | Rerate Line to 4 ft/sec. | MN |  |  | Planned | 1200000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14036 | 2018-04-13 |  | 23157 | 2017-09-15 | LNup | 2018-12-01 | Terminal |  |  | 115 |  |  | Swap the line terminations of the Gopher and Merriam Park 115 kV lines at Terminal | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14036 | 2018-04-13 |  | 23158 | 2017-09-21 | LNup | 2018-12-01 | Terminal |  |  | 115 |  |  | Swap line terminations of the Arden Hills and the Rose Place 115 kV lines at Terminal. | MN |  |  | Planned | 1200000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14037 | 2018-04-13 |  | 23159 | 2017-11-15 | SUB | 2018-12-01 | Sauk River |  |  | 115 | 34.5 |  | Install a second 70 MVA transformer at Sauk River | MN |  |  | Planned | 2400000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14038 | 2018-04-13 |  | 23161 | 2017-11-15 | TX | 2020-05-01 | Wilson |  |  | 115 |  |  | This project will install a 4th distribution transformer at Wilson | MN |  |  | Planned | 4000000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14043 | 2018-04-13 |  | 23163 | 2017-11-15 | SUB | 2019-06-01 | Salida Crossing |  |  | 115 | 34.5 |  | Install a 70 MVA transformer at Salida Crossing | MN |  |  | Planned | 3100000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14043 | 2018-04-13 |  | 23164 | 2017-11-15 | SUB | 2019-06-01 | Salida Crossing |  |  | 115 |  |  | Install a new 115 kV breaker at Salida Crossing for new transformer | MN |  |  | Planned | 800000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14045 | 2018-04-24 |  | 23168 | 2017-11-15 | TX | 2020-05-01 | Louise |  |  | 115 | 13.8 | 50 | This project will install a 2nd 115/13.8 kV 50 MVA transformer, circuit switcher, 2 new feeders, and one 115 kV breaker at Louise substation. | SD |  |  | Planned | 4900000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14046 | 2018-04-13 |  | 23165 | 2017-09-21 | CAP | 2021-06-01 | Falls |  |  | 115 |  |  | Install a 30 MVAR capacitor bank at Falls substation. | SD |  |  | Planned | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14047 | 2018-04-13 |  | 23166 | 2017-09-21 | CAP | 2020-06-01 | Lincoln County |  |  | 115 |  |  | Install a 30 MVAR capacitor bank at Lincoln County substation. | SD |  |  | Planned | 2000000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14048 | 2018-01-08 |  | 23169 | 2017-11-15 | DVAR | 2020-06-01 | Forbes |  |  | 500 |  |  | Retire the existing 500 kV SVC | MN |  |  | Planned | 1000000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14049 | 2018-04-13 |  | 23173 | 2017-09-15 | LNrl | 2019-06-01 | Indiana | Twin Lake |  | 115 |  |  | Relocate Line 0805 – 1.65 miles of line located on western edge of railroad corridor. | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14049 | 2018-04-13 |  | 23176 | 2017-09-15 | LNrl | 2019-06-01 | Indiana | Aldrich |  | 115 |  |  | Line 0805, 1.9 miles of line located on eastern edge of railroad corridor, 0.25 miles of line located on western edge of railroad corridor | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14049 | 2018-04-13 |  | 23175 | 2017-09-15 | LNrl | 2019-06-01 | Aldrich | Medicine Lake |  | 115 |  |  | Relocate Line 0805/0814 - Double Circuit, 0.45 miles of line located on eastern edge of railroad corridor. | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14049 | 2018-04-13 |  | 23174 | 2017-09-15 | LNrl | 2019-06-01 | Indiana | Aldrich |  | 115 |  |  | Relocate Line 0805/0814 - Double Circuit, 0.45 miles of line located on eastern edge of railroad corridor. | MN |  |  | Planned |  |  |  | N | N | N
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | 23189 | 2017-11-15 | CAP | 2017-12-31 | Gleason Lake |  |  | 115 |  |  | 40 MVAR capacitor bank installed at Gleason Lake | MN |  |  | Planned | 1900000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | 23195 | 2017-11-15 | SUB | 2020-06-01 | Hollydale |  |  | 69 | 13.8 |  | Expansion of the existing Hollydale substation to accommodate serving load at Hollydale at 69 kV on a permanent basis. This project includes distribution work in the Hollydale substation and feeder upgrades near the substation. | MN |  |  | Planned | 18200000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | 23194 | 2017-11-15 | SUB | 2018-12-31 | Pomerleau Lake |  |  | 115 | 69 |  | New 115/69 kV substation, tapped off of the Parkers Lake to Plymouth 115 kV line. | MN |  |  | Planned | 12300000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | 23192 | 2017-11-15 | LN | 2018-12-31 | Hollydale | Pomerleau Lake | 1 | 69 |  |  | This is an extension of the old Hollydale to Plymouth 69 kV line. | MN |  | 0.75 | Planned | 2900000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | 23191 | 2017-11-15 | LNrb | 2018-06-01 | Gleason Lake | Parkers Lake | 2 | 115 |  |  | Rebuild Gleason Lake to Parkers Lake 115 kV double circuit to two single circuits. | MN |  |  | Planned | 3400000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14054 | 2018-04-13 |  | 23190 | 2017-11-15 | LNrb | 2018-06-01 | Gleason Lake | Parkers Lake | 1 | 115 |  |  | Rebuild Gleason Lake to Parkers Lake 115 kV double circuit to two single circuits. | MN |  |  | Planned | 3600000 | Planning |  | N | N | N
A in MTEP18 | A | West | XEL | 14844 | 2018-04-24 |  | 23514 | 2018-07-17 | TX | 2023-06-01 | RRK | RRK | 9 | 345 | 115 |  | Upgrade Red Rock TR 9 and associated bus work and equipment to higher rating | MN |  |  | Proposed | 23000000 | Planning | Generator | N | N | N | Y
A in MTEP18 | A | West | XEL | 14844 | 2018-04-24 |  | 23515 | 2018-07-17 | TX | 2023-06-01 | RRK | RRK | 10 | 345 | 115 |  | Upgrade Red Rock TR10 and associated bus work and equipment to higher rating | MN |  |  | Proposed | 23000000 | Planning |  | N | N | N
A in MTEP17 | A | South | AECC | 12603 | 2018-08-22 |  | 22458 | 2018-08-22 | LN | 2018-12-31 | Olmstead | Zion Hill |  | 115 |  |  | 115kV line | AR |  | 5.5 | Planned | 4500000 | Planning |  | N | N | N
A in MTEP17 | A | South | AECC | 13123 | 2018-08-22 |  | 22577 | 2018-08-22 | CB | 2019-11-01 | Oppelo |  |  | 161 |  |  | Add 161kV line breakers | AR |  |  | Planned | 800000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 7801 | 2017-12-08 |  | 20088 | 2018-09-27 | LNrc | 2018-12-31 | Cahokia | Ashely | 1 | 138 |  | 399 | Reconductor 2.6 miles of parallel 350 kcmil copper conductor with conductor capable of carrying 2000 A under summer emergency conditions. | MO,IL | 2.6 |  | Planned | 2200000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 9719 | 2017-12-08 |  | 21100 | 2018-09-27 | SUB | 2018-12-01 | Cahokia |  |  | 138 | 138 | 717 | Upgrade Bus-Tie 3-4 capability to 3000 A. | IL |  |  | Planned | 2500000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 9724 | 2017-12-08 |  | 21108 | 2018-09-28 | SUB | 2018-12-01 | Newton |  |  | 345 | 138 | 450 | Relocate Newton 345/138 kV Transformer #1 connection point. | IL |  |  | Under Construction | 7300000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 9841 | 2017-12-08 |  | 21217 | 2018-07-06 | TX | 2018-09-01 | South Bloomington |  |  | 138 | 34.5 | 112 | Install 138-34.5 kV transformer | IL |  |  | Planned | 5600000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 9842 | 2018-09-28 |  | 21219 | 2018-09-28 | SUB | 2020-12-01 | Hershey |  |  | 138 | 69 | 112 | Install ultimate 6 position 138 kV ring bus and 138-69 kV transformer. | IL |  |  | Planned | 9100000 | Planning |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 10883 | 2018-08-24 |  | 21679 | 2018-01-05 | TEQ | 2025-12-01 | Ina | Benton, NW | 1 | 138 | 138 | 159 | Install 2000 A, 138 kV ring bus at Ina | IL |  |  | Proposed | 7300000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 10883 | 2018-08-24 |  | 21680 | 2016-09-06 | TEQ | 2019-06-01 | Ina | Mt. Vernon | 1 | 138 |  | 159 | Remove metering set | IL |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 10885 | 2017-12-08 |  | 21683 | 2018-07-06 | TEQ | 2018-12-01 | Cahokia |  |  | 138 |  | 240 | Upgrade terminal equipment | IL |  |  | Planned | 100000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11863 | 2017-12-08 |  | 21844 | 2018-09-28 | CB | 2019-12-01 | Havana |  |  | 138 |  |  | Replace six 138 kV breakers | IL |  |  | Planned | 9400000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11924 | 2017-12-08 |  | 21874 | 2018-07-06 | SUB | 2020-12-01 | Mississippi |  |  | 138 |  | 478 | Establish 138 kV ring bus. | IL |  |  | Planned | 9800000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11945 | 2017-12-08 |  | 21906 | 2018-09-28 | SwSta | 2018-10-15 | Herzog |  |  | 138 |  | 478 | Establish 138 kV ring bus | IL |  |  | Planned | 6600000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11946 | 2017-12-08 |  | 21907 | 2018-09-28 | SUB | 2018-12-01 | Granite City 23rd. Street |  |  | 138 |  |  | Establish 138 kV ring bus | IL |  |  | Planned | 11600000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11958 | 2018-04-12 |  | 21919 | 2018-07-06 | LNrl | 2018-10-31 | Venice | Campbell | 1 | 138 |  | 240 | Construct new double-circuit river crossing | IL,MO | 0.5 |  | Planned | 11700000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11958 | 2018-04-12 |  | 21921 | 2018-09-28 | CB | 2018-10-31 | Hall Street |  |  | 138 |  |  | Install three 138 kV breakers | MO |  |  | Planned | 1900000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11958 | 2018-04-12 |  | 21920 | 2018-09-28 | LNrl | 2018-10-31 | Venice | Hall Street |  | 138 |  | 240 | Construct new double-circuit river crossing | IL,MO | 0.5 |  | Planned | 700000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 11973 | 2017-12-08 |  | 21943 | 2018-09-28 | SwSta | 2019-06-01 | Cane |  |  | 138 |  | 478 | Establish a 3-position 138 kV ring bus. | IL |  |  | Planned | 7900000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 12191 | 2017-12-08 |  | 22312 | 2018-09-28 | SUB | 2018-12-01 | Latham |  |  | 138 |  | 478 | Install 138 kV breaker | IL |  |  | Planned | 2200000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | AmerenIL | 12191 | 2017-12-08 |  | 22314 | 2018-09-28 | LNrb | 2018-12-01 | Latham | Latham Tap |  | 138 |  | 399 | construct 138 kV line | IL |  | 1 | Planned | 2800000 | Budgetary |  | N | N | N
A in MTEP17 | A | West | ATC | 7581 | 2017-12-08 | PR06425, F4434, WO601064 | 20004 | 2018-09-28 | IND | 2020-01-14 | Forest Junction |  |  | 138 |  |  | Install new 25 Mvar inductor at Forest Jct 138 kV | WI |  |  | Under Construction | 1762635 | Engineering |  | N | N | N
A in MTEP17 | A | West | ATC | 7600 | 2017-12-08 | PR06459 | 20033 | 2018-06-29 | LNrb | 2023-12-31 | Sheepskin | Stoughton | 1 | 69 |  | 79 | Rebuild Y-12 Stoughton to Sheepskin | WI | 6.46 |  | M1_Final SPM or OOC | 12524014 | Engineering |  | N | N | N
A in MTEP17 | A | West | ATC | 9930 | 2017-12-08 | PR07296, 602003, 602026 | 21343 | 2018-03-30 | LNup | 2019-09-27 | Lost Dauphin | Red Maple | 1 | 138 |  | 246 | Lost Dauphin - Red Maple 138-kV line uprate. | WI |  |  | Under Construction | 180000 |  |  | N | N | N
A in MTEP17 | A | West | ATC | 9968 | 2017-12-08 |  | 21383 | 2018-03-29 | LNrb | 2020-12-31 | Portage | Staff | 1 | 138 |  | 294 | Rebuild 138KV Line X-6 Portage - Staff Substation. | WI |  |  | Planned | 12000000 |  |  | N | N | N
A in MTEP17 | A | West | ATC | 9974 | 2017-12-08 |  | 21391 | 2018-06-29 | LNrb | 2020-07-06 | North Randolph | Staff | 1 | 138 |  | 294 | Rebuild 138KV Line X-97 Staff - North Randolph Substation. | WI |  |  | Planned | 5000000 |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12031 | 2017-12-08 | PR07555 | 22107 | 2018-06-29 | CB | 2020-11-01 | Hilltop |  |  | 69 |  |  | Install breakers at Hilltop Substation. | WI |  |  | Planned | 1000000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12038 | 2017-12-08 | PR07560, PR07033, F4576 | 22116 | 2018-05-09 | CB | 2019-05-22 | Arpin |  |  | 138 |  |  | Install 138KV Breaker Arpin SS | WI |  |  | Under Construction | 5000000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12044 | 2017-12-08 | PR07559 | 22124 | 2018-06-29 | CB | 2019-03-01 | Wells Street |  |  | 69 |  |  | Install Circuit Breaker Wells Street SS | WI |  |  | Planned | 260000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12046 | 2017-12-08 | PR07558 | 22127 | 2018-03-30 | CB | 2020-12-01 | Whitcomb |  |  | 69 |  |  | Install 69KV Breaker Whitcomb SS | WI |  |  | Planned | 1500000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12051 | 2017-12-08 | PR07554 | 22129 | 2018-03-30 | CB | 2019-12-31 | Harrison |  |  | 69 |  |  | Install 69KV Breaker Harrison SS | WI |  |  | Planned | 580000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12054 | 2017-12-08 | PR07552 | 22134 | 2018-03-30 | CB | 2018-12-01 | Highway 8 |  |  | 115 |  |  | Install 115KV Breakers Highway 8 | WI |  |  | Under Construction | 1300000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12058 | 2017-12-08 | PR07515 | 22137 | 2018-06-29 | CB | 2019-03-01 | Burlington |  |  | 138 |  |  | Install 138KV Breakers Burlington SS | WI |  |  | Under Construction | 1400000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12062 | 2017-12-08 | PR07550 | 22141 | 2018-09-28 | CB | 2019-12-01 | Nordic |  |  | 138 |  |  | Install 138KV Breakers Nordic Asset SS | WI |  |  | Under Construction | 5500000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12100 | 2017-12-08 | PR07527 | 22203 | 2018-09-28 | SUB | 2020-06-01 | Waupun |  |  | 69 |  |  | Rebuild Waupun 69KV Substation | WI |  |  | Under Construction | 4200000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12103 | 2017-12-08 | PR07548 | 22212 | 2018-06-29 | CB | 2019-12-28 | Ellinwood |  |  | 138 |  |  | Install 138KV Breakers | WI |  |  | Planned | 2400000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12103 | 2017-12-08 | PR07548 | 22217 | 2018-06-29 | LINE | 2019-12-28 | Ellinwood |  |  | 138 |  | 142 | Uprate line SPTG311 | WI |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12103 | 2017-12-08 | PR07548 | 22213 | 2018-06-29 | BUS | 2019-12-28 | Ellinwood |  |  | 138 |  |  | Bus conductor upgrade | WI |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12115 | 2017-12-08 |  | 22237 | 2016-09-14 | SUB | 2020-12-31 | Coyne Sub | Saratoga Sub |  | 115 |  | 230 | Baker St Substation Re-config. | WI |  |  | Planned | 4360493 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12115 | 2017-12-08 |  | 22240 | 2016-09-14 | LINE | 2020-12-31 | Coyne Sub | Saratoga Sub |  | 115 |  | 89 | Baker St. T-Line work | WI |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12148 | 2017-12-08 |  | 22275 | 2018-03-29 | LNrb | 2020-06-30 | Cedar Ridge | Mullet River |  | 138 |  | 294 | Cedar Ridge Wind Generation Substation – Mullet River Substation | WI | 17 |  | Planned | 22800000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12150 | 2017-12-08 | PR07525, F5011,WO602384 | 22277 | 2018-09-28 | LNrb | 2019-09-30 | Ohmstead | Cedar Ridge |  | 138 |  | 294 | Rebuild Ohmstead Substation - Cedar Ridge Wind Generation Substation | WI | 4.5 |  | Under Construction | 6900000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12177 | 2017-12-08 | PR07233 | 22294 | 2016-09-15 | LNrb | 2020-12-31 | Dane | Waunakee |  | 69 |  | 65 | Rebuild 69kV Y-143 (Dane Substation – Waunakee SW Station | WI | 4.5 |  | Planned | 7000000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12178 | 2017-12-08 | PR4969,F3630,F3636,W00693999,WO069407 | 22296 | 2016-09-15 | LNrb | 2020-12-31 | Saratoga | Coyne |  | 115 |  | 14.4 | Rebuild 115kV Line Saratoga Substation – Coyne Substation (T-72) | WI | 6.3 |  | Planned | 6600000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12183 | 2017-12-08 | PR07574, F5182 | 22301 | 2018-03-30 | CB | 2019-12-01 | Sycamore |  |  | 69 |  |  | Install 69KV Breakers Sycamore SS | WI |  |  | Planned | 1220000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12184 | 2017-12-08 | PR07575 | 22302 | 2018-06-29 | CB | 2019-04-15 | Manrap |  |  | 69 |  |  | Install 69KV Breakers Manrap SS | WI |  |  | M1_Final SPM or OOC | 1336964 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12185 | 2017-12-08 |  | 22303 | 2018-09-28 | LNrb | 2021-06-30 | Butte des Morts | Neevin |  | 138 |  | 292 | Rebuld Butte des Morts- Neevin | WI | 3.03 |  | Planned | 20600000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12185 | 2017-12-08 |  | 22306 | 2018-09-28 | LNrb | 2021-06-30 | Mears Corners | Sunset Point |  | 138 |  | 191 | Rebuild Mears Corners - Sunset Point | WI | 4 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12185 | 2017-12-08 |  | 22305 | 2018-09-28 | LNrb | 2021-06-30 | Woodenshoe | Mears Corners |  | 138 |  | 213 | Rebuild Woodenshoe - Mears Corners | WI | 2.6 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12185 | 2017-12-08 |  | 22304 | 2018-09-28 | LNrb | 2021-06-30 | Neevin | Woodenshoe |  | 138 |  | 298 | Rebuild Neevin - Woodenshoe | WI | 2.6 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12346 | 2017-12-08 |  | 22401 | 2018-03-29 | LN | 2021-03-31 | Pleasant View | Alliant Energy Dane County Substation |  | 138 |  | 272 | Double circuit underground cable 138KV | WI |  | 1.5 | Planned | 26000000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12346 | 2017-12-08 |  | 22403 | 2018-03-30 | SUB | 2021-03-31 | Substatiom |  |  | 138 |  |  | GIS 138KV Distribution Substation | WI |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12346 | 2017-12-08 |  | 22402 | 2018-03-29 | LN | 2021-03-31 | Alliant Energy Dane County Substation | Cross Country |  | 138 |  | 246 | Double circuit underground cable 138KV | WI |  | 1.5 | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ATC | 12464 | 2017-12-08 | PR07605 | 22441 | 2018-03-30 | CB | 2018-12-01 | Glenview |  |  | 69 |  | 3000 | Install 69KV Breaker Glenview SS | WI |  |  | Under Construction | 750000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12465 | 2017-12-08 | PR07604 | 22442 | 2018-06-29 | CB | 2018-08-31 | Maplewood |  |  | 138 |  | 3000 | Install 69KV Breaker Maplewood SS | WI |  |  | Under Construction | 1000000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12466 | 2017-12-08 | PR07591 | 22443 | 2018-03-30 | CB | 2020-09-15 | Venus |  |  | 115 |  | 3000 | Install 115KV Breaker Venus SS | WI |  |  | Planned | 900000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12467 | 2017-12-08 | PR07590 | 22444 | 2018-03-30 | CB | 2018-12-01 | Howard |  |  | 138 |  | 3000 | Install 138KV Breakers Howard SS | WI |  |  | Under Construction | 1400000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 12903 | 2017-12-08 | PR07690 | 22545 | 2018-06-29 | CB | 2019-12-28 | Mount Horeb |  |  | 69 |  |  | Install breaker to Y-175 tap and replace breaker 822-S. | WI |  |  | M1_Final SPM or OOC | 2300000 |  |  | N | N | N
A in MTEP17 | A | West | ATC | 13004 | 2017-12-08 | PR07595 | 22558 | 2018-06-29 | IND | 2019-05-30 | Paddock |  |  | 138 |  | 2000 | Paddock Series Reactor | WI |  |  | Under Construction | 6139927 |  |  | N | N | N
A in MTEP17 | A | West | ATC | 13064 | 2017-12-08 | PR07710 | 22561 | 2018-06-29 | LNup | 2018-06-29 | McMillan | Wildwood |  | 115 |  | 113 | Uprate 115 kV line N-144 | WI | 1 |  | Under Construction | 187000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 13065 | 2017-12-08 | PR07674 | 22562 | 2018-06-29 | CB | 2019-06-01 | Plymouth 4 |  |  | 138 |  | 2000 | Add two 138 kV line breakers at Plymouth 4 | WI |  |  | M1_Final SPM or OOC | 2845750 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 13066 | 2017-12-08 | PR07673 | 22563 | 2018-03-30 | TAP | 2019-07-30 | Edgerton |  |  | 138 |  | 2000 | New 138 kV Edgerton T-D Loop in and out | WI |  |  | Under Construction | 1600000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 13067 | 2017-12-08 | PR07648 | 22564 | 2018-06-29 | BUS | 2020-04-01 | Arcadian |  |  | 138 |  |  | Bus upgrade to accomodate transformer installation. | WI |  |  | Planned | 260000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 13068 | 2017-12-08 | PR07572 | 22565 | 2018-03-30 | CB | 2019-06-08 | Tripp Rd |  |  | 138 |  | 2000 | Tripp Rd add 138 kV line breakers | WI |  |  | Under Construction | 2000000 | Planning |  | N | N | N
A in MTEP17 | A | West | ATC | 13103 | 2017-12-08 | PR07512 | 22574 | 2018-06-29 | SUB | 2019-04-30 | Kittyhawk |  |  | 345 |  |  | 345 kV Substation | WI |  |  | Under Construction | 42067880 | Planning |  | N | Y | Y
A in MTEP17 | A | West | ATC | 13572 | 2017-12-08 | PR07803 F5305 | 22656 | 2018-06-29 | LNup | 2018-11-09 | Plains | Arnold |  | 138 |  | 722 | Plains - Arnold 138 kV | MI |  |  | Under Construction | 2000000 | Planning |  | N | N | N
A in MTEP17 | A | Central | BREC | 12186 | 2017-12-08 | Project No. 1043 | 22344 | 2017-11-14 | CAP | 2017-02-20 | Coleman EHV |  |  | 161 |  |  | Relocation of 48.6 MVAR capacitor bank from Coleman 161 kV Switchyard to Coleman EHV 161 kV substation. Additionally, PCB, phase inductors and switches will be installed for additional reliability. | KY |  |  | Under Construction | 345000 |  |  | N | N | N
A in MTEP17 | A | Central | BREC | 12205 | 2017-12-21 | Project No. 1046 | 22342 | 2017-11-14 | CAP | 2017-09-05 | Reid EHV |  |  | 161 |  |  | Relocation of 48.6 MVAR capacitor bank from Reid 161 kV Switchyard to Reid EHV 161 kV substation. Additionally, PCB, phase inductors and switches will be installed for additional reliability. | KY |  |  | Planned | 350000 |  |  | N | N | N
A in MTEP17 | A | Central | BREC | 12303 | 2017-12-21 | Project No. 1035 | 22385 | 2016-09-30 | TX | 2017-12-31 | Reid EHV |  |  | 161 | 69 |  | The project involves the addition of one (1) 161/69 kV transformer and one (1) 69 kV line terminal in the existing Reid EHV Substation located in Webster County near Sebree, Kentucky. The project is currently expected to be completed in 2017 at an estimated cost of $1,000,000. | KY |  |  | Planned | 1000000 | Planning |  | N | N | N
A in MTEP17 | A | Central | BREC | 12304 | 2017-12-08 | Project No. 817 | 22386 | 2017-11-14 | LN | 2020-06-30 | Wilson | Sacramento |  | 69 |  |  | This system improvement involves 11 miles of new right-of-way (100 foot width) and a terminal addition at the Wilson substation (no physical expansion of the existing substation is necessary). | KY |  |  | Planned | 3635000 | Planning | Generator | N | N | N | Y
A in MTEP17 | A | East | CETO | 12070 | 2017-12-08 |  | 22153 | 2018-09-26 | CB | 2018-12-31 | CE Breaker Replacement Program - 2018 |  |  | 138 |  |  | Replace damaged or defective circuit breakers across the system. | MI |  |  | M4_Pre-Construction | 1300000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 12071 | 2017-12-08 |  | 22154 | 2017-12-21 | CB | 2019-12-31 | CE Breaker Replacement Program - 2019 |  |  | 138 |  |  | Replace damaged or defective circuit breakers across the system. | MI |  |  | M1_Final SPM or OOC | 1000000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 12074 | 2017-12-08 |  | 22156 | 2018-09-26 | TEQ | 2018-12-31 | CE Substation Equipment Replacements - 2018 |  |  | 138 |  |  | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI |  |  | M4_Pre-Construction | 860000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 12075 | 2017-12-08 |  | 22157 | 2017-12-21 | TEQ | 2019-12-31 | CE Substation Equipment Replacements - 2019 |  |  | 138 |  |  | Replace damaged or defective substation equipment, not including breakers, with new equipment | MI |  |  | M1_Final SPM or OOC | 980000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 12077 | 2017-12-08 |  | 22158 | 2018-09-26 | LNup | 2018-12-31 | CE Pole & Line Equipment Replacement Program - 2018 |  |  | 138 |  |  | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI |  |  | M4_Pre-Construction | 360000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 12078 | 2017-12-08 |  | 22160 | 2017-12-21 | LNup | 2019-12-31 | CE Pole & Line Equipment Replacement Program - 2019 |  |  | 138 |  |  | Replace damaged or defective poles, towers, cross arms, insulators, guying, and switches, as needed, to maintain the lines' condition | MI |  |  | M1_Final SPM or OOC | 770000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 12164 | 2017-12-08 |  | 22280 | 2018-09-26 | SwSta | 2019-06-01 | Amber |  |  | 138 |  |  | Rebuild the 138 kV portion of Amber Substation to a five breaker ring bus with a future line exit | MI |  |  | M3_Long Lead Materials | 4800000 | Planning |  | N | N | N
A in MTEP17 | A | East | CETO | 14325 | 2017-12-08 |  | 23312 | 2017-12-21 | SUB | 2020-12-31 | Buck Creek |  |  | 138 |  |  | Install a third partial row and two 138 kV breakers. Add Beals Road to Buck Creek and Hazelwood to Buck Creek 138 kV line exits to the Buck Creek Station. | MI |  |  | M1_Final SPM or OOC | 2800000 | Engineering Preliminary |  | N | N | N | Y
A in MTEP17 | A | East | CETO | 14325 | 2017-12-08 |  | 23313 | 2018-09-26 | SwSta | 2018-12-31 | Buck Creek |  |  | 138 |  |  | Convert the 138 kV bus to a breaker-and-a-half design by adding two 138 kV breakers and buswork | MI |  |  | M4_Pre-Construction | 2700000 | Planning |  | N | N | N | Y
A in MTEP17 | A | South | CLECO | 12138 | 2017-12-08 | 17-ELS-010 | 22609 | 2018-09-26 | RLY | 2019-06-01 | Madisonville |  |  | 230 |  |  | Work needed at Madisonville to accommodate the new line out of Fairview | LA |  |  | Planned | 47924 | Planning |  | N | N | N
A in MTEP17 | A | South | CLECO | 12985 | 2017-12-08 | CLEC | 22551 | 2018-09-17 | SUB | 2020-09-24 | Teche |  |  | 230 | 138 |  | Expand Teche Substation for 230 kV. | LA |  |  | M4_Pre-Construction | 19311000 | Planning |  | N | N | N
A in MTEP17 | A | South | CLECO | 12985 | 2017-12-08 | CLEC | 22554 | 2018-09-17 | LN | 2021-10-25 | Teche | Bayou Vista | 1 | 230 |  |  | Build a new 230 kV line from Teche to Bayou Vista. | LA |  | 22 | M4_Pre-Construction | 59463079 | Planning |  | N | N | N
A in MTEP17 | A | South | CLECO | 12985 | 2017-12-08 | CLEC | 22553 | 2018-09-17 | LN | 2020-09-24 | Segura | Teche | 1 | 230 |  |  | Build a new 230 kV line from Segura Substation to Teche Substation. | LA |  | 25 | M4_Pre-Construction | 55310000 | Planning |  | N | N | N
A in MTEP17 | A | South | CLECO | 12985 | 2017-12-08 | CLEC | 22552 | 2018-09-17 | TX | 2020-12-17 | Teche 230 Sub | Teche 138 Sub | 1 | 230 | 138 |  | Add a 500 MVA 230/138 kV Auto at Teche | LA |  |  | M4_Pre-Construction | 3328000 | Planning |  | N | N | N
A in MTEP17 | A | Central | DEI | 1900 | 2017-12-08 | DIN1730 | 3796 | 2018-09-27 | Dist | 2019-06-01 | Avon Industrial Park | new dist sub | 1 | 138 | 12 | 306 | Avon Industrial Park - Construct 138-12kV - 22.4 MVA sub in the All Points Industrial Park and 2.5 miles of 138kV line | IN |  | 2.5 | M4_Pre-Construction | 3318000 | Engineering w/AFUDC |  | N | N | N | NT
A in MTEP17 | A | Central | DEI | 11912 | 2017-12-08 | AMIN1292-2 | 21869 | 2018-09-27 | TX | 2018-12-31 | Kokomo Highland Park |  |  | 230 | 69 |  | Close in Kokomo H.P. Bks 4, 5, and 6 tertiary windings (69kV) after upgrades completed on separate project. | IN |  |  | Under Construction | 0 | Actual |  | N | N | N
A in MTEP17 | A | Central | DEI | 11957 | 2017-12-08 | DEI-MTEP2017-1 | 21918 | 2018-03-15 | Dist | 2021-06-01 | Wabash River Station |  |  | 230 |  |  | Wabash River Station new industrial load @ 50MW on the 230kV bus section #2 or #3 | IN |  |  | M3_Long Lead Materials | 300000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | Central | DEI | 11983 | 2017-12-08 | DIN1579 | 21951 | 2018-09-27 | Dist | 2019-06-01 | Bracken West |  |  | 69 | 12 |  | Bracken West 69/12kV Distribution Sub - North Manchester area on the 6923 ckt. | IN |  |  | M4_Pre-Construction | 678000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 11984 | 2017-12-08 | TIN1681 | 21952 | 2018-03-15 | LNrb | 2019-06-01 | Seymour Cummins Jct | HE Chestnut Ridge | 1 | 69 |  | 100 | Seymour Cummins Jct to HE Chestnut Ridge 69kV Rebuild - 69156 ckt - use 477acsr - 3.66 miles | IN | 3.66 |  | M3_Long Lead Materials | 4825000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 11988 | 2017-12-08 | TIN1538 | 21960 | 2017-09-27 | LNup | 2018-12-31 | Edwardsport | Wheatland | 1 | 345 |  |  | Edwardsport to Wheatland 345kV Structural Improvements: insert double deadend structures every 2.5 miles in the 34540 ckt. | IN |  |  | Under Construction | 1790000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 11991 | 2017-12-08 | TIN1546 | 21964 | 2018-06-28 | SUB | 2018-10-01 | Whitesville South |  |  | 230 | 69 |  | Whitesville South 230kV and 69kV add breakers, bus, switches, etc. to complete (2) 3-position ring buses | IN |  |  | Under Construction | 5180000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 11992 | 2017-12-08 | TIN1544 | 21965 | 2018-09-27 | RLY | 2018-12-31 | Oakland City |  |  | 138 | 69 |  | Oakland City 138kV and 69kV Relays - replace relays on all 138 and 69kV line breakers | IN |  |  | Under Construction | 5572000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 11999 | 2017-12-08 | TIN1712 | 21987 | 2018-03-15 | LNrb | 2023-12-31 | Attica 69 | Attica 230 | 1 | 69 |  | 100 | Attica 69 to Harrison Stl Jct to Attica 230 69kV Rebuild - Rebuild 6936 ckt - 4.1 miles with 477acsr and steel poles; also rebuild 1.27 miles of 69121 where it is double circuited | IN | 5.37 |  | Planned | 5601000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 12005 | 2017-12-08 | DEI-MTEP2017-2 | 22048 | 2018-03-15 | Dist | 2021-12-31 | Bloomington Rogers St. | Ph 5 dist sub |  | 138 | 12 |  | Bloomington Rogers St. Phase 5: install new 138/12kV Banks 1 and 2 | IN |  |  | Planned | 300000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | Central | DEI | 12005 | 2017-12-08 | DEI-MTEP2017-2 | 22044 | 2018-03-15 | SUB | 2020-12-31 | Bloomington Rogers St. | Ph 4 ring bus |  | 69 |  |  | Bloomington Rogers St. Phase 4: 69kV ring bus (7 breakers); retire 69/12kV banks 1 and 2 | IN |  |  | Planned | 3950000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 12005 | 2017-12-08 | DEI-MTEP2017-2 | 22042 | 2018-03-15 | TX | 2019-12-31 | Bloomington Rogers St. | Ph 3 sub-T xfmr |  | 138 | 69 | 125 | Bloomington Rogers St. Phase 3: relocate 138kV capacitor to new bus position; replace and relocate 138/69kV Bk4 - upgrade to 100MVA; relocate 138/69kV Bk3; retire balance of old 138kV equipment | IN |  |  | M3_Long Lead Materials | 2840000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | Central | DEI | 12005 | 2017-12-08 | DEI-MTEP2017-2 | 22039 | 2018-03-15 | SUB | 2018-12-31 | Bloomington Rogers St. | Ph2 brkr+1/2 |  | 138 |  |  | Bloomington Rogers St. Phase 2: 138kV breaker-and-a-half bus (9 breakers) | IN |  |  | Under Construction | 6181000 | Engineering w/AFUDC |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 9702 | 2017-12-08 | 16-EAI-016 | 21026 | 2018-08-01 | TEQ | 2018-12-01 | Sylvan Hills115kV | Jacksonville North 115kV |  | 115 |  |  | Upgrade line bay bus at Sylvan Hills. | AR |  |  | Planned | 128427 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12039 | 2017-12-08 | 17-EAI-003 | 22119 | 2018-09-26 | SUB | 2024-06-01 | Happy Valley |  |  | 500 |  |  | Tap ANO-Mabelvale and Mayflower-Mabelvale 500 kV lines near the point where the lines start sharing common ROW, to build a new switching station Happy Valley. | AR |  |  | Planned | 180272477 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12039 | 2017-12-08 | 17-EAI-003 | 22120 | 2018-08-21 | LN | 2024-06-01 | Happy Valley | Hot Springs EHV |  | 500 |  |  | Build ~35 mile Hot Springs-Happy Valley 500 kV line. | AR |  | 35 | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12041 | 2018-09-05 | 17-EAI-028 | 22121 | 2018-09-18 | IND | 2020-06-01 | Russellville East |  |  | 161 |  |  | Add a 10 Ohm series reactor at Russellville East 161 kV station. | AR |  |  | Planned | 6129867 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12042 | 2017-12-08 | 17-EAI-004 | 22123 | 2018-09-18 | SUB | 2019-12-01 | West Helena |  |  | 115 |  |  | Close the Normally-Open point at West Helena, and convert the station to a transmission breaker substation. | AR |  |  | Planned | 11534538 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12045 | 2017-12-08 | 17-EAI-023 | 22126 | 2018-09-04 | TX | 2019-12-01 | Independance |  |  | 500 | 161 |  | Add a third 500/161 kV autotransformer at ISES EHV, rated a minimum of 800 MVA. | AR |  |  | Under Construction | 23138117 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12047 | 2017-12-08 | 17-EAI-022 | 22128 | 2018-09-18 | SUB | 2020-06-01 | Greyhawk |  |  | 161 |  |  | Construct a new distribution substation on the 161kV line Vilonia - Holland Bottoms. | AR |  |  | Planned | 7723996 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12063 | 2018-08-31 | 17-EAI-026 | 22143 | 2018-09-18 | SUB | 2020-05-01 | Big Creek |  |  | 115 |  |  | Construct a new 115kV substation called Sheridan East that includes two 115kV breakers and a 40 MVA load transformer. | AR |  |  | Planned | 8645632 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12666 | 2017-12-08 | 17-EAI-012 | 22463 | 2018-08-01 | SUB | 2019-11-01 | MacArthur 115kV |  | 1 | 115 | 13.8 |  | Construct a new substation with a 40 MVA 115/13.8 kV LTC transformer and four feeder breaker bays. | AR |  |  | Planned | 9972694 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12667 | 2017-12-08 | 17-EAI-017 | 22464 | 2018-09-18 | SUB | 2019-11-15 | Pecan Street 161kV |  |  | 161 |  |  | Construct a new substation on the Newport to Parkin 161kV line. Install one 40 MVA LTC transformer and one 2000 Amp main breaker with four 1200 Amp feeder breakers. | AR |  |  | Under Construction | 8053322 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12669 | 2017-12-08 | 17-EAI-014 | 22469 | 2018-09-18 | SUB | 2019-06-01 | Tarleton 230kV |  |  | 230 | 13.8 |  | Construct a new 230/13.8kV substation with two 20 MVA load transformers. | AR |  |  | Under Construction | 14692523 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-AR | 12745 | 2017-12-08 | 17-EAI-013 | 22509 | 2018-09-05 | SUB | 2020-06-01 | Russellville Industrial |  |  | 161 | 13.8 |  | Construct a new substation on E. 6th street and Tyler Road in Russellville, AR. Install one 40 MVA 161/13.8kV LTC and four feeder breaker bays. | AR |  |  | Planned | 10499680 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 4608 | 2017-12-08 | 11-EGL-017 | 8757 | 2018-09-26 | LNrc | 2020-12-01 | Five Points 69 kV substation | Line 281 Tap point 69 kV | 1 | 69 |  | 105 MVA | Reconductor Line | LA | 5.01 |  | Planned | 4711363 |  |  | N | N | N | Y
A in MTEP17 | A | South | Entergy-LA | 4608 | 2017-12-08 | 11-EGL-017 | 8758 | 2018-03-29 | LNrc | 2020-12-01 | Line 281 Tap point 69 kV | Line 247 Tap point 69 kV | 1 | 69 |  | 105 MVA | Reconductor Line | LA | 0.24 |  | Planned |  |  |  | N | N | N | Y
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 20998 | 2018-09-26 | SwSta | 2021-06-01 | Perryville |  |  | 230 |  |  | Perryville 230 kV sub | LA |  |  | Proposed | 119639016 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 21005 | 2017-12-27 | TX | 2021-06-01 | Dunn |  |  | 230 | 115 |  | 230/115 transformer | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 21004 | 2017-12-27 | TX | 2021-06-01 | Rilla |  |  | 230 | 115 |  | New 230/115 AT | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 21003 | 2017-12-27 | TX | 2021-06-01 | Selman Field |  |  | 230 | 69 |  | Change out auto from 115/69 to 230/69 | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 21002 | 2017-12-27 | LN | 2021-06-01 | Selman Field | Rilla | 1 | 230 |  | 640 | Utilizing existing 115 kV Rilla - Selman Field built to 230 kV specifications. | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 21001 | 2016-09-14 | LN | 2021-06-01 | Perryville | Selman Field | 1 | 230 |  |  | Utilizing existing 115 kV Sterlington - Selman Field - Rilla 230 kV constructed line. | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 21000 | 2016-09-14 | LN | 2021-06-01 | Perryville | Dunn | 1 | 230 |  | 779 | New 230 kV line utilizing existing Swartz - Dunn 115 kV line (constructed to 230 kV specifications) | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9683 | 2017-12-08 | 16-ELN-002 | 20999 | 2016-09-14 | TX | 2021-06-01 | Perryville |  |  | 500 | 230 | 615 | 500/230 autotransformer | LA |  |  | Proposed |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9688 | 2017-12-08 | 16-ELN-007 | 21012 | 2018-09-26 | LN | 2020-06-01 | Dunn | Winnsboro | 1 | 115 |  | 390 | New 230 kV line (115 kV energized) | LA |  | 25 | Proposed | 51127726 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9689 | 2017-12-08 | 16-ELN-008 | 21013 | 2018-09-26 | Dist | 2019-06-01 | Beekman |  |  | 115 |  |  | New 115 kV distribution substation | LA |  |  | Proposed | 15828104 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9766 | 2017-12-08 | 16-EGL-007 | 21140 | 2018-09-26 | LNrc | 2019-12-01 | Gloria | Flannery REA | 1 | 69 |  |  | Upgrade Line | LA |  |  | Planned | 3127596 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9781 | 2017-12-08 | 17-ELC-010 | 21155 | 2017-05-10 | LNrb | 2020-06-01 | Jennings | Lawtag | 1 | 69 |  | 105 | Upgrade Line | LA | 4.83 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9781 | 2017-12-08 | 17-ELC-010 | 22591 | 2018-09-26 | LNrb | 2020-06-01 | Jennings | Lawtag | 2 | 69 |  | 105 | rebuild line | LA | 4.7 |  | Planned | 7675841 | Facility Study |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9798 | 2017-12-08 | 16-ELL-001 | 21172 | 2018-09-26 | LNrc | 2020-06-01 | Gypsy | Claytonia | 1 | 115 |  |  | Upgrade line | LA |  |  | Planned | 8072964 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 9804 | 2017-12-08 | 16-ELL-008 | 21178 | 2018-09-26 | LNrc | 2020-06-01 | Avenue C | Paris Tap | 1 | 115 |  |  | Upgrade Line | LA |  |  | Planned | 212807 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12040 | 2018-09-06 | 17-ELN-005 | 22125 | 2018-09-26 | LNrb | 2020-06-01 | Carson Road | Delhi | 1 | 115 |  |  | Rebuild line to minimum 260 MVA rating | LA | 3.18 |  | Planned | 6785081 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12073 | 2017-12-08 | 17-ELB-001 | 22163 | 2018-09-26 | SwSta | 2020-06-01 | Ellem |  |  | 138 |  |  | Reconfigure the local 138 kV network via tying the Monochem to Alchem and Monochem to Southwood 138 kV lines into the new substation adjacent to the Geismar 138 kV substation. The new 138 kV substation should be configured as a 6 breaker ring with a minimum rating of 2000A. | LA |  |  | Planned | 26236261 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12076 | 2017-12-08 | 17-ELC-002 | 22159 | 2018-09-26 | LN | 2022-12-01 | Mud Lake | Big Lake | 1 | 230 |  |  | Construct a 10 mile 230 kV line from Mud Lake to Big Lake using a conductor rated at a minimum of 1950 A. | LA |  |  | Planned | 33036959 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12079 | 2017-12-08 | 17-ELC-004 | 22161 | 2018-09-26 | TX | 2020-06-01 | Lake Charles Bulk |  |  | 138 |  |  | Replace the existing Lake Charles Bulk 138-69 kV Autotransformer #1 with a 200 MVA unit and replace necessary terminal equipment to achieve a through path rating of 200 MVA for autotransformer #1. | LA |  |  | Planned | 7851334 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12079 | 2017-12-08 | 17-ELC-004 | 22162 | 2018-03-30 | TX | 2020-06-01 | Lake Charles Bulk |  |  | 138 |  |  | Replace the existing Lake Charles Bulk 138-69 kV Autotransformer #2 with a 200 MVA unit and replace necessary terminal equipment to achieve a through path rating of 200 MVA for autotransformer #2. | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12082 | 2017-12-08 | 17-ELC-006 | 22165 | 2018-09-26 | SUBmisc | 2020-06-01 | Goosport |  |  | 69 |  |  | Upgrade Goosport to L673 TP 69 kV line switch at Goosport to 1200 A. The new line limit should be the conductor rated at 93 MVA. | LA |  |  | Planned | 146395 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12082 | 2017-12-08 | 17-ELC-006 | 22166 | 2018-06-27 | SUBmisc | 2020-06-01 | Gillis Tap |  |  | 69 |  |  | Upgrade Gillis Tap - East Broad 69 kV line switch at Gillis Gas Tap to 1200 A. The new limit should be the conductor at 93 MVA. | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12110 | 2017-12-08 | 17-ELF-005 | 22218 | 2018-09-26 | CB | 2018-12-01 | Meaux |  |  | 138 |  |  | Install new breaker | LA |  |  | Planned | 1012376 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12112 | 2017-12-08 | 17-ELF-006 | 22221 | 2018-09-26 | SUB | 2021-12-01 | Cankton 230 |  |  | 230 | 138 |  | Build new 230 kV Cankton substation | LA |  |  | Planned | 107621804 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12112 | 2017-12-08 | 17-ELF-006 | 22226 | 2018-06-27 | TX | 2021-12-01 | Cecelia 230 | Cecelia 138 | 1 | 230 | 138 |  | Install auto at Cecelia | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12112 | 2017-12-08 | 17-ELF-006 | 22225 | 2018-06-27 | LN | 2021-12-01 | Cankton | Cecelia | 1 | 230 |  |  | Construct new 230 kV line from Cankton to Cecelia | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12112 | 2017-12-08 | 17-ELF-006 | 22224 | 2018-06-27 | TX | 2021-12-01 | Cankton 230 | Cankton 138 | 1 | 230 | 138 |  | Install Auto at Cankton | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12120 | 2017-12-08 | 17-ELS-001 | 22241 | 2018-09-26 | TEQ | 2019-06-01 | Waterford |  |  | 230 |  |  | Upgrade the line bay riser at Waterford 230 kV to a minimum of 1600 Amps. | LA |  |  | Planned | 82726 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12129 | 2017-12-08 | 17-ELS-005 | 22247 | 2018-09-26 | TX | 2019-12-01 | Snakefarm |  |  | 230 |  |  | Install 2nd 230-115 kV Autotransformer at Snakefarm. | LA |  |  | Planned | 12198867 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12132 | 2017-12-08 | 17-ELS-007 | 22253 | 2018-09-26 | SwSta | 2020-06-01 | Churchill |  |  | 230 |  |  | 1) The construction of a new 230 kV substation named Churchill, south of the Ninemile station. Construct a (5) breaker 3000 Amp 230 kV ring bus to accommodate five 230 kV lines immediately, with room for expansion due to load requests/growth in the area. The Ninemile to Waterford and the Ninemile to Estell 230 kV lines should be cut in an out of Churchill. | LA |  |  | Planned | 109013048 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12132 | 2017-12-08 | 17-ELS-007 | 22259 | 2018-03-30 | LN | 2020-06-01 | Ninemile | Westwego |  | 115 |  |  | 4) Once above phases are completed utilize the existing abandoned Ninemile to Barataria 115 kV line to the point shown on the map below(highlighted as Pink line) and extend to Westwego 115 kV substation. The reutilized portion of Ninemile to Barataria 115 kV line will need to be upgraded to a minimum of 1600amps to achieve a final circuit rating of 1600 amps. | LA |  |  | Planned |  | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12132 | 2017-12-08 | 17-ELS-007 | 22257 | 2018-03-30 | LNcnv | 2020-06-01 | Churchill | Alliance |  | 230 |  |  | Convert the existing Ninemile to Barataria 115 kV line to Churchill to Barataria 230 kV line (Line is being rebuilt to 230 kV specs by Asset Management).Convert the Barataria to Alliance 115 kV line to 230 kV operation. This line is currently built to 230 kV specs. Expand the 230 kV Alliance substation to a minimum of a three breaker ring with room for expansion to accommodate transmission lines to Oakville, Barataria, and the 230-115 kV Autotransformer. | LA |  |  | Planned |  | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12132 | 2017-12-08 | 17-ELS-007 | 22255 | 2018-03-30 | SUB | 2020-06-01 | Barataria |  |  | 230 |  |  | 2) Build a new 230 kV station at Barataria to accommodate the line from Churchill .The new Barataria 230 kV substation will be configured to a minimum of (3) Breaker ring, rated to a minimum of 3000A . Install a new 230-115 kV autotransformer at Barataria Substation, rated at 200 MVA minimum | LA |  |  | Planned |  | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12133 | 2017-12-08 | 17-ENO-001 | 22252 | 2018-09-26 | CAP | 2019-12-01 | Gulf Outlet |  |  | 115 |  |  | Install new Cap Bank | LA |  |  | Planned | 1867901 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12136 | 2018-08-20 | 17-ELS-013 | 22258 | 2018-09-26 | SUB | 2020-06-01 | Cullichia |  |  | 230 |  |  | Construct new station, station name changed to Cullichia | LA |  |  | Planned | 38956808 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12138 | 2017-12-08 | 17-ELS-010 | 22261 | 2018-09-26 | Dist | 2019-06-01 | Robert |  |  | 230 |  |  | New distribution substation | LA |  |  | Planned | 24961851 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12138 | 2017-12-08 | 17-ELS-010 | 22610 | 2018-06-27 | LN | 2019-04-01 | Fairview | Robert |  | 230 |  |  | New double circuit line from Fairview to Robert | LA |  | 25.5 | Planned | 43385448.26 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12138 | 2017-12-08 | 17-ELS-010 | 22608 | 2018-09-26 | BUS | 2019-06-01 | Fairview |  |  | 230 |  |  | Add breakers and convert substation from a reactor station | LA |  |  | Planned | 8059320 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12544 | 2017-12-08 | 17-ELB-011 | 22452 | 2018-09-26 | SwSta | 2018-11-01 | Pecue |  |  | 230 |  |  | Install line breakers at Pecue | LA |  |  | Planned | 2025727 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12743 | 2017-12-08 | 17-ELN-008 | 22507 | 2018-06-27 | SUB | 2020-06-01 | Fairbanks |  |  | 115 |  |  | Fairbanks 115 kV distribution substation (currently no transmission breakers are projected to be installed as part of this project) | LA |  |  | Planned | 16730933 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 12770 | 2017-12-08 | 17-ELC-008 | 22517 | 2018-09-26 | Dist | 2020-10-31 | Kim Street |  |  | 230 |  |  | New substation | LA |  |  | Planned | 22659748 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-LA | 13999 | 2017-12-08 | 17-ELC-002 | 23115 | 2018-09-26 | TEQ | 2019-12-31 | Carlyss |  |  | 230 | 138 |  | Upgrade station equipment at Carlyss 138 kV to achieve full rating of the Carlyss 230-138 kV Autotransformer. | LA |  |  | Planned | 267776 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 7906 | 2017-12-08 | 15-EMI-004 | 20144 | 2018-09-26 | LNrb | 2019-06-01 | Greenwood | Greenwood SS | 1 | 115 |  |  | Upgrade line to 239 MVA | MS | 10.48 |  | Proposed | 9319353 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 7914 | 2017-12-08 | 15-EMI-008 | 20161 | 2018-09-26 | SUB | 2020-12-01 | UMMC |  |  | 115 |  |  | New substation for medical center service. | MS |  |  | Proposed | 31298368 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 7914 | 2017-12-08 | 15-EMI-008 | 20164 | 2018-06-27 | LN | 2020-12-01 | Rex Brown | UMMC | 1 | 115 |  |  | New 115 kV utilizing ROW of removed HICO - Fondren 115 kV line. Approximately 0.5 miles of the line will require new ROW (cut into new UMMC substation) | MS |  | 5.5 | Proposed |  | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 7914 | 2017-12-08 | 15-EMI-008 | 20163 | 2018-06-27 | Remove | 2020-12-01 | HICO | Fondren | 1 | 115 |  |  | 115 kV normally open line | MS |  |  | Proposed |  | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12023 | 2017-12-08 | 17-EMI-002 | 22093 | 2018-09-26 | LNrb | 2019-06-01 | Conehoma Creek | Carthage | 1 | 115 |  | 260 | Upgrade facility to 260MVA. | MS |  | 20.2 | Planned | 13375147 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12024 | 2017-12-08 | 17-EMI-003 | 22094 | 2018-09-26 | LNrb | 2019-12-01 | Carthage | Scott | 1 | 115 |  | 260 | Rebuild to minimum of 260 MVA. Will be constructed to 230 kV specifications for potential future conversion. | MS | 14.49 |  | Under Construction | 13213965 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12025 | 2017-12-08 | 17-EMI-004 | 22095 | 2018-09-26 | LNrb | 2021-12-01 | Scott | Pelahatchie | 1 | 115 |  | 260 | Upgrade facility to minimum 260 MVA. Reconstructed to 230 kV specs for potential future conversion. | MS | 16.79 |  | Planned | 18711399 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12027 | 2017-12-08 | 17-EMI-005 | 22097 | 2018-09-26 | SUB | 2019-06-01 | Henderson Road |  |  | 230 | 13.8 |  | New 230 kV substation | MS |  |  | Under Construction | 17687485 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12027 | 2017-12-08 | 17-EMI-005 | 22098 | 2018-09-26 | SUB | 2019-06-01 | Luckney |  |  | 230 |  |  | Install transmission breakers | MS |  |  | Under Construction |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12029 | 2017-12-08 | 17-EMI-006 | 22101 | 2018-09-26 | SUB | 2021-06-01 | Byhalia |  |  | 230 |  |  | New 230kV distribution substation | MS |  |  | Planned | 17337028 | Planning |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12029 | 2017-12-08 | 17-EMI-006 | 22102 | 2017-10-02 | LN | 2021-06-01 | Getwell | Byhalia | 1 | 230 |  |  | 230 kV transmission facility to interconnect new substation | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12207 | 2018-08-27 |  | 22361 | 2018-09-26 | Dist | 2019-05-01 | Carter |  |  | 115 |  |  | The Carter delivery point requires installing one (1) 115kV switching station with 3 motor operated switches within the distribution substation fence. | MS |  |  | M4_Pre-Construction | 1660000 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12208 | 2018-08-27 |  | 22360 | 2018-09-27 | Dist | 2019-05-31 | Holmesville |  |  | 115 |  |  | The Holmesville delivery point requires installing one (1) 115kV switching station with 3 motor operated switches within the distribution substation fence. | MS |  |  | M4_Pre-Construction | 2060000 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12219 | 2017-12-08 |  | 22345 | 2018-09-27 | SwSta | 2019-12-01 | Acona |  |  | 115 |  |  | Install a new switching station with breakers at Acona. | MS |  |  | Planned | 3760000 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-MS | 12824 | 2017-12-08 | 17-EMI-010 | 22534 | 2018-09-26 | SUB | 2019-12-01 | Coldwater |  |  | 115 |  |  | Coldwater 115 kV breaker installation | MS |  |  | Planned | 4673908 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-TX | 4623 | 2017-12-08 | 13-ETI-014 | 8782 | 2018-09-26 | LNrc | 2020-04-01 | Panorama 138 kV Substation | Longmire 138 kV Substation | 1 | 138 |  | 287 MVA | Reconductor Line | TX | 2.73 |  | Planned | 3647461 |  |  | N | N | N | Y
A in MTEP17 | A | South | Entergy-TX | 12763 | 2017-12-08 | 17-ETI-014 | 22510 | 2018-09-26 | Dist | 2020-05-15 | Commerce |  |  | 138 |  |  | New Substation | TX |  |  | Planned | 12199370 |  |  | N | N | N
A in MTEP17 | A | South | Entergy-TX | 13864 | 2017-12-08 |  | 22920 | 2017-10-10 | SUB | 2023-06-01 | New Substation |  |  | 500 | 230 |  | New 500/230 kV substation; Reconfigure existing Sabine - McFadden and Sabine - Nederland 230 kV transmission lines into new sub | TX |  |  | Proposed | 37145943 | Scoping |  | N | Y | Y | Y
A in MTEP17 | A | South | Entergy-TX | 13864 | 2017-12-08 |  | 22925 | 2017-09-29 | CB | 2023-06-01 | Sabine |  |  | 230 |  |  | Replace overdutied 230 kV bkr | TX |  |  | Proposed | 748790 | Scoping |  | N | Y | Y | Y
A in MTEP17 | A | South | Entergy-TX | 13864 | 2017-12-08 |  | 22924 | 2017-09-29 | LN | 2023-06-01 | New Substation | Tap |  | 230 |  |  | 230 kV double ckt tie-in to new substation from existing 230 kV double ckt line | TX |  | 1 | Proposed | 3256743 | Scoping | Generator | N | Y | Y | Y
A in MTEP17 | A | South | Entergy-TX | 13864 | 2017-12-08 |  | 22923 | 2017-10-13 | CB | 2023-06-01 | Hartburg |  |  | 500 |  |  | 500 kV Breaker plus buswork at Hartburg | TX |  |  | Proposed | 6243884 | Scoping |  | N | Y | Y | Y
A in MTEP17 | A | South | Entergy-TX | 13864 | 2017-12-08 |  | 22921 | 2017-09-29 | LN | 2023-06-01 | Hartburg | New Substation |  | 500 |  |  | New 500kV line from Hartburg to New Substation | TX |  | 21.5 | Proposed | 82283832 | Scoping |  | N | Y | Y | Y
A in MTEP17 | A | South | Entergy-TX | 14002 | 2017-12-08 | 17-ETI-023 | 23117 | 2018-09-26 | LNup | 2019-12-01 | Sam Rayburn | Doucette |  | 138 |  |  | •Replace 26 transmission structures on the Sam Rayburn to Fort Creek to Turkey Creek to Doucette 138kV transmission line •Rating increases to 137MVA from 112MVA | TX | 29 |  | Planned | 796387 | Planning |  | N | N | N
A in MTEP17 | A | South | ETEC | 8203 | 2017-12-08 | SHECO_03_MTEP17 | 20587 | 2016-09-12 | SwSta | 2020-08-01 | TBD |  |  | 138 |  |  | New switching station on Dogwood-Warren 138 kV line. | TX |  |  | Proposed | 2000000 |  |  | N | N | N
A in MTEP17 | A | South | ETEC | 8203 | 2017-12-08 | SHECO_03_MTEP17 | 20589 | 2016-09-12 | SUB | 2020-08-01 | TBD |  |  | 138 |  |  | Construct new 138 kV Fred substation. | TX |  |  | Proposed | 4000000 |  |  | N | N | N
A in MTEP17 | A | South | ETEC | 8203 | 2017-12-08 | SHECO_03_MTEP17 | 20588 | 2016-09-12 | LN | 2020-08-01 | TBD | TBD | 1 | 138 |  |  | Construct new 138 kV line from the new Fred switching station to the new Fred substation. | TX |  |  | Proposed | 18200000 |  |  | N | N | N
A in MTEP17 | A | South | ETEC | 11990 | 2017-12-08 | SHECO_01_MTEP17 | 21966 | 2018-06-29 | SwSta | 2019-06-01 | 334125 |  |  | 138 |  |  | Upgrade existing Staley substation to 6 BKR ring bus configuration | TX |  |  | Planned | 3900000 |  |  | N | N | N
A in MTEP17 | A | South | ETEC | 11990 | 2017-12-08 | SHECO_01_MTEP17 | 21967 | 2018-06-29 | LNrb | 2019-06-01 | 334055 | 334135 | 1 | 138 |  |  | Cut-in existing ETI line #419 Rivtrin - Gulf Trinity (bus #334055-334135) and extend to connect into Staley 138kV substation (bus #334125) | TX | 1 |  | Planned | 750000 |  |  | N | N | N
A in MTEP17 | A | South | ETEC | 12883 | 2018-02-22 | SHECO_04_MTEP17 | 22544 | 2018-06-29 | SwSta | 2019-10-25 | 334130 |  |  | 138 |  |  | Install (2) 138kV line breakers, install CCVT on line side of breakers, install (3) 138kV bus PTs, install relay panels in existing control house | TX |  |  | Planned | 900000 |  |  | N | N | N
A in MTEP17 | A | South | ETEC | 12884 | 2018-02-22 | SHECO_05_MTEP17 | 22543 | 2018-06-29 | SwSta | 2019-10-25 | 334132 |  |  | 138 |  |  | Install (2) 138kV line breakers, install CCVT on line side of breakers, install (3) 138kV bus PTs, install relay panels in existing control house | TX |  |  | Planned | 900000 |  |  | N | N | N
A in MTEP17 | A | West | GRE | 12006 | 2017-12-08 |  | 22096 | 2018-03-06 | SUB | 2018-11-06 | McHenry |  |  | 230 |  |  | Expand McHenry 230 kV bus to ring bus. | ND |  |  | Planned | 5682611.09 | Planning |  | N | N | N
A in MTEP17 | A | West | GRE | 12104 | 2017-12-08 | 204551 | 22211 | 2018-03-06 | LNrb | 2019-02-14 | Burnsville | River Hills | 1 | 69 |  |  | Rebuild 1.11 mile 4/0 ACSR conductor on GRE DA-BR line with 795 ACSS conductor. The line will be built to 115 kV standard, but operated at 69 kV | MN | 1.11 |  | Planned | 2610042.43 | Planning |  | N | N | N
A in MTEP17 | A | West | GRE | 12106 | 2017-12-08 | 204296 | 22214 | 2018-09-14 | LN | 2020-05-29 | Big Fork | Scenic | 1 | 69 |  |  | Build 13.5 mile 69 kV tap line to a new North Itasca distribution substation. | MN |  | 13.5 | Planned | 6022225.3 | Planning |  | N | N | N
A in MTEP17 | A | West | GRE | 12117 | 2017-12-08 | 204636 | 22228 | 2018-03-06 | SwSta | 2019-09-30 | Moon Lake |  |  | 69 |  |  | Install new breaker station at the Lake Wilson distribution site and string one mile of conductor on new Xcel double-circuit 69 kV line from Chandler tap to Moon Lake Breaker Station. | MN |  |  | Planned | 3726311 | Planning |  | N | N | N
A in MTEP17 | A | West | GRE | 12122 | 2017-12-08 | 204146 | 22239 | 2017-09-14 | Dist | 2018-09-28 | Knife Falls |  |  | 115 |  |  | Build 1.0 mile of 115 kV transmission to the new Lake Country Power Brevator substation. | MN |  | 1 | Planned | 968851.61 | Planning |  | N | N | N
A in MTEP17 | A | West | GRE | 12165 | 2017-12-08 | 204147 | 22281 | 2018-09-14 | Dist | 2019-09-30 | Vermillion |  |  | 69 |  |  | Build 0.5 miles of 69 kV transmission line to Lake Country Power's upgraded Vermillion 69 kV distribution substation. | MN |  |  | Planned | 1013275.56 | Planning |  | N | N | N
A in MTEP17 | A | West | GRE | 12166 | 2017-12-08 | 204191 | 22282 | 2017-09-14 | LN | 2018-01-01 | Maine | Star Lake | 1 | 41.6 |  |  | Build approximately 10.0 mile 41.6 kV transmission line to interconnect the new substation to Lake Region Electric Cooperatives existing, Maine substation. | MN |  | 10 | Planned | 5475331.01 | Planning |  | N | N | N
A in MTEP17 | A | Central | HE | 13528 | 2017-12-08 |  | 22646 | 2017-08-24 | LNrc | 2018-12-31 | Worthington | Linton Junction |  | 138 |  |  | MTEP 17 analysis identified overloading on this line for Category P7 contingencies. This project will uprate the segment and resolve the reliability issue. | IN |  |  | Planned | 650000 | Planning | Generator | N | N | N | Y
A in MTEP17 | A | Central | IPL | 12483 | 2017-12-08 |  | 22445 | 2017-11-14 | CB | 2018-12-31 | Guion |  |  | 138 |  |  | 138 kV breaker #10 | IN |  |  | Planned | 300000 |  |  | N | N | N
A in MTEP17 | A | Central | IPL | 13424 | 2017-12-08 |  | 22620 | 2017-11-14 | LNup | 2018-12-31 | Georgetown | Westlane | 41 | 138 |  |  | Upgrade to 343 MVA | IN |  |  | Planned | 0 |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 10783 | 2017-12-08 | Lore-Gardners lane TEQ | 21663 | 2018-06-19 | TEQ | 2018-08-01 | Gardners Lane | Subustation |  | 69 | 69 |  | Upgrade the Gardners Lane 69kV terminal equipment and add a synchronous breaker and move the cap bank to the main 69kV bus. | IA |  |  | Under Construction | 478180 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11963 | 2017-12-08 | Squash Bend | 21928 | 2018-03-27 | SUB | 2018-07-01 | Squash Bend | Substation |  | 69 | 69 |  | Build a new Squash Bend 69kV/distribution substation. | IA |  |  | Under Construction | 2600000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11964 | 2017-12-08 | Oak Hill-Marion 69kV Conv | 21929 | 2016-09-14 | SUB | 2019-12-31 | Oak Hill | Substation |  | 69 | 69 |  | Add a new 69kV terminal at the Oak Hill substation. | IA |  |  | Planned | 283633 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11964 | 2017-12-08 | Oak Hill-Marion 69kV Conv | 22556 | 2017-02-23 | LN | 2019-12-31 | Marion South | line taps |  | 69 | 69 | 77 MVA | Perform line tap work required to connect the new Marion South sub. | IA |  |  | Planned | 684000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11964 | 2017-12-08 | Oak Hill-Marion 69kV Conv | 22555 | 2017-02-23 | SUB | 2019-12-31 | Marion South | Substation |  | 69 | 69 | 143 MVA | Construct a new Marion South substation. The new sub will be a new 69kV/distribution source and a three breaker switch station. | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11964 | 2017-12-08 | Oak Hill-Marion 69kV Conv | 21931 | 2016-09-14 | LNcnv | 2019-12-31 | Oak Hill | Marion | 1 | 69 | 69 | 77 MVA | Convert the Oak Hill-Marion line to 69kV operation (already built for 69kV). | IA | 9.2 |  | Planned | 168000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11964 | 2017-12-08 | Oak Hill-Marion 69kV Conv | 21930 | 2016-09-14 | SUB | 2019-12-31 | Marion | Substation |  | 69 | 69 |  | Add a new 69kV terminal at the Marion substation. | IA |  |  | Planned | 260833 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22022 | 2017-10-12 | LNcnv | 2020-12-31 | Fletcher | Garwin Road | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 6.8 |  | Planned | 600000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22495 | 2017-10-12 | LN | 2020-09-30 | Conrad | Conrad Tap | 1 | 34 | 34 |  | Retire Conrad tap. | IA |  |  | Planned | 60000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22494 | 2016-12-15 | LN | 2019-12-31 | Gladbrook | Gladbrook Tap | 1 | 34 | 34 |  | Retire Gladbrook tap. | IA |  |  | Planned | 252000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22493 | 2017-10-12 | SUB | 2020-11-04 | Conrad | Substation |  | 34 | 34 |  | Retire old Conrad sub. | IA |  |  | Planned | 180000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22492 | 2016-12-15 | LN | 2027-05-01 | Marshalltown | Ckt 2620 | 1 | 34 | 34 |  | Line retirements for a portion of Ckt 2620 | IA |  |  | Planned | 45872 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22491 | 2016-12-15 | SUB | 2027-05-01 | Marshalltown | Ckt 2610 |  | 34 | 34 |  | Retire the 2610 terminal and associated equipment. | IA |  |  | Planned | 102000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22490 | 2016-12-15 | SUB | 2027-05-01 | Fletcher | 69kV expansion |  | 69 | 69 |  | Expand the Fletcher 69kV to allow for 2nd 161/69kV 150 MVA transformer and associated equipment. | IA |  |  | Planned | 3762000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22489 | 2016-12-15 | SUB | 2027-05-01 | Marshalltown | Ckt 2620 terminal | 1 | 34 | 34 |  | Retire the Marshalltown terminal 2620 | IA |  |  | Planned | 102000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22488 | 2016-12-15 | LN | 2027-05-01 | Fishers | Fishers Tap | 1 | 34 | 34 |  | Retire the Fishers Tap | IA |  |  | Planned | 57400 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22487 | 2016-12-15 | LN | 2027-05-01 | Roland | Roland Tap | 1 | 34 | 34 |  | Retire Roland 34kV Tap | IA |  |  | Planned | 194256 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22486 | 2016-12-15 | SUB | 2027-05-01 | Ames | Substation |  | 34 | 34 |  | Retire Ames 34kV Sub | IA |  |  | Planned | 180000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22485 | 2016-12-15 | LN | 2027-05-01 | Marshalltown | Ckt 2640 retirements | 1 | 34 | 34 |  | Retire 34kV lines that are no longer needed. | IA |  |  | Planned | 399224 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22484 | 2016-12-15 | SUBmisc | 2027-05-01 | Timber Creek | Substation | 1 | 69 | 69 | 143 MVA | Add a 69kV breaker position at Timber Creek. | IA |  |  | Planned | 37382 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22483 | 2016-12-15 | CAP | 2027-05-01 | Harcout | Capacitor |  | 69 | 69 | 10.8 MVAR | The capacitor bank should be sized for a single stage of 10.8 (9.18 effective) MVAR, set up to add an additional 10.8 (9.18 effective) MVAR stage. | IA |  |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22482 | 2016-12-15 | LN | 2027-05-01 | Harcourt | line taps |  | 69 | 69 | 143 MVA | Perform line re-terminations to connect the new Harcourt 69kV sub. | IA |  |  | Planned | 515672 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22481 | 2017-03-07 | SUBmisc | 2027-05-01 | Doud | 69kV terminal | 1 | 69 | 69 | 143 MVA | Add 69kV Harcourt terminal at the Doud sub | IA |  |  | Planned | 259104 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22480 | 2017-03-07 | LN | 2027-05-01 | Boone | Ckt 1610 retirements | 1 | 34 | 34 |  | Retire Ckt 1610 that is no longer needed. | IA |  |  | Planned | 48000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22479 | 2016-12-15 | LN | 2027-05-01 | Boone | Ckt 3560 retirements |  | 34 | 34 |  | Ckt 3560 line retirements | IA |  |  | Planned | 120000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22478 | 2016-12-15 | LN | 2027-05-01 | Timer Creek | Ckt 6030 retirements | 1 | 34 | 34 |  | Ckt 6030 line retirements. | IA |  |  | Planned | 299976 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22477 | 2016-12-15 | SUBmisc | 2027-05-01 | Timber Creek | Substation |  | 69 | 69 |  | Upgrade 69kV terminal | IA |  |  | Planned | 99222 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22476 | 2017-10-12 | SUBmisc | 2018-12-31 | Marshalltown | Ckt 0810 | 1 | 34 | 34 |  | Retire Marshalltown terminal 0810 | IA |  |  | Planned | 72000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22079 | 2018-03-28 | SUBmisc | 2022-12-31 | Maxwell North | Substation |  | 69 | 69 |  | Add a 69kV breaker and terminal. | IA |  |  | Planned | 200438 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22078 | 2018-03-28 | LNcnv | 2022-12-31 | Collins REC Tap | Maxwell North | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 7.8 |  | Planned | 436200 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22077 | 2018-03-28 | LNcnv | 2022-12-31 | Collins REC Tap | Collins REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 1.34 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22076 | 2018-03-28 | LNcnv | 2022-12-31 | Rhodes | Collins REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 4 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22075 | 2018-03-28 | LNcnv | 2022-12-31 | Melbourne REC TAp | Rhodes | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 5 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22074 | 2018-03-28 | LNcnv | 2022-12-31 | Melbourne REC Tap | Melbourne REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 2.02 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22073 | 2018-03-28 | LNcnv | 2022-12-31 | Haverhill | Melbourne REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 9.46 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22072 | 2018-03-28 | LNcnv | 2022-12-31 | Timber Creek | Haverhill | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 7 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22071 | 2018-03-28 | LNcnv | 2022-12-31 | Ogden REC | Grand Junction | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 13.7 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22070 | 2018-03-28 | LNcnv | 2022-12-31 | Ogden Muni Tap | Ogden REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 0.9 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22069 | 2018-03-28 | LNcnv | 2022-12-31 | Ogden Muni Tap | Ogden Muni | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 1.6 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22068 | 2018-03-28 | LNcnv | 2022-12-31 | Valley REC Tap | Ogden Muni Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 9.8 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22067 | 2018-03-28 | LNcnv | 2022-12-31 | Valley REC Tap | Valley REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 3.21 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22065 | 2018-03-28 | LNcnv | 2022-12-31 | Boone South | Valley REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 1.15 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22064 | 2018-03-28 | LNcnv | 2022-12-31 | Boone Quartz | Boone South | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 4.75 |  | Planned | 264428 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22063 | 2018-03-28 | SUBmisc | 2022-12-31 | Boone Quartz | Substation | 1 | 69 | 69 |  | Add a 69kV breaker | IA |  |  | Planned | 228210 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22062 | 2018-06-29 | LNcnv | 2022-12-31 | Fraser REC Tap | Doud | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 14.88 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22061 | 2018-06-29 | LNcnv | 2022-12-31 | Fraser REC Tap | Fraser REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 0.75 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22060 | 2018-06-29 | LNcnv | 2022-12-31 | Boxholme | Fraser REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 4.26 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22059 | 2018-06-29 | LNcnv | 2022-12-31 | Hardin REC | Boxholme | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 5.96 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22058 | 2018-06-29 | LNcnv | 2022-12-31 | Webster REC Tap | Hardin REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 3.08 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22057 | 2018-06-29 | LNcnv | 2022-12-31 | Webster REC Tap | Webster REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 3.93 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22056 | 2018-06-29 | LNcnv | 2022-12-31 | Harcourt | Wevster REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 5.55 |  | Planned | 1176000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22055 | 2018-06-29 | LNcnv | 2022-12-31 | Gowrie Tap | Gowrie Muni | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 1.51 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22054 | 2018-06-29 | LNcnv | 2022-12-31 | Gowrie Tap | Gowrie REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 1 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22053 | 2018-06-29 | LNcnv | 2022-12-31 | Harcourt | Gowrie Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kVoperation (already built for 69kV). | IA | 4.43 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22052 | 2018-06-29 | SUB | 2022-12-31 | Harcourt | Substation |  | 69 | 69 |  | Construct a new 4 breaker station with 3 line terminals and a capacitor bank. The site would ideally be located near the Gowrie tap point on Grand Jct N Ckt 2030. The capacitor bank should be sized for a single stage of 10.8 (9.18 effective) MVAR, set up to add an additional 10.8 (9.18 effective) MVAR stage. | IA |  |  | Planned | 3052551 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22051 | 2018-06-29 | LNcnv | 2022-12-31 | Iron Man REC | Harcourt | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 11.55 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22050 | 2018-06-29 | LNcnv | 2022-12-31 | Grand Junction North | Iron Man REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 7.93 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22049 | 2018-06-29 | LNcnv | 2022-12-31 | Grand Junction Muni | Grand Junction North | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 1.85 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22047 | 2018-06-29 | LNcnv | 2022-12-31 | Grand Junction | Grand Junction Muni | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 1.78 |  | Planned | 303078 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22046 | 2018-06-29 | SUBmisc | 2022-12-31 | Grand Junction North | Substation |  | 69 | 69 |  | Add a 69kV breaker | IA |  |  | Planned | 295774 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22045 | 2018-03-28 | LNcnv | 2025-12-31 | East Nevada St | Timber Creek | 1 | 69 | 69 | 140 MVA | Convert this line to 69kV operation (already built for 69kV). | IA | 4.2 |  | Planned | 342000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22041 | 2018-03-28 | LNcnv | 2021-12-31 | Story City Muni Tap | Ames | 1 | 69 | 69 | 77 MVa | Convert this line section to 69kV operation (already built for 69kV). | IA | 7.5 |  | Planned | 505200 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22040 | 2018-03-28 | LNcnv | 2021-12-31 | Story City Muni Tap | Story City 2 | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 1.54 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22038 | 2018-03-28 | LNcnv | 2021-12-31 | Story City 1 | Story City Muni Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 2.86 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22037 | 2018-03-28 | LNcnv | 2021-12-31 | McCallsburg | Story City 1 | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 11.16 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22035 | 2018-03-28 | SUB | 2021-12-31 | McCallsburg | Substation |  | 69 | 69 |  | New McCallsburg 69kV/distribution sub. | IA |  |  | Planned | 2471678 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22034 | 2018-03-28 | LNcnv | 2021-12-31 | McCallsburg | St Anthony REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. | IA | 11.7 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22033 | 2018-03-28 | LNcnv | 2021-12-31 | Albion REC Tap | St Anthony REC | 1 | 69 | 69 | 77 MVAA | Convert this line section to 69kV operation. | IA | 11.6 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22032 | 2018-03-28 | LNcnv | 2021-12-31 | Albion REC | Albion REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 0.27 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22031 | 2018-03-28 | LNcnv | 2021-12-31 | Albion REC Tap | Fletcher | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 13.18 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22030 | 2018-03-28 | LNcnv | 2019-12-31 | East Nevada St | Fletcher | 1 | 69 | 69 | 140 MVA | Convert this line to 69kV operation (already built for 69kV). | IA | 2.6 |  | Planned | 302400 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22029 | 2016-12-15 | TX | 2027-05-01 | Fletcher | Transformer | 2 | 69 | 69 | 150 MVA | Add a 2nd Fletcher 161/69kV 150 MVA transformer and associated equipment. | IA |  |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22027 | 2016-12-05 | LNcnv | 2027-05-01 | Fletcher | Marshalltown North | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 2.54 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22026 | 2018-03-28 | SUB | 2018-12-21 | Marshalltown North | Substation |  | 69 | 69 |  | New Marshalltown North 69kV/distribution sub. | IA |  |  | Planned | 2028000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22025 | 2017-10-12 | SUB | 2020-06-15 | Conrad | Substation |  | 69 | 69 |  | New Conrad 69kV/distribution sub. | IA |  |  | Planned | 1480393 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22024 | 2017-10-12 | LNcnv | 2020-08-04 | Conrad | Union | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 12.65 |  | Planned | 240000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11965 | 2017-12-08 | Mtown-Grand Jct 69kV Conv | 22023 | 2017-10-12 | LNcnv | 2020-08-04 | Garwin Road | Conrad | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 11.15 |  | Planned | 600000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11974 | 2017-12-08 | Mediapolis-New London | 21945 | 2017-11-08 | LNrb | 2019-02-05 | Mediapolis | Burlington North | 1 | 69 | 69 | 77 MVA | Rebuild 6.61 miles of the Mediapolis-Burlington North 69 kV line from Mediapolis to the New London Tap. | IA | 6.61 |  | Planned | 5460000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21955 | 2018-05-18 | SUB | 2020-12-31 | White Pole Rd | Substation |  | 69 | 69 |  | Add 69kV terminal at the White Pole Rd substation. | IA |  |  | M2a_Pre-Project Approval | 248266 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22021 | 2018-03-28 | SUB | 2025-12-31 | Madrid North | Substation |  | 69 | 69 |  | Add 69kV terminal and associated upgrades at the Madrid North sub. | IA |  |  | Planned | 853225 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22019 | 2018-03-28 | LNcnv | 2025-12-31 | Madrid North | Woodward REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 5.14 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22018 | 2018-03-28 | LNcnv | 2025-12-31 | Woodward REC Tap | Woodward REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert this line tap to 69kV operation. | IA | 3.03 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22017 | 2018-03-28 | LNcnv | 2025-12-31 | Berkley REC Tap | Woodward REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 8.54 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22016 | 2018-03-28 | LNcnv | 2025-12-31 | Berkley REC Tap | Berkley REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert this line tap to 69kV operation. | IA | 8.01 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22015 | 2018-03-28 | LNcnv | 2025-12-31 | Perry REC Tap | Berkley REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 6.73 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22014 | 2018-03-28 | LNcnv | 2025-12-31 | Perry REC Tap | Perry REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert this line section to 69kV operation. | IA | 5 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22013 | 2018-03-28 | LNcnv | 2025-12-31 | Dawson | Perry REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 3.62 |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22012 | 2018-03-28 | SUB | 2025-12-31 | Dawson | Substation |  | 69 | 69 |  | Add 69kV breaker and relaying. | IA |  |  | Planned | 1239560 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22011 | 2018-05-21 | SUB | 2024-12-31 | Dawson | Substation |  | 69 | 69 |  | Build a new Dawson 69kV breaker station. | IA |  |  | M2a_Pre-Project Approval | 2421247 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22010 | 2018-05-21 | LNcnv | 2024-12-31 | Bagley REC Tap | Dawson | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 10.5 |  | M2a_Pre-Project Approval | 150600 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22008 | 2018-05-21 | LNcnv | 2024-12-31 | Bagley REC Tap | Bagley REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert this line section to 69kV operation. | IA | 3.5 |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22007 | 2018-05-21 | LNcnv | 2024-12-31 | Railway | Bagley REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 2.5 |  | M2a_Pre-Project Approval | 83400 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22006 | 2018-05-21 | SUB | 2024-12-31 | Railway | Substation |  | 69 | 69 |  | Add a 69kV breaker at Railway. | IA |  |  | M2a_Pre-Project Approval | 273601 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22005 | 2018-05-18 | SUB | 2023-12-31 | Railway | Substation |  | 69 | 69 |  | Add a 69kV breaker at Railway. | IA |  |  | M2a_Pre-Project Approval | 344781 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22004 | 2018-05-18 | LNcnv | 2023-12-31 | Scranton REC | Railway | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 12 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22003 | 2018-05-18 | LNcnv | 2023-12-31 | Scranton Distribution | Scranton REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 4 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22002 | 2018-05-18 | LNcnv | 2023-12-31 | Scranton Switch Station | Scranton Distribution | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 0.9 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22001 | 2018-05-18 | SUB | 2023-12-31 | Scranton | Switch Station |  | 69 | 69 |  | Add 69kV breaker at Scranton. | IA |  |  | M2a_Pre-Project Approval | 389182 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 22000 | 2018-05-18 | SUB | 2022-12-31 | Drager (CBPC) | Substation |  | 69 | 69 |  | CBPC will add a 69kV terminal. | IA |  |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21999 | 2018-05-18 | SUB | 2022-12-31 | Grand Junction (CIPCO) | Substation |  | 69 | 69 |  | CIPCO will add a 69kV terminal. | IA |  |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21998 | 2018-05-18 | LNcnv | 2022-12-31 | Grand Junction | Grand Junction REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 0.02 |  | M2a_Pre-Project Approval | 79500 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21997 | 2018-05-18 | LNcnv | 2022-12-31 | Grand Junction REC | Hardin Hilltop Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 7.3 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21996 | 2018-05-18 | LNcnv | 2022-12-31 | Hardin Hilltop | Hardin Hilltop Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 0.7 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21995 | 2018-05-18 | LNcnv | 2022-12-31 | Hardin Hilltop Tap | Jefferson WCC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 1.5 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21994 | 2018-05-18 | LNcnv | 2022-12-31 | Farlin REC | Jefferson WCC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 4.78 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21993 | 2018-05-18 | LNcnv | 2022-12-31 | Churdan REC Tap | Farlin REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 3.75 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21992 | 2018-05-18 | LNcnv | 2022-12-31 | Churdan REC Tap | Churdan REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert the 69kV tap to Churdan REC. | IA | 3.13 |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21991 | 2018-05-18 | LNcnv | 2022-12-31 | Scranton | Churdan REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 6.8 |  | M2a_Pre-Project Approval | 173700 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21990 | 2018-05-18 | LN | 2022-12-31 | Scranton | Drager | 1 | 69 | 69 | 77 MVA | Build a new 12.5 mile 69kV line. | IA |  | 12.5 | M2a_Pre-Project Approval | 6978774 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21989 | 2018-05-18 | SUB | 2022-12-31 | Jefferson WCC | Substation |  | 69 | 69 |  | Add a 69kV breaker terminal. | IA |  |  | M2a_Pre-Project Approval | 261830 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21988 | 2018-05-18 | SUB | 2022-12-31 | Scranton | Switch Station |  | 69 | 69 |  | Build the Scranton 69kV Switch Station. | IA |  |  | M2a_Pre-Project Approval | 3266836 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21985 | 2018-06-29 | SUB | 2021-12-31 | Grand Junction (CIPCO) | Substation |  | 69 | 69 |  | CIPCO will add a 161/69kV 100MVA transformer and associated upgrades. | IA |  |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21984 | 2018-06-29 | LNcnv | 2021-12-31 | Grand Junction | Panorama REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert from Grand Junction-Rippey-Dawson REC-Dawson-Yale REC-Panorama REC to 69kV operation. | IA |  |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21983 | 2018-05-17 | LN | 2020-12-31 | Railway | Tall Corn | 1 | 69 | 69 |  | CBPC will construct and own approximately 5.5 mile 69kV line. | IA |  | 5.5 | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21982 | 2018-05-17 | SUB | 2020-12-31 | Guthrie Junction (CIPCO) | Substation | 1 | 69 | 69 |  | CIPCO will add a 69kV terminal. | IA |  |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21980 | 2018-05-17 | LNcnv | 2020-12-31 | Guthire Center REC | Guthrie Junction | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 2 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21979 | 2018-05-17 | LNcnv | 2020-12-31 | Guthrie Center | Guthrie Center REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 1.96 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21977 | 2018-05-17 | LNcnv | 2020-12-31 | Guthrie Center | Industrial REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 1.45 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21976 | 2018-05-17 | LNcnv | 2020-12-31 | Seely REC Tap | Industrial REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 4.43 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21975 | 2018-05-17 | LNcnv | 2020-12-31 | Seely REC Tap | Seely REC |  | 69 | 69 | 77 MVA | Convert this line section to 69kV operation (already built for 69kV). | IA | 3.72 |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21974 | 2018-05-17 | LNcnv | 2020-12-31 | Railway | Seely REC Tap | 1 | 69 | 69 | 77 MVA | Convert the line to 69kV operation (already built for 69kV). | IA | 6.15 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21973 | 2018-05-17 | SUB | 2020-12-31 | Railway | Substation |  | 69 | 69 |  | Build a new Railway 69kV breaker station. | IA |  |  | M2a_Pre-Project Approval | 4547318 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21972 | 2018-05-18 | LNcnv | 2020-12-31 | Adair REC Tap | White Pole Rd | 1 | 69 | 69 | 77 MVA | Convert line to 69kV operation (already built for 69kV). | IA |  |  | M2a_Pre-Project Approval | 165600 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21961 | 2018-05-18 | SUB | 2020-12-31 | Anita | Substation |  | 69 | 69 | 77 MVA | CIPCO will add a new 69 kV terminal at the Anita substation. | IA |  |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21959 | 2018-05-18 | LNcnv | 2020-12-31 | Adair REC Tap | Adair REC | 1 | 69 | 69 | 77 MVA | CIPCO will convert the 69kV tap to 69kV operation. | IA | 3.05 |  | M2a_Pre-Project Approval |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21958 | 2018-05-18 | LNcnv | 2020-12-31 | Adair | Adair REC Tap | 1 | 69 | 69 | 77 MVA | Convert this line to 69kV operation (already built for 69kV). | IA | 2.3 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21957 | 2018-05-18 | LNcnv | 2020-12-31 | Anita Muni | Adair | 1 | 69 | 69 | 77 MVA | Convert the line to 69kV operation (already built for 69kV). | IA | 7.7 |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 11977 | 2017-12-08 | Anita-Grand Jct 69 kV Conv | 21956 | 2018-05-18 | LNcnv | 2020-12-31 | Anita | Anita Muni | 1 | 69 | 69 | 77 MVA | Convert line to 69kV operation (already built for 69kV) | IA | 3.5 |  | M2a_Pre-Project Approval | 124800 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12167 | 2017-12-08 | J416 | 22283 | 2018-05-09 | SwSta | 2019-04-01 | Quinn | Switch Station |  | 345 | 345 |  | Construct new Quinn 345 kV switching station in the Killdeer - Blackhawk 345 kV line. | IA |  |  | M1_Final SPM or OOC | 9130862 | Engineering |  | N | Y | Y
A in MTEP17 | A | West | ITCM | 12167 | 2017-12-08 | J416 | 22286 | 2018-05-09 | SUBmisc | 2019-04-01 | Quinn | Switch Station |  | 345 | 345 |  | TOIF at the Quinn 345kV switching station | IA |  |  | M1_Final SPM or OOC | 656210 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12167 | 2017-12-08 | J416 | 22285 | 2018-05-09 | LN | 2019-04-01 | Quinn | J416 collector sub | 1 | 345 | 345 | 700 MVA | Construct radial 345 kV line from Quinn to J416 collector sub. | IA |  | 9.5 | M1_Final SPM or OOC | 15454277 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12167 | 2017-12-08 | J416 | 22284 | 2018-05-09 | LN | 2019-04-01 | Blackhawk | Killdeer | 1 | 345 | 345 |  | Construct the line taps for the Quinn Switch Station tapping the Blackhawk-Killdeer 345kV line. | IA |  |  | M1_Final SPM or OOC | 988669 | Engineering |  | N | Y | Y
A in MTEP17 | A | West | ITCM | 12168 | 2017-12-08 | J278 | 22287 | 2017-06-26 | LNup | 2020-12-31 | Hazleton | Mitchell | 1 | 345 | 345 |  | Raise structures on the Mitchell to Hazelton 345 kV line to achieve 995 MVA summer rating. | IA |  |  | Planned | 3360000 | Engineering |  | N | Y | Y
A in MTEP17 | A | West | ITCM | 12200 | 2017-12-08 | Cust Interconnect Blanket | 22321 | 2016-09-15 | LN | 2020-12-31 | Blanket for Customer Interconnections under $1 million for 2020 | Throughout system |  | 345 | 69 |  | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL |  |  | Planned | 2400000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12201 | 2017-12-08 | ITCM Asset Blanket | 22322 | 2016-09-15 | LN | 2020-12-31 | ITCM Asset Blanket for 2020 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL |  |  | Planned | 37080000 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22391 | 2018-05-07 | SUB | 2020-12-31 | Frytown | Substation |  | 69 | 69 |  | New Frytown 69kv/distribution substation. | IA |  |  | M1_Final SPM or OOC | 3290609 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22568 | 2018-05-07 | LN | 2023-12-31 | Wellman | Wellamn Tap | 1 | 34 | 34 |  | Retire the 8.9 mile Wellman tap after the load is served from Kalona Koe. | IA |  |  | M1_Final SPM or OOC | 485394 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22567 | 2018-05-07 | SUB | 2023-12-31 | Iowa Junction | Substation |  | 34 | 34 |  | Retire the 34kV equipment at Iowa Jct. | IA |  |  | M1_Final SPM or OOC | 329790 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22566 | 2018-05-07 | SUB | 2023-12-31 | Kalona Koe | Substation |  | 69 | 69 |  | Convert the new Kalona Koe substation to 69kV operation. | IA |  |  | M1_Final SPM or OOC | 114065 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22400 | 2018-05-07 | LN | 2023-12-31 | Iowa Junction | Kalona REC Tap | 1 | 69 | 69 |  | Re-terminate the existing Hills - Washington 69kV line to Iowa Junction and then continue to Washington | IA | 9.53 |  | M1_Final SPM or OOC | 201457 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22399 | 2018-05-07 | LN | 2023-12-31 | Hills (MEC) | Iowa Junction | 1 | 69 | 69 |  | Re-terminate the existing Hills - Washington 69kV line to Iowa Junction and then continue to Washington | IA |  | 0.1 | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22398 | 2018-05-07 | LNcnv | 2023-12-31 | Riverside Voyager | Iowa Junction | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation | IA | 2.39 |  | M1_Final SPM or OOC | 201445 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22397 | 2018-05-07 | LNcnv | 2023-12-31 | Kalona Koe | Riverside Voyager | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation | IA | 7.14 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22396 | 2018-05-07 | SUB | 2018-12-31 | Kalona Koe | Substation |  | 69 | 69 | 77 MVA | New Kalona Koe 69kV/distribution substation. Operate at 34kV until conversion. | IA |  |  | M4_Pre-Construction | 2119466 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22395 | 2018-05-07 | LN | 2022-12-31 | Hills (IPL) | New Hills Area Sub | 1 | 69 | 69 | 77 MVA | Build a new circuit, approximately ~0.5 miles of T2-4/0 to be operated at 69kV | IA |  | 1 | M1_Final SPM or OOC | 1207219 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22393 | 2018-05-07 | LNcnv | 2022-12-31 | Frytown | Hills (IPL) |  | 69 | 69 | 77 MVa | Convert this line section to 69kV operation | IA | 11.68 |  | M1_Final SPM or OOC | 674927 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12344 | 2017-12-08 | Kalona-IA Jct 69kV Conv | 22392 | 2018-05-07 | LN | 2021-12-31 | Frytown | Parnell REC | 1 | 69 | 69 | 77 MVA | Build a new circuit, approximately ~12 miles of T2-4/0 to be operated at 69kV | IA |  | 12 | M1_Final SPM or OOC | 5901806 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22415 | 2016-10-12 | SUB | 2019-12-31 | Wyomiing | Substation |  | 161 | 69 |  | Add five 69kV breaker terminals at the Wyoming sub. | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22424 | 2018-05-14 | LNcnv | 2021-12-31 | Dixon | Fulton | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. Includes the conversion of Wyoming South, Massillon, Lowden, and Wheatland distribution subs. | IA |  |  | M2a_Pre-Project Approval | 261203 |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22423 | 2018-05-14 | LNrb | 2021-12-31 | Dixon | Fulton | 1 | 34.5 | 34.5 | 39 MVA | Rebuild 34.5 to 69kV and continue to operate at 34.5kV until conversion is ready. | IA |  |  | M2a_Pre-Project Approval | 1917600 |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22422 | 2016-12-15 | SUB | 2018-12-31 | Sand Springs | Substation |  | 69 | 69 | 77 MVA | Terminal work to connect the Coggon to Sand Springs 69 kV line at Sand Springs. | IA |  |  | Planned | 19902 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22421 | 2016-10-12 | LNcnv | 2019-12-31 | Wyoming | Wyoming REC | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. | IA | 0.5 |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22420 | 2016-12-15 | LNcnv | 2021-12-31 | Wyoming | Dixon | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. Includes the conversion of Wyoming South, Massillon, Lowden, and Wheatland distribution subs. | IA |  |  | Planned | 5311982 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22419 | 2016-10-12 | SUB | 2019-12-31 | Maquoketa (CIPCO) | Switch Station |  | 69 | 69 | 77 MVA | Construct a three (3) breaker Switching Station (CIPCO Project) | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22418 | 2018-06-29 | LNcnv | 2020-12-31 | Wyoming | Maquoketa | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. Includes the conversion of Monmouth REC and Monmouth distribution subs. | IA |  |  | M1_Final SPM or OOC | 103200 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22417 | 2016-12-15 | LNcnv | 2019-12-31 | Wyoming | Bennett | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. Includes the conversion of Olin, Rome REC, Clarence South, and Clarence REC distribution subs. | IA |  |  | Planned | 17864047 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 12403 | 2017-12-08 | East IA Wyoming Conv | 22416 | 2016-12-15 | LNcnv | 2018-12-31 | Wyoming | Monticello Industrial | 1 | 69 | 69 | 77 MVA | Convert this line section to 69kV operation. Includes the conversion of Scotch Grove REC and Lovell REC distribution subs. | IA |  |  | Planned | 490266 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 13083 | 2018-05-03 | Van Allen | 22569 | 2018-05-03 | SUB | 2019-12-31 | Van Allen | Substation |  | 69 | 69 |  | Construct a new Van Allen 69-25-12.5kV 33MVA substation with two 69kV line breakers. | IA |  |  | M3_Long Lead Materials | 1549657 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 13083 | 2018-05-03 | Van Allen | 22571 | 2018-05-03 | LN | 2019-12-31 | Rock Creek | Van Allen | 1 | 69 | 69 |  | Install fiber along the Rock Creek-Van Allen 69kV line to allow for adequate protection. | IA |  |  | M3_Long Lead Materials | 2790652 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 13083 | 2018-05-03 | Van Allen | 22570 | 2018-05-03 | SUB | 2019-12-31 | Beaver Channel | Substation |  | 69 | 69 |  | Upgrades required for fiber and relay work due to the new Van Allen substation. | IA |  |  | M3_Long Lead Materials | 273415 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 13084 | 2017-12-08 | West Okoboji | 22572 | 2018-06-07 | SUB | 2019-04-16 | West Okoboji Lakes | Substation |  | 69 | 69 |  | Construct the new West Okoboji Lake 69/25kV substation with a single transformer, but allow for a second future transformer. | IA |  |  | M3_Long Lead Materials | 1930655 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM | 13084 | 2017-12-08 | West Okoboji | 22573 | 2018-06-07 | LN | 2019-04-16 | West Okoboji Lakes | Substation |  | 69 | 69 |  | Line tap work required for the new West Okoboji Lakes substation. | IA |  |  | M3_Long Lead Materials | 504280 | Engineering |  | N | N | N
A in MTEP17 | A | West | ITCM, MEC | 13644 | 2017-12-08 |  | 22731 | 2017-09-06 | SwSta | 2019-10-01 | J412 |  |  | 345 |  |  | Interconnection substation. | IA |  |  | Planned | 9000000 | Planning |  | N | Y | Y
A in MTEP17 | A | West | ITCM, MEC | 13644 | 2017-12-08 |  | 22732 | 2017-09-06 | TAP | 2019-10-01 | J412 |  |  | 345 |  |  | Line taps | IA |  |  | Planned | 1000000 | Planning |  | N | Y | Y
A in MTEP17 | A | East | ITCT | 9864 | 2018-06-20 | METC_15_021 | 21249 | 2018-06-20 | LNrb | 2020-09-30 | Whiting | Custer | 1 | 120 |  |  | Rebuild 1.26 miles of 636 ACSR from the ITCT portion of the Whiting – Custer 120 kV circuit using 1431 ACSR and OPGW on new 230 kV future double circuit structures | MI | 1.26 |  | M2a_Pre-Project Approval | 3196500 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21317 | 2017-10-03 | LN | 2019-12-31 | Trenton Channel | Jefferson | 4 | 120 |  |  | Six-wiring the Trenton Channel - Jefferson #4 120 kV line with the decommissioned circuit on the other side of its common structures | MI |  |  | Proposed | 104000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21328 | 2017-10-03 | SUB | 2019-12-31 | Riverview |  |  | 120 |  |  | Upgrade station equipment at position "HD" and "HR". | MI |  |  | Proposed | 443000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21326 | 2017-10-03 | SUB | 2019-12-31 | Jefferson |  |  | 120 |  |  | Upgrade station equipment. | MI |  |  | Proposed | 220000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21325 | 2017-10-03 | SUB | 2019-12-31 | Horn |  |  | 120 |  |  | Upgrade station equipment | MI |  |  | Proposed | 73000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21323 | 2017-10-03 | SUB | 2019-12-31 | Trenton Channel |  |  | 120 |  |  | Upgrade station equipment at position "JG" and "HG". | MI |  |  | Proposed | 548000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21321 | 2017-10-03 | LN | 2019-12-31 | Jefferson | Riverview | 2 | 120 |  |  | Rebuild approximately 0.304 mile of 954 ACSR conductor to 1431 ACSR to match with the rest of the circuit | MI | 0.3 |  | Proposed | 104000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21320 | 2017-10-03 | LN | 2019-12-31 | Horn | Jefferson | 1 | 120 |  |  | Six-wiring the Horn - Jefferson 120 kV line with the decommissioned circuit on the other side of its common structures and construct two spans of new double-circuit 954 ACSR and six-wire it to complete the loop in-and-out of Horn toward Jefferson | MI |  | 0.16 | Proposed | 104000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 9909 | 2017-12-08 |  | 21319 | 2017-10-03 | LN | 2019-12-31 | Trenton Channel | Horn | 1 | 120 |  |  | Six-wiring the Trenton Channel - Horn 120 kV line with the decommissioned circuit on the other side of its common structures | MI |  |  | Proposed | 104000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 12004 | 2017-12-08 | ITCT_16_022 | 22020 | 2018-03-27 | SwSta | 2019-12-31 | Elm |  |  | 230 |  |  | Install two 230 kV line breakers at the Elm 230 kV station to terminate the Brownstown - Elm #2 and Elm - Rotunda 230 kV lines. | MI |  |  | M2a_Pre-Project Approval | 3000000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 12187 | 2017-12-08 |  | 22307 | 2016-09-15 | TEQ | 2019-12-31 | Throughout System |  |  | 120 |  |  | Install a new GOAB switch or replace an existing 120 kV, full-load-break pole top switch at necessary tap points. | MI |  |  | Proposed | 2400000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 12188 | 2017-12-08 |  | 22308 | 2016-09-15 | TEQ | 2020-12-31 | Throughout System |  |  | 120 |  |  | Install a new GOAB switch or replace an existing 120 kV, full-load-break pole top switch at necessary tap points. | MI |  |  | Proposed | 2400000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 12193 | 2017-12-08 |  | 22315 | 2016-09-15 | SUB | 2020-12-31 | 2020 ITCT Asset Replacement Program |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | Proposed | 58100000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | ITCT | 12194 | 2017-12-08 |  | 22317 | 2016-09-15 | Dist | 2020-12-31 | Blanket for Customer Interconnections | Throughout System |  | 120 |  |  | Blanket for customer interconnections and retirements less than $1 million | MI |  |  | Proposed | 2000000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | ITCT | 12443 | 2017-12-21 | ITC_16_031 | 22435 | 2018-06-27 | SUB | 2020-06-01 | Nitro |  |  | 120 |  |  | Construct new Northville 120kV station. Station will serve 18MVA of new load. Station will have 2 disjointed buses on the high side. | MI |  |  | M3_Long Lead Materials | 465000 | Planning |  | N | N | N
A in MTEP17 | A | East | ITCT | 12443 | 2017-12-21 | ITC_16_031 | 22436 | 2018-06-27 | TAP | 2020-06-01 | Coventry - Baltic & Hager- Hines | Nitro |  | 120 |  |  | Tap the existing Coventry - Baltic 120kV and Hager- Hines 120kV lines to feed new Nitro 120kV station. | MI |  |  | M3_Long Lead Materials | 4900000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 13144 | 2017-12-08 | ITC_17_003 | 22581 | 2018-03-27 | SUB | 2018-05-01 | Zephyr |  |  | 120 |  |  | Install New 120kV Station with 3 breakers | MI |  |  | M4_Pre-Construction | 2530000 |  |  | N | N | N
A in MTEP17 | A | East | ITCT | 13144 | 2017-12-08 | ITC_17_003 | 22585 | 2018-03-27 | RLY | 2018-05-01 | Navarre |  |  | 120 |  |  | Upgrade relaying at position HG | MI |  |  | M4_Pre-Construction | 190000 |  |  | N | N | N
A in MTEP17 | A | East | ITCT | 13144 | 2017-12-08 | ITC_17_003 | 22584 | 2018-03-27 | RLY | 2018-05-01 | Brownstown |  |  | 120 |  |  | Upgrade relaying at position JB | MI |  |  | M4_Pre-Construction | 230000 |  |  | N | N | N
A in MTEP17 | A | East | ITCT | 13144 | 2017-12-08 | ITC_17_003 | 22583 | 2018-03-27 | LINE | 2018-05-01 | Brownstown | Zephyr | 1 | 120 |  |  | Cut Brownstown - Navarre 1 120 kV circuit into the new Zephyr station | MI |  |  | M4_Pre-Construction | 370000 |  |  | N | N | N
A in MTEP17 | A | East | ITCT | 13144 | 2017-12-08 | ITC_17_003 | 22582 | 2018-03-27 | LINE | 2018-05-01 | Navarre | Zephyr | 1 | 120 |  |  | Cut Brownstown - Navarre 1 120 kV circuit into the new Zephyr station. Install OPGW for relay communication on Navarre to Zephyr. | MI |  |  | M4_Pre-Construction | 380000 |  |  | N | N | N
A in MTEP17 | A | East | ITCT | 13573 | 2017-12-08 | ITC_16_018 | 22655 | 2017-08-25 | LNup | 2019-12-31 | Bunce Creek | Menlo | 1 | 120 |  |  | Fully remediate the sag limit on the 266.8 ACSR from the Bunce Creek - Menlo 120 kV circuit in order to increase its summer emergency rating to 730 A (152 MVA). | MI |  |  | Proposed | 60000 | Engineering |  | N | N | N
A in MTEP17 | A | East | ITCT | 14265 | 2018-01-29 |  | 23300 | 2018-02-21 | LNrc | 2020-06-01 | Monroe | Bayshore |  | 345 |  |  | MISO-PJM interregional upgrade, ATSI to replace river span (reconductor), no ITCT capital work. The cost reported is the total MISO share. | MI,OH |  |  | Planned | 110000 |  |  | N | Y | N | Y
A in MTEP17 | A | West | MDU | 12787 | 2017-12-08 |  | 22528 | 2018-06-18 | LINE | 2019-06-30 | WAPA Watford City | MDU Watford City | 1 | 230 |  | 343 | A radial 230 kV line from WAPA Watford City to MDU Watford City | ND |  | 0.6 | Planned | 200000 | Planning |  | N | N | N
A in MTEP17 | A | West | MDU | 12787 | 2017-12-08 |  | 22530 | 2018-06-18 | SUB | 2019-06-30 | MDU Watford City |  |  | 230 | 34.5 | 42 | A new 230/34.5 kV substation with a 42 MVA 230/34.5 kV transformer | ND |  |  | Planned | 3300000 | Planning |  | N | N | N
A in MTEP17 | A | West | MEC | 12049 | 2017-12-08 |  | 22135 | 2018-03-30 | SUB | 2018-06-01 | 34th Avenue NW |  |  | 161 |  |  | Expand the 34th Avenue NW Substation to accommodate 2 additional terminals on the ring bus. Three 161 kV circuit breakers will be added to the ring bus. Project costs reflect 161 kV network transmission facilities. | IA |  |  | Under Construction | 1650000 | Planning |  | N | N | N
A in MTEP17 | A | West | MEC | 12064 | 2017-12-08 |  | 22142 | 2018-03-30 | SUB | 2018-12-31 | Willow Creek |  |  | 161 | 13.2 | 50 | Add three new 161 kV circuit breakers to accommodate the addition of a new 50 MVA 161-13 kV transformer to meet increasing customer load. | IA |  |  | Under Construction | 1420000 | Planning |  | N | N | N
A in MTEP17 | A | West | MEC | 12107 | 2017-12-08 |  | 22219 | 2017-08-29 | SUB | 2019-06-01 | Valley Drive Substation |  |  | 69 | 13 | 25 | Install a new 69 kV Substation including 69 kV line breakers and one 25 MVA distribution transformer. Includes two short 69 kV line taps approx. .125 miles each. | IA |  | 0.25 | Planned | 4270000 | Planning |  | N | N | N
A in MTEP17 | A | West | MEC | 12363 | 2017-12-08 |  | 22407 | 2018-03-30 | CB | 2019-12-01 | Bondurant |  |  | 161 |  | 40 kA | Replace existing 161 kV circuit breaker DAH803 at Bondurant Substation with a circuit breaker rated 40 kA. | IA |  |  | Planned | 325000 | Planning |  | N | N | N
A in MTEP17 | A | West | MEC | 12503 | 2017-12-08 |  | 22446 | 2018-06-29 | LNrb | 2019-03-31 | Prairie City | Monroe |  | 69 |  |  | Rebuild the Prairie City to Monroe REC 69 kV line with new poles and conductor. | IA | 7.79 | 0 | Planned | 3712100 | Budgetary |  | N | N | N
A in MTEP17 | A | West | MEC | 12723 | 2017-12-08 |  | 22499 | 2017-06-26 | LNup | 2018-09-01 | Arbor Hill | Grimes | 1 | 345 |  |  | Line Transposition Structures | IA |  |  | Planned | 1300000 | Planning Preliminary |  | N | Y | Y
A in MTEP17 | A | West | MEC | 12723 | 2017-12-08 |  | 22501 | 2018-09-28 | TAP | 2018-09-01 | Arbor Hill |  |  | 345 |  |  | Line Taps for Arbor Hill Substation | IA |  |  | Under Construction | 1500000 | Planning Preliminary |  | N | Y | Y
A in MTEP17 | A | West | MEC | 12723 | 2017-12-08 |  | 22500 | 2018-09-28 | SwSta | 2018-09-01 | Arbor Hill |  |  | 345 |  |  | The 345 kV Interconnection Substation will consist of a 345 kV ring bus, three 345 kV breakers, two 345 kV dead-end structures, and associated equipment. | IA |  |  | Under Construction | 7200000 | Planning Preliminary |  | N | Y | Y
A in MTEP17 | A | West | MEC | 12725 | 2017-12-08 |  | 22503 | 2018-09-28 | SwSta | 2018-12-01 | Orient |  |  | 345 |  |  | The 345 kV Interconnection Substation will consist of 345 kV bus, eight (8) 345 kV breakers, four (4) 345 kV dead-end structures, and associated equipment. | IA |  |  | Under Construction | 22500000 | Planning Preliminary |  | N | Y | Y
A in MTEP17 | A | West | MEC | 12725 | 2017-12-08 |  | 22505 | 2018-09-28 | TAP | 2019-08-01 | Atchison County | Booneville | 1 | 345 |  |  | Transmission Owner will install line taps for tap-in tap-out facilities to connect the Atchison County–Booneville 345 kV line to the Interconnection Substation. It is assumed that two intermediate structures per line tap will be needed to reach the assumed substation site from Atchison County-Booneville line. It is assumed that the substation site will be adjacent to the existing lines. It is further assumed that the substation site and the existing lines are contiguous and that the existing right-of-way for the existing lines and the new land to be provided to and owned by the Transmission Owner will be adequate to tap the lines such that franchising is not required for the new facilities. It is expected that two (2) single pole dead-end structures would be installed. It is assumed drilled pier reinforced concrete foundations will be utilized. It is assumed four intermediate structures would also be installed. A standard 345 kV conductor with a rating equal to or greater than the existing conductor will be installed from each tap structure to the substation dead-ends. The 345 kV dead-end suspension insulators will be installed on the dead-end structures for the tap. | IA |  |  | Planned | 1200000 | Planning Preliminary |  | N | Y | Y
A in MTEP17 | A | West | MEC | 12725 | 2017-12-08 |  | 22504 | 2018-09-28 | LNup | 2019-12-01 | Rolling Hills | Madison County | 1 | 345 |  |  | Transposition Structures | IA |  |  | Planned | 871000 | Planning Preliminary |  | N | Y | Y
A in MTEP17 | A | West | MEC | 13584 | 2017-12-08 | T90LH | 22689 | 2018-07-09 | LNup | 2019-08-01 | J529/J590 | Obrien County | 1 | 345 |  |  | Two transpositions | IA |  |  | Planned | 871000 | Planning |  | N | Y | Y
A in MTEP17 | A | West | MEC | 13584 | 2017-12-08 | T90LH | 22691 | 2018-07-09 | TAP | 2019-08-01 | J529/J590 |  |  | 345 |  |  | Line taps | IA |  |  | Planned | 950000 | Planning |  | N | Y | Y
A in MTEP17 | A | West | MEC | 13584 | 2017-12-08 | T90LH | 22690 | 2018-07-09 | SwSta | 2019-08-01 | J529/J590 |  |  | 345 |  |  | Interconnection Substation | IA |  |  | Planned | 8179000 | Planning |  | N | Y | Y
A in MTEP17 | A | East | METC | 9864 | 2018-06-20 | METC_15_021 | 21248 | 2018-06-20 | LNrb | 2020-09-30 | Whiting | Custer | 1 | 120 |  |  | Rebuild 7.87 miles of 636 ACSR from the METC portion of the Whiting – Custer 120 kV circuit using 1431 ACSR and OPGW on new 230 kV future double circuit structures | MI | 7.87 |  | M2a_Pre-Project Approval | 11096500 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 9864 | 2018-06-20 | METC_15_021 | 21257 | 2018-06-20 | TEQ | 2020-09-30 | Custer |  |  | 120 |  |  | Replace limiting terminal equipment at the Custer station | MI |  |  | M2a_Pre-Project Approval | 5000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 9864 | 2018-06-20 | METC_15_021 | 21250 | 2018-06-20 | TEQ | 2020-09-30 | Whiting |  |  | 120 |  |  | Replace limiting terminal equipment at the Whiting station | MI |  |  | M2a_Pre-Project Approval | 2000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 11663 | 2017-12-08 | METC_16_036 | 21808 | 2018-03-27 | LNup | 2019-12-31 | Blackstone | Leoni | 1 | 138 |  |  | Remediate the sag limit on the Blackstone–Leoni #1 138kV circuit to 308 MVA. | MI |  |  | M2a_Pre-Project Approval | 90000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 11664 | 2017-12-08 | METC_16_037 | 21809 | 2018-03-27 | LNup | 2019-12-31 | Blackstone | Leoni | 2 | 138 |  |  | Remediate the sag limit on the Blackstone–Leoni #2 138kV circuit from 194 MVA to 636 ACSR conductor limit of 310 MVA. | MI |  |  | M2a_Pre-Project Approval | 266000 | Engineering Preliminary |  | N | N | N
A in MTEP17 | A | East | METC | 11665 | 2017-12-08 | METC_16_038 | 21810 | 2018-03-27 | LNup | 2019-12-31 | Blackstone | Leoni | 3 | 138 |  |  | Remediate the sag limit on the Blackstone–Leoni #3 138kV circuit from 221 MVA to 636 ACSR conductor limit of 310 MVA. | MI |  |  | M2a_Pre-Project Approval | 53000 | Engineering Preliminary |  | N | N | N
A in MTEP17 | A | East | METC | 11884 | 2017-12-08 | METC_15_020 | 21849 | 2018-03-27 | LNrb | 2020-12-31 | Batavia | Alder Creek |  | 138 |  |  | Rebuild 15.62 miles of 266.8 ACSR from the Alder Creek – Batavia section of the Verona – Batavia 138 kV circuit using 954 ACSR and OPGW on new double circuit structures constructed at 230 kV standards. The structures will have one side vacant and available for a future circuit. | MI | 15.62 |  | M2a_Pre-Project Approval | 23150000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 11884 | 2017-12-08 | METC_15_020 | 21851 | 2018-03-27 | TEQ | 2020-12-31 | Batavia |  |  | 138 |  |  | Upgrade limiting equipment at the Batavia 138 kV station. | MI |  |  | M2a_Pre-Project Approval | 20000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 11884 | 2017-12-08 | METC_15_020 | 21850 | 2018-03-27 | LNrb | 2020-12-31 | Alder Creek | Barnum Creek Jct. |  | 138 |  |  | Rebuild 6.62 miles of 266.8 ACSR from the Barnum Creek Jct. – Alder Creek section of the Verona – Batavia 138 kV circuit using 954 ACSR and OPGW on new double circuit structures constructed at 230 kV standards. The structures will have one side vacant and available for a future circuit. Also replace PTS 3199. | MI | 6.62 |  | M2a_Pre-Project Approval | 11190000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12032 | 2017-12-08 | METC_16_039 | 22108 | 2018-03-27 | LNup | 2019-12-31 | Rice Creek | Denso J. | 1 | 138 |  |  | Remediate the sag limit on the Rice Creek–Denso J. 138kV section from 89 MVA to 150 MVA. | MI |  |  | M2a_Pre-Project Approval | 468000 | Engineering Preliminary |  | N | N | N
A in MTEP17 | A | East | METC | 12128 | 2017-12-08 | METC_16_032 | 22248 | 2018-03-27 | LNrb | 2020-12-31 | Stover | Van Tyle | 1 | 138 |  |  | Rebuild about 21.7 miles of 266.8 ACSR and 0.19 mile of 336.4 ACSR to 954 ACSR on Stover – Alba Junction - Van Tyle 138kV utilizing 954 ACSR conductor on 230 kV double circuit towers. Also upgrade the Van Tyle relay to address tripping limits. | MI | 22 |  | M2a_Pre-Project Approval | 28800000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12189 | 2017-12-08 |  | 22310 | 2016-09-15 | TEQ | 2019-12-31 | Throughout System |  |  | 138 |  |  | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points across the METC system. | MI |  |  | Proposed | 3600000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12190 | 2017-12-08 |  | 22311 | 2016-09-15 | TEQ | 2020-12-31 | Throughout System |  |  | 138 |  |  | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points across the METC system. | MI |  |  | Planned | 3600000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12192 | 2017-12-08 |  | 22313 | 2016-09-15 | SUB | 2020-12-31 | 2020 METC Asset Replacement Program |  |  | 345 | 138 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | Proposed | 49000000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | METC | 12197 | 2017-12-08 |  | 22319 | 2016-09-15 | Dist | 2020-12-31 | Blanket for Customer Interconnectoins | Throughout System |  | 138 |  |  | Blanket for customer interconnections and retirements less than $1 million | MI |  |  | Proposed | 2500000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | METC | 12385 | 2018-03-27 | METC_16_041 | 22412 | 2018-03-27 | SUB | 2022-01-01 | Henry 138 kV |  |  | 138 |  |  | New 138 kV substation including 138 kV, 5-breaker ring bus and a 36 MVAR Capacitor Bank. | MI |  |  | M3_Long Lead Materials | 6400000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12385 | 2018-03-27 | METC_16_041 | 22448 | 2018-03-27 | RLY | 2022-01-01 | Plaster Creek 138 |  |  | 138 |  |  | Upgrade relaying at Plaster Creek to accommodate the new 138 kV Henry Substation | MI |  |  | M3_Long Lead Materials | 100000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12385 | 2018-03-27 | METC_16_041 | 22447 | 2018-03-27 | RLY | 2022-01-01 | Gaines 138 |  |  | 138 |  |  | Upgrade relaying at Gaines to accommodate the new Henry Substation | MI |  |  | M3_Long Lead Materials | 130000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12385 | 2018-03-27 | METC_16_041 | 22414 | 2018-03-27 | LN | 2022-01-01 | Gaines | Henry | 1 | 138 |  |  | New 138 kV line created by looping the existing Plaster Creek-Gaines line approx. 0.1 miles into Henry. | MI |  | 0.1 | M3_Long Lead Materials | 185000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12385 | 2018-03-27 | METC_16_041 | 22413 | 2018-03-27 | LN | 2022-01-01 | Plaster Creek | Henry | 1 | 138 |  |  | New 138 kV line created by looping the existing Plaster Creek-Gaines line approx. 0.1 miles into Henry. | MI |  | 0.1 | M3_Long Lead Materials | 185000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12423 | 2018-07-10 |  | 22425 | 2018-07-10 | LNup | 2022-01-01 | Campbell | Hudsonville Junction | 1 | 138 |  |  | Perform sag remediation to get the rating of Campbell-Hudsonville Junction section of the Campbell-Ransom 138 kV line to at least 330 MVA (1381 A) | MI |  |  | Proposed | 80000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 12444 | 2017-12-08 |  | 22438 | 2016-10-19 | SUBmisc | 2018-12-31 | Tallmadge 138 kV |  |  | 138 |  |  | New battery and charger at Tallmadge. | MI |  |  | Planned | 73000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 13384 | 2017-12-08 | METC_17_027 | 22614 | 2017-12-21 | SwSta | 2018-10-26 | Luce |  |  | 138 |  |  | METC to construct new Luce 138kV substation to support the J589 interconnection. | MI |  |  | M4_Pre-Construction | 4500000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 13384 | 2017-12-08 | METC_17_027 | 22618 | 2017-12-21 | RLY | 2018-10-26 | REGAL |  |  | 138 |  |  | upgrade relaying at Regal on position 20 | MI |  |  | M4_Pre-Construction | 90000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 13384 | 2017-12-08 | METC_17_027 | 22617 | 2017-12-21 | LNrc | 2018-10-26 | Summerton | Luce | 1 | 138 |  |  | Install OPGW on Summerton to Luce | MI |  |  | M4_Pre-Construction | 2180000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 13384 | 2017-12-08 | METC_17_027 | 22616 | 2017-12-21 | LNrc | 2018-10-26 | REGAL | LUCE | 1 | 138 |  |  | Install OPGW on Regal to Luce | MI |  |  | M4_Pre-Construction | 530000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 13384 | 2017-12-08 | METC_17_027 | 22615 | 2017-12-21 | LN | 2018-10-26 | REGAL | SUMMERTON | 1 | 138 |  |  | Cut Regal-Summerton 138kV line into new Luce (J589) station | MI |  | 0.1 | M4_Pre-Construction | 815000 | Engineering |  | N | N | N
A in MTEP17 | A | East | METC | 13444 | 2017-12-08 |  | 22621 | 2017-08-30 | SUB | 2020-09-01 | Nelson Rd |  |  | 345 |  |  | Installation of 4-345 kV breakers | MI |  |  | Planned | 4281000 |  |  | N | Y | Y
A in MTEP17 | A | East | METC | 14324 | 2017-12-08 |  | 23309 | 2018-03-27 | LINE | 2020-12-31 | Buck Creek | Hazelwood | 1 | 138 |  |  | Cut the existing Beals Road - Hazelwood 138kV line into Buck Creek. | MI |  |  | M2a_Pre-Project Approval | 833000 | Engineering | Generator | N | N | N | Y
A in MTEP17 | A | East | METC | 14324 | 2017-12-08 |  | 23311 | 2018-03-27 | RLY | 2020-12-31 | Beals Rd |  |  | 138 |  |  | Relay modifications | MI |  |  | M2a_Pre-Project Approval | 150000 | Engineering |  | N | N | N | Y
A in MTEP17 | A | East | METC | 14324 | 2017-12-08 |  | 23310 | 2018-03-27 | LINE | 2020-12-31 | Beals Road | Buck Creek | 1 | 138 |  |  | Cut the existing Beals Road - Hazelwood 138kV line into Buck Creek. Remediate the sag on this Beals Road – Buck Creek 138 kV line to at least 282 MVA (1,180 Amp). | MI |  |  | M2a_Pre-Project Approval | 833000 | Engineering |  | N | N | N | Y
A in MTEP17 | A | West | MP | 12323 | 2017-12-08 | 93 Line Upgrade | 22387 | 2018-04-03 | LNup | 2019-03-31 | Blackberry | Forbes | 1 | 230 |  | 470 | Thermal upgrade | MN | 33 | 0 | Planned | 3500000 | Planning |  | N | N | N
A in MTEP17 | A | West | MP | 12563 | 2017-12-08 | Boswell 230/115 kV Transformer | 22454 | 2018-04-03 | SUB | 2018-12-31 | Boswell |  |  | 230 | 115 | 373 | New 115 kV substation yard adjacent to the Boswell 230 kV yard. A new 230/115 kV transformer will connect both yards. | MN | 0 | 0 | Under Construction | 8876129 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | West | MP | 12563 | 2017-12-08 | Boswell 230/115 kV Transformer | 22455 | 2018-04-03 | LN | 2018-12-31 | Boswell | Blandin |  | 115 |  |  | Extend existing line into new 115 kV yard | MN | 0 | 0.25 | Under Construction | 2556265 |  |  | N | N | N
A in MTEP17 | A | West | MP | 12583 | 2017-12-08 | 76 Line Upgrade | 22457 | 2018-08-30 | TEQ | 2018-05-01 | Hibbard |  |  | 115 |  | 182 | Replace 800 Amp equipment at Hibbard Substation | MN | 0 | 0 | Under Construction | 250000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | West | MP | 12644 | 2017-12-08 | North Shore STATCOM | 22460 | 2018-04-03 | SVC | 2019-09-01 | North Shore Switching Station |  |  | 115 |  | 75 | New +/-75 MVAR STATCOM | MN | 0 | 0 | Under Construction | 19000000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | West | MPW | 2935 | 2018-07-10 | MPW-WR | 5108 | 2018-06-14 | LN | 2020-06-01 | Wiggins | Power Plant | 1 | 69 |  | 89 | Reconductor Line from 336.4 to 636 ACSR | IA | 4.2 |  | Proposed | 2200000 | Planning |  | N | N | N | Y
A in MTEP17 | A | West | MPW | 9001 | 2018-06-14 | MPW-WS-TT-L95 | 20794 | 2018-06-14 | SUB | 2019-06-01 | West | Isett | 1 | 69 |  | 89 | Upgrade CT limits at Isett and West substations to 89 MVA conductor rating at both terminals | IA |  |  | Proposed | 82000 |  |  | N | N | N
A in MTEP17 | A | West | MPW | 9022 | 2017-12-08 | MPW-PS-TT-L98 | 20796 | 2017-12-29 | LNrc | 2019-06-01 | Pine St | Isett | 1 | 69 |  | 89 | Reconductor Pine St. to Isett substations to obtain 89 MVA. | IA |  |  | Proposed | 1930000 |  |  | N | N | N
A in MTEP17 | A | West | MPW | 12227 | 2018-09-28 | MPW-PP-GV-L90 | 22383 | 2018-09-28 | LNup | 2019-09-01 | Power Plant | Grandview Tap | 1 | 69 |  | 89 | Upgrade Power Plant terminals for Line 90 (Power Plant to Grandview) to obtain 89 MVA conductor rating. | IA |  |  | Planned | 15000 |  |  | N | N | N
A in MTEP17 | A | West | MPW | 13223 | 2018-09-28 | MPW-TT | 22594 | 2018-09-28 | CAP | 2020-06-01 | 633451 Isett 8 |  |  | 69 |  | 6 MVAR | Add 6 MVAR of 69 kV capacitors at MPW bus 633451 Isett 8 | IA |  |  | Planned | 180000 | Planning |  | N | N | N
A in MTEP17 | A | West | MPW | 13223 | 2018-09-28 | MPW-TT | 22596 | 2017-05-25 | CAP | 2023-06-01 | 633451 Isett 8 |  |  | 69 |  | 10 MVAR | Add additional 4 MVAR of 69 kV capacitors at MPW bus 633451 Isett 8 for a total of 10 MVAR | IA |  |  | Planned |  | Planning |  | N | N | N
A in MTEP17 | A | East | NIPS | 14264 | 2017-12-08 |  | 23299 | 2018-02-21 | SUB | 2020-06-01 | Munster |  |  | 345 |  |  | Reconfigure Munster substation (NIPS) to a ring bus | IN |  |  | Planned | 864000 |  |  | N | Y | N | Y
A in MTEP17 | A | East | NIPS | 14266 | 2017-12-08 |  | 23301 | 2018-02-21 | LNrc | 2020-06-01 | Michigan City | Bosserman |  | 138 |  |  | Reconductor Michigan City - Bosserman | IN |  |  | Planned | 600000 |  |  | N | Y | N | Y
A in MTEP17 | A | East | NIPS | 14267 | 2017-12-08 |  | 23302 | 2018-02-21 | SUBmisc | 2020-06-01 | Reynolds |  |  | 138 |  |  | Replace switches | IN |  |  | Planned | 70800 |  |  | N | Y | N | Y
A in MTEP17 | A | East | NIPS | 14268 | 2017-12-08 |  | 23303 | 2018-02-21 | LNrc | 2020-06-01 | Roxana | Praxair |  | 138 |  |  | Reconductor Roxana - Praxair | IN |  |  | Planned | 4636000 |  |  | N | Y | N | Y
A in MTEP17 | A | West | OTP | 12923 | 2018-06-29 |  | 22546 | 2018-06-29 | INT | 2018-12-31 | Big Stone South 345 |  |  | 230 |  |  | The Transmission Owner Interconnection Upgrades will consist of a new 230 kV deadend structure, one 230 kV motor operated switch, three arrestors, control house equipment and grounding materials to accommodate the customer's new 230 kV radial line. | SD |  |  | Planned | 0 | Planning |  | N | N | N
A in MTEP17 | A | West | OTP | 12923 | 2018-06-29 |  | 22547 | 2018-06-29 | SUB | 2018-12-31 | Big Stone South 345 |  |  | 230 |  |  | The Transmission Owner Network Upgrades consists of expanding the 230 kV bay with new bus work, breakers, switches, along with the necessary protection and controls. | SD |  |  | Planned | 0 | Planning |  | N | N | N
A in MTEP17 | A | West | OTP | 13043 | 2018-06-29 | OTP | 22559 | 2018-06-29 | CAP | 2019-11-30 | Donaldson 115 kV |  |  | 115 |  |  | Install capacitor banks on 115 kV at Donaldson 2x15 MVAR | MN |  |  | Planned | 975000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | West | OTP | 13344 | 2018-06-29 | 13344 | 22611 | 2018-06-29 | INT | 2018-09-01 | Red Lake Falls SW 41.6 kV | Gentilly 41.6 kV |  | 41.6 |  |  | Transmission Owner interconnection upgrades consist of GOVB switch, laminated wood structure, grading structure, and communication equipment. | MN |  |  | Planned | 0 | Planning |  | N | N | N
A in MTEP17 | A | West | OTP | 13344 | 2018-06-29 | 13344 | 22613 | 2018-06-29 | SUB | 2018-09-01 | Crookston 115/41.6 kV |  |  | 115 | 41.6 |  | Transmission Owner network upgrades consist of modifying protection with a new relay at the Crookston 115/41.6 kV substation. | MN |  |  | Planned | 10000 | Planning |  | N | N | N
A in MTEP17 | A | West | OTP | 13344 | 2018-06-29 | 13344 | 22612 | 2018-06-29 | SUB | 2018-09-01 | Plummer 115/41.6 kV |  |  | 115 | 41.6 |  | Transmission Owner network upgrades consist of modifying protection with a new relay, a lockout and associated test switches, two new 115kV single phase CCVTs, and cables at the Plummer 115/41.6 kV substation. | MN |  |  | Planned | 62630 | Planning |  | N | N | N
A in MTEP17 | A | Central | PPI | 11976 | 2017-12-08 | 1 | 21947 | 2018-06-22 | SUB | 2019-06-01 | Grand Island 138 | Grand Island 69 | 1 | 138 | 69 | 84 | 84 MVA 138/69 kV transformer. | IL | 0 | 0 | Under Construction | 4625000 | Planning |  | N | N | N
A in MTEP17 | A | Central | PPI | 11976 | 2017-12-08 | 1 | 21986 | 2018-03-22 | LN | 2019-06-01 | Grand Island 138 | Grand Island Ameren | 1 | 138 |  | 229 | Build short line tying PPI sub to Ameren sub. | IL | 0 | 0.1 | M3_Long Lead Materials | 110000 | Planning |  | N | N | N
A in MTEP17 | A | Central | PPI | 11976 | 2017-12-08 | 1 | 21950 | 2018-03-22 | Dist | 2019-12-31 | Kilbourne 69/12.47 kV Substation |  |  | 69 | 12.47 | 7.5 | Build Kilbourne 69/12.47 kV 7.5 MVA substation. | IL | 0 | 0 | Planned | 12000000 | Planning |  | N | N | N
A in MTEP17 | A | Central | PPI | 11976 | 2017-12-08 | 1 | 21949 | 2018-03-22 | LN | 2019-12-31 | Poplar City 69 kV | Kilbourne 69 kV | 1 | 69 |  |  | Build approximately 9.0 miles of 69 kV line with 336.4 MCM ACSR conductor. | IL | 0 | 9 | Planned | 4620000 | Planning |  | N | N | N
A in MTEP17 | A | Central | PPI | 11976 | 2017-12-08 | 1 | 21948 | 2018-03-22 | LNrb | 2019-06-01 | Grand Island 69 kV | Poplar City 69 kV | 1 | 69 |  | 50 | Rebuild approximately 2 miles of 69 kV line with 336.4 MCM ACSR conductor. | IL | 2 | 0 | Planned | 800000 | Planning |  | N | N | N
A in MTEP17 | A | Central | PPI | 12844 | 2018-09-17 |  | 22537 | 2018-09-17 | Dist | 2020-12-31 | Mechanicsburg 69/12.47 Substation |  |  | 69 | 12.47 | 7.5 | New distribution substation consisting of a 7.5 MVA transformer | IL | 0 | 0 | Planned | 1200000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | PPI | 12844 | 2018-09-17 |  | 22538 | 2018-09-17 | LN | 2020-12-31 | E. Lanesville 69 kV Substation | Mechanicsburg 69/12.47 kV Substation | 1 | 69 |  |  | New 69 kV line to Mechanicsburg | IL | 0 | 9.23 | Planned | 4625000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | PPI | 12845 | 2017-12-08 |  | 22539 | 2017-02-14 | Dist | 2025-12-31 | Williams 69/12.47 kV Substation |  |  | 69 | 12.47 | 7.5 | New distribution substation consisting of a 7.5 MVA transformer. | IL | 0 | 0 | Conceptual | 1200000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | Central | PPI | 12845 | 2017-12-08 |  | 22540 | 2017-02-14 | LN | 2025-12-31 | Athens 69 kV Substation | Williams 69 kV Substation | 1 | 69 |  |  | New 69 kV line to Williams Substation | IL | 0 | 7.9 | Conceptual | 4000000 | Planning Preliminary |  | N | N | N
A in MTEP17 | A | South | SMEPA | 12209 | 2018-08-27 |  | 22358 | 2018-09-27 | LNrb | 2018-11-01 | Cole Road | W. Hattiesburg |  | 69 |  |  | Rebuild Line 80A (Cole Rd – Breland GOAB) as a double circuit 69kV line and rebuild Line 40A (Breland GOAB – W. Hattiesburg S.S.) using 795 ACSR conductor. | MS |  |  | Under Construction | 648100 |  |  | N | N | N
A in MTEP17 | A | South | SMEPA | 12209 | 2018-08-27 |  | 22359 | 2018-09-27 | LNrl | 2018-11-01 | Rawls Springs | Cole Road |  | 69 |  |  | Loop Line 40 (Rawls Springs to Breland GOAB) into Cole Road substation. | MS |  |  | Under Construction | 794400 |  |  | N | N | N
A in MTEP17 | A | South | SMEPA | 12213 | 2017-12-08 |  | 22355 | 2017-01-20 | SUB | 2021-01-01 | Morrow | Oak Grove |  | 161 | 69 |  | A 161kV source will be established at the Oak Grove substation by rebuilding approximately 2.5 miles of SMEPA’s existing de-energized 161kV Line 170 (Morrow to Purvis Bulk) and building approximately 0.5 miles of new transmission line to the substation site. A breakered 161/69kV substation will be constructed with a single 112MVA, 161/69kV transformer. SMEPA’s existing 69kV Lines 39, 39B and 91 will be routed into the 161/69kV substation utilizing the same transmission right-of-way corridor. | MS |  |  | Proposed | 6991000 |  |  | N | N | N
A in MTEP17 | A | South | SMEPA | 12214 | 2018-08-27 |  | 22350 | 2018-09-27 | Dist | 2018-11-01 | Cole Road |  |  | 69 |  |  | The new delivery point is adjacent to SMEPA’s Cole Road substation and will require adding a 69kV bay and breaker to SMEPA’s existing Cole Road substation. A short 69kV service feed will be constructed to the new delivery point. | MS |  |  | M4_Pre-Construction | 540000 |  |  | N | N | N
A in MTEP17 | A | Central | Vectren | 9950 | 2017-12-08 | 2016SIGE15 | 21397 | 2018-09-13 | LNrb | 2018-10-31 | New Harmony | Northwest | Y76 | 69 |  |  | Rebuild of 19 miles of Y76 69kV line from New Harmony sub to Northwest sub | IN |  |  | M4_Pre-Construction | 9250000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | Vectren | 11844 | 2017-12-08 | 2017SIGE06 | 21837 | 2018-03-29 | LNrc | 2022-12-31 | Mead Johnson |  |  | 69 |  |  | 69kV Y32 line re-conductor (0.9 miles) from Mead Johnson Park substation to Mead Johnson Tap | IN |  |  | M2a_Pre-Project Approval | 485000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | Vectren | 11845 | 2017-12-08 | 2018SIGE07 | 21838 | 2018-03-29 | SUB | 2018-09-28 | Culley 138 |  |  | 138 |  |  | Replace four oil breakers with gas breakers at Culley 138kV substation in 2018. | IN |  |  | M4_Pre-Construction | 950000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | Vectren | 11848 | 2017-12-08 | 2018SIGE10 | 21841 | 2018-03-29 | TAP | 2021-12-31 | Perry Township |  |  | 69 |  |  | 69kV line Y32 Loop for Perry Twp Sub and Perry Twp Sub Modifications | IN |  |  | M1_Final SPM or OOC | 3600000 | Budgetary |  | N | N | N
A in MTEP17 | A | Central | Vectren | 11850 | 2017-12-08 | 2018SIGE12 | 21843 | 2018-09-13 | LNrb | 2019-12-31 | Winslow 69kV |  |  | 69 |  |  | Y36 Winslow Rebuild | IN |  |  | Planned | 2000000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 8362 | 2017-12-08 | CV-WC Rebuild | 20651 | 2015-09-15 | LNrb | 2019-12-31 | Casnovia | White Cloud |  | 69 |  |  | This 69kV transmission line segment was built in 1963. This line segment has 67% condemned, rotten tops, or damaged structures. This rebuild is necessary due to the age of the line and poles. Because there are so many poles in need of replacing, it is cost-effective to demolish the existing line and rebuild to our new standard configuration | MI | 22.85 |  | Proposed | 11500000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 8363 | 2017-12-08 | VB-CF rebuild | 20652 | 2015-09-15 | LNrb | 2019-12-31 | Vestaburg | Crawford |  | 69 |  |  | This 69kV transmission line segment was built in 1973. This line segment has 58% condemned, rotten tops, or damaged structures. This rebuild is necessary due to the age of the line and poles. Because there are so many poles in need of replacing, it is cost-effective to demolish the existing line and rebuild to our new standard configuration. | MI | 9 |  | Proposed | 4500000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 9903 | 2017-12-08 | WC-RG Rebuild | 21309 | 2015-09-15 | LNrb | 2020-12-31 | White Cloud | Wrights Creek | 1 | 69 |  | 143.4 | Rebuild the White Cloud to Rogers 69kV line, install new poles and hardware with 795ACSS conductor | MI | 14.36 |  | Proposed | 7200000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 9903 | 2017-12-08 | WC-RG Rebuild | 21312 | 2016-09-15 | LNrb | 2020-12-31 | Hesperia | Rogers | 1 | 69 |  |  | Rebuild the White Cloud to Rogers 69kV line, install new poles and hardware with 795ACSS conductor | MI | 13.96 |  | Proposed | 7200000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 9903 | 2017-12-08 | WC-RG Rebuild | 21310 | 2016-09-15 | LNrb | 2020-12-31 | Wrights Creek | Hesperia | 1 | 69 |  |  | Rebuild the White Cloud to Rogers 69kV line, install new poles and hardware with 795ACSS conductor | MI | 7.68 |  | Proposed | 4100000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 10266 | 2017-12-08 |  | 21509 | 2016-09-15 | SwSta | 2019-12-31 | East Jordan |  |  | 69 |  |  | East Jordan Station Rebuild | MI |  |  | Planned | 350000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12195 | 2017-12-08 | 2018 Battery Replacement Project | 22316 | 2016-09-15 | SwSta | 2018-12-31 | Unknown |  |  | 69 |  |  | This project replaces battery banks and chargers that have reached the end of their useful life | MI |  |  | Planned | 70000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12196 | 2017-12-08 | 2019 Battery Bank Replacement Project | 22318 | 2016-09-15 | SwSta | 2019-12-31 | Unknown |  |  | 69 |  |  | This project replaces battery banks and chargers that have reached the end of their useful life | MI |  |  | Planned | 35000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12216 | 2017-12-08 | Cadillac to Hersey OPGW | 22343 | 2016-09-15 | COM | 2018-12-31 | Cadillac | Hersey |  | 138 |  |  | Install OPGW | MI | 35 |  | Planned | 2300000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12221 | 2017-12-08 |  | 22351 | 2016-09-15 | LNrb | 2018-12-31 | Leroay | Tustin |  | 69 |  |  | Rebuild line | MI | 7.67 |  | Planned | 4000000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12223 | 2017-12-08 | Leroy to Hartwick Rebuild | 22352 | 2016-09-15 | LNrb | 2019-12-31 | Leroy | Hartwick |  | 138 |  |  | Rebuild Line | MI | 9.7 |  | Planned | 5000000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12224 | 2017-12-08 | Lemon Junction to Silver Lake Rebuild | 22354 | 2016-09-15 | LNrb | 2020-12-31 | Lemon Junction | Silver Lake |  | 138 |  |  | Rebuild line | MI | 6.3 |  | Proposed | 3300000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 12285 | 2017-12-08 | Altona to Vestaburg Rebuild | 22382 | 2016-09-27 | LNrb | 2018-12-31 | Altona | Vestaburg |  | 69 |  |  | Line Rebuild | MI | 19.5 |  | Proposed | 10000000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 13163 | 2017-12-08 |  | 22587 | 2017-04-20 | TAP | 2018-03-01 | Iron Works |  |  | 138 |  |  | Install in-and-out loop through 138kV bus to provide interconnection service to new industrial customer. | MI |  |  | Planned | 950000 | Budgetary |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22657 | 2017-08-25 | LN | 2018-12-31 | Lake County |  |  | 138 |  |  | Modify line connections into Lake County station | MI | 0 |  | Proposed | 500000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22676 | 2017-08-25 | TAP | 2020-12-31 | Shelby |  |  | 138 |  |  | Upgrade switches to 138kV | MI |  |  | Proposed | 200000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22675 | 2017-08-25 | SwSta | 2020-12-31 | Lemon Junction |  |  | 138 |  |  | Construct new 138kV station | MI |  |  | Proposed | 800000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22674 | 2017-08-25 | LNrc | 2020-12-31 | Rogers | Redwood |  | 138 |  |  | Reconductor existing line to 795ACSS | MI | 8.75 |  | Proposed | 800000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22673 | 2017-08-25 | SwSta | 2020-12-31 | Rogers |  |  | 138 |  |  | Construct new 138KV Rogers station | MI |  |  | Planned | 800000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22672 | 2017-08-25 | LNrb | 2019-12-31 | Newaygo | Brooks |  | 138 |  |  | Rebuild line to 138kV design | MI | 3.2 |  | Proposed | 1500000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22671 | 2017-08-25 | LNrb | 2019-12-31 | Casnovia | Sternberg |  | 138 |  |  | Rebuild the line to 138kV design, 795ACSS conductor and OPGW | MI | 19.4 |  | Planned | 10000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22670 | 2017-08-25 | SUB | 2019-12-31 | Casnovia |  |  | 138 |  |  | Construct new Casnovia 138/69kV station | MI |  |  | Proposed | 6000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22669 | 2017-08-25 | SwSta | 2019-12-31 | White Cloud |  |  | 138 |  |  | Construct a new 138KV ring bus station | MI |  |  | Proposed | 3000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22668 | 2017-08-25 | LNrb | 2019-12-31 | Paris Junction | Paris |  | 138 |  |  | Rebuild the Paris Junction to Paris line to 138kV design | MI | 1.26 |  | Proposed | 600000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22667 | 2017-08-25 | LNrb | 2019-12-31 | Brohman Junction | Brohman |  | 138 |  |  | Rebuild the Brohman Junction to Brohman line to 138KV design | MI | 1.34 |  | Proposed | 625000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22666 | 2017-08-25 | LNrb | 2019-12-31 | Hersey | White Cloud |  | 138 |  |  | Rebuild line to 138kV design with 795ACSS and OPGW | MI | 26 |  | Proposed | 13000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22665 | 2018-06-08 | LNrb | 2018-12-31 | Lake County | Pere Marquette | 1 | 138 |  |  | Rebuild the Lake County to Pere Marquette line to 795ACSS conductor with OPGW | MI | 18.5 |  | Proposed | 10900000 |  |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22664 | 2017-08-25 | LNrl | 2018-12-31 | Hersey |  |  | 138 |  |  | Relocate lines at the existing Hersey facility into new bus | MI |  |  | Proposed | 500000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22663 | 2017-08-25 | LNrb | 2018-12-31 | Hersey | Lincoln Junction | 1 | 69 |  |  | Install 2nd circuit on existing poles from Hersey to Lincoln Junction | MI | 3.29 |  | Proposed | 800000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22662 | 2017-08-25 | SUB | 2018-12-31 | Hersey |  |  | 138 |  |  | Upgrade the Hersey station to add a 138kV bus and install a 138/69kV transformer. | MI |  |  | Proposed | 4000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22661 | 2017-08-25 | TAP | 2018-12-31 | Baldwin |  |  | 138 |  |  | Install 138kV switches | MI |  |  | Proposed | 200000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22660 | 2017-08-25 | LNrb | 2018-12-31 | Plains Junction | Hart | 1 | 138 |  |  | Rebuild the Plains Junction to Hart line to 138KV design, 795ACSS conductor with OPGW | MI | 22 |  | Proposed | 11000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22659 | 2017-08-25 | SwSta | 2018-12-31 | Plains Junction |  |  | 138 |  |  | Construct a new 138kV ring bus station to replace the existing Plains Junction station | MI |  |  | Proposed | 3000000 | Planning |  | N | N | N
A in MTEP17 | A | East | WPSC | 13574 | 2017-12-08 |  | 22658 | 2017-08-25 | TAP | 2018-12-31 | Star Lake |  |  | 138 |  |  | Upgrade switches to 138KV | MI |  |  | Proposed | 200000 | Planning |  | N | N | N
A in MTEP17 | A | West | XEL | 4695 | 2017-12-08 |  | 8879 | 2018-09-28 | TEQ | 2021-06-01 | Wilson |  |  | 115 |  |  | Rebuild Wilson Straight bus into a breaker and a half scheme | MN |  |  | Planned | 17000000 |  |  | N | N | N | Y
A in MTEP17 | A | West | XEL | 11644 | 2017-12-08 |  | 21804 | 2018-06-28 | LNup | 2018-10-01 | Wilmarth | Swan Lake | 1 | 115 |  | 150.7 | The Mankato Energy Center expansion, identified as G261, is causing the existing 115 kV line between Wilmarth and Swan Lake to overload. This was identified in the G261 Facilities Study as needing a 150 MVA rating. To achieve the necessary rating, Xcel Energy will mitigate clearance issues on this line. The new line rating will be 150.7 MVA. | MN |  |  | Under Construction | 500000 |  |  | N | N | N
A in MTEP17 | A | West | XEL | 11987 | 2017-12-08 |  | 21962 | 2018-07-05 | CB | 2018-12-20 | French Island |  |  | 69 |  |  | Replace breakers identified in overstressed breaker study in French Island substation | WI |  |  | Planned | 375000 | Planning |  | N | N | N
A in MTEP17 | A | West | XEL | 11993 | 2017-12-08 |  | 21969 | 2018-09-28 | TEQ | 2019-12-01 | Black Dog |  |  | 115 |  |  | Replace equipment at Black Dog substation to allow an uprate of the existing Black Dog-Wilson #1 and Black Dog-Wilson #3 115 kV lines. | MN |  |  | Planned | 5383000 | Planning |  | N | N | N
A in MTEP17 | A | West | XEL | 12007 | 2017-12-08 |  | 22066 | 2017-02-21 | Dist | 2019-06-01 | Farmers Inn |  |  | 69 | 12.5 |  | Installing a 2nd 69/12.47 kV transformer and 1 new feeder at Farmers Inn | WI |  |  | Planned | 1100000 |  |  | N | N | N
A in MTEP17 | A | West | XEL | 12008 | 2017-12-08 |  | 22080 | 2018-09-28 | Dist | 2018-11-15 | Griffin Street |  |  | 69 | 12.5 |  | Installing a 2nd 69/12.47 kV transformer and 2 new feeders at Griffin Street | WI |  |  | Under Construction | 330000 |  |  | N | N | N
A in MTEP17 | A | West | XEL | 12009 | 2017-12-08 |  | 22081 | 2018-06-27 | SUB | 2018-12-31 | Ironwood |  |  | 115 |  |  | Installing a 115 kV bus tie breaker at Ironwood to separate the two 115 kV lines and two 115/34.5 kV transformers | MI |  |  | Planned | 2670482 |  |  | N | N | N
A in MTEP17 | A | West | XEL | 12013 | 2017-12-08 |  | 22085 | 2018-09-28 | Dist | 2018-12-15 | Nordic |  |  | 115 | 12.5 |  | Install a third Distribution Transformer to accommodate increasing demand in the area | ND |  |  | Planned | 400000 |  |  | N | N | N
A in MTEP17 | A | West | XEL | 12623 | 2017-12-08 |  | 22531 | 2018-06-28 | TX | 2018-12-15 | Chanarambie |  |  | 115 | 34.5 | 120 | Expand Chanarambie substation to accommodate transformer #3, bus tie breaker, and 34.5 kV feeders. This project is required as part of J426 wind farm generation interconnection. | MN |  |  | Under Construction | 5250000 | Planning |  | N | N | N
A in MTEP16 | A | South | AECC | 9663 | 2017-01-09 |  | 20988 | 2018-08-22 | SUB | 2020-04-01 | Newport East |  |  | 161 | 13.2 |  | Construct 20 MVA, 161/13.2 kV substation. | AR |  |  | Planned | 500000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | South | AECC | 10204 | 2018-08-22 |  | 21491 | 2018-08-22 | SUB | 2018-12-31 | Hunter North 161/13.2kV Substation |  |  | 161 |  |  | 161/13.2kV Hunter North substation | AR |  |  | Proposed | 500000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | South | AECC | 10206 | 2017-01-09 |  | 21495 | 2016-05-06 | SwSta | 2020-12-01 | Clinton West |  |  | 161 |  |  | 5 position ring bus | AR |  |  | Proposed | 5000000 |  |  | N | N | N
A in MTEP16 | A | South | AECC | 10206 | 2017-01-09 |  | 21497 | 2016-05-06 | SUB | 2020-12-01 | Partain |  |  | 161 | 69 | 100MVA | build 3 position ring bus and 100MVA 161/69kV stepdown station with 2 69kV breakers | AR |  |  | Proposed | 4000000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | South | AECC | 10206 | 2017-01-09 |  | 21496 | 2016-05-06 | LN | 2020-12-01 | Clinton West | Partain |  | 161 |  |  | 14.0 mile line from the existing Clinton West to the proposed Partain substation | AR |  |  | Proposed | 18000000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | Central | AmerenIL | 9726 | 2017-01-09 |  | 21110 | 2018-09-28 | SUB | 2021-06-01 | Fogarty |  |  | 138 | 34.5 | 112 | Provide 138 kV connection to supply 138-34.5 kV transformer. | IL |  |  | Planned | 1900000 | Planning |  | N | N | N
A in MTEP16 | A | Central | AmerenIL | 9727 | 2017-01-09 |  | 21111 | 2018-01-05 | SUB | 2021-12-01 | Wakefield |  |  | 138 | 34.5 | 112 | Establish 138 kV ring bus; connect ot South Bloomington-Clinton-1372 line. | IL |  |  | Proposed | 7360755 | Planning |  | N | N | N
A in MTEP16 | A | Central | AmerenIL | 9853 | 2018-09-28 |  | 21230 | 2018-09-28 | TEQ | 2040-06-01 | Prairie State | Mt. Vernon, West | 1 | 345 | 345 | 1401 | Upgrade terminal equipment at Mt. Vernon, West | IL |  |  | Proposed |  |  |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20011 | 2018-06-29 | LNrb | 2019-12-31 | Lone Rock | Richland | 1 | 69 |  |  | Rebuild Y-78 Lone Rock - Richmond 69 kV | WI | 11.28 |  | Under Construction | 32400000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20017 | 2018-06-29 | LNrb | 2019-12-31 | Blue River Tap | Boscobel | 1 | 69 |  | 79 | Rebuild Y-124 Blue River Tap - Boscobel 69 kV | WI | 6.1 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20016 | 2018-06-29 | LNrb | 2019-12-31 | Muscoda | Blue River Tap | 1 | 69 |  | 79 | Rebuild Y-124 Muscoda - Blue River Tap 69 kV | WI | 8.9 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20015 | 2018-06-29 | LNrb | 2019-12-31 | Avoca Tap | Muscoda Ind. Park | 1 | 69 |  | 79 | Rebuild Y-124 Avoca Tap - Muscoda Ind. Park 69 kV | WI | 4.32 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20014 | 2018-06-29 | LNrb | 2019-12-31 | Muscoda Ind. Park | Muscoda | 1 | 69 |  | 79 | Rebuild Y-124 Muscoda Ind. Park - Muscoda 69 kV | WI | 0.33 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20013 | 2018-06-29 | LNrb | 2019-12-31 | Avoca Tap | Avoca | 1 | 69 |  | 79 | Rebuild Y-124 Avoca Tap - Avoca 69 KV | WI | 0.87 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7583 | 2017-01-09 | PR04985 | 20012 | 2018-06-29 | LNrb | 2019-12-31 | Lone Rock | Avoca Tap | 1 | 69 |  | 79 | Rebuild Y-124 Lone Rock - Avoca Tap 69 kV | WI | 7.93 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP16 | A | West | ATC | 7986 | 2017-01-13 | PR05253 | 20256 | 2018-03-30 | CB | 2019-04-01 | Highway V |  |  | 138 |  |  | Install high side breakers on both Highway V transformers. | WI |  |  | Planned | 9000000 | Planning |  | N | N | N
A in MTEP16 | A | West | ATC | 8640 | 2017-01-09 |  | 20710 | 2018-03-30 | BUS | 2018-12-20 | City Limits |  | 1 | 138 |  | 332 | Replace bus conductor at City Limits bus 1-2 with 2500 kcmil Lupine | WI |  |  | Under Construction | 300000 | Planning |  | N | N | N
A in MTEP16 | A | West | ATC | 8640 | 2017-01-09 |  | 20711 | 2017-03-31 | BUS | 2018-12-20 | City Limits |  | 2 | 138 |  | 484 | Replace bus conductor at City Limits bus 2-3 with 2500 kcmil Lupine | WI |  |  | Proposed |  | Planning |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20752 | 2018-09-28 | LNrb | 2020-03-31 | Finger Rd | Luxemburg | 1 | 69 |  | 39 | Rebuild J-10 Finger Road 69 - Luxemburg 69 with T2 4/0 ACSR | WI | 12.49 |  | M1_Final SPM or OOC | 13191000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20758 | 2018-09-28 | LNrb | 2020-03-31 | Canal | Algoma | 1 | 69 |  | 39 | Rebuild J-10 Canal 69 - Algoma 69 with 4/0 T2 ACSR. | WI | 18.73 |  | M1_Final SPM or OOC | 22678000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20757 | 2018-09-28 | LNrb | 2020-03-31 | Algoma | Algoma | 1 | 69 |  | 39 | Rebuild J-10 Algoma 69 - Algoma S Tap 69 with 4/0 T2 ACSR. | WI | 1.74 |  | M1_Final SPM or OOC | 2980000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20756 | 2018-09-28 | LNrb | 2020-03-31 | Algoma | Barnett | 1 | 69 |  | 46 | Rebuild J-10 Algoma S Tap 69 - Barnett 69 with 4/0 T2 ACSR. | WI | 7.01 |  | M1_Final SPM or OOC | 7235000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20755 | 2018-09-28 | LNrb | 2020-03-31 | Barnett | Beardsley | 1 | 69 |  | 46 | Rebuild J-10 Barnett 69 - Beardsley 69 with 4/0 T2 ACSR. | WI | 3.32 |  | M1_Final SPM or OOC | 3477000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20754 | 2018-09-28 | LNrb | 2020-03-31 | Booster | Beardsley | 1 | 69 |  | 46 | Rebuild J-10 Booster 69 - Beardsley 69 with 4/0 T2 ACSR. | WI | 5.51 |  | M1_Final SPM or OOC | 5671000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 8841 | 2017-01-09 | PR04988 | 20753 | 2018-09-28 | LNrb | 2020-03-31 | Luxemburg | Booster | 1 | 69 |  | 46 | Rebuild J-10 Luxemburg 69 - Booster 69 with 4/0 T2 ACSR. | WI | 6.23 |  | M1_Final SPM or OOC | 5485000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 9923 | 2017-01-09 |  | 21335 | 2018-03-30 | SUB | 2018-12-30 | Mukwonago |  |  | 138 |  |  | Install line breaker on line 67K61. | WI |  |  | Under Construction | 900000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 9934 | 2017-01-09 | PR07285 | 21349 | 2018-09-27 | LNup | 2019-04-15 | Oak Creek | Hayes | 1 | 138 |  | 310 | Oak Creek - Hayes 138-kV line 811 upgrade and reconfiguration. | WI |  |  | Under Construction | 18000000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 9954 | 2017-01-09 | PR07375 | 21369 | 2017-10-02 | TX | 2019-09-27 | Lost Dauphin |  |  | 138 |  |  | Replace Lost Dauphin T1 Transformer. | WI |  |  | Planned | 6700000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 9961 | 2017-01-09 |  | 21372 | 2018-06-29 | TX | 2019-12-01 | Nelson Dewey |  |  | 138 |  |  | Replace Nelson Dewey T31/T32 Transformers. | WI |  |  | M1_Final SPM or OOC | 5375625 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 9977 | 2017-01-09 |  | 21394 | 2018-06-29 | LNrb | 2020-06-30 | Goodman | Caldron Falls | 1 | 69 |  |  | Rebuild 69KV Line J-88 Goodman - Caldron Falls Substation. | WI |  |  | M1_Final SPM or OOC | 28225000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 9986 | 2017-01-09 | PR07410, 602097,602099 | 21408 | 2018-09-28 | LNrb | 2021-05-31 | Port Washington | Saukville | 1 | 138 |  | 321 | Rebuild 138KV Line 762 Port Washington - Saukville Substation. | WI |  |  | Under Construction | 21000000 |  |  | N | N | N | Y
A in MTEP16 | A | West | ATC | 10484 | 2017-01-09 | PR07373 | 21588 | 2018-04-24 | LN | 2023-12-01 | HWY V | Eaton | 1 | 138 |  | 690 | Construct a new ATC 138KV loop through at Eaton Substation. | WI | 6.54 |  | Planned | 2500000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10484 | 2017-01-09 | PR07373 | 21590 | 2018-04-24 | SUB | 2023-12-01 | Eaton |  |  | 138 | 24.9 |  | New Eaton 138 KV substation | WI |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10484 | 2017-01-09 | PR07373 | 21589 | 2018-04-24 | LN | 2023-12-01 | Eaton | East Krok | 1 | 138 |  |  | Construct a new ATC 138KV loop through at Eaton Substation. | WI | 14.92 |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10485 | 2017-01-09 | PR007372 | 21591 | 2018-03-30 | LN | 2022-06-01 | HWY V | BAY RIDGE | 1 | 138 |  | 526 | Construct a new ATC 138KV loop through at Bay Ridge Substation. | WI | 1.06 |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10485 | 2017-01-09 | PR007372 | 21593 | 2018-06-29 | SUB | 2022-06-01 | BAYRIDGE |  |  | 138 | 24.9 |  | Construct a new ATC 138KV loop through at Bay Ridge Substation. | WI |  |  | M1_Final SPM or OOC | 2122335 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10485 | 2017-01-09 | PR007372 | 21592 | 2018-03-30 | LN | 2022-06-01 | BAY RIDGE | ONTARIO | 1 | 138 |  |  | Construct a new ATC 138KV loop through at Bay Ridge Substation. | WI | 1.61 |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10603 | 2017-01-09 | PR07299 | 21623 | 2018-03-30 | LN | 2018-08-31 | Wild Rose | Springwater | 1 | 69 |  | 660 | Construct T - D Springwater Substation. | WI |  | 1.25 | Planned | 3800000 |  |  | N | N | N
A in MTEP16 | A | West | ATC | 10686 | 2017-01-09 | PR07392 | 21646 | 2018-06-29 | BUS | 2021-06-01 | Roosevelt Road |  |  | 138 |  | 1391 | ATC bus expansion and T-D distribution transformer addition. | WI |  |  | M1_Final SPM or OOC | 1102365 |  |  | N | N | N
A in MTEP16 | A | West | CFU-PMEU | 11383 | 2017-01-09 | Pella RRHD | 21764 | 2016-06-15 | CAP | 2017-08-01 | Pella West sub | Pella Clark St. sub | na | 69 |  |  | Move the capacitor from the Pella West Sub to Pella Clark St. Sub to make room for J329 interconnection at Pella West. | IA |  |  | Under Construction | 169250 | GIA |  | N | N | N
A in MTEP16 | A | West | CFU-PMEU | 11383 | 2017-01-09 | Pella RRHD | 21767 | 2016-06-15 | RLY | 2017-08-01 | Pella West Substation |  |  | 69 |  |  | Line relaying for G329 including relaying changes for capacitor bank move to Pella clark st sub. | IA |  |  | Proposed | 74400 | GIA |  | N | N | N
A in MTEP16 | A | West | CFU-PMEU | 11383 | 2017-01-09 | Pella RRHD | 21766 | 2016-06-15 | TEQ | 2017-08-01 | Pella West Substation |  |  | 69 |  |  | Terminal for J329 69kV line into the Pella West substation. | IA |  |  | Under Construction | 800050 | GIA |  | N | N | N
A in MTEP16 | A | Central | DEI | 2873 | 2017-01-09 | DIN0216 | 5026 | 2018-09-27 | Dist | 2018-12-31 | Danville East | new dist sub | 1 | 69 | 12 |  | Construct new Danville East substation near HRH hospital - single 22.4MVA transformer - 6945 ckt to be looped through | IN |  | 0.5 | Under Construction | 1040000 | Planning |  | N | N | N | NT
A in MTEP16 | A | Central | DEI | 9834 | 2018-07-11 | AMIN1055 | 21211 | 2018-07-11 | LNrb | 2020-12-31 | Noblesville Gen Station | Tipton West | 1 | 230 |  | 501 | Noblesville to Tipton West 23008 ckt: Replace all single/H-frame pole structures with steel poles, reconductor with 954ACSR45X7 OVAL / OPGW and build Switching Station with 3-2000A line switches near existing Carmel 146th St. junction. | IN | 12 |  | M3_Long Lead Materials | 3000000 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9855 | 2017-01-09 | TIN1422 | 21232 | 2017-03-08 | CB | 2020-12-31 | Columbus North |  |  | 230 | 69 |  | Columbus North: Replace OCB 6975, 6929, 69230-1, 6950 and obsolete relays on CIR 6929, 6950, 6975, 6982. Also replace relays on CIR 23019. | IN |  |  | M1_Final SPM or OOC | 2711016 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9858 | 2017-01-09 | TIN1469 | 21238 | 2018-09-27 | TX | 2018-12-31 | Bedford 345kV |  |  | 345 | 138 | 400 | Bedford 345: Replace 345/138kV Bank 7 | IN |  |  | Under Construction | 4151661 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9858 | 2017-01-09 | TIN1469 | 21239 | 2018-09-27 | CB | 2018-12-31 | Bedford 345kV |  |  | 345 | 69 |  | Bedford 345: Replace relays on CIR 6995, 13829, 13837, 34506, 34521. Replace all 69kV and 138kV Oil Circuit Breakers. | IN |  |  | Under Construction | 7927152 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9888 | 2017-01-09 | TIN1528 | 21275 | 2017-06-02 | LNrb | 2020-12-31 | Middlefork | Deer Crk. Jct. | 1 | 69 |  | 100 | Rebuild 6988 ckt. from MiddleFork sub to deadend 879/1041-01 and from Deer Cr Jct to 879/1046. 477acsr@120C w/ OPGW - 187 wood poles to be replaced with light duty steel. | IN | 7.1 |  | M3_Long Lead Materials | 4860632 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9889 | 2017-01-09 | TIN1530 | 21277 | 2018-06-28 | LNrb | 2018-08-01 | Sharpsville | Kokomo Southeast |  | 69 |  | 100 | Rebuild 69174 ckt. from Sharpsville sub to Kokomo SE. 477acsr@120C w/ OPGW - 174 wood poles to be replaced with light duty steel. | IN | 7.3 |  | Under Construction | 4287945 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9890 | 2017-01-09 | TIN1536 | 21278 | 2017-03-08 | LNup | 2020-12-31 | Gibson Gen. Sta. | HE Merom Gen. Sta. |  | 345 |  |  | Gibson to Merom: Install (10) double deadend structures in the 34511 ckt. | IN |  |  | M1_Final SPM or OOC | 4433734 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9891 | 2017-01-09 | TIN1534 | 21279 | 2017-02-09 | LNup | 2020-12-31 | Flat Rock | Hope Jct. |  | 69 |  |  | Flat Rock to Hope Jct. 6975 ckt. pole replacements (45), replace line switches at both ends. Transfer existing conductor to new poles. | IN | 3.3 |  | M3_Long Lead Materials | 1087274 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9892 | 2017-01-09 | TIN1533 | 21280 | 2018-09-27 | LNup | 2018-12-31 | Lewis Crk. | Flat Rock |  | 69 |  |  | Lewis Crk. to Flat Rock 6975 ckt. pole replacements (100), replace line switches at Lewis Crk with 1200A. Transfer existing conductor to new poles. | IN | 5.7 |  | M4_Pre-Construction | 1875342 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9893 | 2017-01-09 | TIN1581 | 21281 | 2017-12-22 | CB | 2021-06-01 | Shelbyville Northeast |  |  | 138 | 69 |  | Shelbyville Northeast - Replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | IN |  |  | M1_Final SPM or OOC | 3511433 | Engineering w/AFUDC |  | N | N | N
A in MTEP16 | A | Central | DEI | 9897 | 2017-01-09 | DIN1393 | 21295 | 2017-03-08 | Dist | 2018-12-31 | River Ridge Gateway |  |  | 138 | 12 |  | River Ridge Gateway 138-12kV Sub. to be inserted in the 13857 ckt. between Clark Maritime and HE Northport | IN |  |  | M3_Long Lead Materials | 1141000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | Central | DEI | 9926 | 2017-01-09 | DIN1620 | 21338 | 2018-09-26 | Dist | 2019-12-31 | Spelterville |  |  | 138 | 34 |  | Spelterville: expand sub footprint, Install 138/34kV 60MVA Bank | IN |  |  | M3_Long Lead Materials | 1332000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | South | Entergy-AR | 4665 | 2017-01-09 | 12-EAI-019 | 8845 | 2018-09-18 | TX | 2019-06-30 | Mabelvale 500 kV Substation | Mabelvale 115 kV Substation | 1 | 500 | 115 | 598 | Replace transformer | AR |  |  | Under Construction | 23540744 | Planning |  | N | N | N | Y
A in MTEP16 | A | South | Entergy-AR | 4665 | 2017-01-09 | 12-EAI-019 | 8846 | 2018-09-18 | TX | 2019-06-30 | Mabelvale 500 kV Substation | Mabelvale 115 kV Substation | 2 | 500 | 115 | 598 | Replace transformer | AR |  |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP16 | A | South | Entergy-AR | 7942 | 2017-01-09 | 15-EAI-004 | 20193 | 2018-09-11 | LNrb | 2019-06-01 | Mayflower 115kV substation | Morgan 115kV substation | 1 | 115 |  | 390MVA | Rebuild 5 miles of 115kV line from Mayflower to Morgan. | AR | 5 |  | Under Construction | 5415875 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-AR | 9673 | 2017-01-09 | 16-EAI-002 | 20991 | 2018-09-18 | TX | 2019-06-30 | El Dorado EHV |  |  | 500 | 115 |  | 598 MVA - 500/115 kV autotransformer | AR |  |  | Planned | 14155715 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-AR | 9696 | 2017-01-09 | 16-AI-017 | 21020 | 2018-09-18 | SwSta | 2018-12-01 | Newport SS |  |  | 161 |  |  | Build a 4-breaker switching station near Newport Industrial and re-terminate the Newport-Swifton 161 kV line into the new switching station. Build a new 161 kV line between the Newport switching station and Newport Industrial to eliminate the voltage issue. | AR |  |  | Under Construction | 18233177 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-AR | 9698 | 2017-01-09 | 16-EAI-006 | 21022 | 2018-09-18 | LNrb | 2018-12-01 | El Dorado East 115kV | El Dorado Jackson 115kV |  | 115 |  |  | Re-build the 2.92 mile long 115 kV line to a minimum rating of 259 MVA (1300 Amps) to eliminate the thermal constraints | AR | 2.92 |  | Under Construction | 6614767 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-AR | 9704 | 2017-01-09 | 16-EAI-008 | 21035 | 2018-09-18 | SUB | 2018-12-31 | London North 161kV |  |  | 161 |  |  | Purchase substation Site with enough land for future second transformer. Install 1-40 MVA - 161/13.8 kV - LTC substation transformer and three (3) breaker bays. Construct the feeder bays for overhead exits. Install one 2000 amp / 15 kV main breaker and three 1200 amp / 15kV feeder breakers. Install SCADA and metering in accordance with Entergy standards. Build 300 feet of 795 AA for new circuit XXXX from substation north to Highway 64. Replace 1.4 miles of 3 phase #6 copper with 336 acsr from substation site west on Highway 64 to the town of London. Replace Recloser 7Y21with a 600 amp air break to be normally OPEN.. Build 500 feet of 795 for new circuit XXXX to tie in to 336 Acsr that travels south via Transmission Line to the ANO plant. Build 300 feet of 795 AA for new circuit XXXX from substation north to Highway 64 to tie into the existing 336 east toward Russellville North substation. Reconductor 0.8 mile of 336 Acssr with 795 AA from substation east on Highway 64 to Mill creek Road. Install 2-1200 amp Air breaks on Highway 64. Install 1200 amp getaway disconects on each feeder circuit. | AR |  |  | Under Construction | 6592341 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-AR | 9709 | 2018-01-03 | 16-EAI-012 | 21042 | 2018-09-18 | SUB | 2021-06-01 | Mabelvale 115kV |  |  | 115 |  |  | Reconfigure the Mabelvale 115 kV substation so that a single bus tie breaker failure will not open all the elements in the Mabelvale 115 kV substation. Some potential configurations are double bus double breaker, breaker and a half, and ring bus. The final configuration will be decided during project scoping. | AR |  |  | Planned | 11563954 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 7949 | 2017-01-09 | 15-EGL-010 | 20209 | 2018-09-26 | TX | 2019-03-10 | SOLAC 230 | SOLAC 69 | 1 | 230 | 69 | 300 | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. Each of the 138-69 kV Solac autotransformers will exceed their thermal rating during the single contingency (P1-3) transformer loss of one autotransformer on the other. This project will mitigate the thermal load violations on the two autotransformers by installing a third 138-69 kV Autotransformer at Solac." | LA |  |  | Planned | 17034225 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 7949 | 2017-01-09 | 15-EGL-010 | 21135 | 2017-12-27 | TX | 2019-03-10 | Solac 230 | Solac 69 | 2 | 230 | 69 | 300 | Upgrade AT2 | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 7950 | 2017-01-09 | 15-EGL-011 | 20210 | 2018-09-26 | LNrc | 2018-12-31 | 335235 East Broad 69 | 335237 Ford 69 | 1 | 69 |  | 143 MVA | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The East Broad to Ford 69 kV line will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Contraband to Solac 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor." | LA | 1.49 |  | Planned | 2946372 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 7952 | 2017-01-09 | 15-EGL-012 | 20212 | 2018-09-26 | LNrc | 2018-09-01 | 335239 SOLAC 69 | 335240 SOLAC 69 | 1 | 69 |  | 143 MVA | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Contraband to Solac 69 kV line will exceed its thermal rating during the single contingency (P2-1) open breaker at East Broad toward Ford 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading the line conductor." | LA | 2.26 |  | Planned | 9015967 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9686 | 2017-01-09 | 16-ELN-005 | 21009 | 2018-09-26 | Dist | 2023-06-01 | Lake Providence |  |  | 115 |  |  | New Lake Providence distribution sub. | LA |  |  | Planned | 50446621 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9686 | 2017-01-09 | 16-ELN-005 | 21010 | 2018-09-26 | LN | 2023-06-01 | OakGrove | Lake Providence | 1 | 115 |  | 176 | New 115 kV line to new distribution substation. | LA |  | 15 | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9690 | 2017-01-09 | 16-ELN-010 | 21014 | 2018-09-26 | Dist | 2019-12-01 | Hodge |  |  | 230 |  |  | 230 kV substation | LA |  |  | Planned | 26660631 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9763 | 2017-01-09 | 16-EGL-004 | 21137 | 2018-09-26 | LNrc | 2019-06-01 | Baker | Blount | 1 | 69 |  |  | Upgrade Line | LA |  |  | Planned | 4385051 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9771 | 2017-01-09 | 16-EGL-012-1 | 21145 | 2018-09-26 | SUB | 2018-09-30 | Jefferson Davis |  |  | 138 | 69 |  | Build new Sub | LA |  |  | Under Construction | 102266403 |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9772 | 2017-01-09 | 16-EGL-012-2 | 21146 | 2017-09-28 | LN | 2018-10-31 | Colonial Welsh Tap | Jefferson Davis | 1 | 138 |  |  | Construct New Line | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9773 | 2017-01-09 | 16-EGL-012-3 | 21147 | 2018-06-27 | LN | 2019-02-28 | Jefferson Davis | Carter | 1 | 69 |  |  | Build new line | LA |  |  | Under Construction |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9774 | 2017-01-09 | 16-EGL-012-4 | 21148 | 2017-09-28 | LN | 2019-06-30 | Jefferson Davis | L-13 | 1 | 69 |  |  | Cut L-13 in and out of Jeff Davis 69 kV sub | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9775 | 2017-01-09 | 16-EGL-012-5 | 21149 | 2017-09-28 | TAP | 2019-04-30 | Derouen |  |  | 69 |  |  | Cut Derouen into Line 11 | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9776 | 2017-01-09 | 16-EGL-012-6 | 21150 | 2017-09-28 | TAP | 2019-03-30 | Lawtag |  |  | 69 |  |  | Cut Lawtag sub in and out of Line 13. | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9777 | 2017-01-09 | 16-EGL-012-7 | 21151 | 2017-09-28 | TAP | 2019-03-30 | Welsh |  |  | 69 |  |  | Cut Welsh in and out of line 13A | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9778 | 2017-01-09 | 16-EGL-012-8 | 21152 | 2017-09-28 | LNrc | 2018-10-31 | Colonial Welsh Tap | Jefferson Davis | 1 | 138 |  |  | Reconductor Line | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9779 | 2017-01-09 | 16-EGL-013 | 21153 | 2017-12-27 | LNrc | 2019-11-30 | Carter | Serpent | 1 | 69 |  |  | Reconductor Line | LA |  |  | Planned |  | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9780 | 2017-01-09 | 16-EGL-014 | 21154 | 2018-09-26 | LNrc | 2019-09-30 | Compton | Elton | 1 | 69 |  |  | Reconductor Line | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9782 | 2017-01-09 | 16-EGL-016 | 21156 | 2017-12-27 | SUBmisc | 2019-03-30 | Lake Arthur |  |  | 69 |  |  | Adjust Normally Open Point | LA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9791 | 2017-01-09 | 16-EGL-027 | 21165 | 2018-09-26 | Dist | 2020-04-01 | Thompson Road |  |  | 230 |  |  | New distribution substation | LA |  |  | Planned | 23792173 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9792 | 2017-01-09 | 16-EGL-028 | 21166 | 2018-09-26 | Dist | 2019-06-01 | Lowe Grout Road |  |  | 138 |  |  | New Distribution Substation | LA |  |  | Planned | 19003650 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 9805 | 2017-01-09 | 16-ENO-001 | 21179 | 2018-09-26 | LNrc | 2019-12-01 | Patterson | Pontchartrain Park | 1 | 115 |  |  | Upgrade Line | LA |  |  | Planned | 4279679 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10008 | 2017-01-09 | 15-EGL-023 | 21432 | 2018-09-26 | LN | 2020-06-01 | Nelson 230 kV | Menena 230 kV | 1 | 230 |  | 779 | Approximately 5.5 miles of 1272 ACSS single conductor. | LA | 0 | 5.5 | Planned | 14234001 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10583 | 2017-01-09 | 16-EGL-037 | 21605 | 2018-09-26 | CB | 2018-10-01 | Coly 230 |  |  | 230 |  |  | Add 230 kV Breaker at Coly | LA |  |  | Planned | 1073527 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10584 | 2017-01-09 | 16-EGL-038 | 21606 | 2018-09-26 | CB | 2018-11-01 | Tiger 230 |  |  | 230 |  |  | Add breaker at Tiger 230 kV | LA |  |  | Planned | 996703 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10588 | 2017-01-09 | 16-ELL-010 | 21616 | 2018-09-26 | SUB | 2020-06-01 | Fleur 230 |  |  | 230 |  |  | Construct new substation on the Oakville to Alliance 230 kV line. | LA |  |  | Planned | 9125021 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10588 | 2017-01-09 | 16-ELL-010 | 21669 | 2018-09-26 | LNrb | 2019-06-01 | Ninemile | Barataria | 1 | 115 |  |  | Rebuild Line | LA |  |  | Under Construction | 53730589 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10623 | 2018-09-19 | 16-EGL-042 | 21626 | 2018-09-26 | SUB | 2022-12-31 | Sadie |  |  | 230 |  |  | Construct New 230 kV Substation on the PPG to Rosebluff line | LA |  |  | Planned | 19953332 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 10624 | 2017-01-09 | 16-EGL-043 | 21627 | 2018-09-26 | SUB | 2022-07-01 | Big Lake |  |  | 230 |  |  | Construct 230 kV substation on the Vincent to Graywood 230 kV line. | LA |  |  | Planned | 16936133 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-LA | 12017 | 2017-01-09 |  | 22088 | 2017-09-28 | SUB | 2022-06-01 | NSUB1 |  |  | 230 |  |  | New substation south of Ninemile substation | LA |  |  | Planned |  |  |  | N | N | N | Y
A in MTEP16 | A | South | Entergy-LA | 12017 | 2017-01-09 |  | 22090 | 2017-09-28 | TEQ | 2022-06-01 | Waterford |  |  | 230 |  |  | Waterford Substation Modifications | LA |  |  | Planned |  |  |  | N | N | N | Y
A in MTEP16 | A | South | Entergy-LA | 12017 | 2017-01-09 |  | 22089 | 2018-09-26 | LN | 2022-06-01 | Waterford | NSUB1 |  | 230 |  |  | New 230 kV transmission line connecting existing Waterford 230 kV to the new (NSUB1) substation | LA |  | 27 | Planned | 97159798 |  |  | N | N | N | Y
A in MTEP16 | A | South | Entergy-MS | 9822 | 2017-01-09 | 16-EMI-001 | 21197 | 2018-09-26 | SwSta | 2018-12-01 | Harper |  |  | 115 |  |  | New 115 kV switching station on the Gloster - Crosby 115 kV. The Gloster - Centreville line will be rerouted from Gloster to Harper. | MS |  |  | Under Construction | 8307991 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-MS | 9833 | 2017-01-09 | 16-EMI-007 | 21209 | 2018-09-26 | CAP | 2018-11-01 | Greenville North |  |  | 115 |  |  | Install 2nd capacitor bank | MS |  |  | Planned | 1736875 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-MS | 9949 | 2018-08-27 |  | 21826 | 2018-09-27 | SwSta | 2018-12-01 | International Paper |  |  | 115 |  |  | The Cloverdale DP will be served from the existing Entergy IP to Johns Manville 115kV transmission line via a looped transmission feed into a new switching station to be constructed at the DP site. | MS |  |  | Under Construction | 1896000 |  |  | N | N | N
A in MTEP16 | A | South | Entergy-MS | 10943 | 2017-01-09 | 16-EMI-016 | 21692 | 2018-09-26 | SUB | 2018-11-01 | Norrel Road |  |  | 230 |  |  | New 230 kV delivery point | MS |  |  | Under Construction | 10741044 | Facility Study |  | N | N | N
A in MTEP16 | A | South | Entergy-MS | 11783 | 2017-01-09 | 16-EMI-019 | 21828 | 2018-09-26 | TX | 2019-12-01 | McAdams |  |  | 500 | 230 |  | Replace current autotransformers at McAdams with autotransformers that have at least a 700 MVA rating. | MS |  |  | Planned | 5379046 | Facility Study |  | N | N | N
A in MTEP16 | A | South | Entergy-MS | 11783 | 2017-01-09 | 16-EMI-019 | 21829 | 2017-12-27 | TX | 2019-12-01 | McAdams |  |  | 500 | 230 |  | Replace current autotransformers at McAdams with autotransformers that have at least a 700 MVA rating. | MS |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-MS | 12015 | 2017-01-09 |  | 22086 | 2018-09-26 | TX | 2019-12-01 | Lakeover |  |  | 500 | 230 |  | Relocate existing 500/230kV transformer from McAdams to Lakeover | MS |  |  | M3_Long Lead Materials | 9116231 |  |  | N | N | N | Y
A in MTEP16 | A | South | Entergy-TX | 7930 | 2017-01-09 | 15-ETI-008 | 20186 | 2018-09-26 | Dist | 2019-06-01 | Heights |  |  | 230 | 34.5 | 75 | Construct new substation | TX |  |  | Planned | 38504354 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9806 | 2017-01-09 | 16-ETI-001 | 21180 | 2018-09-26 | TX | 2020-06-01 | Bryan 138 | Bryan 69 | 1 | 138 | 69 |  | Replace Auto | TX |  |  | Planned | 35577866 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9806 | 2017-01-09 | 16-ETI-001 | 21181 | 2018-09-26 | TX | 2020-06-01 | Bryan 138 | Bryan 69 | 2 | 138 | 69 |  | Replace Auto | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9807 | 2017-01-09 | 16-ETI-002 | 21182 | 2018-09-26 | SwSta | 2020-03-01 | Pintail |  |  | 138 |  |  | New Switching Station | TX |  |  | Planned | 9758690 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9809 | 2017-01-09 | 16-ETI-007 | 21184 | 2018-09-26 | LNrc | 2020-12-01 | Hull | Sour Lake |  | 69 |  |  | Upgrade Line | TX |  |  | Planned | 45999870 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9812 | 2017-01-09 | 16-ETI-014-1 | 21187 | 2018-09-26 | SwSta | 2020-06-01 | Garden |  |  | 230 |  |  | Build New Substation | TX |  |  | Planned | 72661738 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9813 | 2017-01-09 | 16-ETI-014-2 | 21188 | 2017-09-28 | LN | 2020-06-01 | Garden | Legend | 1 | 230 |  |  | Build new line | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9814 | 2017-01-09 | 16-ETI-014-3 | 21189 | 2017-09-28 | SwSta | 2020-06-01 | Legend |  |  | 230 |  |  | Build New Substation | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9817 | 2017-01-09 | 16-ETI-016 | 21192 | 2018-09-26 | CB | 2019-12-01 | Helbig |  |  | 230 |  |  | Add Circuit Breakers | TX |  |  | Planned | 6626348 | Planning |  | N | N | N
A in MTEP16 | A | South | Entergy-TX | 9818 | 2017-01-09 | 16-ETI-017 | 21193 | 2018-09-26 | LNcnv | 2019-06-01 | Stowell | Himex | 1 | 138 |  |  | Convert line to 138 kV | TX |  |  | Planned | 12730884 | Planning |  | N | N | N
A in MTEP16 | A | West | GRE | 4378 | 2017-01-09 | 202970 | 8387 | 2013-09-13 | CB | 2020-09-01 | Long Lake |  |  | 115 |  |  | Circuit breakers for new lines related to Hubbard-Potato Lake line | MN |  |  | Proposed | 835000 | Planning |  | N | N | N | Y
A in MTEP16 | A | West | GRE | 7884 | 2017-01-09 | 203079 | 20114 | 2017-09-12 | SUB | 2018-12-10 | Riverview |  |  | 345 | 115 | 448 | Construct the new Riverview 345/115/69 kV substation directly off the CapX 345 kV line between the Melrose East and Millwood 69 kV substations. The transformers will be a 448 MVA, 345/115 kV transformer and a 70 MVA 115/69 MVA transformer. This substation will initially have two 345 line terminating breakers, a single 345 kV breaker on the high side of the transformer, two 69 kV line termination breakers in addition to a low side 69 kV breaker. The substation should be designed for future development and be laid out for nine 345 breaker (3 rows of 345 kV breakers in a breaker and half scheme), six 115 kV (2 rows of 115 kV breakers in a breaker and half scheme), and four 69 kV breakers in a straight bus configuration. | MN |  |  | Proposed | 14224845.12 | Planning Preliminary |  | N | N | N | Y
A in MTEP16 | A | West | GRE | 7884 | 2017-01-09 | 203079 | 20129 | 2017-09-12 | LNrb | 2018-12-10 | Melrose | Riverview | 1 | 69 | 69 |  | Rebuild E Melrose to Millwood Tap 4.6 mile line. | MN | 4.6 |  | Proposed | 2200000 | Planning Preliminary |  | N | N | N
A in MTEP16 | A | West | GRE | 7884 | 2017-01-09 | 203079 | 20128 | 2016-04-14 | SUB | 2018-12-10 | Riverview |  |  | 115 | 69 | 70 | Construct the new Millwood (Riverview Road ) 345/115/69 kV substation directly off the CapX 345 kV line between the Melrose East and Millwood 69 kV substations. The transformers will be a 448 MVA, 345/115 kV transformer and a 70 MVA 115/69 MVA transformer. This substation will initially have two 345 line terminating breakers, a single 345 kV breaker on the high side of the transformer, two 69 kV line termination breakers in addition to a low side 69 kV breaker. The substation should be designed for future development and be laid out for nine 345 breaker (3 rows of 345 kV breakers in a breaker and half scheme), six 115 kV (2 rows of 115 kV breakers in a breaker and half scheme), and four 69 kV breakers in a straight bus configuration.. Please see the online diagram included in this PDR. This project will also be coordinated with Xcel Energy for rebuilding the existing Melrose-Millwood 69 kV line with 795 ACSS and 115 kV design. Desired in-service date is spring 2017. | MN |  |  | Proposed | 4583671.1 | Planning Preliminary |  | N | N | N | Y
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21050 | 2018-05-07 | SwSta | 2018-12-31 | White Pole Road | Switch Station |  | 69 | 69 |  | Construct a new 3 terminal switch station named White Pole Road. | IA |  |  | M3_Long Lead Materials | 2341176 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21071 | 2018-05-07 | LNcnv | 2019-12-31 | Panorama REC Tap | Panorama REC | 1 | 69 | 69 |  | Convert Panorama REC Tap - Panorama REC to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 0.8 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21070 | 2018-05-07 | LNcnv | 2019-12-31 | Panora Muni Tap | Panorama REC Tap | 1 | 69 | 69 |  | Convert Panora Muni Tap - Panorama REC Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 1.57 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21069 | 2018-05-07 | LNcnv | 2019-12-31 | Panora Muni Tap | Panora Muni | 1 | 69 | 69 |  | Convert Panora Muni Tap - Panora Muni to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 0.61 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21068 | 2018-05-07 | LNcnv | 2019-12-31 | Panora Switch Station | Panora Muni Tap | 1 | 69 | 69 |  | Convert Panora Switch Station - Panora Muni Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 5.72 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21067 | 2018-05-07 | LNcnv | 2019-12-31 | Panora Switch Station | Panora REC | 1 | 69 | 69 |  | Convert Panora Switch Station - Panora REC to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 0.7 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21066 | 2018-05-07 | LNcnv | 2019-12-31 | Panora Switch Station | Guthrie | 1 | 69 | 69 |  | Convert Panora Switch Station - Guthrie to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 6 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21065 | 2018-05-07 | SwSta | 2019-12-31 | Paonra Switch Station | Switch Station |  | 69 | 69 |  | CIPCO will construct a new Panora 69 kV 3 terminal switch station | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21064 | 2018-05-07 | LNcnv | 2019-12-31 | Redfield Tap | Panora Switch Station | 1 | 69 | 69 |  | Convert Redfield Tap - Panora Switch Station to 69 kV | IA | 10 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21063 | 2018-05-07 | LNcnv | 2019-12-31 | Redfield Tap | Redfield | 1 | 69 | 69 |  | Convert Redfield Tap - Redfield to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 0.7 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21062 | 2018-05-07 | LNcnv | 2019-12-31 | Diamondhead REC Tap | Redfield Tap | 1 | 69 | 69 |  | Convert Diamondhead REC Tap - Redfield Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 1.85 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21061 | 2018-05-07 | LNcnv | 2019-12-31 | Diamondhead REC Tap | Diamondhead REC | 1 | 69 | 69 |  | Convert Diamondhead REC Tap - Diamondhead REC to 69 kV (existing 34.5 kV line built to 69 kV construction | IA | 1.75 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21060 | 2018-05-07 | LNcnv | 2019-12-31 | Stuart Muni Tap | Diamondhead REC Tap | 1 | 69 | 69 |  | Convert Stuart Muni Tap - Diamondhead REC Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 8 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21059 | 2018-05-07 | LNcnv | 2019-12-31 | Stuart Muni Tap | Stuart Muni | 1 | 69 | 69 |  | Convert Stuart Muni Tap - Stuart Muni to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA | 0.8 |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21058 | 2018-05-07 | LNcnv | 2019-12-31 | Stuart REC Tap | Stuart Muni Tap | 1 | 69 | 69 |  | Convert Stuart REC Tap - Stuart Muni Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21057 | 2018-05-07 | LNcnv | 2019-12-31 | Stuart Muni South Tap | Stuart REC | 1 | 69 | 69 |  | Convert Stuart Muni South Tap - Stuart REC to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21056 | 2018-05-07 | LNcnv | 2019-12-31 | Stuart Muni South Tap | Stuart Muni South | 1 | 69 | 69 |  | Convert Stuart Muni South Tap - Stuart Muni South Sub to 69 kV (existing 34.5 kV line built to 69 kV construction | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21055 | 2018-05-07 | LNcnv | 2019-12-31 | Stuart REC Tap | Stuart Muni South Tap | 1 | 69 | 69 |  | Convert Stuart REC Tap - Stuart Muni South Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21054 | 2018-05-07 | LNcnv | 2019-12-31 | Hawkeye REC | Stuart REC Tap | 1 | 69 | 69 |  | Convert Hawkeye REC - Stuart REC Tap to 69 kV (existing 34.5 kV line built to 69 kV construction) Add load break capability and SCADA controlled motor operators at Hawkeye REC. | IA |  |  | M3_Long Lead Materials | 264000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21053 | 2018-05-07 | LNcnv | 2019-12-31 | White Pole Raod | Hawkeye REC | 1 | 69 | 69 |  | Convert White Pole Rd - Hawkeye REC to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21052 | 2018-05-07 | LNcnv | 2019-12-31 | Guthrie | White Pole Road | 1 | 69 | 69 |  | Convert Guthrie - White Pole Rd to 69 kV (existing 34.5 kV line built to 69 kV construction) | IA |  |  | M3_Long Lead Materials | 240000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9664 | 2017-01-09 | Guthrie-Panora 34 to 69 Conv | 21051 | 2018-05-07 | TAP | 2018-12-31 | White Pole Road | Switch Station |  | 69 | 69 |  | 69 kV line taps for the new White Pole Road station | IA |  |  | M3_Long Lead Materials | 540000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9665 | 2018-05-17 | PCI-Oak Hill 34 to 69 Conv | 21037 | 2018-09-28 | SUB | 2019-04-01 | PCI | Substation |  | 69 | 69 |  | Convert PCI-Oak Hill to 69 kV operation | IA |  |  | M4_Pre-Construction | 12000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9665 | 2018-05-17 | PCI-Oak Hill 34 to 69 Conv | 21039 | 2018-09-28 | LN | 2019-04-01 | PCI | Oak Hill | 1 | 69 | 69 |  | Convert to 69 kV operation (already built for 69 kV). | IA | 4.5 |  | M4_Pre-Construction | 21600 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9665 | 2018-05-17 | PCI-Oak Hill 34 to 69 Conv | 21038 | 2018-09-28 | Dist | 2019-04-01 | Oak Hill | Substation |  | 69 | 69 |  | Convert to 69 kV operation | IA |  |  | M4_Pre-Construction | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21027 | 2018-05-08 | LNcnv | 2020-12-31 | Emerald Isle | Harrison | 1 | 69 | 69 | 77 MVA | Convert Emerald Isle-Harrison line to 69 kV operation (already built for 69 kV) | IA | 3.5 |  | M2a_Pre-Project Approval | 240000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21034 | 2018-05-08 | SUB | 2020-12-31 | Beverly | Substation |  | 69 | 69 |  | Add two new 69 kV line terminals and a 69 kV bus tie breaker at the Beverly substation. | IA |  |  | M2a_Pre-Project Approval | 1461539 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21033 | 2018-05-08 | LNrb | 2020-12-31 | PCI | Beverly | 1 | 69 | 69 | 103 MVA | Rebuild a portion of the PCI-Beverly line to double circuit 69 kV. | IA | 1.2 |  | M2a_Pre-Project Approval | 1466754 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21032 | 2018-05-08 | LNcnv | 2020-12-31 | Taylor | Beverly | 1 | 69 | 69 | 77 MVA | Convert the Beverly-Taylor line to 69kV operation | IA | 5.15 |  | M2a_Pre-Project Approval | 1502754 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21030 | 2018-05-08 | Dist | 2021-12-31 | Taylor | Substation |  | 69 | 69 |  | New Taylor 69kV/distribution substation | IA |  |  | M2a_Pre-Project Approval | 5590370 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21029 | 2018-05-08 | LNcnv | 2020-12-31 | Harrison | Taylor | 1 | 69 | 69 |  | Convert Harrison-Taylor line to 69 kv operation (already built for 69 kV) | IA |  |  | M2a_Pre-Project Approval | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9666 | 2017-01-09 | Emerald Isle-Beverly 34 to 69 kV Conv | 21028 | 2018-05-08 | SUB | 2020-12-31 | Emerald Isle | Substation |  | 69 | 69 |  | Add 69 kV terminal at Emerald Isle | IA |  |  | M2a_Pre-Project Approval | 443671 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21079 | 2016-01-29 | SUB | 2019-12-31 | New Hills area | Substation |  | 345 | 69 |  | Construct a new substation in the Hills area. | IA |  |  | Planned | 19029110 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21092 | 2015-09-11 | LN | 2025-12-31 | Conroy | Homestead | 1 | 69 | 69 |  | New CIPCO owned Conroy-Homestead 69 kV line | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21091 | 2016-01-29 | SwSta | 2025-12-31 | Conroy | Switch Station |  | 69 | 69 |  | New Conroy 69 kV switching station | IA |  |  | Planned | 3979450 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21090 | 2016-01-29 | SwSta | 2025-12-31 | Homestead | Switch Station |  | 69 | 69 |  | New Homestead 69 kV switching station | IA |  |  | Planned | 3979450 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21089 | 2016-01-29 | SUB | 2022-12-31 | Fairfax | Substation |  | 161 | 161 |  | Add a 161 kV terminal for the new North Liberty-Fairfax 161 kV line | IA |  |  | Planned | 904828 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21088 | 2016-01-29 | LN | 2022-12-31 | North Liberty | Tharp | 1 | 69 | 69 |  | Re-build existing North Liberty REC - Tharp line (double circuit with new North Liberty - Fairfax 161 kV) | IA |  |  | Planned | 11080800 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21087 | 2016-01-29 | LN | 2022-12-31 | North Liberty | Fairfax | 1 | 161 | 161 | 446 MVA | New 161 kV line from North Liberty-Fairfax (double circuit with new North Liberty-Tharp 69 kV line). | IA |  |  | Planned | 27788400 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21086 | 2015-09-11 | TX | 2019-12-31 | New North Liberty | Transformer | 1 | 161 | 69 | 200 MVA | New CIPCO owned 161/69 kV 200 MVA transformer. | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21085 | 2015-09-11 | SUB | 2019-12-31 | New North Liberty | Substation |  | 161 | 69 |  | New CIPCO owned 161/69 kV North Liberty sub | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21084 | 2016-01-29 | LN | 2019-12-31 | New Hills area | Clear Creek | 1 | 69 | 69 |  | New ITC owned 69 kv line double circuit with the new Hills area to North Liberty 161 kv line owned by CIPCO. | IA |  |  | Planned | 8678400 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21083 | 2015-09-11 | LN | 2019-12-31 | New Hills area | North Liberty | 1 | 161 | 161 |  | CIPCO will own a new 161 kV line from the new Hills area sub to the new North Liberty sub. The new line will be double circuit with a new 69 kV line owned by ITC. | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21082 | 2015-09-11 | SwSta | 2019-12-31 | ClearCreek | Switch Station |  | 69 | 69 |  | CIPCO will construct a new switch station | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21081 | 2015-09-11 | TX | 2019-12-31 | New Hills area | Transformer | 1 | 161 | 69 | 150 MVA | CIPCO will install a new 161/69kV 150 MVA tranformer | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9668 | 2017-01-09 | CR-North Liberty-Hills | 21080 | 2015-09-11 | TX | 2019-12-31 | New Hills area sub | Transformer | 1 | 345 | 161 | 450 MVA | Install a new 345/161 kV 450 MVA transformer. | IA |  |  | Planned |  |  |  | N | N | N
A in MTEP16 | A | West | ITCM | 9670 | 2017-01-09 | Columbus Junction Breaker add | 21049 | 2015-11-18 | SUB | 2020-12-31 | Columbus Junction | Substation |  | 69 | 69 |  | Install a second 69 kV breaker at Columbus Jct | IA |  |  | Planned | 932101 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9672 | 2017-01-09 | 76th AVE SW | 20992 | 2018-06-29 | SUB | 2022-12-31 | 76th AVE SW | Substation |  | 69 | 69 |  | Construct a new four (4) terminal, four (4) break 69 kV substation southeast of the city of Cedar Rapids | IA |  |  | M1_Final SPM or OOC | 3757232 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9672 | 2017-01-09 | 76th AVE SW | 20995 | 2018-06-29 | CAP | 2022-12-31 | 76th AVE SW | Capacitor |  | 69 | 69 | 13.2 MVAR | Install a 13.2MVAR cap bank at the new 76th AVE SW substation | IA |  |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9672 | 2017-01-09 | 76th AVE SW | 20994 | 2018-06-29 | LN | 2022-12-31 | Prairie Creek | CKT 0210 | 1 | 69 | 69 |  | Tap the 69kV Prairie Creek CKT 0210 | IA |  |  | M1_Final SPM or OOC | 149536 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9672 | 2017-01-09 | 76th AVE SW | 20993 | 2018-06-29 | LN | 2022-12-31 | PCI | Tharp | 1 | 69 | 69 |  | Tap PCI-Tharp 69kV line for 2 of the new line terminals | IA |  |  | M1_Final SPM or OOC | 149536 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21291 | 2018-05-09 | SwSta | 2020-12-31 | Lyon | Switch Station |  | 69 | 69 |  | Construct a new 3 terminal switch station near Lyon (official name TBD). | IA |  |  | M1_Final SPM or OOC | 3420000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21632 | 2018-05-09 | SUB | 2021-12-31 | Lyon | Substation |  | 69 | 69 |  | Retire the old Lyon 34kV substation. | IA |  |  | M1_Final SPM or OOC | 180000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21631 | 2018-05-09 | LN | 2021-12-31 | Boone CKT 2230 |  | 1 | 69 | 69 |  | Retire the 34kV Boone CKT 2230. | IA |  |  | M1_Final SPM or OOC | 360000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21300 | 2018-05-09 | LNcnv | 2021-08-04 | Jewell | Lyon | 1 | 69 | 69 |  | Jewell to Lyon Breaker Station 34.5 to 69 kV line conversion | IA | 0.96 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21298 | 2018-05-09 | LNcnv | 2021-08-04 | Stanhope Muni Tap | Jewell | 1 | 69 | 69 |  | Stanhope Muni Tap to Jewell 34.5 to 69 kV line conversion | IA | 10.22 |  | M1_Final SPM or OOC | 257505 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21297 | 2018-05-09 | LNcnv | 2021-08-04 | Stanhope Muni Tap | Stanhope Muni | 1 | 69 | 69 |  | Stanhope Muni Tap to Stanhope Muni 34.5 to 69 kV line conversion | IA | 0.25 |  | M1_Final SPM or OOC | 420974 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21296 | 2018-05-09 | LNcnv | 2021-08-04 | Stratford REC Tap | Stanhope Muni Tap | 1 | 69 | 69 |  | Startford REC Tap to Stanhoep Muni Tap 34.5 to 69 kV line conversion | IA | 4.98 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21294 | 2018-05-09 | LNcnv | 2021-08-04 | Stratford REC Tap | Stratford REC | 1 | 69 | 69 |  | Stratford REC Tap to Startford REC 34.5 to 69 kV line conversion | IA | 2.7 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21293 | 2018-05-09 | LNcnv | 2021-08-04 | Ridgeport REC | Stratford REC Tap | 1 | 69 | 69 |  | Ridgeport REC to Stratford REC Tap 34.5 to 69 kV line conversion | IA | 4.94 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9714 | 2018-05-09 | Doud-Lyon 34 to 69 kV Conv | 21292 | 2018-05-09 | LNcnv | 2021-08-04 | Doud | Ridgeport REc | 1 | 69 | 69 |  | Doud to Ridgeport REC 34.5 to 69 kV line conversion | IA | 11.15 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9901 | 2017-01-09 | Mount Ayr 69 kV Sub Rebuild | 21306 | 2018-05-09 | SUB | 2018-08-01 | Kneedler | Substation |  | 69 | 69 |  | New sub north of Mt. Ayr instead of rebuilding the Mount Ayr 69 kV substation. | IA |  |  | M3_Long Lead Materials | 3674915 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9901 | 2017-01-09 | Mount Ayr 69 kV Sub Rebuild | 21753 | 2018-05-09 | CAP | 2018-08-01 | Mt Ayr (Kneedler) | Substation |  | 69 | 69 |  | Add a 21.42 MVAr cap at Kneedler sub. (Three stages of 7.1 MVAr) | IA |  |  | M3_Long Lead Materials | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9901 | 2017-01-09 | Mount Ayr 69 kV Sub Rebuild | 21752 | 2018-05-09 | TAP | 2018-08-01 | Mt Ayr (Kneedler) | Substation |  | 69 | 69 |  | 69kV line tap work for the new Kneedler substation | IA |  |  | M3_Long Lead Materials | 444000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9907 | 2018-05-09 | Summit to Dovray 69 kV Rebuild | 21315 | 2018-05-09 | LNrb | 2022-12-31 | Summit | Dovray | 1 | 69 | 69 |  | Rebuild ~12.9 miles of old line to new T2-4/0 ACSR | MN | 12.89 |  | M1_Final SPM or OOC | 9162091 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9908 | 2018-05-09 | Dovray to Fulda 69 kV Rebuild | 21316 | 2018-05-09 | LNrb | 2023-12-31 | Dovray | Fulda |  | 69 | 69 |  | Rebuild 69kV line from Dovrey substation to the Fulda Junction | MN | 14.5 |  | M1_Final SPM or OOC | 9410124 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9910 | 2018-05-09 | Fulda to Heron Lake 69 kV Rebuild | 21318 | 2018-05-09 | LNrb | 2024-12-31 | Fulda Junction | Heron Lake | 1 | 69 | 69 |  | Rebuild 69kV line from Fulda Junction to Heron Lake | MN | 20.14 |  | M1_Final SPM or OOC | 14976652 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9985 | 2017-01-09 | Newhall-Williamsburg 161 kV | 21411 | 2017-06-30 | LNrb | 2020-05-04 | Newhall | Willaimsburg | 1 | 161 | 161 |  | Rebuild Williamsburg 115kV tap to 161kV | IA | 23 | 3 | Planned | 40174153 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9988 | 2017-01-09 | Newhall 161 kV Breaker Station | 21409 | 2018-03-29 | SwSta | 2019-12-31 | Newhall | Switch Station |  | 161 | 161 |  | Construct 3 position 161kV Breaker Station | IA |  |  | M2a_Pre-Project Approval | 6924478 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 9988 | 2017-01-09 | Newhall 161 kV Breaker Station | 21757 | 2018-03-29 | TAP | 2019-12-31 | Newhall | Line Taps |  | 161 | 161 |  | Construct 161kV line taps for 3 position 161kV Breaker Station | IA |  |  | M2a_Pre-Project Approval | 1166404 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10022 | 2017-01-09 | PCI-Mt.Vernon-Lisbon-76thAVE Conv | 21434 | 2018-06-29 | SUB | 2022-12-31 | Lisbon North | Substation | 1 | 69 | 69 |  | Two (2) 69 kV breakers and associated equipment will be installed at the Lisbon North substation | IA |  |  | M1_Final SPM or OOC | 598171 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10022 | 2017-01-09 | PCI-Mt.Vernon-Lisbon-76thAVE Conv | 21633 | 2018-06-29 | LNcnv | 2022-12-31 | PCI | Mt. Vernon | 1 | 69 | 69 |  | Convert to 69kV operation. | IA |  |  | M1_Final SPM or OOC | 661200 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10022 | 2017-01-09 | PCI-Mt.Vernon-Lisbon-76thAVE Conv | 21437 | 2018-06-29 | LNup | 2022-12-31 | 76th AVE (Eagle) | Tharp | 1 | 69 | 69 |  | OPGW will need to be installed. | IA |  |  | M1_Final SPM or OOC | 2175600 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10022 | 2017-01-09 | PCI-Mt.Vernon-Lisbon-76thAVE Conv | 21436 | 2018-06-29 | LN | 2022-12-31 | PCI | 76th AVE (Eagle) | 1 | 69 | 69 |  | approximately 0.6 mile of new 69 kV transmission line will be constructed to complete the PCI to 76th Ave circuit | IA |  |  | M1_Final SPM or OOC | 2037600 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10022 | 2017-01-09 | PCI-Mt.Vernon-Lisbon-76thAVE Conv | 21435 | 2018-06-29 | SUB | 2022-12-31 | PCI | Substation | 1 | 69 | 69 |  | A 69 kV breaker and associated equipment will be installed at the PCI substation | IA |  |  | M1_Final SPM or OOC | 321361 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10023 | 2017-01-09 | ITCM Asset Blanket | 21443 | 2016-05-25 | LN | 2019-12-31 | ITCM Asset Blanket for 2019 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL |  |  | Planned | 37200000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10023 | 2017-01-09 | ITCM Asset Blanket | 21442 | 2018-02-01 | LN | 2018-12-31 | ITCM Asset Blanket for 2018 | Throughout system |  | 345 | 69 |  | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA,MN,IL |  |  | Under Construction | 37200000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10024 | 2017-01-09 | Cust Interconnet Blanket | 21438 | 2015-09-15 | LN | 2019-12-31 | Blanket for Customer Interconnections under $1 million for 2019 | Throughout system |  | 345 | 69 |  | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL |  |  | Planned | 2000000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10303 | 2017-01-09 | Willaimsburg 161kV Temp Conv | 21559 | 2017-12-28 | SUB | 2019-03-18 | Williamsburg | Substation |  | 161 | 34 |  | The two aging and miss-matched 115/34.5kV transformers will be replaced with a newer and larger 161/36kV transformer from the Hiawatha Substation. This will provide an increased level of reliability to Williamsburg by serving the high-side from a newly rebuilt and shorter 161kV line compared to an older and longer 115kV line. | IA |  |  | Planned | 1204368 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 10303 | 2017-01-09 | Willaimsburg 161kV Temp Conv | 21560 | 2017-12-28 | LN | 2019-03-18 | Parnell | Williamsburg | 1 | 161 | 161 |  | To provide a reliable conversion to 69kV the 34.5kV will need temporary configurations to provide a reliable transition. The Williamsburg 115kV high side will be converted to 161kV. | IA |  |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 11163 | 2018-05-08 | Devils Creek | 21722 | 2018-05-08 | SUB | 2018-12-01 | Ft. Madison Devils Creek | Substation |  | 69 |  |  | New Ft. Madison Devils Creek Distribution Substation | IA |  |  | M3_Long Lead Materials | 2005592 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 11163 | 2018-05-08 | Devils Creek | 21725 | 2018-05-08 | SUB | 2018-12-01 | Dial | Substation |  | 69 |  |  | Retire the Dial substation. | IA |  |  | M3_Long Lead Materials | 420000 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 11163 | 2018-05-08 | Devils Creek | 21724 | 2018-05-08 | LN | 2018-12-01 | Viele 9660 Ckt | Viele 9660 Ckt | 1 | 69 |  |  | Retire the Viele 9660 Ckt (~3.6 miles) and the Viele bkr 9660 | IA |  |  | M3_Long Lead Materials | 38333 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 11163 | 2018-05-08 | Devils Creek | 21723 | 2018-05-08 | LN | 2018-12-01 | Ft. Madison Devils Creek | Substation |  | 69 |  |  | Line work for new 69kV line taps to the new Devil's Creek distribution substation. | IA |  |  | M3_Long Lead Materials | 260596 | Engineering |  | N | N | N
A in MTEP16 | A | West | ITCM | 11883 | 2017-01-09 |  | 21852 | 2017-06-26 | SUBmisc | 2022-01-01 | Huntley |  |  | 345 |  |  | Substation modifications at Huntley | MN |  |  | Planned | 2471713 |  |  | N | Y | Y | Y
A in MTEP16 | A | West | ITCM, XEL | 11883 | 2017-01-09 |  | 21848 | 2017-06-26 | LN | 2022-01-01 | Huntley | Wilmarth |  | 345 |  |  | 38.5 miles of 345 kV Single Ckt | MN |  | 38.5 | Planned | 103056574 |  |  | N | Y | Y | Y
A in MTEP16 | A | East | ITCT | 9685 | 2017-01-19 | ITC_15_016 | 21008 | 2017-12-21 | LNup | 2018-06-01 | Jacob | St. Clair | 1 | 120 |  |  | Remediate the Sag Limit on Jacob-St. Clair 120 kV to 292 MVA (1405 Amp) | MI |  |  | M3_Long Lead Materials | 139000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9692 | 2017-01-09 | ITC_15_022 | 21016 | 2017-06-27 | LNup | 2018-12-31 | Seneca | Spokane | 1 | 120 |  |  | Raise the Sag Limit on Seneca-Spokane 120 kV to 283 MVA (1362 Amp) | MI |  |  | M3_Long Lead Materials | 339000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9883 | 2017-01-09 | ITC_15_025 | 21271 | 2017-12-21 | CB | 2019-12-31 | Ironton |  |  | 120 |  |  | Install two 120 kV breakers to terminate the two River Rouge–Ironton 120 kV connections at Ironton | MI |  |  | M3_Long Lead Materials | 910000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9884 | 2017-01-09 | ITC_15_015 | 21272 | 2018-03-27 | LNup | 2019-12-31 | Belle River | Pontiac | 1 | 345 |  |  | Raise the Sag Limit on Belle River-Pontiac 345 kV to 1414 MVA (2366 Amp) | MI |  |  | M3_Long Lead Materials | 340000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9887 | 2017-01-09 | ITC_15_019 | 21276 | 2017-12-21 | LNup | 2019-12-31 | Pontiac | Wxom | 1 | 345 |  |  | Raise the Sag Limit on Pontiac-Wixom 345 kV to 1185 MVA (1983 Amp) | MI |  |  | M3_Long Lead Materials | 305000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9900 | 2017-01-09 | ITC_15_020 | 21301 | 2017-06-27 | LNup | 2018-12-31 | River Rouge | Ironton | 2 | 120 |  |  | Raise the Sag Limit on River Rouge-Ironton #2 120 kV to 271 MVA (1304 Amps) | MI |  |  | M3_Long Lead Materials | 340000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9902 | 2017-01-09 | ITC_15_030 | 21308 | 2018-03-27 | SUB | 2018-12-31 | Sterling |  |  | 120 |  |  | Install a new 120 kV bus and one 120 kV breaker to convert Sterling to a ring bus. Also move the Sterling transformer #201 connection to the new bus and install a disconnect switch on the low side. Breaker “HT” will become the bus-tie between bus #101 and #104 | MI |  |  | M3_Long Lead Materials | 1100000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9994 | 2017-01-09 | ITC_15_007 | 21418 | 2017-12-21 | LNrb | 2019-12-31 | Custer | Monroe | 1 | 120 |  |  | Rebuild the entire Custer – Monroe 120 kV line. Pre-build it to 230 kV construction to facilitate future 230 kV expansion in southern Michigan. Replace the existing assets (all structures and 954 ACSR 45/7 conductor) with new double-circuit structures that are designed for bundled 2-954 ACSR 54/7 conductor and install this conductor along with an OPGW path for the existing line only. | MI |  |  | M3_Long Lead Materials | 14500000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 9999 | 2017-01-09 |  | 21421 | 2018-06-27 | SUB | 2018-12-31 | ITCT Asset Replacement Program - 2018 |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | M4_Pre-Construction | 53250000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | ITCT | 10000 | 2017-01-09 |  | 21423 | 2015-09-15 | SUB | 2019-12-31 | ITCT Asset Replacement Program - 2019 |  |  | 345 | 120 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | Proposed | 53310000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | ITCT | 10010 | 2017-01-09 |  | 21433 | 2016-12-20 | Dist | 2019-12-31 | Blanket for Customer Interconnections 2019 | Througout System |  | 120 |  |  | Connect interconnecting entities as requested | MI |  |  | M2a_Pre-Project Approval | 2000000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | ITCT | 10243 | 2017-01-09 |  | 21501 | 2017-06-27 | CB | 2018-06-30 | Navarre |  |  | 120 |  |  | Upgrade the existing Navarre 120 kV breaker HX to have an interrupting capability of 50 kA. | MI |  |  | M3_Long Lead Materials | 70000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 10425 | 2018-06-18 |  | 21583 | 2018-06-18 | LN | 2018-12-31 | J340 Substation | Grassmere | 1 | 120 |  |  | Rebuild 5.3 miles of the existing 120 kV Cosmo tap using double circuit structures, and string 954 ACSR conductor between the J340 Interconnection substation and Grassmere. Relocate the Harvest Wind tap point to the new line to create the J340-Havest Wind-Grassmere 120 kV 3 terminal line. | MI | 5.3 |  | Under Construction | 7170000 | Engineering |  | N | Y | N
A in MTEP16 | A | East | ITCT | 10924 | 2017-01-09 |  | 21691 | 2016-12-20 | TEQ | 2018-12-31 | Throughout System |  |  | 120 |  |  | Install a new GOAB switch or replace an existing 120 kV, full-load-break pole top switch at necessary tap points. | MI |  |  | M2a_Pre-Project Approval | 2400000 | Engineering |  | N | N | N
A in MTEP16 | A | East | ITCT | 11583 | 2017-06-27 |  | 21787 | 2018-06-27 | SUB | 2018-10-15 | Kirk 345 kV |  |  | 345 |  |  | New 345 kV, 3-breaker substation laid out in a ring bus configuration | MI |  |  | M4_Pre-Construction | 7559500 | GIA |  | N | Y | Y
A in MTEP16 | A | East | ITCT | 11583 | 2017-06-27 |  | 21790 | 2018-06-27 | TEQ | 2018-10-15 | Kirk 345 kV |  |  | 345 |  |  | TOIFs associated with the J301 Project. This includes a 345 kV disconnect switch and entrance structure at the POI. | MI |  |  | M4_Pre-Construction | 685000 | GIA |  | N | N | N
A in MTEP16 | A | East | ITCT | 11583 | 2017-06-27 |  | 21789 | 2018-06-27 | LN | 2018-10-15 | Kirk | Bauer | 1 | 345 |  |  | New 345 kV line created by looping the Bauer-Ringle 345 kV line into Kirk. | MI |  | 0.1 | M4_Pre-Construction | 626250 | GIA |  | N | Y | Y
A in MTEP16 | A | East | ITCT | 11583 | 2017-06-27 |  | 21788 | 2018-06-27 | LN | 2018-10-15 | Kirk | Ringle | 1 | 345 |  |  | New 345 kV line created by looping the Bauer-Ringle 345 kV line into Kirk. | MI |  | 0.1 | M4_Pre-Construction | 626250 | GIA |  | N | Y | Y
A in MTEP16 | A | East | ITCT | 11584 | 2017-06-27 |  | 21791 | 2017-06-27 | SUB | 2018-10-15 | Helena 345 kV |  |  | 345 |  |  | New 345 kV, 3-breaker substation laid out in a ring bus configuration. | MI |  |  | M3_Long Lead Materials | 7495000 | GIA |  | N | Y | Y
A in MTEP16 | A | East | ITCT | 11584 | 2017-06-27 |  | 21794 | 2017-06-27 | TEQ | 2018-10-15 | Helena 345 kV |  |  | 345 |  |  | TOIFs for the J308 Project. These include a 345 kV disconnect switch and entrance structure at the POI. | MI |  |  | M3_Long Lead Materials | 673000 | GIA |  | N | N | N
A in MTEP16 | A | East | ITCT | 11584 | 2017-06-27 |  | 21793 | 2017-06-27 | LN | 2018-10-15 | Helena | Greenwood | 1 | 345 |  |  | New 345 kV line created by looping in the Greenwood-Rapson #2 line into Helena. | MI |  | 0.1 | M3_Long Lead Materials | 626500 | GIA |  | N | Y | Y
A in MTEP16 | A | East | ITCT | 11584 | 2017-06-27 |  | 21792 | 2017-06-27 | LN | 2018-10-15 | Helena | Rapson | 1 | 345 |  |  | New 345 kV line created by looping in the Greenwood-Rapson #2 line into Helena. | MI |  | 0.1 | M3_Long Lead Materials | 626500 | GIA |  | N | Y | Y
A in MTEP16 | A | East | ITCT | 11604 | 2017-01-24 |  | 21800 | 2017-01-24 | SUBmisc | 2019-06-30 | Milan 120 kV |  |  | 120 |  |  | Extend 120 kV Bus 103 at Milan substation | MI |  |  | M3_Long Lead Materials | 136000 | GIA |  | N | Y | N
A in MTEP16 | A | East | ITCT | 11604 | 2017-01-24 |  | 21801 | 2017-01-24 | SUB | 2019-06-30 | Milan 120 kV |  |  | 120 |  |  | TOIFs for the J419 project. These include a 120 kV breaker and associated disconnects at pos. HD at Milan | MI |  |  | M3_Long Lead Materials | 667000 | GIA |  | N | N | N
A in MTEP16 | A | South | LAFA | 8821 | 2018-07-27 |  | 20746 | 2017-09-20 | LN | 2020-06-30 | Northeast | Peck |  | 69 |  |  | 69kv line connecting Northeast station to Peck station. | LA |  |  | Planned | 3360000 |  |  | N | N | N
A in MTEP16 | A | West | MDU | 4140 | 2017-01-09 | Bowdle | 7871 | 2017-01-16 | SUB | 2019-03-31 | Bowdle Jct |  |  | 115 | 41.6 |  | A new 115/41.6 kV substation | SD |  |  | Planned | 5500000 | Engineering |  | N | N | N | Y
A in MTEP16 | A | West | MDU | 9120 | 2017-01-09 |  | 20815 | 2018-06-18 | LN | 2019-09-30 | Ellendale Jct | Leola Jct | 1 | 115 |  | 127 | New Ellendale Jct-Leola Jct 115 kV line | SD,ND |  | 45 | Planned | 8830000 | Budgetary |  | N | N | N
A in MTEP16 | A | West | MDU | 9120 | 2017-01-09 |  | 20816 | 2017-06-21 | SUB | 2018-12-31 | Leola Jct |  |  | 115 | 41.6 | 50 | New 115/41.6 kV substation connecting to the Ellendale Jct - Bowdle Jct 41.6 kV line | SD |  |  | Planned | 4005000 | Budgetary |  | N | N | N
A in MTEP16 | A | West | MEC | 9947 | 2018-08-28 |  | 21366 | 2018-06-29 | SUB | 2018-12-31 | Polk City |  |  | 161 | 13 | 33 | New Polk City 33 MVA 161-13 kV distribution substation | IA |  |  | Under Construction | 1300000 | Planning |  | N | N | N
A in MTEP16 | A | West | MEC | 9947 | 2018-08-28 |  | 21368 | 2018-06-29 | LN | 2018-12-31 | Polk City | NE Ankeny | 1 | 161 |  |  | New 3 mile line from Polk City Substation to existing Bittersweet-NE Ankeny 161 kV line. | IA |  | 3 | Under Construction | 2500000 | Planning |  | N | N | N
A in MTEP16 | A | West | MEC | 9947 | 2018-08-28 |  | 21367 | 2018-06-29 | LN | 2018-12-31 | Polk City | Bittersweet | 1 | 161 |  | 210 | Build four miles of new 161 kV line from Polk City to the existing Bittersweet - NE Ankeny 161 kV line | IA |  | 4 | Under Construction | 3200000 | Planning |  | N | N | N
A in MTEP16 | A | East | METC | 2809 | 2017-01-09 | 87 | 336 | 2017-12-21 | LNrb | 2019-12-31 | Garfield Avenue | Hemphill | 1 | 138 |  |  | Rebuild a ~9.5 mile-long portion of 336 ACSR conductor utilizing 1431 ACSR conductor on double-circuit, 138 kV structures, relocate a portion of the Weadock – Hemphill 138 kV line to the other side of the new structures | MI | 9.5 |  | M3_Long Lead Materials | 11000000 | Engineering |  | N | N | N | Y
A in MTEP16 | A | East | METC | 3133 | 2017-01-09 | METC_15_022 | 5510 | 2017-12-21 | LNrb | 2019-12-31 | Bell Road | Cornell | 1 | 138 |  |  | Rebuild a ~4.3 mile-long portion of the Claremont – Cornell 2 line between Bell Road and Cornell. | MI | 4.3 |  | M3_Long Lead Materials | 4350000 | Engineering |  | N | N | N | Y
A in MTEP16 | A | East | METC | 9695 | 2017-01-09 | METC_15_028 | 21019 | 2017-06-27 | TEQ | 2018-12-31 | Bullock |  |  | 138 |  |  | Upgrade terminal equipment at Bullock on the Dow Corning 138 kV line | MI |  |  | M3_Long Lead Materials | 300000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9705 | 2017-01-09 | METC_15_024 | 21036 | 2017-12-21 | LNup | 2018-12-31 | Alma | Regal | 2 | 138 |  |  | Remediate the sag limit on the Alma – Regal 2 138 kV line to a minimum of 208 MVA / 871 Amps | MI |  |  | M3_Long Lead Materials | 200000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9876 | 2017-06-23 | METC_15_027 | 21261 | 2017-12-21 | LNup | 2019-12-31 | Karn | Manning | 1 | 138 |  |  | Remediate the sag limit on the Karn - Manning 138 kV line to a minimum of 396 MVA / 1657 Amps | MI |  |  | M3_Long Lead Materials | 470000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9876 | 2017-06-23 | METC_15_027 | 21262 | 2017-12-21 | TEQ | 2019-12-31 | Karn |  |  | 138 |  |  | Upgrade terminal equipment at Karn | MI |  |  | M3_Long Lead Materials | 150000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9932 | 2017-01-09 | METC_14_026 | 21345 | 2017-12-21 | LNrb | 2019-12-31 | Karn | Saginaw River | 1 | 138 |  |  | Rebuild a ~2.7 mile-long portion of the Karn – Saginaw River 138 kV line that is comprised of only 2-3/0 copper conductor in a six-wired configuration utilizing 1431 ACSR conductor on single-circuit, 138 kV structures | MI | 16 |  | M3_Long Lead Materials | 4500000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9932 | 2017-01-09 | METC_14_026 | 21348 | 2017-12-21 | TEQ | 2019-12-31 | Saginaw River |  |  | 138 |  |  | Upgrade terminal equipment at Saginaw River | MI |  |  | M3_Long Lead Materials | 2920000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9932 | 2017-01-09 | METC_14_026 | 21347 | 2017-12-21 | TEQ | 2019-12-31 | Karn |  |  | 138 |  |  | Upgrade terminal equipment at Karn | MI |  |  | M3_Long Lead Materials | 162000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9932 | 2017-01-09 | METC_14_026 | 21346 | 2017-12-21 | LNup | 2019-12-31 | Karn | Saginaw River | 1 | 138 |  |  | Remediate the sag limit on the existing 1431 ACSR conductor to at least the planned target summer normal/summer emergency rating of 412 MVA/1724 Amps | MI |  |  | M3_Long Lead Materials | 918000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9956 | 2017-01-09 |  | 21371 | 2018-06-27 | SUB | 2018-12-31 | METC Asset Replacement Program - 2018 |  |  | 345 | 138 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs | MI |  |  | M3_Long Lead Materials | 49398000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | METC | 9959 | 2017-01-09 |  | 21373 | 2018-06-27 | Dist | 2017-12-31 | Blanket for Customer Interconnections 2019 | Throughout System |  | 138 |  |  | Connect interconnecting entities as requested | MI |  |  | M3_Long Lead Materials | 2500000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | METC | 9960 | 2017-01-09 |  | 21374 | 2016-12-20 | SUB | 2019-12-31 | METC Asset Replacement Program - 2019 |  |  | 345 | 138 |  | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | M2a_Pre-Project Approval | 49398000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | METC | 9972 | 2017-01-09 |  | 21389 | 2016-12-20 | RLY | 2017-12-31 | Four Mile |  |  | 138 |  |  | Replace METC relaying and controls at Four Mile Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | M2a_Pre-Project Approval | 3520000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9975 | 2017-01-09 |  | 21393 | 2016-12-20 | RLY | 2017-12-31 | Verona |  |  | 138 |  |  | Replace METC relaying and controls at Verona Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | M2a_Pre-Project Approval | 2940000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9978 | 2017-01-09 |  | 21399 | 2017-12-21 | SUB | 2018-06-30 | Eureka |  |  | 138 |  |  | Replace the Eureka 138 kV circuit switcher 256 with a synchronous breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA | MI |  |  | M3_Long Lead Materials | 510000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 9984 | 2017-01-09 |  | 21407 | 2017-12-21 | SUB | 2018-06-30 | Tittabawassee |  |  | 345 |  |  | Replace the Tittabawassee 345 kV breaker 38H9 with a breaker that has a continuous rating of 3000 amp and a minimum interrupting capability of 40 kA. | MI |  |  | M3_Long Lead Materials | 790000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 10286 | 2017-01-09 | METC_12_001 | 21531 | 2018-06-27 | TEQ | 2018-12-31 | Campbell |  |  | 138 |  |  | Remove the Campbell 508 disconnect switch. Modify the relaying to remove 588 breaker sparing capability. | MI |  |  | M3_Long Lead Materials | 88000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21673 | 2018-03-27 | SUB | 2019-12-31 | Michigan Ave 138kV |  |  | 138 |  |  | Install 2-138 kV line breakers and associated disconnect switches, along with a new control house at Michigan Ave substation | MI |  |  | M3_Long Lead Materials | 2137000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21744 | 2018-03-27 | LN | 2019-12-31 | Batavia | Wagner | 1 | 138 |  |  | Line created by looping the Alder Creek-Batavia 138 kV circuit into Wagner substation. | MI |  | 0.1 | M3_Long Lead Materials | 412000 | Planning |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21743 | 2018-03-27 | LN | 2019-12-31 | Alder Creek | Wagner | 1 | 138 |  |  | Line created by looping the Alder Creek-Batavia 138 kV circuit into Wagner substation. | MI |  | 0.1 | M3_Long Lead Materials | 412000 | Planning |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21742 | 2018-03-27 | LN | 2019-12-31 | Newton | Wagner | 1 | 138 |  |  | Construct an approx. 13 mile, 138 kV line, on new future double circuit structures, using 954 ACSR between Newton and Wagner substations | MI |  | 13 | M3_Long Lead Materials | 26117000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21741 | 2018-03-27 | RLY | 2019-12-31 | Coldwater 138 kV |  |  | 138 |  |  | Upgrade relaying on pos. 3040 @ Coldwater substation. | MI |  |  | M3_Long Lead Materials | 188000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21740 | 2018-03-27 | RLY | 2019-12-31 | Batavia 138 kV |  |  | 138 |  |  | Upgrade relaying at pos. BM37 @ Batavia substation | MI |  |  | M3_Long Lead Materials | 21000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 10323 | 2018-03-27 |  | 21739 | 2018-03-27 | SUB | 2019-12-31 | Wagner 138 kV |  |  | 138 |  |  | Add a 138 kV, 3 breaker substation laid out in a ring bus configuration named Wagner, in Union City, MI | MI |  |  | M3_Long Lead Materials | 5122000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 11243 | 2018-03-27 | METC_15_019 | 21747 | 2018-03-27 | LNrb | 2018-12-31 | Verona | Barnum Creek Jct. |  | 138 |  |  | Rebuild the Verona – Barnum Creek Jct. section of the Verona – Batavia 138 kV circuit using 954 ACSR and OGPW on new 230 kV future double circuit structures. Replace PTS 3186. Upgrade terminal equipment at the Verona station. | MI | 6.2 |  | M4_Pre-Construction | 13300000 | Engineering |  | N | N | N
A in MTEP16 | A | East | METC | 11243 | 2018-03-27 | METC_15_019 | 21748 | 2018-03-27 | LNrc | 2018-12-31 | Verona | Convis Jct. |  | 138 |  |  | Reconductor approximately 0.6 miles of the Verona – Foundry 138 kV circuit where it shares common structures with the Verona – Batavia 138 kV circuit. | MI | 0.6 |  | M4_Pre-Construction |  |  |  | N | N | N
A in MTEP16 | A | West | MP | 7910 | 2017-01-09 | 5 Line Upgrade | 20153 | 2018-08-30 | LNrc | 2018-12-31 | Brainerd | Mud Lake | 1 | 115 |  | 182 | Reconductor Brainerd - Mud Lake 115 kV Line with 636 ACSR @ 100C | MN | 4.41 | 0 | Under Construction | 2200000 | Planning |  | N | N | N | Y
A in MTEP16 | A | West | MP | 7996 | 2017-01-09 | 15 Line Upgrade | 20269 | 2018-04-03 | LNrb | 2019-11-01 | FondDuLac | Hibbard | 1 | 115 |  | 122 | Fond Du Lac - Hibbard 115 kV Line | MN | 11.3 | 0 | Under Construction | 10000000 | Planning Preliminary |  | N | N | N | Y
A in MTEP16 | A | West | MP | 7997 | 2017-01-09 | 15th Ave West | 20938 | 2017-09-19 | CB | 2018-05-01 | 15th Avenue West |  |  | 115 |  |  | 115 kV "21-71MW" breaker replacement | MN | 0 | 0 | Under Construction | 250000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 7997 | 2017-01-09 | 15th Ave West | 20276 | 2017-09-19 | CB | 2018-12-31 | 15th Avenue West |  | 1 | 115 |  |  | 115 kV "21L" breaker replacement | MN | 0 | 0 | Under Construction | 250000 | Planning |  | N | N | N | Y
A in MTEP16 | A | West | MP | 7997 | 2017-01-09 | 15th Ave West | 20274 | 2017-09-19 | CB | 2018-12-31 | 15th Avenue West |  | 1 | 115 |  |  | 115 kV "71L" breaker replacement | MN | 0 | 0 | Under Construction | 250000 | Planning |  | N | N | N | Y
A in MTEP16 | A | West | MP | 9622 | 2017-01-09 | 83 Line Upgrade | 20940 | 2015-09-04 | TEQ | 2019-06-01 | Boswell |  |  | 230 |  |  | Replace limiting switches at Boswell | MN | 0 | 0 | Proposed | 250000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9622 | 2017-01-09 | 83 Line Upgrade | 20941 | 2015-09-04 | TEQ | 2019-06-01 | Blackberry |  |  | 230 |  |  | Replace limiting switches at Blackberry | MN | 0 | 0 | Proposed | 250000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20945 | 2018-04-03 | SwSta | 2019-07-01 | Nemadji |  |  | 115 |  |  | NEW Nemadji Switching Station | WI | 0 | 0 | Under Construction | 4630000 | Engineering |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20953 | 2018-04-03 | LN | 2019-07-01 | Nemadji | Gary | 1 | 115 |  | 235 | Extend existing 115 kV line from Gary into Nemadji | WI | 0 | 0.08 | Under Construction | 50000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20952 | 2018-04-03 | LN | 2019-07-01 | Nemadji | Enbridge South | 1 | 115 |  | 182 | Nemadji - South 115 kV Line | WI | 0 | 0.2 | Under Construction | 100000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20951 | 2018-04-03 | LN | 2019-07-01 | Enbridge East | Enbridge South | 1 | 115 |  | 182 | Replace switch structure in East - South 115 kV Line | WI | 0 | 0 | Under Construction | 150000 | Engineering |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20950 | 2018-04-03 | LN | 2019-07-01 | Enbridge North | Enbridge East |  | 115 |  | 182 | North - East 115 kV Line (partial double ckt with Nemadji - Stinson) | WI | 0 | 0.72 | Under Construction | 200000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20949 | 2018-04-03 | LN | 2019-07-01 | Nemadji | Enbridge North | 1 | 115 |  | 182 | Nemadji - North 115 kV Line (double ckt with Nemadji - Stinson) | WI | 0 | 0.64 | Under Construction | 150000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20948 | 2018-04-03 | LN | 2019-07-01 | Nemadji | Stinson | 1 | 115 |  | 235 | Nemadji - Stinson 115 kV Line (double circuit with Nemadji - North - East) | WI | 0 | 1.2 | Under Construction | 1500000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20947 | 2018-04-03 | TEQ | 2019-07-01 | Various Customer-Owned |  |  | 115 |  |  | Enbridge Substation Modifications | WI | 0 | 0 | Under Construction | 1530000 | Engineering |  | N | N | N
A in MTEP16 | A | West | MP | 9625 | 2017-01-09 | Nemadji | 20946 | 2018-04-03 | CAP | 2019-07-01 | Nemadji |  |  | 115 |  |  | Nemadji Cap Bank | WI | 0 | 0 | Under Construction | 380000 | Engineering |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21570 | 2018-04-03 | BUS | 2020-12-31 | Laskin |  |  | 115 |  | 144 | Remove 138/115 kV transformer and bus through transformer position to reconnect Laskin - Hoyt Lakes 115 kV Line (43 Line) | MN | 0 | 0 | Planned | 100000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21584 | 2018-04-03 | CAP | 2020-12-31 | Hoyt Lakes |  |  | 115 |  | 20 | New 2x20 MVAr cap bank at Hoyt Lakes Substation | MN | 0 | 0 | Planned | 400000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21575 | 2018-04-03 | BUS | 2020-12-31 | Taconite Harbor |  |  | 115 |  |  | Convert Taconite Harbor 138 kV Main Bus to 115 kV and connect to existing 115 kV bus | MN | 0 | 0 | Planned | 419000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21574 | 2018-04-03 | TEQ | 2020-12-31 | Hoyt Lakes |  |  | 115 |  |  | Replace 138 kV equipment with 115 kV | MN | 0 | 0 | Planned | 250000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21573 | 2018-04-03 | TX | 2020-12-31 | Hoyt Lakes |  |  | 115 | 13.8 | 50 | Replace existing Hoyt Lakes 138/13.8 kV transformer with 115/13.8 kV transformers (customer-funded) | MN | 0 | 0 | Planned | 1000000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21572 | 2018-04-03 | TX | 2020-12-31 | Skibo |  |  | 115 | 13.8 | 33.6 | Replace Skibo 138/13.8 kV transformer with a 115/13.8 kV transformer (Relocate existing) | MN | 0 | 0 | Planned | 65000 | Planning |  | N | N | N
A in MTEP16 | A | West | MP | 10383 | 2018-01-25 | Voltage Conversion | 21571 | 2018-04-03 | TEQ | 2020-12-31 | Skibo |  |  | 115 |  |  | Replace 138 kV equipment with 115 kV | MN | 0 | 0 | Planned | 250000 | Planning |  | N | N | N
A in MTEP16 | A | West | OTP | 9990 | 2017-01-09 |  | 21415 | 2016-09-27 | RLY | 2017-12-31 | Devils Lake East 41.6 |  |  | 41.6 |  |  | Relay upgrades | ND |  |  | Planned | 37500 | Planning |  | N | N | N
A in MTEP16 | A | West | OTP | 10007 | 2017-09-26 |  | 21431 | 2017-09-26 | LNrb | 2019-12-31 | Max 41.6 kV | Ryder 41.6 kV | 1 | 41.6 |  |  | To correct this material failure problem with the conductor, a project has been scoped and scheduled out for four years. The project will start in 2015 and be completed in 2018. The project will replace failing insulation, cross arms and poles identified through patrols and inspections and replace the failing 1/0 ACSR conductor for approximately 34 miles between Max, ND and Ryder, ND. | ND | 34 |  | Planned | 2500000 | Planning |  | N | N | N
A in MTEP16 | A | Central | PPI | 9564 | 2017-12-21 | 2016-12,38,39,43 | 20933 | 2017-12-21 | SwSta | 2022-12-31 | Athens Tap |  |  | 69 |  |  | Athens Tap 69 kV breaker station to sectionalize the Amos-Athens-East Lanesville 69 kV line | IL |  |  | Planned | 2204000 | Budgetary |  | N | N | N
A in MTEP16 | A | Central | PPI | 9564 | 2017-12-21 | 2016-12,38,39,43 | 20932 | 2017-12-21 | SUB | 2022-12-31 | Athens 138 kV | Athens 69 kV |  | 138 | 69 | 75 | Athens 138/69 kV substation | IL |  |  | Planned | 4653000 | Budgetary |  | N | N | N
A in MTEP16 | A | Central | PPI | 9564 | 2017-12-21 | 2016-12,38,39,43 | 20931 | 2017-12-21 | LN | 2022-12-31 | Turris W-ICG Viper Mine | Athens | 1 | 138 |  | 229 | New 138 kV transmission line | IL |  |  | Planned | 5316000 | Budgetary |  | N | N | N
A in MTEP16 | A | Central | Vectren | 4393 | 2017-06-30 | 2013SIGE7 | 8410 | 2018-09-13 | LNrb | 2019-12-31 | Dubois 69 | Huntingburg 69 | 67-2 | 69 |  | 103 MVA | Rebuild and Reconductor approx. 3.5 miles | IN | 3.54 | 0 | Planned | 2625000 | Planning |  | N | N | N | Y
A in MTEP16 | A | Central | Vectren | 9946 | 2017-06-30 | 2016SIGE11 | 21392 | 2018-03-29 | Dist | 2019-12-31 | ANGEL MOUNDS | HEIDELBACH | Z85 | 138 | 12 |  | 138kV/69kV/12kV Substation | IN |  |  | M3_Long Lead Materials | 4000000 | Budgetary |  | N | N | N
A in MTEP16 | A | Central | Vectren | 9952 | 2017-06-30 | 2016SIGE13 | 21400 | 2018-03-29 | LN | 2019-12-31 | HEIDELBACH | PIGEON CREEK | Y43 | 69 |  |  | Y43 69kV loop to Berry substation | IN |  |  | M3_Long Lead Materials | 1850000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | WPSC | 4385 | 2017-01-09 | BP-FV | 8400 | 2015-09-15 | LNrb | 2018-12-31 | Burnips | Drenthe | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 10.5 |  | Proposed | 3150000 | Planning |  | N | N | N | Y
A in MTEP16 | A | East | WPSC | 4385 | 2017-01-09 | BP-FV | 8401 | 2013-12-16 | LNrb | 2018-12-31 | Drenthe | Fairview | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 1.1 |  | Proposed | 350000 |  |  | N | N | N | Y
A in MTEP16 | A | East | WPSC | 9899 | 2017-01-09 | RW-SV Rebuild | 21302 | 2015-09-15 | LNrb | 2018-12-31 | Redwood | Crystal Valley Junction | 1 | 69 |  | 143.4 | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor | MI | 6.92 |  | Proposed | 3075000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | WPSC | 9899 | 2017-01-09 | RW-SV Rebuild | 21305 | 2015-09-15 | LNrb | 2018-12-31 | Riverton | Scottville | 1 | 69 |  |  | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor | MI | 0.1 |  | Proposed | 500000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | WPSC | 9899 | 2017-01-09 | RW-SV Rebuild | 21304 | 2016-09-15 | LNrb | 2018-12-31 | Eden | Riverton | 1 | 69 |  |  | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor | MI | 6.12 |  | Proposed | 3325000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | WPSC | 9899 | 2017-01-09 | RW-SV Rebuild | 21303 | 2015-09-15 | LNrb | 2018-12-01 | Crystal Valley Junction | Eden | 1 | 69 |  | 143.4 | Rebuild the Redwood to Scottville 69kV line, install new poles and hardware with 795ACSS conductor | MI | 7.45 |  | Proposed | 3600000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | WPSC | 9915 | 2017-01-09 | OE Relay Upgrade | 21329 | 2015-09-15 | RLY | 2017-12-31 | Oden |  |  | 69 |  |  | Upgrade relaying at Oden on the Oden - Emmet terminal | MI |  |  | Proposed | 35000 | Budgetary |  | N | N | N
A in MTEP16 | A | East | WPSC | 11023 | 2017-01-09 |  | 21706 | 2018-03-21 | SUB | 2018-10-31 | Gaylord (WPSC) |  |  | 138 |  |  | Phase II - Convert Gaylord 138kV bus to 6 breaker ring bus design to accommodate 2nd 138/69kV transformer. | MI |  |  | Planned | 2244651 | Budgetary |  | N | N | N
A in MTEP16 | A | West | XEL | 4696 | 2017-01-09 |  | 8880 | 2018-09-28 | LNrb | 2019-05-01 | Prentice | Medford |  | 69 |  | 71.7 | Rebuild this line to 795 ACSR due to age and condition of the line | WI | 33.5 |  | Under Construction | 4449013 |  |  | N | N | N | Y
A in MTEP16 | A | West | XEL | 10045 | 2017-01-09 |  | 21484 | 2018-06-27 | SUB | 2018-12-01 | City of Chaska |  |  | 115 |  |  | This is the new substation associated with the City of Chaska's new interconnection. | MN |  |  | Under Construction | 1200000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10045 | 2017-01-09 |  | 21527 | 2018-06-27 | TAP | 2018-11-15 | Bluff Creek | City of Chaska |  | 115 |  |  | Install line tapping double circuit South of Bluff Creek to new City of Chaska Sub | MN |  |  | Under Construction | 2000000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10069 | 2017-01-09 |  | 21545 | 2017-06-24 | SUB | 2019-12-15 | Twin Creek |  |  | 69 |  |  | Install a 2 position 69 kV breaker station | WI |  |  | Planned | 2866000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10074 | 2017-01-09 |  | 21536 | 2017-06-24 | LNrb | 2020-12-15 | Airport | Rogers Lake |  | 115 |  |  | rebuilds the Airport - Rogers Lake 115 kV line using 795 ACSS conductor. | MN | 3.4 |  | Planned | 4092000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10076 | 2017-01-09 |  | 21535 | 2018-06-29 | LNrb | 2023-12-31 | West St. Cloud | Milwood Tap |  | 69 |  |  | Rebuild 24 miles of line from West St. Cloud to Millwood Tap using 477 ACSR conductor. | MN | 24 |  | Planned | 10400000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10288 | 2017-01-09 |  | 21550 | 2018-06-28 | SUB | 2018-12-30 | Osprey |  |  | 69 |  |  | Install 69 kV straight bus with 3 x 69 kV breakers | WI |  |  | Under Construction | 1850000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10288 | 2017-01-09 |  | 21552 | 2018-06-28 | LN | 2018-12-30 | Osprey | Whitetail Tap |  | 69 |  |  | Reterminate line from Whitetail Tap into Osprey. Rebuild last 0.4 miles of 69 kV line | WI |  |  | Under Construction | 710000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10288 | 2017-01-09 |  | 21551 | 2018-06-28 | LN | 2018-12-30 | Osprey | Flambeau |  | 69 |  |  | Reterminate line from DPC Flambeau | WI |  |  | Under Construction | 320000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10289 | 2017-01-09 |  | 21554 | 2018-09-28 | LNrb | 2018-10-15 | Comfort | Eau Galle | 1 | 69 |  |  | Rebuild the existing 2/0 conductor to 477 ACSR due to age and condition | WI |  |  | Under Construction | 3000000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 10291 | 2017-01-09 |  | 21556 | 2017-02-23 | SUB | 2019-12-01 | Stasik | LCO Hydro |  | 34.5 | 23.9 |  | Install single 34.5/23.9 kV TR to connect the Lac Courte Oreilles (LCO) hydro facility to the NCP system near Radisson | WI |  |  | Planned | 180000 |  |  | N | N | N
A in MTEP16 | A | West | XEL | 11883 | 2017-01-09 |  | 21853 | 2017-06-26 | SUBmisc | 2022-01-01 | Wilmarth |  |  | 345 |  |  | Substation modifications at Wilmarth | MN |  |  | Planned | 2471713 |  | Generator | N | Y | Y | Y
A in MTEP15 | A | South | AECC | 8320 | 2015-12-28 |  | 20638 | 2018-09-14 | SwSta | 2019-05-15 | EAI El Dorado - Monticello East 115 kV line |  |  | 115 |  |  | Switching station needed to tap Entergy line | AR |  |  | Planned | 4000000 |  |  | N | N | N
A in MTEP15 | A | South | AECC | 8320 | 2015-12-28 |  | 20640 | 2018-09-14 | SUB | 2019-05-15 | 115 kV radial tap |  |  | 115 | 13.2 |  | Hermitage 115/13.2 kV substation | AR |  |  | Planned | 2000000 |  |  | N | N | N
A in MTEP15 | A | South | AECC | 8320 | 2015-12-28 |  | 20639 | 2018-08-22 | LN | 2019-05-15 | EAI El Dorado - Monticello East 115 kV line | Hermtage 115/13.2 kV substation |  | 115 |  |  | 1.6 miles of 115 kV line | AR |  |  | Planned | 2060000 |  |  | N | N | N
A in MTEP15 | A | South | AECC | 8402 | 2018-08-22 |  | 20661 | 2018-08-22 | LN | 2022-12-01 | Camden South |  |  | 115 |  |  | 7 mile 115kV transmission line from existing Camden South delivery point/substation to the proposed Camden West substation. | AR |  | 7 | Planned | 3950000 |  |  | N | N | N
A in MTEP15 | A | South | AECC | 8402 | 2018-08-22 |  | 20662 | 2018-08-22 | SUB | 2022-12-01 | 115kV line |  |  | 115 | 13.2 |  | 115/13.2 kV substation | AR |  |  | Planned |  |  |  | N | N | N
A in MTEP15 | A | South | AECC | 8420 | 2017-10-25 |  | 20664 | 2018-08-23 | LN | 2018-10-01 | Pocahontas North | Ingram |  | 161 |  |  | 7 mile radial 161kV transmission line from Entergy's Pocahontas North station to the new Clay County Ingram substation | AR |  | 7 | Proposed | 3611500 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | South | AECC | 8420 | 2017-10-25 |  | 20665 | 2018-08-23 | Dist | 2019-10-31 | Ingram |  |  | 161 | 24.9 |  | new 161/25kV substation with initial projected load of 12,000kW. Uncertain at the moment of the transformer size. Will likely be a 12/16/20 MVA. | AR |  |  | Proposed | 4000000 | Engineering Preliminary |  | N | N | N
A in MTEP15 | A | South | AECC | 8480 | 2015-12-28 |  | 20676 | 2015-07-09 | LN | 2017-01-01 | Marmaduke 161 kV | Gainesville | 1 | 161 |  | 57.7 MVA | 10-mile, 336 ACSR 26/7 161 kV transmission line. | AR |  |  | Conceptual | 2000000 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | South | AECC | 8480 | 2015-12-28 |  | 20677 | 2015-07-09 | Dist | 2017-01-01 | Gainesville |  |  | 161 | 13.2 | 12/16/20 MVA | 161/13.2 kV distribution substation | AR |  |  | Conceptual | 5000000 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | Central | AmerenIL | 7825 | 2015-12-28 |  | 20096 | 2018-09-27 | SwSta | 2019-06-01 | Mascoutah Municipal (Hilgard) |  |  | 138 |  |  | Install a 4-breaker 138 kV ring bus (2000 A, 40 kA) at or near the tap to Mascoutah Municipal on the existing Turkey Hill-Ashley 138 kV Line 1482. | IL |  |  | Under Construction | 6700000 | Engineering |  | N | N | N
A in MTEP15 | A | Central | AmerenIL | 8054 | 2018-03-28 |  | 20351 | 2018-03-29 | LNrc | 2040-12-01 | Tilden Jct | Sparta |  | 138 |  |  | Reconductor 5.7 miles of line | IL | 5.7 |  | Proposed | 2710721 | Planning Preliminary |  | N | N | N | Y
A in MTEP15 | A | Central | AmerenIL | 8055 | 2018-03-28 |  | 20352 | 2018-03-29 | LNrc | 2040-12-01 | Sparta Tap | Steelville |  | 138 |  |  | Reconductor 7.4 miles of line | IL | 7.4 |  | Proposed | 2318247 | Planning Preliminary |  | N | N | N | Y
A in MTEP15 | A | Central | AmerenIL | 8134 | 2015-12-28 |  | 20488 | 2015-04-01 | LNrc | 2015-12-01 | Tilden Jct | Tilden |  | 138 |  |  | Reconductor one span of line | IL |  |  | Proposed | 175920 | Planning Preliminary |  | N | N | N | Y
A in MTEP15 | A | Central | AmerenIL | 8581 | 2015-12-28 |  | 20686 | 2016-10-19 | TEQ | 2017-03-02 | Vermillion |  |  | 138 |  |  | Increase of wind farm capacity to 250 MW | IL |  |  | Planned |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 4421 | 2015-12-28 | PR06011 | 8441 | 2018-03-30 | LN | 2018-12-31 | Elkhorn | Williams Bay | 1 | 138 |  | 197 | Loop Elkhorn - Brick Church (X-44) 138kV line into Williams Bay | WI | 7.67 |  | Under Construction |  | Engineering |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4421 | 2015-12-28 | PR06011 | 8444 | 2018-03-30 | CB | 2018-12-31 | Williams Bay |  |  | 138 |  |  | Add line breaker to Brick Church - Williams Bay (X-44) 138kV line at Williams Bay | WI |  |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4421 | 2015-12-28 | PR06011 | 8443 | 2018-03-30 | CB | 2018-12-31 | Williams Bay |  |  | 138 |  |  | Add line breaker to Elkhorn - Williams Bay (X-44) 138kV line at Williams Bay | WI |  |  | Under Construction | 4200000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4421 | 2015-12-28 | PR06011 | 8442 | 2018-03-30 | LN | 2018-12-31 | Brick Church | Williams Bay | 1 | 138 |  | 188 | Loop Elkhorn - Brick Church (X-44) 138kV line into Williams Bay | WI | 6.62 |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4732 | 2015-12-28 | PR06105 | 8969 | 2018-06-29 | LN | 2021-01-12 | Ogden St. | Bayshore | 1 | 69 |  | 123 | Construct a new 69kV line from Ogden St. - Bayshore | WI |  | 0.54 | Planned | 10400000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4732 | 2015-12-28 | PR06105 | 8973 | 2018-06-29 | CB | 2021-01-12 | Ogden St. |  |  | 69 |  |  | Odgen St. - Bayshore 69kV breaker | WI |  |  | Planned |  |  |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4732 | 2015-12-28 | PR06105 | 8972 | 2018-06-29 | CB | 2021-01-12 | Ogden St. |  |  | 69 |  |  | Odgen St. - Wells St. 69kV breaker | WI |  |  | Planned |  |  |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4732 | 2015-12-28 | PR06105 | 8971 | 2018-06-29 | LNrb | 2021-01-12 | 2nd St. | Fiber swtiching structure | 1 | 69 |  | 123 | Rebuild 2nd St. - Fiber switching structure (N-14) 69kV | WI | 0.59 |  | Planned |  |  |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 4732 | 2015-12-28 | PR06105 | 8970 | 2018-06-29 | LNrb | 2021-01-12 | Bayshore | 2nd St. | 1 | 69 |  | 123 | Rebuild Bayshore - 2nd St. (N-14) 69kV | WI | 0.15 |  | Planned |  |  |  | N | N | N | Y
A in MTEP15 | A | West | ATC | 7602 | 2015-12-28 | PR05440 | 20037 | 2018-03-30 | LNup | 2019-11-01 | Bunker Hill | Kelly | 1 | 115 |  | 145 | Rerate Bunker Hill - Kelly 115 kV as part of Blackbrook/Bunker Hill retirment (PR05440) | WI | 19.47 |  | Planned | 3100000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20038 | 2018-06-29 | Remove | 2019-05-01 | Blackbrook |  |  | 115 |  |  | Retire Blackbrook 115 kV station | WI |  |  | Under Construction | 29724000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20044 | 2018-06-29 | LNrb | 2019-05-01 | Roehring Rd | Pine | 1 | 115 |  | 145 | Rebuild M-13b Pine - Roehring Rd 115 kV with double circuit structures | WI | 10.89 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20043 | 2018-06-29 | LNrb | 2019-05-01 | Roehring Rd | Kelly | 1 | 115 |  | 145 | Rebuild M-13a Kelly - Roehring Rd 115 kV | WI | 19.47 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20042 | 2018-06-29 | LNrb | 2019-05-01 | Roehring Rd | Antigo | 1 | 115 |  | 145 | Rebuild A-313b Antigo - Roehring Rd 115kV | WI | 5.85 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20041 | 2018-06-29 | LNrb | 2019-05-01 | Roehring Rd | Gardner Park | 1 | 115 |  | 145 | Rebuild A-313a Gardner Park - Roehring Rd 115kV with double circuit structures | WI | 34.33 |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20040 | 2018-06-29 | SwSta | 2019-05-01 | Roehring Rd |  |  | 115 |  |  | Build new 115 kV 4 position ring bus named Roehring Rd | WI |  |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 7603 | 2015-12-28 | PR05440 | 20039 | 2018-06-29 | Remove | 2019-05-01 | Bunker Hill |  |  | 115 |  |  | Retire Bunker Hill 115 kV station | WI |  |  | Under Construction |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ATC | 8660 | 2017-09-15 | PR07030 | 20719 | 2018-03-30 | TX | 2018-12-14 | Somers |  | 2 | 138 | 24.9 | 66 | 2nd Somers distribution transformer | WI |  |  | Planned | 4000000 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ATC | 8660 | 2017-09-15 | PR07030 | 20721 | 2018-03-30 | CB | 2018-12-14 | Albers |  |  | 138 |  |  | New line breaker from Albers to Somers. | WI |  |  | Planned |  | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ATC | 8660 | 2017-09-15 | PR07030 | 20720 | 2018-03-30 | CB | 2018-12-14 | Albers |  | 1 | 138 |  |  | New line breaker for Bain - Albers | WI |  |  | Planned |  | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ATC | 9080 | 2016-12-30 | PR07203, F4691, WO601606 | 20810 | 2018-03-30 | CB | 2019-03-31 | W. Marinette |  | 2 | 138 |  |  | Install high and low side breakers on existing 138/69 kV transformer on circuit 2. | WI |  |  | Planned | 2200000 | Planning |  | N | N | N
A in MTEP15 | A | West | ATC | 9080 | 2016-12-30 | PR07203, F4691, WO601606 | 20812 | 2018-03-30 | CB | 2019-03-31 | W. Marinette |  | 1 | 138 |  |  | Install W. Marinette 138-69 kV transformer high-side protection on circuit 1. | WI |  |  | Planned |  | Planning |  | N | N | N
A in MTEP15 | A | Central | BREC | 3435 | 2015-12-28 | LRP1 | 6338 | 2010-11-15 | LNrc | 2017-12-31 | Rome Junction | West Owensboro | 1 | 69 |  | 72 MVA | reconductor line | KY | 5.8 | 0 | Proposed | 440000 | Planning |  | N | N | N | NT
A in MTEP15 | A | Central | BREC | 3436 | 2015-12-28 | LRP2 | 6339 | 2010-11-15 | LN | 2018-12-31 | Wilson | Sacremento | 1 | 69 |  | 72 MVA | new line | KY | 0 | 11 | Proposed | 2100000 | Planning |  | N | N | N | NT
A in MTEP15 | A | Central | BREC | 3437 | 2015-12-28 | LRP3 | 6340 | 2010-11-15 | LNrc | 2018-12-31 | Thruston Junction | East Owensboro | 1 | 69 |  | 67 MVA | reconductor line | KY | 0.4 | 0 | Proposed | 40000 | Planning |  | N | N | N | NT
A in MTEP15 | A | Central | BREC | 3438 | 2015-12-28 | LRP4 | 6341 | 2010-11-15 | LNrc | 2018-12-31 | Daviess County | Philpot Tap | 1 | 69 |  | 72 MVA | reconductor line | KY | 7.7 | 0 | Proposed | 580000 | Planning |  | N | N | N | NT
A in MTEP15 | A | Central | BREC | 3441 | 2015-12-28 | LRP7 | 6344 | 2014-06-10 | LNrc | 2015-12-31 | Olivet Church Road | Olivet Church Road Tap | 1 | 69 |  | 72 MVA | reconductor line | KY | 1.4 | 0 | Proposed | 150000 | Planning |  | N | N | N | NT
A in MTEP15 | A | Central | BREC | 3444 | 2015-12-28 | LRP10 | 6347 | 2014-06-10 | TX | 2015-12-31 | Meade County 161 kV | Meade County 69 kV |  | 161 | 69 | 56 MVA | new transformers | KY |  |  | Proposed | 4000000 | Planning |  | N | N | N | Y
A in MTEP15 | A | Central | BREC | 9420 | 2015-12-28 |  | 21557 | 2015-11-05 | LINE | 2017-03-31 | Coleman EHV | Aleris (LAM1) |  | 161 |  |  | Construction of a 1.7 mile long 161 kV radial circuit from Coleman EHV to serve the 28 MW load at the existing 161/13.8 kV delivery point. | KY |  | 1.7 | Planned | 640000 | Planning |  | N | N | N | Y
A in MTEP15 | A | Central | BREC | 9420 | 2015-12-28 |  | 21562 | 2016-01-12 | TEQ | 2017-03-31 | Coleman EHV |  |  | 161 |  |  | Terminal equipment and breakers will be installed at Coleman EHV 161 kV to accommodate service to the direct-serve Aleris loads (LAM1 & LAM2). | KY |  |  | Planned | 1150000 | Planning |  | N | N | N
A in MTEP15 | A | Central | BREC | 9420 | 2015-12-28 |  | 21561 | 2015-11-05 | SUB | 2017-03-31 | Aleris (LAM2) | Coleman EHV |  | 161 |  |  | This substation will provide the planned 33 MW direct-serve load expansion at Aleris (LAM2). The existing 28 MW direct-serve load will be served from the existing Aleris (LAM1) substation. Both circuits will normally be fed from Coleman EHV 161 kV. In the event of an emergency, existing backup service feeds from the Hancock 161 kV substation remain available. | KY |  |  | Planned | 7000000 | Planning |  | N | N | N
A in MTEP15 | A | Central | BREC | 9420 | 2015-12-28 |  | 21558 | 2015-11-05 | LINE | 2017-03-31 | Coleman EHV | Aleris (LAM2) |  | 161 |  |  | Construction of a 2 mile 161 kV circuit to provide service to a new 161/13.8 kV delivery point necessary to serve the expanded load . | KY |  | 2 | Planned | 760000 | Planning |  | N | N | N | Y
A in MTEP15 | A | Central | BREC | 10142 | 2018-06-22 |  | 21472 | 2017-05-22 | TEQ | 2021-01-01 | Coleman |  |  | 345 |  |  | Sub upgrades at Coleman | KY |  |  | Planned | 5200000 | Planning Preliminary |  | N | Y | Y | Y
A in MTEP15 | A | Central | BREC, Vectren | 10142 | 2018-06-22 |  | 21471 | 2018-04-25 | LN | 2021-01-01 | Duff | Coleman |  | 345 |  |  | New Duff-Coleman 345 kV, single circuit. MISO portion is 2 segments - 24.5 and 4 miles, cut into by double circuit PJM section to Rockport | IN,KY |  | 31 | Planned | 53848417 | Planning Preliminary |  | N | Y | Y | Y
A in MTEP15 | A | South | CLECO | 7988 | 2015-12-28 | 15-ELL-001 | 20260 | 2018-09-26 | SUB | 2019-06-30 | Bayou Vista 230 | Bayou Vista 138 kV | 1 | 230 | 138 | 500 MVA | CLECO will expand Bayou Vista substation to 230 kV and install 230-138 kV autotransformer | LA |  |  | Under Construction | 64736816 | Planning |  | N | N | N
A in MTEP15 | A | Central | DEI | 7882 | 2015-12-28 | AMIN1047 | 20111 | 2018-06-28 | LN | 2018-11-07 | Bloomington Rogers St. | Bloomington Dunn St. | 1 | 69 |  | 153 | Construct new 69kV line from Bloomington Rogers St. to Bloomington Dunn St. (also includes Dunn St. bus work - AMIN1046) 954ACSR@100C | IN |  | 3 | Under Construction | 4820000 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7883 | 2015-12-28 | AMIN1093 | 20112 | 2018-09-27 | Dist | 2018-12-01 | Bloomington Downtown | new distribution sub |  | 69 | 12 |  | Construct new 22.4MVA - 69/12kV sub near downtown Bloomington in the new line established by project AMIN1047 / 7882. | IN |  |  | Under Construction | 602000 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7885 | 2015-12-28 | AMIN1052 | 20115 | 2018-06-28 | LNrc | 2018-10-01 | Frankfort Burlington St. | Middlefork | 1 | 69 |  | 153 | Frankfort Burlington St to Middlefork 69kV - 69133 ckt: Reconductor 12.4 miles with 954ACSR@100C | IN | 12.4 |  | Under Construction | 6636000 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7903 | 2015-12-28 | AMIN0701 | 20140 | 2018-09-26 | LNrc | 2024-06-01 | Martinsville SE | HE Park Ave | 1 | 69 |  | 153 | Martinsville SE - HE Park Ave 69kV - 6903 ckt: Reconductor 3.4 miles with 954ACSR@100C | IN | 3.4 |  | M1_Final SPM or OOC | 2102000 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7911 | 2015-12-28 | AMIN1146 | 20155 | 2018-09-27 | SUB | 2018-12-31 | Frankfort 230kV |  |  | 230 | 69 | 2000A | Frankfort 230kV: complete 4-brkr ring bus; 69kV: complete 6-brkr ring bus and retire Jefferson Jct with new line terminal for 69kV line to Frankfort Muni. | IN |  |  | M4_Pre-Construction | 5109020 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7946 | 2015-12-28 | AMIN1070 | 20197 | 2018-06-28 | LN | 2019-03-01 | Speed | Jeffersonville | 1 | 138 |  | 306 | Loop existing 138kV line from Speed to Clark Maritime to Jeffersonville. Add 2.52 mile 138kV line section from Speed to Memphis Jct and tie into existing 13890 circuit. Add .01 mile 138kV line section from Jeffersonville Jct. to Jeffersonville sub. Install 138kV line terminals at Speed and Jeffersonville. | IN |  | 2.53 | Under Construction | 5472000 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7963 | 2015-12-28 | AMIN1291 | 20226 | 2018-09-27 | CB | 2018-12-31 | New Castle 138 |  |  | 138 |  |  | New Castle 138kV Breaker Replacements: replace OCB 13805, 13835, 13842, 13873, 13869-1, 13869-2, and relays at line terminals 13805, 13835, 13842, 13873, 13843 | IN |  |  | M4_Pre-Construction | 2516322 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7964 | 2015-12-28 | AMIN1292 | 20227 | 2018-09-27 | CB | 2018-12-31 | Kokomo Highland Park |  |  | 138 | 69 |  | Kokomo Highland Park Equipment: Replace OCB 69230-4, -5, -6, -7, OCB BK 7 CAP, 69kV primary UG cables, relays at terminals 6910, 6911, 6913, 6928, 6992, 13879, 13887, 138kV TRANSFER | IN |  |  | Under Construction | 3351124 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 7992 | 2015-12-28 | AMIN1281 | 20265 | 2018-09-27 | LNrc | 2018-12-31 | Hillenbrand Jct | Andersonville Jct | 1 | 69 |  | 100 | Hillenbrand Jct - Batesville North - Andersonville Jct 69kV - 6919 ckt: Rebuild 7.93 mile line with 477ACSR@100C - replacing all structures with steel poles. | IN | 7.93 |  | Under Construction | 6472095 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 9246 | 2015-12-28 | TIN1607 | 20849 | 2018-09-27 | LN | 2019-06-01 | Lafayette Southeast | Lafayette South Jct 2 | 1 | 138 |  | 301 | Lafayette SE to new Lafayette S Jct 2 (in existing 13808 ckt.) - build new 138kV - 1.75 mile - 954acsr@100c - 13899 ckt.; add new breaker in Laf SE ring; add (2) line switches at new jct and operate Laf S Jct to Laf S Jct 2 N.O. | IN |  | 1.75 | M4_Pre-Construction | 3976181 | Engineering w/AFUDC |  | N | N | N
A in MTEP15 | A | Central | DEI | 9247 | 2015-12-28 | TIN1674-AMIN1151 | 20850 | 2018-06-28 | SUB | 2018-12-31 | Lafayette 230kV | bus tie brkr |  | 138 |  |  | Lafayette 230 sub - insert a redundant 138kV bus tie breaker in series with existing breaker; add redundant bus differential relays to both 138kV bus 1 and 2. Scope also includes (5) 138Kv antiquated breaker and relay replacements, disconnect switches and misc buswork. | IN |  |  | Under Construction | 3400000 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | South | Entergy-AR | 4666 | 2015-12-28 | 12-EAI-014 | 8847 | 2018-09-18 | LNrc | 2019-12-01 | Mabelvale 115 kV Substation | Bryant 115 kV Substation | 1 | 115 |  | 390 MVA | Reconductor Line | AR | 5 |  | Planned | 8798431 | Planning |  | N | N | N | Y
A in MTEP15 | A | South | Entergy-AR | 4666 | 2015-12-28 | 12-EAI-014 | 21439 | 2016-09-14 | LNrb | 2019-12-01 | Bryant | Bryant South | 1 | 115 |  |  | 115 kV line | AR |  |  | Planned |  |  |  | N | N | N
A in MTEP15 | A | South | Entergy-AR | 4669 | 2018-02-15 | 11-EAI-015 | 8850 | 2018-09-26 | LNcnv | 2019-05-31 | Jim Hill 161 kV substation | Datto 161 kV Substation | 1 | 161 |  | 363 MVA | rebuild line and convert from 115kV to 161kV operation | AR | 39.3 |  | Under Construction | 64418541 | Planning |  | N | N | N | Y
A in MTEP15 | A | South | Entergy-AR | 4669 | 2018-02-15 | 11-EAI-015 | 8851 | 2018-08-03 | CB | 2019-06-01 | Corning 161 kV Substation |  | 1 | 161 |  | 363MVA | Install breakers at Datto | AR |  |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP15 | A | South | Entergy-LA | 4606 | 2017-10-05 | 14-EGL-004 | 8754 | 2018-09-26 | TX | 2019-04-07 | Fancy Point 500 kV substation | Fancy Point 230 kV substation | 2 | 500 | 230 | 1200 MVA | Add transformer | LA |  |  | Planned | 64346901 | Planning |  | N | N | N | Y
A in MTEP15 | A | South | Entergy-LA | 7923 | 2015-12-28 | 15-EGL-005 | 20178 | 2018-09-26 | LNrc | 2018-11-30 | Lake Charles Bulk 69 kV | Chlomal 69 kV | 1 | 69 |  | 117 MVA | "NERC TPL-001-4 Reliability Standards and Entergy's Planning Guidelines. The Lake Charles Bulk to Chlomal 69 kV line will exceed its thermal rating during the single contingency (P1-2) breaker to breaker loss of the Calcasieu to Pecan Grove 230 kV line or the Lake Charles Bulk to East Broad 69 kV line. This project will result in an increase in the thermal rating of the circuit by upgrading line conductor and station equipment at Lake Charles Bulk." | LA | 3.07 |  | Under Construction | 10201219 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | South | Entergy-LA | 7923 | 2015-12-28 | 15-EGL-005 | 20236 | 2018-09-26 | TEQ | 2018-11-30 | Lake Charles Bulk |  |  | 69 |  | 117 MVA | LC Bulk-Cholmal Upgrade 600 A switches to 1200 A and upgrade line conductor. | LA |  |  | Under Construction |  | Planning |  | N | N | N
A in MTEP15 | A | South | Entergy-LA | 9285 | 2015-12-28 | 15-ELL-005 | 20863 | 2018-09-26 | LNrb | 2019-06-01 | Waterford | Vacherie | 1 | 230 |  |  | Reconductor Waterford to Vacherie 230 kV line. | LA |  |  | Planned | 36631106 |  |  | N | N | N
A in MTEP15 | A | South | Entergy-TX | 9280 | 2015-12-28 | 15-ETI-016 | 20858 | 2018-09-26 | TX | 2020-06-01 | Cypress 500 | Cypress 138 | 2 | 500 | 138 |  | 2nd Cypress 500/138 kV Auto. | TX |  |  | Planned | 17420213 |  |  | N | N | N
A in MTEP15 | A | South | Entergy-TX | 9482 | 2015-12-28 | 15-ETI-023 | 20916 | 2018-09-26 | LN | 2019-05-01 | China 230 | Stowell 230 | 1 | 230 |  |  | New 230 kV line from China to Stowell | TX |  |  | Under Construction | 66172893 | Planning |  | N | N | N
A in MTEP15 | A | South | Entergy-TX | 9482 | 2015-12-28 | 15-ETI-023 | 20917 | 2018-09-26 | TX | 2019-05-01 | Stowell 230 | Stowell 138 | 1 | 230 | 138 | 400 | 230/138 kV Auto Transformer | TX |  |  | Under Construction |  | Planning |  | N | N | N
A in MTEP15 | A | South | Entergy-TX | 10487 | 2017-10-12 | 15-ETI-024; 15-ETI-025 | 21596 | 2018-09-26 | TX | 2020-06-01 | Grimes 345 | Grimes 230 | 2 | 345 | 230 |  | Install 2nd 345/230 Auto | TX |  |  | Planned | 126511689 | Planning |  | N | N | N
A in MTEP15 | A | South | Entergy-TX | 10487 | 2017-10-12 | 15-ETI-024; 15-ETI-025 | 21598 | 2018-09-26 | LNrc | 2019-06-01 | Newton Bulk | Leach | 1 | 138 |  |  | Rebuild Newton Bulk to Leach 138 kV line | TX |  |  | Under Construction | 23733203 | Planning |  | N | N | N
A in MTEP15 | A | South | Entergy-TX | 10487 | 2017-10-12 | 15-ETI-024; 15-ETI-025 | 21597 | 2017-10-12 | LN | 2020-06-01 | Grimes | Lewis Creek | 1 | 230 |  |  | New 230 kV line from Grimes to Lewis Creek | TX |  |  | Planned |  |  |  | N | N | N
A in MTEP15 | A | South | ETEC | 8208 | 2015-12-28 | PRJ 07 | 20596 | 2018-06-29 | LN | 2018-11-01 | TBD | TBD |  | 138 |  |  | Cut into Tarkington-Long John 138 kV line and extend line to Luce Bayou substation. | TX |  |  | Under Construction | 10800000 |  |  | N | N | N
A in MTEP15 | A | South | ETEC | 8208 | 2015-12-28 | PRJ 07 | 20597 | 2018-06-29 | SUB | 2018-11-01 | TBD |  |  | 138 |  |  | Install new Luce Bayou 138 kV in-and-out substation. | TX |  |  | Under Construction | 5500000 |  |  | N | N | N
A in MTEP15 | A | West | GRE | 7912 | 2015-12-28 | 202919 | 20152 | 2017-09-12 | LNrb | 2022-10-21 | Bass Lake | Lawndale | 1 | 115 | 115 |  | Construct two miles of 115 kV line with 795 ACSS conductor from the 3 way switch to the high side structure of new Wright Hennepin Electric Cooperative?s Lawndale #2 distribution substation. | MN | 2 |  | Proposed | 2000000 | Planning Preliminary |  | N | N | N | Y
A in MTEP15 | A | Central | HE | 10343 | 2015-12-28 |  | 21569 | 2015-11-16 | SUB | 2016-06-01 | Hubbell |  |  | 138 |  |  | Construct a 138kV ring bus and add a second 138/69kV transformer | IN |  |  | Planned | 10047000 |  |  | N | N | N | Y
A in MTEP15 | A | Central | IPL | 9402 | 2015-12-28 |  | 20892 | 2015-07-27 | LNup | 2017-07-15 | Guion | Westlane | 40 | 138 |  | 298 | Increase line rating to 298 MVA by increased clearance. | IN | 2.2 |  | Planned |  |  |  | N | N | N
A in MTEP15 | A | West | ITCM | 8042 | 2015-12-28 | Burl Sourth Sub | 20325 | 2015-01-23 | LN | 2016-12-31 | Burlington South |  |  | 69 |  |  | ITC will build new 69kV line taps for the new Burlington South Alliant Energy distribution sub. | IA |  |  | Planned | 60000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8043 | 2015-12-28 | Cust Interconnet Blanket | 20327 | 2018-02-01 | LN | 2018-12-31 | Blanket for Customer Interconnections under $1 million for 2018 | Throughout system |  | 345 | 69 |  | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA,MN,IL |  |  | Under Construction | 2400000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8106 | 2015-12-28 | Hrn Lk Sub & Cap | 20437 | 2017-06-30 | CAP | 2022-12-31 | Heron Lake | Capacitor |  | 161 |  | 42 MVAR | Install two 21MVAR 161kV cap banks | MN |  |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8106 | 2015-12-28 | Hrn Lk Sub & Cap | 20440 | 2017-06-30 | SUB | 2022-12-31 | Heron Lake | Substation |  | 161 | 69 |  | Rebuild the Heron Lake 161kV to a ring bus (convertable to bkr and 1/2) | MN |  |  | Planned | 16929252 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8125 | 2015-12-28 | Anita-Grand Jct Rblds ph1 | 20478 | 2017-11-10 | LN | 2019-02-01 | Anita | Thompson | 1 | 69 |  |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) | IA | 17.6 |  | Planned | 11159322 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8128 | 2015-12-28 | Anita-Grand Jct Rblds ph2 | 20490 | 2018-03-27 | LN | 2018-08-31 | Redfield | Panora REC Tap | 1 | 69 |  |  | Build new 69 kV line (operate at 34kV until 69kV/dist subs are ready) | IA | 10 |  | Planned | 8852758.8 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8128 | 2015-12-28 | Anita-Grand Jct Rblds ph2 | 20502 | 2016-06-28 | LN | 2019-12-31 | Bagley | Perry | 1 | 69 |  |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) | IA | 19 |  | Planned | 11841000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8129 | 2015-12-28 | Anita-Grand Jct Rblds ph3 | 20511 | 2017-11-08 | LN | 2020-12-31 | Jefferson WCC | Scranton Distribution | 1 | 69 |  |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) | IA | 14.5 |  | Planned | 11837228.4 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8132 | 2015-12-28 | Anita-Grand Jct Rblds ph4 | 20516 | 2015-01-21 | LN | 2019-12-31 | Bagley Jct | Scranton | 1 | 69 |  |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) | IA | 16 |  | Planned | 8104200 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8150 | 2015-12-28 | Belle Plaine Conv | 20534 | 2017-10-13 | SUB | 2024-12-31 | Belle Plaine | Substation |  | 161 | 69 |  | Add four 69kV breakers that are needed at Belle Plaine and add a 100MVA 161/69kV transformer. | IA |  |  | Planned | 4891935.6 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8150 | 2015-12-28 | Belle Plaine Conv | 20724 | 2017-10-13 | SUB | 2024-12-31 | 34.5kV substation retirements |  |  | 34.5 |  |  | Retire the 34.5kV substation equipment that is no longer needed. | IA |  |  | Planned | 600000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8150 | 2015-12-28 | Belle Plaine Conv | 20537 | 2018-05-11 | SwSta | 2021-06-15 | Haven | Switch Station |  | 69 | 69 | 143 MVA | Haven Three (3) Terminal 69kV Switch Station | IA |  |  | M2a_Pre-Project Approval | 2987673 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8150 | 2015-12-28 | Belle Plaine Conv | 20536 | 2017-10-13 | SwSta | 2024-12-31 | Belle Plaine South (River Valley) | Switch Station |  | 69 | 69 | 143 MVA | Belle Plaine South (now named River Valley) Three (3) Terminal 69kV Switch Station | IA |  |  | Planned | 3043446 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8150 | 2015-12-28 | Belle Plaine Conv | 20535 | 2017-10-13 | TX | 2024-12-31 | Belle Plaine | Transformer |  | 161 | 69 | 100 MVA | Add a 161/69kV 100MVA transformer at Belle Plaine | IA |  |  | Planned | 0 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ITCM | 8151 | 2015-12-28 | B Plaine-Vinton-Traer | 20538 | 2015-01-21 | SUB | 2025-12-31 | Vinton | Substation |  | 69 |  | 143 MVA | Two additional 69kV breakers are needed at the Vinton substation. | IA |  |  | Planned | 1164487.2 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8151 | 2015-12-28 | B Plaine-Vinton-Traer | 20539 | 2015-01-21 | SUB | 2025-12-31 | Traer | Substation |  | 69 |  | 143 MVA | One additional 69kV breaker is needed at the Traer substation. | IA |  |  | Planned | 768123.6 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8152 | 2015-12-28 | Conroy-Parnell Conv | 20542 | 2015-01-21 | SUB | 2025-12-31 | Parnell | Substation |  | 161 | 69 |  | Three 69kV breakers are needed at the Parnell Substation. | IA |  |  | Planned | 3812623.2 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8152 | 2015-12-28 | Conroy-Parnell Conv | 20543 | 2014-09-15 | TX | 2025-12-31 | Parnell | Transformer | 1 | 161 | 69 | 100 MVA | A new 161/69kV 100MVA transformer is needed at the Parnell Substation. | IA |  |  | Planned | 0 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ITCM | 8153 | 2015-12-28 | Parnell-Keswick Conv | 20544 | 2015-01-21 | SwSta | 2025-12-31 | Keswick | Switch Station |  | 69 |  | 143 MVA | Add a Keswick 3 terminal switch station | IA |  |  | Planned | 2931082.8 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8154 | 2015-12-28 | Fairfax-Marengo Conv | 20545 | 2018-04-26 | SUB | 2023-12-31 | Fairfax | Substation |  | 69 |  |  | Two 69kV breakers are needed at the Fairfax Substation. | IA |  |  | Planned | 1278863 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8154 | 2015-12-28 | Fairfax-Marengo Conv | 20728 | 2018-04-26 | LN | 2023-12-31 | various 34.5kV | various 34.5kV |  | 34.5 |  |  | retire 34.5kV lines that are no longer needed | IA |  |  | Planned | 974404.8 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8154 | 2015-12-28 | Fairfax-Marengo Conv | 20727 | 2018-04-26 | SUB | 2023-12-31 | various 34.5 kV subs |  |  | 34.5 |  |  | retire 34.5kV subs | IA |  |  | Planned | 180000 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8155 | 2015-12-28 | Mtown-Tama-Laurel Conv | 20547 | 2015-01-21 | SUB | 2025-12-31 | Fletcher | Substation |  | 69 |  |  | One (1) 69kV Terminal at Fletcher Substation | IA |  |  | Planned | 367443.6 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8155 | 2015-12-28 | Mtown-Tama-Laurel Conv | 20726 | 2015-01-21 | LN | 2025-12-31 | new switch stations |  |  | 69 |  |  | Perform the 69kV line work for new switch stations for the conversion. | IA |  |  | Planned | 600060 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8155 | 2015-12-28 | Mtown-Tama-Laurel Conv | 20549 | 2018-05-11 | SwSta | 2022-12-31 | Laurel | Switch Station |  | 69 |  |  | Three 69kV breakers and one 69kV bus tie breaker are needed at the Laurel switch station. | IA |  |  | M2a_Pre-Project Approval | 2898200 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8155 | 2015-12-28 | Mtown-Tama-Laurel Conv | 20548 | 2018-05-11 | SwSta | 2019-12-31 | Tama Paper | Switch Station |  | 69 |  |  | Three 69kV line breakers and one 69kV bus tie breaker are needed at the Tama Breaker Substation. | IA |  |  | M3_Long Lead Materials | 3262754 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | 20554 | 2016-06-29 | SwSta | 2021-05-01 | Morgan Valley | Switch Station |  | 345 | 345 |  | Add a new Morgan Valley 345kV three terminal switch station on the Duane Arnold-Tiffin 345kV line. | IA |  |  | Planned | 0 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | 20737 | 2016-06-29 | CAP | 2021-05-01 | Beverly | Capacitor |  | 69 |  | 33 MVAR | Add a 33 MVAR cap on the Beverly 69kV bus | IA |  |  | Planned |  | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | 20559 | 2016-06-29 | SUB | 2021-05-01 | Beverly | Substation |  | 345 | 161 |  | Add a new Beverly 345/161kV substation adjacent to the existing Beverly 161kV sub. Add a 161kV terminal at the existing Beverly sub to tie to the low side (161kV) of the new 345/161kV substation. | IA |  |  | Planned | 14864540.4 | Engineering |  | N | N | N
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | 20558 | 2016-06-29 | TX | 2021-05-01 | New Beverly 345/161kV | Substation | 1 | 345 | 161 | 450 MVA | New Beverly 345/161kV 450MVA autotransformer | IA |  |  | Planned | 0 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | 20557 | 2016-06-29 | SUB | 2021-05-01 | New Beverly 345/161 kV | Substation |  | 345 | 161 |  | Add a new Beverly 345/161kV substation adjacent to the existing Beverly 161kV sub. | IA |  |  | Planned | 0 | Planning Preliminary |  | N | N | N
A in MTEP15 | A | West | ITCM | 8160 | 2015-12-28 | Morgan Valley-Beverly 345 | 20555 | 2016-06-29 | LN | 2021-05-01 | Morgan Valley | New Beverly 345/161kV | 1 | 345 |  |  | Add a new 6.5 mile 345 kV line from the new Morgan Valley Switchstation to a new 345/161 kV substation adjacent to the existing Beverly 161/69/34.5 kV substation. | IA |  | 6.5 | Planned | 23292051.6 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 7892 | 2017-12-21 | ITC_14_028 | 20319 | 2017-12-21 | LN | 2020-06-01 | Hood | Bartlett |  | 120 |  |  | New 120 kV transmission line to loop in Bartlett. | MI |  |  | M2a_Pre-Project Approval | 2490000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 7892 | 2017-12-21 | ITC_14_028 | 20845 | 2017-12-21 | RLY | 2020-06-01 | Bloomfield |  |  | 120 |  |  | Relay Upgrades at Bloomfield | MI |  |  | M2a_Pre-Project Approval | 15000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 7892 | 2017-12-21 | ITC_14_028 | 20844 | 2017-12-21 | RLY | 2020-06-01 | Hood |  |  | 120 |  |  | Relay Upgrades at Hood Substation | MI |  |  | M2a_Pre-Project Approval | 15000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 7892 | 2017-12-21 | ITC_14_028 | 20321 | 2017-12-21 | TAP | 2020-06-01 | Bartlett |  |  | 120 |  |  | New distribution substation | MI |  |  | M2a_Pre-Project Approval | 2910000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 7892 | 2017-12-21 | ITC_14_028 | 20320 | 2017-12-21 | LN | 2020-06-01 | Bloomfield | Bartlett | 1 | 120 |  |  | New 120 kV transmission line to loop in Bartlett Substation | MI |  |  | M2a_Pre-Project Approval | 2490000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 8083 | 2018-06-28 | ITC_14_013 | 20408 | 2018-06-28 | RLY | 2019-12-31 | Cortland |  |  | 120 |  |  | Upgrade limiting relay at Cortland. | MI |  |  | M3_Long Lead Materials | 300000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 8087 | 2018-03-29 | ITC_14_022 | 20411 | 2018-03-29 | CAP | 2025-12-31 | Stratford |  |  | 120 |  |  | 33.3 MVAR capacitor bank at Stratford 120 kV station. | MI |  |  | M2a_Pre-Project Approval | 820000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 8094 | 2015-12-28 | ITC_14_018 | 20422 | 2018-06-27 | TX | 2018-12-31 | Fitz |  | 301 | 345 | 120 |  | Add a 345/120 kV transformer at Fitz Substation | MI |  |  | M4_Pre-Construction | 5500000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 8094 | 2015-12-28 | ITC_14_018 | 20431 | 2018-06-27 | SUB | 2018-12-31 | Fitz |  |  | 345 | 120 |  | Install 345 and 120 kV substation equipment at Fitz to accomodate the installation of the new 345/120 kV transformer and looping the 120 kV Adams to Bunce line into Fitz. | MI |  |  | M4_Pre-Construction | 6500000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 8094 | 2015-12-28 | ITC_14_018 | 20427 | 2018-06-27 | LN | 2018-12-31 | Fitz | Bunce | 1 | 120 |  |  | 120 kV line created by looping the Adams-Bunce 120 kV line into Fitz. This requires approx. 0.1 miles of new double circuit structures in new ROW utilizing 1431 ACSR Conductor. | MI |  | 0.1 | M4_Pre-Construction | 600000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 8094 | 2015-12-28 | ITC_14_018 | 20426 | 2018-06-27 | LN | 2018-12-31 | Adams | Fitz | 1 | 120 |  |  | 120 kV line created by looping the Adams-Bunce 120 kV line into Fitz. This requires approx. 0.1 miles of new double circuit structures in new ROW utilizing 1431 ACSR Conductor. | MI |  | 0.1 | M4_Pre-Construction | 600000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20880 | 2016-12-20 | SUB | 2018-12-31 | Apex (formerly “Blue”) 120/41.6 kV |  |  | 120 | 41.6 |  | Install 3-120 kV breakers w/ associated disconnects in a straight bus configuration, a control house, and all other 120 kV equipment owned by ITCT at Apex (formerly “Blue”) substation. | MI |  |  | M3_Long Lead Materials | 2600000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 21449 | 2016-08-11 | SUBmisc | 2018-12-31 | Lark 120 kV |  |  | 120 |  |  | Upgrade relaying associated with position HI at Lark | MI |  |  | M3_Long Lead Materials | 309000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20887 | 2016-12-20 | LNug | 2018-12-31 | Phoenix | Apex (formerly “Blue”) | 2 | 120 |  |  | Construct a 2.6 mile underground line using 2500 XLPE cable between Phoenix and Apex (formerly “Blue”) to create the Apex-Phoenix #2 line. | MI |  | 2.6 | M3_Long Lead Materials | 39060000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20886 | 2016-12-20 | LNug | 2018-12-31 | Phoenix | Apex (formerly “Blue”) | 1 | 120 |  |  | Construct a 2.6 mile underground line using 2500 XLPE cable between Phoenix and Apex (formerly “Blue”) to create the Apex-Phoenix #1 line. | MI |  | 2.6 | M3_Long Lead Materials | 39060000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20885 | 2017-03-29 | LN | 2019-05-01 | Pioneer | State | 2 | 120 |  |  | Construct 2.7 miles of new double circuit structures and string 954 ACSR on both sides between Pioneer and State (formerly "Maize")to create the State (formerly "Maize") - Pioneer #1 and #2 lines. | MI |  | 2.7 | M2a_Pre-Project Approval | 5252000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20884 | 2017-03-29 | LN | 2019-05-01 | Pioneer | State | 1 | 120 |  |  | Construct 2.7 miles of new double circuit structures and string 954 ACSR on both sides between Pioneer and State (formerly "Maize") to create the State (formerly "Maize") - Pioneer #1 and #2 lines. | MI |  | 2.7 | M2a_Pre-Project Approval | 5252000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20883 | 2016-08-11 | SUB | 2018-12-31 | Phoenix 120/41.6 kV |  |  | 120 | 41.6 |  | Install 2-120 kV line breakers and 1-120 kV section breaker at ITC's existing Phoenix substation. Also reterminate the Phoenix end of the Lark-Phoenix circuit to a different bus inside of Phoenix | MI |  |  | M2a_Pre-Project Approval | 2492000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20882 | 2017-03-29 | SUB | 2019-05-01 | Pioneer 120/41.6 kV |  |  | 120 | 41.6 |  | Install 2-120 kV line breakers at ITC's existing Pioneer substation | MI |  |  | M2a_Pre-Project Approval | 1428000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9362 | 2017-03-29 | ITC_15_005 & ITC_15_006 | 20881 | 2017-03-29 | SUB | 2019-05-01 | State 120/41.6 kV |  |  | 120 | 41.6 |  | Install 3-120 kV breakers w/ associated dsconnects in a straight bus configuration, a control house, and all other 120 kV equipment owned by ITCT at State (formerly "Maize") substation. | MI |  |  | M2a_Pre-Project Approval | 2420000 | Engineering |  | N | N | N
A in MTEP15 | A | East | ITCT | 9440 | 2017-03-29 | ITC_14_027 | 20905 | 2017-03-29 | LNrl | 2020-06-30 | Waterman | DIG-Navarre | 1 | 230 |  |  | Relocate a portion of the overhead circuit exiting Waterman station | MI |  |  | M3_Long Lead Materials | 0 | Engineering Preliminary |  | N | N | N
A in MTEP15 | A | East | ITCT | 9440 | 2017-03-29 | ITC_14_027 | 20904 | 2017-03-29 | LNrl | 2020-06-30 | Waterman | Zug | 1 | 120 |  |  | Relocate a portion of the overhead circuit exiting Waterman station | MI |  |  | M3_Long Lead Materials | 0 | Engineering Preliminary |  | N | N | N
A in MTEP15 | A | South | LAFA | 8820 | 2018-07-27 |  | 20743 | 2017-09-20 | TX | 2019-06-30 | Pont Des Mouton |  |  | 230 | 69 |  | 230-69 autotransformer to feed new 69kv station | LA |  |  | Planned | 3750000 | Planning |  | N | N | N
A in MTEP15 | A | South | LAFA | 8820 | 2018-07-27 |  | 20745 | 2017-09-20 | SUB | 2019-06-30 | Northeast |  |  | 69 |  |  | Station to alleviate distribution loading. | LA |  |  | Planned | 4250000 | Planning |  | N | N | N
A in MTEP15 | A | South | LAFA | 8820 | 2018-07-27 |  | 20744 | 2017-09-20 | LN | 2019-06-30 | Pont Des Mouton | Northeast |  | 69 |  |  | New 69kv line from Pont Des Mouton to Peck stations. | LA |  |  | Planned | 2500000 | Planning |  | N | N | N
A in MTEP15 | A | West | MEC | 8020 | 2015-12-28 |  | 20294 | 2018-03-30 | LN | 2019-10-01 | Pleasant Corner | Beacon | 1 | 161 |  | 410 MVA | New 161 kV Line from Pleasant Corner to Beacon | IA | 0 | 16 | Planned | 14500000 | Planning |  | N | N | N
A in MTEP15 | A | West | MEC | 8020 | 2015-12-28 |  | 20295 | 2018-03-30 | TEQ | 2019-10-01 | Beacon |  |  | 161 |  | 2000A | New 161 kV Line Terminal at the Beacon Substation | IA |  |  | Planned | 1130000 | Planning |  | N | N | N
A in MTEP15 | A | West | MEC | 8028 | 2016-06-30 |  | 20304 | 2017-12-21 | TX | 2023-06-01 | Hastings |  |  | 161 | 69 | 125 MVA | Replace the Hastings transformer with a 125 MVA transformer. | IA |  |  | Proposed | 2600000 | Planning |  | N | N | N | NT
A in MTEP15 | A | West | MEC | 8030 | 2015-12-28 |  | 20305 | 2018-03-30 | LN | 2018-12-31 | Clarksville East | Waverly West | 1 | 69 |  |  | New 69 kV Line from Clarksville East to Waverly West. Retire Clarksville East - Waverly Junction. | IA | 0 | 3 | Under Construction | 2600000 | Planning |  | N | N | N | NT
A in MTEP15 | A | West | MEC | 8039 | 2016-09-16 | G7154 | 20379 | 2016-09-14 | LNup | 2020-11-01 | Sub R | GRS Tap |  | 69 |  | 119 MVA | Rebuild the 69 kV line from Sub R to the three way GRS tap (FAC N38) in Rock Island. Replace underground cable and upgrade overhead section as needed to match cable rating. | IL | 1.55 | 0 | Proposed | 3325000 | Planning |  | N | N | N | NT
A in MTEP15 | A | West | MEC | 8340 | 2015-12-28 |  | 20644 | 2018-06-29 | LNrc | 2018-12-31 | Willow Creek | Greenfield Plaza | 1 | 161 |  | 410 | Rebuild and reconductor the Willow Creek to Greenfield Plaza 161 kV line with T-2 556.5 MCM ACSR conductor. | IA | 4.78 | 0 | Under Construction | 2033100 | Planning |  | N | N | N
A in MTEP15 | A | East | METC | 2810 | 2018-06-20 | METC_13_038 | 4941 | 2018-06-20 | LNrb | 2019-09-30 | Delhi | Canal Jct | 1 | 138 |  | 303 MVA | Rebuild 7.2 miles of 4/0 ACSR and 336.4 ACSR to 954 ACSR on new 138 kV structures. | MI | 7.2 |  | M3_Long Lead Materials | 7500000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | METC | 2810 | 2018-06-20 | METC_13_038 | 8629 | 2018-06-20 | TEQ | 2019-09-30 | Delhi |  |  | 138 |  | 303 MVA | Terminal equipment upgrade at Delhi station. | MI |  |  | M3_Long Lead Materials |  |  |  | N | N | N | Y
A in MTEP15 | A | East | METC | 3926 | 2018-03-27 | METC_14_016 | 7488 | 2018-03-27 | TEQ | 2018-09-28 | Dort | Pasadena | 1 | 138 |  |  | Replace/reset relay equipment and replace trainers in the Dort station | MI |  |  | M4_Pre-Construction | 225000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | METC | 4506 | 2017-10-10 | METC_14_018 | 8632 | 2018-06-27 | LNrb | 2020-03-31 | Four Mile | Wealthy Street | 1 | 138 |  | 304 MVA | Rebuild 0.96 miles of 266.8 ACSR + 3/0 Cu, 6.75 miles of 2-3/0 Cu, and 0.49 miles of 795 ACSR conductor utilizing 954 ACSR on new 138 kV structures. Install OPGW along the entire length of the circuit. | MI | 7.71 |  | M2a_Pre-Project Approval | 8200000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | METC | 4506 | 2017-10-10 | METC_14_018 | 8634 | 2018-06-27 | TEQ | 2020-03-31 | Wealthy Street |  |  | 138 |  |  | Station equipment upgrade at Wealthy Street. | MI |  |  | M2a_Pre-Project Approval | 130000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | METC | 4506 | 2017-10-10 | METC_14_018 | 8633 | 2018-06-27 | TEQ | 2020-03-31 | Four Mile |  |  | 138 |  |  | Station equipment upgrade at Four Mile. | MI |  |  | M2a_Pre-Project Approval | 270000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | METC | 4509 | 2018-03-27 | METC_13_043 | 8638 | 2018-03-27 | TEQ | 2018-06-29 | Battle Creek |  |  | 345 |  |  | Upgrade terminal equipment at Battle Creek. | MI |  |  | M4_Pre-Construction | 68000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | METC | 8066 | 2017-12-21 | METC_14_022 | 20374 | 2017-12-21 | LNrb | 2019-06-14 | Amber | Donaldson Creek | 1 | 138 |  | 199 | Rebuild approx. 19.8 miles of 336 ACSR conductor utilizing 954 ACSR and OPGW on 138kV future double circuit structures. | MI | 19.8 | 0 | M3_Long Lead Materials | 23000000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8072 | 2018-04-27 | METC_14_047 | 20394 | 2018-04-27 | LNrb | 2021-12-31 | Riggsville | Port Calcite | 1 | 138 |  |  | Rebuild 45 miles of 336.4 ACSR strung on 138 kV single circuit wood poles installed in 1960. | MI | 45 |  | M3_Long Lead Materials | 62048000 | Engineering Preliminary |  | N | N | N
A in MTEP15 | A | East | METC | 8072 | 2018-04-27 | METC_14_047 | 20396 | 2018-04-27 | LNrb | 2021-12-31 | Port Calcite | Rockport | 1 | 138 |  |  | Rebuild 24 miles of 266.8 ACSR strung on 138 kV single circuit wood poles installed in 1958. | MI | 24 |  | M3_Long Lead Materials | 34457000 | Engineering Preliminary |  | N | N | N
A in MTEP15 | A | East | METC | 8077 | 2018-06-20 | METC_14_039 | 20418 | 2018-06-27 | LNrb | 2020-12-31 | Vestaburg | Alma | 1 | 138 |  |  | Rebuild the Vestaburg - Alma 138 kV circuit utilizing 138 kV single circuit steel poles and 954 ACSR conductor. Install OPGW along the entire length of the circuit. Also reconductor 2.9 miles of the Eureka – Vestaburg 138 kV circuit using 954 ACSR. | MI | 16.7 |  | M3_Long Lead Materials | 22900000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8078 | 2017-02-23 | METC_14_025 | 20401 | 2017-02-23 | CAP | 2019-06-01 | Donaldson Creek |  |  | 138 |  |  | 33.3 MVAR Capacitor | MI |  |  | M2a_Pre-Project Approval | 1200000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8090 | 2015-12-28 | METC_14_035 | 20416 | 2016-06-07 | LNup | 2018-06-01 | Cornell | Blue Water Jct. | 1 | 138 |  |  | Remediate the sag limit to at least 760 A. | MI |  |  | M3_Long Lead Materials | 320000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8091 | 2017-12-05 | METC_14_030 | 20417 | 2017-12-05 | LNup | 2019-06-01 | Donaldson Creek | White Lake | 1 | 138 |  |  | Remediate sag limit. | MI |  |  | M2a_Pre-Project Approval | 360000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8118 | 2018-06-20 | METC_14_040 | 20466 | 2018-06-20 | TEQ | 2019-09-30 | Beecher |  |  | 138 |  |  | Replace overloaded terminal equipment at Beecher. | MI |  |  | M3_Long Lead Materials | 350000 | Planning |  | N | N | N
A in MTEP15 | A | East | METC | 8118 | 2018-06-20 | METC_14_040 | 20801 | 2018-06-20 | LNrc | 2019-09-30 | Beecher | Whiting | 1 | 138 |  |  | Relocate the Beecher-Whiting 138 kV line to the open side of the new structures. | MI |  |  | M3_Long Lead Materials | 4000000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8118 | 2018-06-20 | METC_14_040 | 20800 | 2018-06-20 | RLY | 2019-09-30 | Morocco |  |  | 138 |  |  | Upgrade relays at Morocco station. | MI |  |  | M3_Long Lead Materials | 250000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8118 | 2018-06-20 | METC_14_040 | 20468 | 2018-06-20 | LNrb | 2019-09-30 | Beecher | Samaria | 1 | 138 |  |  | Rebuild the 636 ACSR portion of the Beecher to Samaria 138 kV circuit utilizing 954 ACSR on 138 kV double circuit steel poles. | MI |  |  | M3_Long Lead Materials | 21000000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8121 | 2018-02-01 | METC_14_037 | 20472 | 2018-02-01 | LNup | 2019-11-01 | Hackett Jct. | Laundra Jct. | 1 | 138 |  |  | Remediate the sag limit on the Hackett Jct. to Laundra Jct. section of the Bullock to Saginaw River 138 kV circuit. | MI |  |  | M3_Long Lead Materials | 90000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8122 | 2016-08-30 |  | 20474 | 2015-12-28 | LNup | 2018-12-31 | METC Pole Top Switches Additions-Replacement Program |  |  | 138 |  |  | Install or replace an existing a new 138 kV, 2-way, full-load-break pole top switch at various tap points across the METC system. | MI |  |  | M2a_Pre-Project Approval | 3600000 |  |  | N | N | N
A in MTEP15 | A | East | METC | 8124 | 2018-06-25 | METC_14_046 | 20476 | 2018-06-25 | LNrb | 2022-03-31 | Argenta | Morrow | 1 | 138 |  |  | Rebuild approximately 10 miles of existing 138 kV steel lattice towers with wood cross arms to double circuit capable 230 kV construction steel monopoles and string one side with 954 ACSR. | MI | 10.5 |  | M3_Long Lead Materials | 13900000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8127 | 2016-08-30 | METC_14_024 | 20484 | 2016-12-20 | CB | 2017-12-31 | Ludington |  |  | 345 |  |  | Replace Ludington 345 kV circuit breakers 22H9, 24H9, 25H9 and 22F7, 24F7, 25F7 with 345 kV live tank circuit breakers containing 400 OHM pre-insertion resistors. | MI |  |  | M3_Long Lead Materials | 8640000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20521 | 2017-10-16 | TX | 2019-12-31 | Meyer (formerly “Hayes Street”) |  |  | 345 | 138 |  | Install a 345/138 kV transformer at the new Meyer substation. | MI |  |  | M3_Long Lead Materials | 4500000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20531 | 2018-06-27 | SUB | 2019-12-31 | Tallmadge |  |  | 345 |  |  | Replace 345 kV terminal equipment at Talmadge substation | MI |  |  | M3_Long Lead Materials | 140000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20529 | 2018-06-27 | SUB | 2019-12-31 | Meyer (formerly “Hayes Street”) |  |  | 345 | 138 |  | Construct the Meyer substation and install all 345 and 138 kV terminal equipment to accommodate the new transformer and looping in the Ludington - Tallmadge #2 345 kV, Argenta-Kenowa 345 kV, and Cobb-Tallmadge #1 138 kV circuits. | MI |  |  | M3_Long Lead Materials | 20200000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20528 | 2018-06-27 | LN | 2019-12-31 | Meyer (formerly “Hayes Street”) | Cobb | 1 | 138 |  |  | Construct approx. 0.25 miles of new 138 kV, double circuit structures, and loop the Cobb-Tallmadge #1 138 kV line into Meyer utilizing 954 ACSR conductor. | MI |  | 0.1 | M3_Long Lead Materials | 960000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20527 | 2018-06-27 | LN | 2019-12-31 | Meyer (formerly “Hayes Street”) | Tallmadge | 2 | 138 |  |  | Construct approx. 0.25 miles of new 138 kV, double circuit structures, and loop the Cobb-Tallmadge #1 138 kV line into Meyer utilizing 954 ACSR conductor. | MI |  | 0.1 | M3_Long Lead Materials | 900000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20526 | 2018-06-27 | LN | 2019-12-31 | Meyer (formerly “Hayes Street”) | Kenowa | 1 | 345 |  |  | Construct approx. 0.1 miles of new 345 kV, double circuit structures, and loop the Kenowa - Argenta 345 kV line into Meyer utilizing 2-954 ACSR conductor. | MI |  | 0.1 | M3_Long Lead Materials | 1300000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20525 | 2018-06-27 | LN | 2019-12-31 | Meyer (formerly “Hayes Street”) | Argenta | 1 | 345 |  |  | Construct approx. 0.1 miles of new 345 kV, double circuit structures, and loop the Kenowa - Argenta 345 kV line into Meyer utilizing 2-954 ACSR conductor. Also remediate the sag limit on the Meyer - Argenta 345 kV circuit to a minimum of 1524 MVA. | MI |  | 0.1 | M3_Long Lead Materials | 1300000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20524 | 2018-06-27 | LN | 2019-12-31 | Meyer (formerly “Hayes Street”) | Ludington | 1 | 345 |  |  | Construct approx. 0.1 miles of new 345 kV, double circuit structures, and loop the Ludington-Tallmadge #2 345 kV line into Meyer utilizing 2-954 ACSR conductor. | MI |  | 0.1 | M3_Long Lead Materials | 1200000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8144 | 2017-10-16 | METC_14_029 | 20523 | 2018-06-27 | LN | 2019-12-31 | Meyer (formerly “Hayes Street”) | Tallmadge | 1 | 345 |  |  | Construct approx. 0.1 miles of new 345 kV, double circuit structures, and loop the Ludington-Tallmadge #2 345 kV line into Meyer utilizing 2-954 ACSR conductor. Also remediate the sag limit on the Meyer -Tallmadge #1 345 kV circuit to a minimum of 2007 MVA | MI |  | 0.1 | M3_Long Lead Materials | 1200000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8171 | 2018-03-27 | METC_13_016 | 20576 | 2018-03-27 | RLY | 2018-04-02 | Croton | Felch Road | 1 | 138 |  |  | 1. Install dual pilot relay protection system on Croton to Felch Road 138 kV circuit so that 3 phase to ground faults on the circuit will be cleared within 7 cycles. 2. Remove the sparing scheme of using Croton 138 kV breaker 500 to spare breaker 388 for Croton to Felch Road 138 kV circuit. 3. Remove Felch Road 138 kV BK 188 Bypassing | MI |  |  | M4_Pre-Construction | 540000 | Engineering |  | N | N | N
A in MTEP15 | A | East | METC | 8460 | 2018-03-27 | METC_14_045 | 20675 | 2018-03-27 | LNup | 2018-06-01 | Hemphill | Sabine | 1 | 138 |  | 180 | Remediate the sag limit on the Sabine - Hemphill 138 kV line to increase its summer emergency rating to the 336 ACSR conductor rating of 208 MVA (871 Amps). | MI |  |  | M4_Pre-Construction | 140000 | Engineering |  | N | N | N
A in MTEP15 | A | West | MP | 8000 | 2015-12-28 | 16 Line Relocation | 20284 | 2018-04-03 | LNrl | 2020-05-01 | Arrowhead | 16L Tap | 1 | 115 |  | 55 | Relocate line segment | MN | 0 | 3 | Planned | 3450000 | Engineering |  | N | N | N | Y
A in MTEP15 | A | East | NIPS | 8500 | 2015-12-28 |  | 20678 | 2016-03-15 | BUS | 2018-12-31 | Lagrange | Lagrange |  | 138 | 138 |  | Make necessary upgrades at Lagrange 138kV Substation to create ring bus. | IN |  |  | Planned | 2715000 | Planning |  | N | N | N
A in MTEP15 | A | East | NIPS | 9405 | 2015-12-28 |  | 20896 | 2018-02-01 | SUBmisc | 2019-11-08 | Kosciusko |  |  | 138 |  |  | Replace Line switch and substation Conductor | IN |  |  | Planned | 147845 | Planning |  | N | N | N
A in MTEP15 | A | West | OTP | 8281 | 2018-06-29 |  | 20627 | 2018-06-29 | SUB | 2019-11-30 | Donaldson 115 | Drayton 115 |  | 115 |  |  | Add a new 115 kV breaker at Donaldson to the Donaldson to Drayton 115 kV line to improve reliability of area loads. This breaker will reduce fault exposure to Donaldson loads by 17 miles and improve operations, maintenance, and relaying flexibility at Donaldson. | MN |  |  | Planned | 370000 | Planning Preliminary |  | N | N | N | Y
A in MTEP15 | A | Central | PPI | 7881 | 2018-09-17 | 2015-12 | 20113 | 2018-09-17 | LN | 2021-12-31 | Fishhook | Pittsfield | 1 | 138 |  | 229 | 14.5 mile single pole 138 kV line constructed with 795 MCM ACSR conductor. Portions of the line will be double circuited with the Fishhook-Liberty 138 kV line and the Pittsfield-Pittsfield Distribution 69 kV line. | IL |  | 14.5 | Planned | 13680000 | Engineering |  | N | N | N
A in MTEP15 | A | Central | PPI | 7881 | 2018-09-17 | 2015-12 | 20121 | 2018-09-17 | LNrb | 2021-12-31 | Pittsfield | Pittsfield Distribution | 1 | 69 | 69 | 50 | 69 kV Underbuild on portion of Fishhook-Pittsfield 138 kV line. Replace approximately 2.5 miles of 4/0 conductor from Pittsfield-Pittsfield Distribution 69 kV with 336.4 MCM ACSR conductor. | IL | 2.5 |  | Planned | 750000 |  |  | N | N | N
A in MTEP15 | A | Central | PPI | 7889 | 2018-03-22 | 2015-14,35,37 | 20123 | 2018-03-22 | LN | 2019-12-31 | Fishhook 138 kV | Liberty 138 kV |  | 138 | 138 | 229 | Construct 12 mile 138 kV line from Fishhook substation to Liberty substation. | IL |  | 12 | M4_Pre-Construction | 1000000 | Engineering |  | N | N | N
A in MTEP15 | A | Central | PPI | 7889 | 2018-03-22 | 2015-14,35,37 | 20125 | 2016-09-09 | TX | 2019-12-31 | St. Anthony 138 kV | St. Anthony 69 kV |  | 138 | 69 | 75 | Replace 50 MVA delta-wye 138/69 kV transformer with 75 MVA wye-wye transformer with LTC. | IL |  |  | Planned | 1251800 | Engineering |  | N | N | N
A in MTEP15 | A | Central | PPI | 7889 | 2018-03-22 | 2015-14,35,37 | 20124 | 2018-03-22 | SUB | 2019-12-31 | Liberty 138 kV | Liberty 69 kV | 1 | 138 | 69 | 75 | New 138/69 kV substation including 75 MVA 138/69 kV transformer. | IL |  |  | Under Construction | 4653000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20682 | 2018-09-27 | LNcnv | 2018-08-01 | Waynesboro | Missionary | 1 | 230 |  | 501 MVA | Convert Waynesboro - Missionary 161kV line to 230kV operation. | MS | 38.31 |  | M5_In Service | 535000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20703 | 2018-06-29 | LNrb | 2021-09-01 | Homewood | Missionary |  | 161 |  | 296 | Rebuild existing 69kV lines from span from Homewood - Missionary using double circuit provisions for the addition of the 161kV path from Homewood - Missionary. | MS | 19.5 |  | Planned | 7289000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20702 | 2018-06-29 | LN | 2021-09-01 | Homewood | Missionary | 1 | 161 |  | 296 | Add additional 161kV circuit to existing double circuit line. | MS | 31 |  | Planned | 3874000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20701 | 2017-06-22 | BUS | 2019-01-01 | Homewood |  |  | 161 |  |  | Add 161kV Bay with Breaker at Homewood. | MS |  |  | Planned | 545000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20700 | 2018-09-27 | BUS | 2018-08-01 | Missionary |  |  | 161 |  |  | Add 161kV breaker to existing bay at Missionary substation. | MS |  |  | M5_In Service | 165000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20699 | 2018-09-27 | SUB | 2018-08-01 | Missionary |  |  | 230 | 161 | 250 MVA | Add 230/161kV Transformer (250 MVA) at existing SMEPA owned Missionary substation. | MS |  |  | M5_In Service | 2900000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20685 | 2018-09-27 | BUS | 2018-08-01 | Waynesboro |  |  | 230 |  |  | Add 230kV bay with breaker at Waynesboro (Create Ring Bus Configuration) | MS |  |  | M5_In Service | 670000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20684 | 2018-09-27 | BUS | 2018-08-01 | Waynesboro |  |  | 230 |  |  | Add 230kV Breaker to existing bay at Waynesboro | MS |  |  | M5_In Service | 230000 | Engineering |  | N | N | N
A in MTEP15 | A | South | SMEPA | 8560 | 2016-02-03 |  | 20683 | 2018-09-27 | BUS | 2018-08-01 | Missionary |  |  | 230 |  |  | Add 230kV Bay with Breaker at Missionary | MS |  |  | M5_In Service | 670000 | Engineering |  | N | N | N
A in MTEP15 | A | Central | Vectren | 4391 | 2016-05-19 | 2013SIGE5 | 8408 | 2018-03-29 | CAP | 2019-12-31 | Pigeon Creek 69 | Capacitor |  | 69 |  | 15.6 MVAR | Add a 15.6 MVAR cap bank at the Pigeon Creek Sub | IN | 0 | 0 | M2a_Pre-Project Approval | 770000 | Planning |  | N | N | N | Y
A in MTEP15 | A | Central | Vectren | 10142 | 2018-06-22 |  | 21473 | 2016-01-13 | TEQ | 2021-01-01 | Duff |  |  | 345 |  |  | Sub upgrades at Duff | IN |  |  | Planned | 3092381 |  |  | N | Y | N | Y
A in MTEP15 | A | East | WPSC | 3567 | 2015-12-28 | HY-WN | 6651 | 2015-09-15 | LNrb | 2017-12-31 | Hersey | Osceola Jct | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 4.02 |  | Planned | 2100000 | Budgetary |  | N | N | N | Y
A in MTEP15 | A | East | WPSC | 3567 | 2015-12-28 | HY-WN | 6654 | 2015-09-15 | LNrb | 2017-12-31 | Martiny | Weidman | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 8.37 |  | Planned | 4200000 | Budgetary |  | N | N | N | Y
A in MTEP15 | A | East | WPSC | 3567 | 2015-12-28 | HY-WN | 6653 | 2015-09-15 | LNrb | 2017-12-31 | Barryton | Martiny | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 1 |  | Planned | 500000 | Budgetary |  | N | N | N | Y
A in MTEP15 | A | East | WPSC | 3567 | 2015-12-28 | HY-WN | 6652 | 2015-09-15 | LNrb | 2017-12-31 | Osceola Jct | Barryton | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 9.69 |  | Planned | 4700000 | Budgetary |  | N | N | N | Y
A in MTEP15 | A | East | WPSC | 4086 | 2015-12-28 | FNX-SV | 7739 | 2015-09-15 | LNrb | 2016-12-31 | Fountain Junction | Scottville | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 9.15 |  | Planned | 4650000 | Planning |  | N | N | N | Y
A in MTEP15 | A | East | WPSC | 4384 | 2015-12-28 | Airport Xmsn | 8399 | 2014-09-25 | SUB | 2017-12-31 | Airport | Substation Upgrade |  | 138 | 69 |  | 138kV Breaker Replacement and Protective Equipment Upgrade | MI |  |  | Proposed | 4100000 | Budgetary |  | N | N | N | Y
A in MTEP15 | A | East | WPSC | 4384 | 2015-12-28 | Airport Xmsn | 21503 | 2015-10-28 | SUB | 2018-12-31 | Airport |  |  | 138 |  |  | Landscaping costs | MI |  |  | Planned | 50000 | Budgetary |  | N | N | N
A in MTEP15 | A | East | WPSC | 4384 | 2015-12-28 | Airport Xmsn | 21502 | 2015-10-28 | SUB | 2017-01-01 | Airport |  |  | 138 |  |  | Airport Substation zoning costs | MI |  |  | Planned | 40000 | Budgetary |  | N | N | N
A in MTEP15 | A | East | WPSC | 7661 | 2015-12-28 | Vestaburg Transmission | 20048 | 2016-09-15 | BUS | 2017-12-31 | Vestaburg Transmission |  |  | 69 |  |  | Switch and bus upgrades, including a sparing scheme addition | MI |  |  | Planned | 170000 | Planning |  | N | N | N
A in MTEP15 | A | East | WPSC | 8221 | 2015-12-28 | Airport Line Mods | 20609 | 2014-10-30 | LN | 2017-12-31 | Airport 138kV & 69kV |  |  | 138 | 69 |  | This project will construct the line modifications required to route lines into the new Airport station. | MI |  |  | Proposed | 1000000 | Budgetary |  | N | N | N
A in MTEP15 | A | East | WPSC | 8380 | 2015-12-28 | Advance Line Mods | 20653 | 2014-11-04 | LN | 2016-12-31 | Advance Transmission |  |  | 69 |  |  | Line modifications to support the Advance Transmission station project | MI |  |  | Planned | 1250000 | Budgetary |  | N | N | N
A in MTEP15 | A | West | XEL | 8079 | 2015-12-28 |  | 20403 | 2017-06-24 | LINE | 2022-12-01 | Madelia Switching Station | Village of Madelia | 1 | 69 |  |  | Rebuild 3.6 miles of 69 kV line from Madelia Switching Station to Village of Madelia to 336 ACSR | MN | 3.6 |  | Planned | 1594000 | Scoping |  | N | N | N
A in MTEP15 | A | West | XEL | 8113 | 2015-12-28 |  | 20449 | 2018-09-28 | SUB | 2018-12-01 | Ward County |  |  | 230 | 115 |  | New 230/115 kV substation near Minot, ND | ND |  |  | Under Construction | 8500000 | Scoping |  | N | N | N
A in MTEP15 | A | West | XEL | 8113 | 2015-12-28 |  | 20453 | 2018-09-28 | LN | 2018-12-01 | Ward County | McHenry | 1 | 230 |  | 500 | New 230 kV line from Ward County - McHenry | ND |  | 20 | Under Construction | 24500000 | Scoping |  | N | N | N
A in MTEP15 | A | West | XEL | 8117 | 2015-12-28 |  | 20471 | 2018-09-28 | LNrb | 2018-12-01 | Ward County | Souris | 1 | 115 |  | 230 | Rebuild the 115 kV line between Ward County and Souris | ND | 7 |  | Under Construction | 4700000 | Scoping |  | N | N | N
A in MTEP15 | A | West | XEL | 8117 | 2015-12-28 |  | 20473 | 2018-09-28 | LNrb | 2018-12-01 | Ward County | Souris | 2 | 115 |  | 230 | Rebuild the 115 kV line between Ward County and Souris | ND | 7 |  | Under Construction | 4700000 | Scoping |  | N | N | N
A in MTEP15 | A | West | XEL | 8149 | 2015-12-28 |  | 20540 | 2017-09-28 | LN | 2020-03-15 | New Sub (South) | New Sub (North) | 1 | 69 |  |  | New 69 kV line tapping the existing Stinson - Bayfront 115 kV line to a new substation near Bayfield | WI |  | 20 | Planned | 10400000 | Planning |  | N | N | N
A in MTEP15 | A | West | XEL | 8149 | 2015-12-28 |  | 20561 | 2017-09-28 | LNrb | 2022-12-01 | Cornucopia | Bayfield Tap | 1 | 69 |  |  | Rebuild Cornucopia - Bayfield Tap 34.5 kV to 69 kV using 477 ACSR | WI | 18 |  | Planned | 7200000 | Planning |  | N | N | N
A in MTEP15 | A | West | XEL | 8149 | 2015-12-28 |  | 20560 | 2017-09-28 | SUB | 2020-03-15 | New Sub (North) |  |  | 69 | 34.5 |  | New 69/34.5 kV line near Bayfield Tap. Includes one 3 MVAR 34.5 kV cap bank. | WI |  |  | Planned | 4600000 | Planning |  | N | N | N
A in MTEP15 | A | West | XEL | 8149 | 2015-12-28 |  | 20556 | 2017-09-28 | LNrb | 2022-12-01 | Iron River | Herbster | 1 | 69 |  |  | Rebuild Iron River - Herbster 34.5 kV to 69 kV using 477 ACSR | WI | 25 |  | Planned | 11700000 | Planning |  | N | N | N
A in MTEP15 | A | West | XEL | 8149 | 2015-12-28 |  | 20541 | 2017-09-28 | SUB | 2020-03-15 | New Sub (South) |  |  | 115 | 69 |  | New 115/69 kV substation on the Stinson - Bayfront 115 kV line | WI |  |  | Planned | 6100000 | Planning |  | N | N | N
A in MTEP14 | A | Central | AmerenIL | 4471 | 2015-01-09 |  | 8570 | 2018-09-27 | LN | 2018-12-01 | Cahokia | Dupo Ferry | 1 | 138 |  |  | Replace 6.98 miles of 2-300 kcmil Copper conductor with largest size conductor existing structures will carry. (Minimum capability of 1600 A) | IL | 6.98 |  | Planned | 5200000 | Planning |  | N | N | N | Y
A in MTEP14 | A | Central | AmerenIL | 4480 | 2017-03-10 |  | 8588 | 2018-09-27 | SUB | 2023-06-01 | Oglesby | Rebuild Substation |  | 138 |  |  | Rebuild Oglesby Substation. Utilize a breaker-and-a-half arrangement. | IL |  |  | Proposed | 34600000 | Planning |  | N | N | N | Y
A in MTEP14 | A | Central | AmerenMO | 4723 | 2015-01-09 |  | 8952 | 2014-08-22 | LN | 2017-12-01 | Kelso | Lutesville | 1 | 345 |  | 1178 | Replace 50% of structures (17.6 miles) to maintain at least a 100 degree C conductor temperature capability on this line. | MO | 17.6 |  | Proposed | 8441336 |  |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 1624 | 2014-12-17 | PR05259, F4004 | 3241 | 2016-09-29 | LN | 2022-06-01 | Portage | Trienda | 2 | 138 |  | 294 | Uprate X-67 Portage - Trienda 138-kV | WI | 3.4 |  | Proposed | 2000000 |  |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3096 | 2017-11-27 | PR04463, F3735 | 5421 | 2018-06-29 | LN | 2019-05-01 | Munising | Timber Products | 1 | 69 |  | 37 MVA | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance | MI | 6.2 |  | M1_Final SPM or OOC | 18187669 | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3096 | 2017-11-27 | PR04463, F3735 | 5423 | 2018-06-29 | LN | 2019-05-01 | Seney | Blaney Park | 1 | 69 |  | 37 MVA | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance | MI | 18 |  | Planned |  | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3096 | 2017-11-27 | PR04463, F3735 | 5422 | 2018-06-29 | LN | 2019-05-01 | Timber Products | Seney | 1 | 69 |  | 37 MVA | Increase ground clearance for the Inland line Munising-Blaney Park 69kV to 167 deg f (37 MVA) clearance | MI | 28.4 |  | Planned |  | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3510 | 2016-09-15 | PR04651, F3421 | 6481 | 2018-06-29 | LN | 2019-06-15 | Mukwonago | Edgewood | 1 | 138 |  | 293 | 671K61 Mukwonago-Edgewood 138-kV rebuild | WI | 7.19 |  | M1_Final SPM or OOC | 24736000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3510 | 2016-09-15 | PR04651, F3421 | 6482 | 2018-06-29 | LN | 2019-06-15 | Edgewood | St. Martins | 1 | 138 |  | 287 | 3013 Edgewood-St. Martins 138-kV rebuild | WI | 7.07 |  | M1_Final SPM or OOC | 0 | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7149 | 2018-04-02 | TX | 2019-12-31 | Geneva |  | 1 | 138 | 69 | 100 | New Geneva 138-69 kV Transformer | WI |  |  | Under Construction | 12155000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7155 | 2018-04-02 | LN | 2019-12-31 | Twin Lakes | Geneva | 1 | 69 |  | 116 | Construct new Twin Lakes-Geneva 69 kV line with T2-336 | WI | 1 |  | Under Construction | 7391000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7154 | 2018-04-02 | LNrc | 2019-12-31 | Richmond Road | Twin Lakes | 1 | 69 |  | 116 | Reconductor Twin Lakes-Richmond 69 kV line with T2-336 | WI | 2.3 |  | Under Construction | 2675000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7153 | 2018-04-02 | LNrc | 2019-12-31 | Katzenberg | Richmond Road | 1 | 69 |  | 116 | Reconductor Katzenberg-Richmond 69 kV line with T2-336 | WI | 2.6 |  | Under Construction | 3024000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7152 | 2018-04-02 | LN | 2019-12-31 | Geneva | North Lake Geneva | 1 | 138 |  | 293 | Construct new Geneva-North Lake Geneva 138 kV line with T2-477 | WI | 12.5 |  | Under Construction | 17420000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7151 | 2018-04-02 | LN | 2019-12-31 | Spring Valley | Geneva | 1 | 138 |  | 293 | Construct new Spring Valley-Geneva 138 kV line with T2-477 | WI | 11.55 |  | Under Construction | 26567000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ATC | 3808 | 2014-12-17 | PR04505, F2570 | 7150 | 2018-04-02 | LNrc | 2019-12-31 | Bain | Spring Valley | 1 | 138 |  | 293 | Reconductor Bain-Spring Valley 138 kV line with T2-477 | WI | 14.45 |  | Under Construction | 1314000 | Planning |  | N | N | N | Y
A in MTEP14 | A | Central | DEI | 4411 | 2015-01-09 | AMIN0863&4&5 | 8430 | 2018-06-28 | LNrb | 2018-10-01 | Bloomington Meadow Pk | HE Brummett Crk Jct |  | 69 |  | 154 | AMIN0865 - Reconductor 6991 ckt from Bloomington Meadow Pk to HE Brummett Crk Jct - 1.6 miles of 954ACSS@200C | IN | 1.6 |  | Under Construction | 1843000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | Central | DEI | 4415 | 2015-01-09 | AMIN0890 | 8434 | 2014-09-23 | TX | 2020-06-01 | Veedersburg West | xmr addition |  | 230 | 69 | 75 | Veedersburg West: Add 75MVA 230/69 Bk 2 with LTC at Veedersburg West sub; add breaker to 69kV ring bus and tie in new bank; convert 230kV bus into 4-breaker ring | IN |  |  | M1_Final SPM or OOC | 3509000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | Central | DEI | 4417 | 2015-01-09 | AMIN0988 | 8436 | 2018-06-28 | CB | 2018-10-01 | Pumpkin Center | brkr replacements |  | 69 |  |  | Pumpkin Center: Replace OCB 6952, OCB 69123, OCB 69230, (1) Ground Switch, (2) 230KV ABS and Motor Mechs, Lightning Arrestors, Line & Bus Pots, (7) 69KV Disconnect Switches and Station Service Transformer. Replace the 230kV Bk1 "230-69" Circuit Switcher w | IN |  |  | Under Construction | 2424000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | Central | DEM | 3550 | 2016-08-03 | AMIN0499 | 6619 | 2018-06-28 | LN | 2018-12-31 | Martinsville Southeast | Martinsville E. | 1 | 69 |  | 153 | Construct approximately 1.5 mi of 69kv line to complete a normally open loop between Martinsville SE and Martinsville East distribution subs. | IN |  | 1.5 | Under Construction | 1434000 | Engineering |  | N | N | N | NT
A in MTEP14 | A | South | Entergy-AR | 4751 | 2014-12-17 | 14-EAI-020-8 | 9019 | 2018-09-26 | CB | 2019-06-30 | Jacksonville North 115 kV substation |  |  | 115 |  |  | Upgrade Circuit Breaker: Jacksonville North 115 kV B3621-CBO | AR |  |  | Under Construction | 84000 |  |  | N | N | N | Y
A in MTEP14 | A | South | Entergy-AR | 4757 | 2015-09-10 | 14-EAI-022-4 | 9025 | 2018-09-18 | TEQ | 2019-06-30 | El Dorado 500 kV substation |  |  | 500 |  |  | EAI SPOF Projects: Modify relaying at El Dorado 500 kV | AR |  |  | Planned | 4698843 | Scoping |  | N | N | N | Y
A in MTEP14 | A | South | Entergy-LA | 4761 | 2014-12-17 | 14-EGL-022-1 | 9029 | 2018-09-26 | SUB | 2019-06-01 | Willow Glen 500 kV substation |  |  | 500 |  |  | EGSL SPOF Projects: Modify relaying at Willow Glen 500 kV | LA |  |  | Under Construction | 6502968 | Planning |  | N | N | N | Y
A in MTEP14 | A | South | Entergy-LA | 4773 | 2014-12-17 | 14-ELL-009-1 | 9041 | 2018-09-26 | TEQ | 2019-01-31 | Ninemile 230 kV |  |  | 230 |  |  | ELL SPOF Projects: Modify relaying at Ninemile 230 kV | LA |  |  | Under Construction | 5981188 | Planning |  | N | N | N | Y
A in MTEP14 | A | South | Entergy-LA | 4774 | 2014-12-17 | 14-ELL-009-2 | 9042 | 2018-06-27 | TEQ | 2018-09-30 | Southport 230 kV |  |  | 230 |  |  | ELL SPOF Projects: Modify relaying at Southport 230 kV | LA |  |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP14 | A | South | Entergy-LA | 4775 | 2014-12-17 | 14-ELL-009-3 | 9043 | 2018-06-27 | TEQ | 2018-09-30 | Labarre 230 kV |  |  | 230 |  |  | ELL SPOF Projects: Modify relaying at Labarre 230 kV | LA |  |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP14 | A | South | Entergy-LA | 4778 | 2014-12-17 | 14-ENO-003-1 | 9046 | 2018-06-27 | TEQ | 2018-11-16 | Market Street 230 kV |  |  | 230 |  |  | ELL SPOF Projects: Modify relaying at Market Street 230 kV | LA |  |  | Under Construction |  |  |  | N | N | N | Y
A in MTEP14 | A | West | GRE-WMU | 4380 | 2015-01-09 | 202647 | 8394 | 2016-09-15 | SUB | 2019-05-01 | Priam |  |  | 115 | 69 |  | Move Willmar 115/69 kV transformer to new Priam 115 kV substation | MN |  |  | Proposed | 3000000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | GRE-WMU | 4380 | 2015-01-09 | 202647 | 8395 | 2016-09-15 | LN | 2019-05-01 | Priam | Pennock/Willmar Waste Water | 1 | 69 |  |  | Establish 69 kV outlets from Priam | MN |  | 1.5 | Proposed | 1000000 | Planning |  | N | N | N | Y
A in MTEP14 | A | Central | HE | 4714 | 2015-01-09 | 1052 Ratts 138/161 kV Transformer Upgrade | 8940 | 2013-11-07 | TX | 2014-05-15 | 07Ratts 138/161 kV | 07Ratts8 138/161 kV | 1 | 161 | 138 | 322 | Replace Ratts AT3 | IN |  |  | Planned | 3500000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | Central | HE | 4715 | 2015-01-09 | 1052 Ratts 138 kV Transmission Upgrade | 8941 | 2013-11-07 | LNrc | 2014-05-15 | 07Ratts8 | 07Rattap | 1 | 138 |  | 327 | Reconductor 138 kV line | IN | 0.1 |  | Planned | 200000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | 8619 | 2018-03-27 | SwSta | 2019-05-30 | Carrigan |  |  | 120 |  |  | Construct a new 4-breaker 120 kV switching station named "Carrigan" in the Thumb area. Loop the Lee - Menlo & Wabash - Yuma 120 kV circuits into Carrigan. | MI |  |  | M4_Pre-Construction | 4930000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | 8624 | 2018-03-27 | LNup | 2019-05-30 | Carrigan | Yuma | 1 | 120 |  | 134 MVA | New line created by looping the Wabash - Yuma 120 kV circuit into Carrigan. | MI |  |  | M4_Pre-Construction |  |  |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | 8623 | 2018-03-27 | LNup | 2019-05-30 | Carrigan | Wabash | 1 | 120 |  | 274 MVA | New line created by looping the Wabash - Yuma 120 kV circuit into Carrigan and associated relay upgrades. | MI |  |  | M4_Pre-Construction | 265000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | 8622 | 2018-03-27 | LNup | 2019-05-30 | Carrigan | Menlo | 1 | 120 |  | 134 MVA | New line created by looping the Menlo - Lake Huron Pumping 1 Tap (to Lee) circuit into Carrigan and associated relay upgrades | MI |  |  | M4_Pre-Construction | 210000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | 8621 | 2018-03-27 | LNup | 2019-05-30 | Carrigan | Lake Huron Pumping 1 Tap | 1 | 120 |  | 305 MVA | New line created by looping the Menlo - Lake Huron Pumping 1 Tap (to Lee) circuit into Carrigan and associated relay upgrades | MI |  |  | M4_Pre-Construction | 275000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4500 | 2018-02-01 | ITCT_13_043 | 8620 | 2018-03-27 | LNrb | 2019-05-30 | Lee | Menlo | 1 | 120 |  | 305 MVA | Replace the existing structures from a one-mile segment of the Lee - Menlo 120 kV circuit with double circuit structures and install 954 ACSR on both sides. | MI | 1 | 1 | M4_Pre-Construction | 1700000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | ITC, ITCT | 4567 | 2016-03-23 |  | 8709 | 2014-12-29 | TEQ | 2018-12-31 | Blanket for Customer Interconnections 2018 | Throughout system |  | 120 |  |  | Connect interconnecting entities as requested | MI |  |  | M2a_Pre-Project Approval | 2000000 |  |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4456 | 2014-12-17 | East Nevada St | 8523 | 2016-06-28 | SUB | 2020-12-31 | East Nevada Street | Substation | 1 | 34 |  |  | Add two 69kV breakers at the East Nevada distribution sub to allow for 69kV conversion. | IA |  |  | Planned | 400000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4459 | 2014-12-17 | East IA phase 3 | 8529 | 2016-06-28 | LN | 2018-12-31 | Rome REC | Rome REC Tap |  | 69 |  | 77 MVA | Build a new 69kV line from Rome REC back to the present line. | IA | 2 |  | Planned | 1080000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4459 | 2014-12-17 | East IA phase 3 | 8532 | 2016-06-28 | LN | 2018-12-31 | Marion | Amber |  | 69 |  | 77 MVA | Convert the 34kV line, already built for 69kV, to 69kV operation. | IA |  |  | Planned | 1200000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4459 | 2014-12-17 | East IA phase 3 | 8530 | 2016-06-28 | LN | 2018-12-31 | Clarence | Clarence REC |  | 69 |  | 77 MVA | Build a new 69kV line from Clarence to Clarence REC | IA | 2 |  | Planned | 1080000 | Planning | Generator | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4462 | 2014-12-17 | Keswick-Victor Conv | 8539 | 2015-12-30 | SUB | 2021-12-30 | Victor Switching | Substation |  | 69 | 34 |  | ITC will add two 69kV breakers and a 69/34kV transformer at the new Victor substation. | IA |  |  | Planned | 3000000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | 8540 | 2015-12-30 | LN | 2019-12-31 | Fletcher | Green Mountain |  | 69 |  | 77 MVA | Retire the 34kV line terminal out of Marshalltown and route the line to the new Fletcher 69kV bus built adjacent to Marshalltown. Convert the 34kV line, already built for 69kV, to 69kV operation. | IA | 6.84 |  | Planned | 240000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | 8545 | 2015-12-30 | LN | 2019-12-31 | Otter Creek | Hubbard Pump Tap |  | 69 |  | 77 MVA | Convert the 34kV line, already built for 69kV, to 69kV operation. | IA | 14.17 |  | Planned | 0 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | 8544 | 2015-12-30 | LN | 2019-12-31 | Otter Creek | CB Union |  | 69 |  | 77 MVA | Convert the 34kV line, already built for 69kV, to 69kV operation. | IA | 10.01 |  | Planned | 0 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | 8543 | 2015-12-30 | LN | 2019-12-31 | CB Union | Union |  | 69 |  | 77 MVA | Convert the 34kV line, already built for 69kV, to 69kV operation. | IA | 1.05 |  | Planned | 0 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | 8542 | 2015-12-30 | LN | 2019-12-31 | Conrad | Union |  | 69 |  | 77 MVA | Convert the 34kV line, already built for 69kV, to 69kV operation. | IA | 12.65 |  | Planned | 0 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4463 | 2014-12-17 | OtterCk-Fletcher | 8541 | 2015-12-30 | LN | 2019-12-31 | Conrad | Green Mountain |  | 69 |  | 77 MVA | Convert the 34kV line, already built for 69kV, to 69kV operation. | IA | 11.15 |  | Planned | 0 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4467 | 2014-12-17 | Fairbank-Oelwein | 8560 | 2017-03-07 | LN | 2019-12-31 | Oelwein | Fairbank |  | 69 |  | 77 MVA | Rebuild 5.5 miles of the Oelwein-Fairbank 69kV line. | IA | 5.5 |  | Planned | 5492400 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8919 | 2016-06-30 | LN | 2019-09-02 | Kalona South Tap | Iowa Jct | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 4.92 |  | Planned | 2212000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8918 | 2018-06-28 | LN | 2018-10-17 | Frytown Tap | Kalona South Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 6.02 |  | Under Construction | 2709000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8917 | 2018-03-28 | LN | 2018-12-20 | Hills | Frytown | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 11.08 |  | Planned | 4986000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8916 | 2018-06-28 | LN | 2019-02-20 | Ferguson REC Tap | Gilman Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 3.75 |  | Under Construction | 1687500 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8915 | 2016-06-30 | LN | 2020-12-31 | Traer | Dysart | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 8.28 |  | Planned | 3726000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8914 | 2018-05-10 | LN | 2019-12-31 | Sutherland | LeGrand | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 6.27 |  | M3_Long Lead Materials | 5366227 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8913 | 2018-06-28 | LN | 2018-11-19 | Ferguson | Timber Creek Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 3.75 |  | Under Construction | 1687500 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8912 | 2018-03-28 | LN | 2018-09-15 | Vining REC Tap | Tama East | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 10.63 |  | Planned | 7505760 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8911 | 2016-06-30 | LN | 2020-12-31 | Belle Plaine Jct | Vining REC Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 12.68 |  | Planned | 5706000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8910 | 2016-06-30 | LN | 2021-12-31 | Benco | Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 1.57 |  | Planned | 706500 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8908 | 2018-06-28 | LN | 2018-12-02 | Willaimsburg South | Parnell | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 15 |  | Under Construction | 6750000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8907 | 2018-03-28 | LN | 2018-11-01 | Koszta REC Tap | Belle Plaine Jct | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 5.7 |  | Planned | 2565000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8906 | 2016-06-30 | LN | 2018-05-04 | Willamsbug South | Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 3 |  | Planned | 1350000 | Planning |  | N | N | N | Y
A in MTEP14 | A | West | ITCM | 4704 | 2014-12-17 | Mtown-Parnell-CR | 8904 | 2017-11-10 | LN | 2021-05-04 | Blairstown Tap | Tap | 1 | 34 |  | 39 MVA | Rebuild 34kV to 69kV statandards and continue to operate at 34kV | IA | 2.6 |  | Planned | 1896425 | Planning |  | N | N | N | Y
A in MTEP14 | A | East | ITCT | 4518 | 2016-11-07 | ITC_15_004 | 8649 | 2016-11-07 | TX | 2019-12-31 | Monroe 345/120 kV Transformer 304 |  | 4 | 345 | 120 | 649 MVA | Replace the 345/120 kV Transformer 304 at Monroe. | MI |  |  | M3_Long Lead Materials | 3800000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | MDU | 3083 | 2015-03-31 | Dickinson Loop | 5365 | 2018-09-27 | CB | 2019-11-30 | North Dickinson | 2 PCB |  | 115 |  |  | Complete North Dickinson bus | ND |  |  | Planned | 1500000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | West | MDU | 3083 | 2015-03-31 | Dickinson Loop | 5364 | 2018-09-27 | LN | 2019-11-30 | North Dickinson | Dickinson West | 1 | 115 |  | 120 | New line Segment | ND |  | 3 | Planned | 750000 | Engineering |  | N | N | N | Y
A in MTEP14 | A | East | METC | 4538 | 2016-03-23 | METC-996 | 8680 | 2014-12-29 | Dist | 2018-12-31 | Blanket for Customer Interconnections 2018 | Throughout system |  | 138 |  |  | Connect interconnecting entities as requested | MI |  |  | M2a_Pre-Project Approval | 2500000 |  |  | N | N | N | Y
A in MTEP14 | A | East | METC | 4539 | 2018-03-27 | METC-995 | 8681 | 2018-03-27 | RLY | 2019-01-24 | METC Hemphill Control Relocation Project - Years 2015, 2016, 2017 | Hemphill |  |  |  |  | Replace METC relaying and controls at Hemphill Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | M4_Pre-Construction | 3640000 |  |  | N | N | N | Y
A in MTEP14 | A | East | METC | 4542 | 2018-03-27 | METC-990 | 8684 | 2018-03-27 | RLY | 2019-12-30 | METC Morrow Control Relocation Project - Years 2015, 2016, 2017 | Morrow |  |  |  |  | Replace METC relaying and controls at Morrow Substation. Locate the new relaying and controls in a new dedicated METC control center. Install dedicated METC AC and DC systems. | MI |  |  | M3_Long Lead Materials | 3110000 |  |  | N | N | N | Y
A in MTEP14 | A | East | METC | 4555 | 2018-06-20 | METC_13_018 | 8697 | 2018-06-27 | TEQ | 2019-04-30 | Tippy | Stronach | 1 | 138 |  |  | Install a dual pilot relay protection system on the Tippy to Stronach 138 kV circuit so that three (3) phase to ground faults will be cleared within 5 cycles. The Tippy 138 kV BK 177 bypassing will also be removed. | MI |  |  | M4_Pre-Construction | 575000 |  |  | N | N | N | Y
A in MTEP14 | A | East | METC | 4556 | 2016-11-10 | METC_13_032 | 8698 | 2017-12-21 | TEQ | 2017-12-31 | Blackstone |  |  | 138 |  |  | install a second bus relay scheme on Blackstone blue and white busses and install second independent relay components on Blackstone end of the Blackstone-Marshall 138 kV circuit, Blackstone-Tompkins 138 kV ckts #1 and #2 and Blackstone-Leoni 138 kV ckts # | MI |  |  | M4_Pre-Construction | 845000 |  |  | N | N | N | Y
A in MTEP14 | A | East | METC | 4557 | 2017-02-21 | METC_13_017 | 8699 | 2018-06-27 | TEQ | 2019-12-31 | Croton | Four Mile | 1 | 138 |  |  | Add a dual pilot relay protection system on Croton to Four Mile 138 kV circuit so that 3 phase to ground faults on the circuit will be cleared within 5 cycles. | MI |  |  | M4_Pre-Construction | 483000 |  |  | N | N | N | Y
A in MTEP14 | A | West | MH, MP | 3831 | 2014-12-17 | GNTL | 7200 | 2014-09-24 | LN | 2020-06-01 | Dorsey | US/MB Border | 1 | 500 |  | 1732 | Dorsey-US/Manitoba Border 500 kV Line | MB |  | 160 | Planned |  |  |  | N | N | N | Y
A in MTEP14 | A | West | MH, MP | 3831 | 2014-12-17 | GNTL | 7622 | 2014-11-18 | SC | 2020-06-01 | Warroad River |  |  | 500 |  | 1732 | New midpoint series compensation station on Dorsey - Iron Range 500 kV Line | MN | 0 | 0 | Planned | 52433712 | Facility Study |  | N | N | N | Y
A in MTEP14 | A | West | MH, MP | 3831 | 2014-12-17 | GNTL | 7202 | 2014-09-24 | SUB | 2020-06-01 | Iron Range |  |  | 500 | 230 | 1200 | New Iron Range 500/230 kV Substation adjacent to existing Blackberry 230/115 kV Substation | MN | 0 | 0 | Planned | 46023004 | Facility Study |  | N | N | N | Y
A in MTEP14 | A | West | MH, MP | 3831 | 2014-12-17 | GNTL | 7201 | 2014-11-18 | LN | 2020-06-01 | US/MB Border | Iron Range | 1 | 500 |  | 1732 | US/Manitoba Border-Iron Range 500 kV Line | MN |  | 220 | Planned | 573207005 | Facility Study |  | N | N | N | Y
A in MTEP14 | A | West | MP | 3831 | 2014-12-17 | GNTL | 20289 | 2015-01-06 | LNrl | 2020-06-01 | Iron Range | various |  | 230 |  |  | Modifications to and reroutes of existing 230 kV and 115 kV lines at Iron Range Substation site | MN | 0 | 2 | Planned | 3891711 | Facility Study |  | N | N | N
A in MTEP14 | A | West | MP | 3831 | 2014-12-17 | GNTL | 20293 | 2015-01-06 | RLY | 2020-06-01 | Hilltop |  |  | 230 |  |  | One 230 kV panel replacement at Hilltop to facilitate interconnection of Iron Range 500/230 kV Substation | MN | 0 | 0 | Planned | 137500 | Facility Study |  | N | N | N
A in MTEP14 | A | West | MP | 3831 | 2014-12-17 | GNTL | 20292 | 2015-01-06 | RLY | 2020-06-01 | Arrowhead |  |  | 230 |  |  | One 230 kV panel replacement at Arrowhead to facilitate interconnection of Iron Range 500/230 kV Substation | MN | 0 | 0 | Planned | 137500 | Facility Study |  | N | N | N
A in MTEP14 | A | West | MP | 3831 | 2014-12-17 | GNTL | 20291 | 2015-01-06 | RLY | 2020-06-01 | Forbes |  |  | 230 |  |  | One 230 kV panel replacement at Forbes to facilitate interconnection of Iron Range 500/230 kV Substation | MN | 0 | 0 | Planned | 137500 | Facility Study |  | N | N | N
A in MTEP14 | A | West | MP | 3831 | 2014-12-17 | GNTL | 20290 | 2015-01-06 | RLY | 2020-06-01 | Blackberry |  |  | 230 |  |  | Two 230 kV panel replacements at Blackberry to facilitate interconnection of Iron Range 500/230 kV Substation | MN | 0 | 0 | Planned | 275000 | Facility Study |  | N | N | N
A in MTEP14 | A | West | OTP | 4444 | 2016-12-22 | OTP | 8503 | 2016-12-22 | LNup | 2017-01-31 | NERC Alert Facility Ratings for Low Priority | Throughout system |  | 115 |  |  | Verify and remediate facilities as required due to the industry-wide NERC alert | MN,ND,SD |  |  | Planned | 7701028 | Construction |  | N | N | N | Y
A in MTEP13 | A | Central | DEM | 4032 | 2012-09-12 | AMIN0744 | 7665 | 2018-06-28 | CB | 2019-04-01 | Five Points 230kV | brkr replacements |  | 230 | 138 |  | Five Points Station Upgrade Phase I ? Install new prefabricated control building. Replace 230kV breakers and relays. Replace 230kV circuit switchers with 230kV breakers. Replace 230-138kV bank protection. Replace 230kV bus protection. 230kV wave traps | IN |  |  | Under Construction | 5406000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | Central | DEM | 4033 | 2016-10-04 | AMIN0758 | 7666 | 2018-09-27 | LNrb | 2018-12-31 | Camp Atterbury | Edinburg |  | 69 |  | 100 | Camp Atterbury to Edinburg 6950 Reconductor 2/0 Cu (4.0 miles) to 477ACSR and uprate existing 477ACSR 80C to 477ACSR 100C (4.5 miles). | IN | 8.5 |  | M4_Pre-Construction | 1650765 | Engineering |  | N | N | N | NT
A in MTEP13 | A | Central | DEM | 4037 | 2012-09-12 | AMIN0841 | 7670 | 2016-08-23 | SUB | 2019-12-31 | Lafayette 230 | breaker |  | 230 |  |  | Lafayette 230kV Sub Ring Bus - Phase 2, install one 230kV breaker, support structures, bus and 954KCM jumpers to complete five-breaker - 230kV ring bus. Insert between Banks 3 and 4. | IN |  |  | M3_Long Lead Materials | 1618000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 7892 | 2018-06-18 | SwSta | 2020-12-31 | Toll Road 120kV |  |  | 120 |  |  | Construct a 120kV switching station (Toll Road). | MI |  |  | M4_Pre-Construction | 15000000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 8318 | 2018-03-27 | SVC | 2018-12-31 | Toll Road |  |  | 120 |  |  | Install a 100 MVAR SVC at Toll Road. | MI |  |  | M4_Pre-Construction | 25000000 | Planning |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 8317 | 2018-06-18 | LN | 2020-12-31 | Toll Road | Fermi | 3 | 120 |  |  | Loop the existing Fermi - Swan Creek 120kV line into Toll Road. | MI |  |  | M4_Pre-Construction | 0 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 7898 | 2018-06-18 | LN | 2020-12-31 | Toll Road | Swan Creek | 1 | 120 |  |  | Loop the existing Fermi - Swan Creek 120kV line into Toll Road. | MI |  |  | M4_Pre-Construction | 0 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 7897 | 2018-06-18 | LN | 2020-12-31 | Toll Road | Fermi | 2 | 120 |  |  | Loop the existing Fermi - Radka 120kV line into Toll Road. | MI |  |  | M4_Pre-Construction | 0 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 7896 | 2018-06-18 | LN | 2020-12-31 | Toll Road | Radka | 1 | 120 |  |  | Loop the existing Fermi - Radka 120kV line into Toll Road. | MI |  |  | M4_Pre-Construction | 0 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 7895 | 2018-06-18 | LN | 2020-12-31 | Toll Road | Fermi | 1 | 120 |  |  | Loop the existing Fermi - Shoal 120kV line into Toll Road. | MI |  |  | M4_Pre-Construction | 0 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4153 | 2018-06-18 | ITC_13_021 | 7894 | 2018-06-18 | LN | 2020-12-31 | Toll Road | Shoal | 1 | 120 |  |  | Loop the existing Fermi - Shoal 120kV line into Toll Road. | MI |  |  | M4_Pre-Construction | 0 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4175 | 2016-08-30 | ITC-015 | 6706 | 2017-06-28 | TEQ | 2018-09-30 | Seville 1 & 2 |  |  | 120 |  |  | Install a new 120 kV, 3-way, full-load-break pole top switch at each tap | MI |  |  | M4_Pre-Construction |  |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4175 | 2016-08-30 | ITC-015 | 7922 | 2014-11-06 | TEQ | 2014-12-31 | ITCT Pole Top Switch Additions/Replacement 2014 | Throughout system |  |  |  |  | Install a new or replace an existing120 kV, 1-way, full-load-break pole top switch at needed tap points. | MI |  |  | Under Construction | 2400000 |  |  | N | N | N | Y
A in MTEP13 | A | East | ITC, ITCT | 4175 | 2016-08-30 | ITC-015 | 6711 | 2016-03-22 | TEQ | 2016-06-30 | Topaz 2 | Peru |  | 120 |  |  | Install a new 120 kV, 1-way, full-load-break pole top switch (toward Peru) | MI |  |  | M4_Pre-Construction |  |  |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4099 | 2012-09-14 | AleaW-SBroadway | 7763 | 2017-11-10 | LN | 2022-12-31 | Albert Lea Westside | South Broadway | 1 | 69 | 69 | 40 MVA | Rebuild the Albert Lea Westside-South Broadway 69kV to T2-4/0. | MN | 2 |  | M1_Final SPM or OOC | 840000 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4101 | 2012-09-14 | Montgomery-Waseca | 7766 | 2016-06-30 | LN | 2020-12-31 | GRE-French Lake Tap | Waseca Junction | 1 | 69 | 69 | 77 MVA | Rebuild the French Lake tap-Waseca Jct. to T2-4/0. | MN | 16.34 |  | M3_Long Lead Materials | 13654256 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4102 | 2012-09-14 | Columbus Jct-Newport | 7767 | 2018-06-29 | LN | 2023-12-31 | Newport | Cairo REC | 1 | 69 | 69 | 36 MVA | Rebuild the Newport-Cairo REC 69kV to T2-4/0. | IA | 8.65 |  | M1_Final SPM or OOC | 6242696 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4102 | 2012-09-14 | Columbus Jct-Newport | 7770 | 2018-06-29 | LN | 2023-12-31 | IBP Tap | Columbus Jct | 1 | 69 | 69 | 59 MVA | Rebuild the IBP Tap-Columbus Jct 69kV to T2-4/0. | IA | 0.1 |  | M1_Final SPM or OOC | 72170 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4102 | 2012-09-14 | Columbus Jct-Newport | 7769 | 2018-06-29 | LN | 2023-12-31 | Winfield Tap | IBP Tap | 1 | 69 | 69 | 77 MVA | Rebuild the Winfield Tap-IBP Tap 69kV to T2-4/0. | IA | 7.61 |  | M1_Final SPM or OOC | 5492130 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4102 | 2012-09-14 | Columbus Jct-Newport | 7768 | 2018-06-29 | LN | 2023-12-31 | Cairo REC | Winfield Tap | 1 | 69 | 69 | 77 MVA | Rebuild the Cairo REC-Winfield Tap 69kV to T2-4/0. | IA | 2.76 |  | M1_Final SPM or OOC | 1991889 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4103 | 2018-10-04 | NBurl-Mediapolis | 7771 | 2017-10-09 | LN | 2018-08-27 | North Burlington | North Burlington Tap | 1 | 69 | 69 | 69 MVA | Rebuild the North Burlington-North Burlington Tap 69kV to T2-4/0. | IA | 8.76 |  | M1_Final SPM or OOC | 5760000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4104 | 2012-09-14 | Lansing-Monona | 7772 | 2017-06-30 | LN | 2021-12-31 | Lansing | Harper's Ferry Tap | 1 | 69 | 69 | 57 MVA | Rebuild the Lansing-Harper's Ferry Tap 69kV to T2-4/0. | IA | 6.57 |  | M3_Long Lead Materials | 5777996 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4104 | 2012-09-14 | Lansing-Monona | 7774 | 2017-06-30 | LN | 2021-12-31 | WatervilleTap | Monona | 1 | 69 | 69 | 48 MVA | Rebuild the Waterville Tap-Monona 69kV to T2-4/0. | IA | 15.59 |  | M3_Long Lead Materials | 13025337 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4104 | 2012-09-14 | Lansing-Monona | 7773 | 2017-06-30 | LN | 2021-12-31 | Harper's Ferry Tap | WatervilleTap | 1 | 69 | 69 | 77 MVA | Rebuild the Harper's Ferry Tap-Waterville Tap 69kV to T2-4/0. | IA | 2.63 |  | M3_Long Lead Materials | 2171703 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4105 | 2012-09-14 | Decorah-Waukon | 7775 | 2016-06-29 | LN | 2022-12-31 | Decorah | Ludlow Tap | 1 | 69 | 69 | 69 MVA | Rebuild the Decorah-Ludlow Tap 69kV to T2-4/0. | IA | 20.48 |  | M1_Final SPM or OOC | 8600000 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4105 | 2012-09-14 | Decorah-Waukon | 7776 | 2016-06-29 | LN | 2022-12-31 | Ludlow Tap | Waukon - IPL | 1 | 69 | 69 | 59 MVA | Rebuild the Ludlow Tap-Waukon 69kV to T2-4/0. | IA | 2.51 |  | M1_Final SPM or OOC | 1060000 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4106 | 2012-09-14 | Windsor-Richfield | 7777 | 2017-06-30 | LN | 2022-12-31 | Windsor | Hawk Tap | 1 | 69 | 69 | 48 MVA | Rebuild the Windsor-Hawk Tap 69kV to T2-4/0. | IA | 6.6 |  | M1_Final SPM or OOC | 2775000 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4106 | 2012-09-14 | Windsor-Richfield | 7778 | 2017-06-30 | LN | 2022-12-31 | Hawk Tap | Richfield | 1 | 69 | 69 | 45 MVA | Rebuild the Hawk Tap-Richfield 69kV to T2-4/0. | IA | 4.64 |  | M1_Final SPM or OOC | 1975000 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4108 | 2012-09-14 | Ellendale-WOwatonna | 7779 | 2016-06-30 | LN | 2022-12-31 | Ellendale | Steele Center Tap | 1 | 69 | 69 | 77 MVA | Rebuild the Ellendale-Steele Center Tap to T2-4/0 | MN | 1.98 |  | M1_Final SPM or OOC | 1091365 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4108 | 2012-09-14 | Ellendale-WOwatonna | 7781 | 2016-06-30 | LN | 2022-12-31 | Pratt Tap | West Owatonna | 1 | 69 | 69 | 77 MVA | Rebuild the Pratt Tap-West Owatonna to T2-4/0 | MN | 4.25 |  | M1_Final SPM or OOC | 2342576 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4108 | 2012-09-14 | Ellendale-WOwatonna | 7780 | 2016-06-30 | LN | 2022-12-31 | Steele Center Tap | Pratt Tap | 1 | 69 | 69 | 77 MVA | Rebuild the Steele Center Tap-Pratt Tap to T2-4/0 | MN | 6.98 |  | M1_Final SPM or OOC | 3847336 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4115 | 2012-09-14 | Fletcher Sub | 7808 | 2016-06-30 | SUB | 2019-12-31 | Fletcher | Substation | 1 | 161 | 69 |  | Build new Fletcher 161kV & 69kV sub | IA |  |  | M1_Final SPM or OOC | 5173600 | Engineering |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4115 | 2012-09-14 | Fletcher Sub | 7809 | 2016-06-30 | TX | 2019-12-31 | Fletcher | Transformer | 1 | 161 | 69 | 150 MVA | New Fletcher 150 MVA 161/69kV TRF | IA |  |  | M1_Final SPM or OOC | 2000000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | West | ITCM | 4116 | 2012-09-14 | East IA phase 2 | 7804 | 2017-10-03 | LN | 2018-09-05 | Springville | Amber | 1 | 69 | 69 | 77 MVA | Rebuild the Springville-Amber to T2-4/0 | IA | 21.1 |  | M1_Final SPM or OOC | 9120000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | West | ITCM, MEC | 3249 | 2014-03-31 | G5566, 32337 | 6052 | 2017-09-27 | LN | 2019-12-01 | NE 54th Ave. | Bondurant | 1 | 161 |  | 410 | New 161 kV line from NE 54th Ave. to Bondurant and associated substation equipment additions. | IA | 0 | 8.3 | Planned | 11221895 | Planning |  | N | N | N | Y
A in MTEP13 | A | East | ITCT | 4286 | 2015-04-03 | ITC_12_015 | 8093 | 2015-03-25 | LN | 2018-05-31 | Frisbie | Waterman | 1 | 120 |  |  | Loop in the Frisbie ? Waterman 120 kV underground cable to feed the Henry Ford substation. Splices and terminals will be installed and underground cable run from the existing line to the new substation. The substation is located approximated 150 feet fro | MI |  |  | M2a_Pre-Project Approval | 5000000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | West | MEC | 3248 | 2015-09-15 | G2705, 32335 | 6048 | 2018-06-29 | LN | 2019-06-01 | Rising Sun Substation | NE 54th Ave. | 1 | 161 |  | 410 | New 161 kV line from Rising Sun Substation on DPS-Reasnor line to East Altoona and associated substation equipment additions. | IA | 0 | 6 | Under Construction | 8100000 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | MEC | 3248 | 2015-09-15 | G2705, 32335 | 6049 | 2018-06-29 | SwSta | 2019-06-01 | Rising Sun Substation |  |  | 161 |  |  | New 161 kV breakered substation off the DPS-Reasnor 161 kV line | IA |  |  | Under Construction | 5200000 | Planning |  | N | N | N | Y
A in MTEP13 | A | East | METC | 4149 | 2017-12-21 | METC_12_026 | 7884 | 2017-12-21 | LNup | 2018-09-15 | Argenta | Tallmadge | 1 | 345 |  |  | Remediate sag on the Argenta ? Tallmadge 345kV line to bring its thermal rating up to 2422 Amp (1447 MVA) | MI |  |  | M4_Pre-Construction | 1500000 | Engineering |  | N | N | N | Y
A in MTEP13 | A | East | WPSC | 4084 | 2015-04-03 | NS-VB | 7737 | 2016-09-15 | LNrb | 2018-12-31 | North Shade | Vestaburg | 1 | 69 |  | 143.4MVA | Rebuild Line (Poles have reached the end of their useful life) | MI | 19.29 |  | Planned | 10000000 |  |  | N | N | N | Y
A in MTEP13 | A | East | WPSC | 4085 | 2015-04-03 | LC-FNX | 7738 | 2017-03-07 | LNrb | 2016-12-31 | Lake County | Fountain Junction | 1 | 69 |  | 143.4MVA | Rebuild Overloaded line (Peak case) | MI | 6.35 |  | Planned | 3100000 |  |  | N | N | N | Y
A in MTEP13 | A | West | XEL | 4314 | 2013-01-10 |  | 8251 | 2017-12-26 | LNrb | 2022-12-01 | Bay Front | Saxon Pump | 1 | 88 |  |  | It is expected to rebuild this line to 115 kV capable 795 ACSR conductor operated at 88 kV. | WI |  |  | Planned | 26377500 | Planning |  | N | N | N | Y
A in MTEP13 | A | West | XEL | 4314 | 2013-01-10 |  | 8252 | 2017-12-26 | LNrb | 2022-12-01 | Saxon Pump | Norrie | 1 | 88 |  |  | It is expected to rebuild this line to 115 kV capable 795 ACSR conductor operated at 88 kV. | WI,MI |  |  | Planned | 9600000 | Planning |  | N | N | N | Y
A in MTEP12 | A | Central | AmerenMO | 3366 | 2015-09-11 |  | 6237 | 2015-09-11 | CB | 2018-12-01 | Wallen Creek | Install 1200 A breaker and disconnect switches |  | 138 |  | 240 | Install 2000 A breaker and 2-2000 A 138 kV motor operated disconnect switches | MO |  |  | Planned | 2635000 | Engineering |  | N | N | N | Y
A in MTEP12 | A | West | ATC, ATC LLC | 3679 | 2014-06-13 | NP-Package2_3 F3501 WO069260 | 6912 | 2018-09-28 | LN | 2018-10-25 | North Appleton | Morgan | 1 | 345 |  | 1204 | New 345 kV line from North Appleton - Morgan | WI |  | 40 | Under Construction | 119433000 | Engineering |  | N | Y | Y | Y
A in MTEP12 | A | West | ATC, ATC LLC | 3679 | 2014-06-13 | NP-Package2_3 F3501 WO069260 | 6911 | 2018-09-28 | SUB | 2018-06-21 | North Appleton |  |  | 345 |  |  | New 345 kV Switchyard North Appleton | WI |  |  | M5_In Service | 38486000 | Engineering |  | N | Y | Y | Y
A in MTEP12 | A | West | ATC, ATC LLC | 3952 | 2014-06-13 | NP_GB-M 138, PR05016 F3501 WO069260 | 6927 | 2018-09-28 | LN | 2018-10-28 | North Appleton | Morgan | 1 | 138 |  | 294 | New 138 kV line from North Appleton-Morgan | WI |  | 40 | Under Construction | 56309000 | Engineering |  | N | N | N | Y
A in MTEP12 | A | Central | BREC | 3792 | 2012-04-20 | Matanzas | 7127 | 2018-05-08 | LN | 2016-01-01 | BR Tap (3 terminal midpoint) | Matanzas (LKE) | 1 | 161 |  | 509 | 10.5 Mile 161 kV of line from Wilson Substation to new 161kV station - only 600 feet of new construction required. | KY |  | 0.2 | Under Construction | 0 | Planning |  | N | N | N | Y
A in MTEP12 | A | Central | DEM | 3542 | 2015-09-15 | AMIN0447 | 6611 | 2016-11-04 | Dist | 2019-12-31 | New Castle Ingersoll |  |  | 69 | 12 |  | New Castle Ingersoll 1 Bank 2 Repl ? Replace 34/12kV bank w/22MVA 69/12kV Bank. Add 69kV tap line to existing sub. | IN |  | 0.23 | Under Construction | 579657 | Engineering |  | N | N | N | NT
A in MTEP12 | A | West | GRE | 11543 | 2016-07-25 | 200497 | 21785 | 2016-07-25 | TAP | 2018-11-01 | Glacial Ridge |  |  | 69 |  |  | Install new 69kV 3-way switch structure. | MN |  |  | Proposed | 150000 | Planning |  | N | N | N
A in MTEP12 | A | West | GRE | 11563 | 2016-07-25 | 202038 | 21786 | 2017-03-28 | SUB | 2018-09-20 | McHenry |  |  | 115 |  |  | Install 115 kV ring bus | ND |  |  | Planned | 4952173 | Planning |  | N | N | N
A in MTEP12 | A | East | ITC, ITCT | 3591 | 2018-03-27 | ITC_13_028 | 6690 | 2018-03-27 | TEQ | 2018-06-01 | St. Clair |  |  | 345 |  |  | Replace 345kV station equipment in the B, C and D rows at St. Clair. | MI |  |  | Under Construction | 924000 |  |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3630 | 2011-12-13 | Adams-Stewartville | 6739 | 2017-06-30 | LN | 2023-12-31 | Adams | Stewartvillle 6th Street | 1 | 69 |  | 77 MVA | Rebuild 69kV line to T2-4/0 ACSR | IA | 29.88 |  | Planned | 10500000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3630 | 2011-12-13 | Adams-Stewartville | 6740 | 2017-06-30 | LN | 2023-12-31 | Stewartvillle 6th Street | Stewartville Junction | 1 | 69 |  | 77 MVA | Rebuild 69kV line to T2-4/0 ACSR | IA | 4.68 |  | Planned | 1700000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3632 | 2011-12-13 | Arnold 161 | 6753 | 2018-05-09 | SUB | 2018-12-30 | Arnold | Substation | 1 | 161 |  |  | Add two new 161kV breakers and reroute Hiawatha line terminal off the generation bus. | IA |  |  | Under Construction | 2529402 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3638 | 2011-12-13 | Corydon Sub Rbld | 6755 | 2017-10-11 | SUB | 2019-06-28 | Corydon | Substation | 1 | 69 |  | 143 MVA | Complte rebuild of the Corydon sub | IA |  |  | M1_Final SPM or OOC | 5129204 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3640 | 2011-12-13 | Belmond-Meservey | 6761 | 2018-05-10 | LN | 2019-12-31 | Belmond | Meservey Tap | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 4.65 |  | M3_Long Lead Materials | 1056316 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3643 | 2011-12-13 | Osceola-Woodburn | 6765 | 2016-06-30 | LN | 2022-12-31 | Osceola | Woodburn Junction | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 5.5 |  | M1_Final SPM or OOC | 1950000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3644 | 2011-12-13 | Knoxville-Lucas | 6766 | 2018-06-29 | LN | 2023-12-31 | Knoxville | Lucas | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 10.6 |  | M1_Final SPM or OOC | 3750000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3645 | 2011-12-13 | Tirboji-Orleans Tap | 6767 | 2017-10-06 | LN | 2027-12-31 | Triboji | Montgomery | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 5.75 |  | M1_Final SPM or OOC | 2000000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3645 | 2011-12-13 | Tirboji-Orleans Tap | 6770 | 2017-10-06 | LN | 2027-12-31 | Spirti Lake | Orleans Tap | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 0.4 |  | M1_Final SPM or OOC | 200000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3645 | 2011-12-13 | Tirboji-Orleans Tap | 6769 | 2017-10-06 | LN | 2027-12-31 | Bosworth | Spirti Lake | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 1.17 |  | M1_Final SPM or OOC | 400000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3645 | 2011-12-13 | Tirboji-Orleans Tap | 6768 | 2017-10-06 | LN | 2027-12-31 | Bosworth | Montgomery | 1 | 69 |  | 77 MVA | Rebuild the 69kV line section | IA | 2.16 |  | M1_Final SPM or OOC | 750000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 7116 | 2018-05-02 | LN | 2021-12-31 | Dixon | Fulton | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 17 |  | M2a_Pre-Project Approval | 10890000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 7114 | 2018-06-29 | LN | 2022-05-20 | PCI | Putnam | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA |  | 0.5 | M1_Final SPM or OOC | 175000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 7113 | 2018-06-29 | LN | 2018-12-02 | Mt Vernon | Lisbon | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 2 | 2 | Under Construction | 3358200 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 7111 | 2018-06-29 | LN | 2022-05-25 | Clarence | Clarence REC | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA |  | 2 | M4_Pre-Construction | 1627555 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 7110 | 2018-06-29 | LN | 2019-04-15 | Rome Tap | Rome | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA |  | 2 | M4_Pre-Construction | 5898850 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 6816 | 2018-06-29 | LN | 2019-01-15 | Prairie Creek | Bertam JU | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 6 |  | M4_Pre-Construction | 3880200 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 6815 | 2018-06-29 | LN | 2019-07-30 | Clarence | Wyoming | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 11 |  | M3_Long Lead Materials | 4881061 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3647 | 2011-12-13 | East IA Rebuilds | 6814 | 2018-06-29 | LN | 2019-07-30 | Clarence | Clarence Tap | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 1 |  | M3_Long Lead Materials | 389000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3648 | 2011-12-13 | Marshalltown-Grand Jct | 6791 | 2018-05-02 | LN | 2019-12-31 | Boone Jct | Ridgeport REC | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 2.75 |  | M3_Long Lead Materials | 3928512 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3648 | 2011-12-13 | Marshalltown-Grand Jct | 6805 | 2018-05-02 | LN | 2019-02-28 | Valley RECTap | Odgen Muni Tap | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 1.7 |  | M3_Long Lead Materials | 4778628 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3648 | 2011-12-13 | Marshalltown-Grand Jct | 6804 | 2018-05-02 | LN | 2019-05-06 | Boone South | Valley RECTap | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 1.15 |  | M3_Long Lead Materials | 715536 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3648 | 2011-12-13 | Marshalltown-Grand Jct | 6803 | 2018-05-02 | LN | 2019-05-06 | Quartz Ave | Boone South | 1 | 34 |  | 77 MVA | Rebuild the 34kV line section to 69kV for future conversion | IA | 5.2 |  | M3_Long Lead Materials | 2416730 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3649 | 2011-12-13 | Plaza LI | 6758 | 2017-06-30 | SUB | 2025-12-31 | Plaza | Substation | 1 | 161 |  | 143 MVA | New Plaza 161/12.5kV substation with 161kV in and out breakers and bus tie breaker | IA |  |  | M1_Final SPM or OOC | 1550000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3649 | 2011-12-13 | Plaza LI | 6760 | 2017-06-30 | LN | 2025-12-31 | Plaza | Marshalltown | 1 | 161 |  |  | Tap the Marshalltown-Timber Creek 161kV for new Plaza sub. | IA |  |  | M1_Final SPM or OOC | 100000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | ITCM | 3649 | 2011-12-13 | Plaza LI | 6759 | 2017-06-30 | LN | 2025-12-31 | Plaza | Timber Creek | 1 | 161 |  |  | Tap the Marshalltown-Timber Creek 161kV for new Plaza sub. | IA |  |  | M1_Final SPM or OOC | 100000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | MEC | 3710 | 2014-03-31 | T3094 | 7023 | 2018-03-30 | SUB | 2019-11-01 | Norwalk |  |  | 161 | 13.2 | 33 | Norwalk 161-13 kV XFMR | IA |  |  | Planned | 886413 | Planning |  | N | N | N | Y
A in MTEP12 | A | East | METC | 3590 | 2015-02-26 |  | 8297 | 2015-02-26 | SVC | 2030-06-01 | Tippy | SVC |  | 138 |  |  | Install an svc at tippy sub | MI |  |  | Planned | 28500000 |  |  | N | Y | N | Y
A in MTEP12 | A | East | METC | 3599 | 2014-03-31 |  | 6698 | 2015-09-28 | TEQ | 2018-12-31 | Palisades |  |  | 345 |  |  | Upgrade the station equipment at Palisades in rows 25, 27, and 29 for the existing configuration. | MI |  |  | M4_Pre-Construction | 4000000 |  |  | N | N | N | Y
A in MTEP12 | A | West | XEL | 3769 | 2011-12-13 | Mankato - Twin Cities through flow mitigation | 7048 | 2018-03-30 | LN | 2022-05-31 | Carver County | Arlington | 1 | 69 |  |  | Rebuild 13 miles of 69 kV line to 477 ACSR to reduce impedance and increase capacity | MN | 13 |  | Planned | 6364887 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | XEL | 3797 | 2012-01-07 | Maple River - Red River 2nd 115 kV circuit | 7134 | 2018-03-30 | LN | 2019-05-31 | Maple River | Red River | 2 | 115 |  |  | New 5 mile 115 kV line | ND |  |  | Under Construction | 13900000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | XEL | 3797 | 2012-01-07 | Maple River - Red River 2nd 115 kV circuit | 7136 | 2018-03-30 | SUB | 2019-05-31 | Red River | substation |  | 115 |  |  | New Line and Termination Work | ND |  |  | Under Construction | 3800000 | Planning |  | N | N | N | Y
A in MTEP12 | A | West | XEL | 3797 | 2012-01-07 | Maple River - Red River 2nd 115 kV circuit | 7135 | 2018-06-27 | SUB | 2019-05-31 | Maple River | substation |  | 115 |  |  | New Line and Termination Work | ND |  |  | Under Construction | 3199014 | Planning |  | N | N | N | Y
A in MTEP11 | A | Central | AmerenIL | 2237 | 2011-11-03 | 11 Prop. MVP Port.1 (62) | 4154 | 2017-06-30 | LN | 2019-11-15 | Kansas | Sugar Creek | 1 | 345 |  | 1793 | new line - 34.5 miles 345 kV; Kansas to Indiana State Line | IL |  | 34.5 | M3_Long Lead Materials | 83394282 |  |  | N | Y | Y | Y
A in MTEP11 | A | Central | AmerenMO | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | 4160 | 2018-03-27 | LN | 2019-05-31 | Ottumwa | Zachary | 1 | 345 | 161 | 1793 | MO portion of new line – Construct 31 mile, 345/161 kV double circuit line | MO |  | 31 | M3_Long Lead Materials | 74000000 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | Central | AmerenMO | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | 20771 | 2018-03-27 | TEQ | 2019-05-31 | Zachary |  |  | 161 |  |  | Area Connection work associated with Zachary Substation | MO |  |  | M3_Long Lead Materials | 3000000 | Budgetary |  | N | Y | Y | Y
A in MTEP11 | A | Central | AmerenMO | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | 5187 | 2018-07-06 | SUB | 2019-05-31 | Zachary | Install Transformer | 1 | 345 | 161 | 560 | Adair Substation - New 560 MVA, 345/161 kV Transformer, 345 kV ring bus.capability | MO |  |  | Under Construction | 27000000 |  |  | N | Y | Y | Y
A in MTEP11 | A | Central | AmerenMO | 3170 | 2017-10-24 | 08 Prop. MVP Port.1 | 5601 | 2018-09-27 | LN | 2019-12-15 | Zachary | Maywood | 1 | 345 | 161 | 1793 | Construct 64 mile, 345/161 kV double circuit line | MO |  | 64 | Under Construction | 139800000 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 23507 | 2018-09-28 | SUBmisc | 2023-12-31 | Eden |  |  | 138 |  |  | Includes remote end work at Eden SS and minimal work at Wyoming Valley Switching Station. | WI |  |  | M1_Final SPM or OOC | 624000 | Planning Preliminary |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 23506 | 2018-09-28 | SUBmisc | 2023-12-31 | Neslon Dewey |  |  | 161 | 138 |  | Includes remote end work at Nelson Dewey SS | WI |  |  | M1_Final SPM or OOC | 1752000 | Planning Preliminary |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 20581 | 2018-09-28 | SUB | 2023-12-31 | Cardinal |  |  | 345 |  |  | Cardinal Substation modifications | WI |  |  | M1_Final SPM or OOC | 2549000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 20580 | 2018-10-01 | SUB | 2023-12-31 | Hill Valley |  |  | 345 | 138 |  | Construct a new Hill Valley Substation, terminate new 345 kV lines, install a 345/138 kV transformer, and loop the Nelson Dewey – Eden 138 kV line into the new station | WI |  |  | M1_Final SPM or OOC | 33101000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC, ATC LLC, XEL | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 5626 | 2018-06-29 | LN | 2018-12-31 | Briggs Road | North Madison | 1 | 345 |  | 1446 | Construct a Briggs Road - North Madison 345-kV line | WI |  | 161.8 | Under Construction | 463376000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC, DPC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 20578 | 2018-09-28 | LN | 2023-12-31 | Hill Valley | Cardinal | 1 | 345 |  | 1399 | New line | WI |  | 60 | M1_Final SPM or OOC | 219303000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ATC, XEL | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 6573 | 2018-06-29 | SUB | 2018-12-31 | Briggs Road (North LaCrosse) | Substation |  | 345 |  |  | Terminate North Madison - North LaCrosse 345 kV line into Briggs Road, create 345 kV breaker ring bus, and 50 MVAR of 34.5 kV reactors on the tertiary | WI |  |  | Under Construction | 9148000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | Central | DEI | 2237 | 2011-11-03 | 11 Prop. MVP Port.1 (62) | 8313 | 2017-07-11 | LN | 2018-11-15 | IL/IN State Line | Sugar Creek | 1 | 345 |  | 1793 | Sugar Creek 345kV ring breaker addition and 1.5 mile - 3000A - 345kV line to IL/IN state line. | IN |  | 1.5 | M3_Long Lead Materials | 8809000 | Engineering |  | N | N | N | Y
A in MTEP11 | A | Central | DEM | 3386 | 2010-09-15 | AMIN0379 | 6259 | 406770 | LN | 2019-06-01 | Carmel Springmill Rd. | Hortonville | 1 | 69 |  | 143 | Carmel Springmill Rd. Sub - Add 3-69kV breakers; straight bus config; build .23 mi 69kV 954ACSS@200C from Springmill to old Springmill Jct. Completes circuit to Hortonville. Change operating mode at Homeplace to close loop from 146th to Springmill. | IN |  | 0.23 | M3_Long Lead Materials | 1866000 | Engineering |  | N | N | N | NT
A in MTEP11 | A | West | DPC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 23503 | 2018-06-27 | SUBmisc | 2023-12-31 | Stoneman |  |  | 161 | 69 |  | Stoneman Substation modifications due to routing | WI |  |  | Planned | 260000 | Planning Preliminary |  | N | Y | Y | Y
A in MTEP11 | A | West | DPC | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 23504 | 2018-06-27 | LN | 2023-12-31 | Millville | Turkey River | 1 | 69 |  | 86 | Short connection to existing DPC 69 kV line due to routing | IA |  | 0.5 | Planned | 73500 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | DPC, ITCM | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 20577 | 2018-06-29 | LN | 2023-12-31 | Hill Valley | Hickory Creek | 1 | 345 |  | 1399 | New circuit | WI,IA |  | 48.3 | M1_Final SPM or OOC | 221214500 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | GRE | 2679 | 2010-09-15 | 200331 | 4696 | 2013-09-25 | LN | 2021-05-31 | Ramsey | Grand Forks | 1 | 230 |  |  | 230 kV rebuild | MN | 81.02 |  | Under Construction | 41496024.63 | Planning |  | N | N | N | Y
A in MTEP11 | A | West | GRE | 3454 | 2014-09-12 | 201035 | 6659 | 2017-06-27 | LN | 2018-12-21 | Pomerleau Lake | Plymouth/Parkers Lake | 1&2 | 115 |  |  | In and Out tap to Pomerleau Lake substation | MN |  | 0.25 | Planned | 428949.26 | Engineering |  | N | N | N | Y
A in MTEP11 | A | East | ITC, ITCT | 3285 | 2018-06-27 | ITCT_12_007 | 6516 | 2018-06-27 | SUB | 2020-12-31 | Shoal | 33.3 Mvar capacitor |  | 120 |  |  | Install a 33.3 Mvar Capacitor at Shoal 120kV station as well as two line breakers and a tie breaker. | MI |  |  | M4_Pre-Construction | 3430000 | Engineering |  | N | N | N | Y
A in MTEP11 | A | West | ITCM | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | 20770 | 2018-08-23 | LN | 2019-05-19 | Ottumwa | IA/MO Border | 1 | 345 | 161 | 1793 | 345/161kV double circuit line. ITC Midwest portion ~20 miles | IA |  | 14 | M3_Long Lead Materials | 51600000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 20579 | 2018-06-29 | SUB | 2023-12-31 | Hickory Creek |  |  | 345 |  |  | Hickory Creek Substation modifications | IA |  |  | Under Construction | 13339000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM | 3127 | 2018-09-28 | PR04030 F3398 WO68924, WO68924 | 23505 | 2018-06-27 | SUBmisc | 2023-12-31 | Turkey River |  |  | 161 | 69 |  | Turkey River Substation modifications | IA |  |  | Planned |  | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM | 3213 | 2014-03-31 | 04 Prop. MVP Port.1 | 6539 | 2018-09-28 | LN | 2018-10-05 | Worth County | Colby | 1 | 161 |  |  | Retire existing 161kV H frame circuit | IA |  |  | Under Construction | 0 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM | 3213 | 2014-03-31 | 04 Prop. MVP Port.1 | 6538 | 2018-09-28 | LN | 2018-08-15 | Ledyard | Winnco | 1 | 161 |  |  | Retire existing 161kV H frame circuit | IA |  |  | M5_In Service | 0 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM | 3213 | 2014-03-31 | 04 Prop. MVP Port.1 | 6537 | 2018-09-28 | LN | 2018-10-05 | Colby | Worth County | 1 | 161 |  | 200 MVA | Construct 345-161kV double circuit | IA |  | 7 | Under Construction | 0 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM | 3213 | 2014-03-31 | 04 Prop. MVP Port.1 | 6536 | 2018-09-28 | LN | 2019-06-30 | Ledyard | Colby | 1 | 345 |  | 1800 MVA | Construct 345-161kV double circuit | IA |  | 61 | Under Construction | 178500000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | West | ITCM, MEC | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | 6566 | 2018-08-23 | TEQ | 2019-05-19 | Ottumwa | 345 kV terminal |  | 345 |  |  | add 345 kV terminal for Zachary line | IA |  |  | M3_Long Lead Materials | 12700000 | Engineering |  | N | Y | Y | Y
A in MTEP11 | A | East | ITCT | 3285 | 2018-06-27 | ITCT_12_007 | 8994 | 2018-06-27 | LNup | 2020-12-31 | Shoal | Custer | 1 | 120 |  |  | OPGW installation | MI |  |  | M4_Pre-Construction | 900000 |  |  | N | N | N | Y
A in MTEP11 | A | West | MDU | 2220 | 2018-07-31 | 06 Prop. MVP Port.1 | 6382 | 2018-08-08 | TX | 2019-06-30 | Ellendale 345/230 | Transformer |  | 345 | 230 | 560 MVA | Substation, Transformer 345/230, Line Reactor | ND |  |  | Under Construction | 30000000 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | MDU, OTP | 2220 | 2018-07-31 | 06 Prop. MVP Port.1 | 4092 | 2018-07-31 | LN | 2019-06-30 | Big Stone South | Ellendale |  | 345 |  | 1800 MVA | Line | SD,ND |  | 163 | Under Construction | 244000000 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | West | MEC | 2248 | 2015-03-24 | 07 Prop. MVP Port.1 | 6565 | 2018-06-29 | LN | 2019-05-16 | Ottumwa | Iowa border | 1 | 345 | 161 |  | 345/161 double circuit line; MEC's portion | IA | 29 |  | M2a_Pre-Project Approval | 54658799 | Budgetary |  | N | Y | Y | Y
A in MTEP11 | A | East | NIPS | 3203 | 2011-11-03 | 12 Prop. MVP Port.1 | 5949 | 2018-08-01 | LN | 2018-09-30 | Reynolds | Hiple | 2 | 345 |  |  | new line tap at Burr Oak | IN |  |  | Under Construction | 404800000 | Planning |  | N | Y | Y | Y
A in MTEP11 | A | East | WPSC | 3335 | 2010-09-15 | Burnips Xmsn | 6200 | 2016-09-15 | SUB | 2022-12-31 | Burnips | Substation Upgrade |  | 69 |  |  | Replace bus work, breakers, relays, and any other necessary components | MI |  |  | Planned | 800000 |  |  | N | N | N | Y
A in MTEP10 | A | Central | DEM | 2143 | 2017-09-27 | 602J3066 | 2929 | 2017-09-27 | TX | 2023-06-01 | Frances Creek | bank 2 | 2 | 345 | 69 | 200 | Add Frances Creek 345/69kV Bank 2 - 200MVA with LTC | IN |  |  | M1_Final SPM or OOC | 6887000 | Engineering |  | N | N | N | NT
A in MTEP10 | A | West | GRE | 2577 | 2016-02-10 | 20312 | 4588 | 2016-06-29 | SUB | 2021-05-18 | Columbus | Columbus Tap | 1 | 69 |  |  | New Distribution | MN |  | 0 | Planned | 140000 | Planning |  | N | N | N | NT
A in MTEP10 | A | West | GRE | 2579 | 2010-09-15 | 20273 | 4590 | 2017-09-12 | SUB | 2021-11-01 | Foster Lake | Foster Lake Tap | 1 | 69 |  |  | New Distribution | MN |  | 0 | Planned | 140000 | Planning |  | N | N | N | NT
A in MTEP10 | A | West | GRE | 2589 | 2009-11-19 | 20328 | 4600 | 2017-09-13 | LN | 2023-07-20 | Rich Valley | Rich Valley Tap | 1 | 69 |  |  | New Distribution | MN |  | 2 | Planned | 115001 | Engineering |  | N | N | N | NT
A in MTEP10 | A | West | GRE | 2670 | 2018-09-11 | 20446 | 4687 | 2018-09-11 | TX | 2019-11-01 | Schuster Lake | transformer | 1 | 115 | 41.6 | 70 | North Perham land acquisition and 115/41.6 kV source | MN |  |  | Planned | 6676163.28 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3048 | 2009-09-14 | Jeff-Perlee | 5266 | 2016-06-28 | LN | 2022-12-31 | Jefferson Co | Perlee | 1 | 69 | 69 | 57 MVA | Rebuild Jefferson Co-Perlee line | IA | 7.38 | 0 | Planned | 2700000 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3053 | 2017-11-09 | Keokuk-Carbide | 5297 | 2018-06-28 | LN | 2020-06-15 | Commercial | Carbide | 1 | 69 | 69 | 100 MVA | Rebild to doulbe ckt 69kV | IA |  |  | Planned | 13694000 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3053 | 2017-11-09 | Keokuk-Carbide | 5296 | 2018-06-28 | LN | 2020-06-15 | Messenger | Commercial | 1 | 69 | 69 | 100 MVA | Rebild to doulbe ckt 69kV | IA |  |  | M3_Long Lead Materials | 4068760 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3055 | 2018-05-04 | CR 34kV Plan | 5293 | 2018-07-09 | SUB | 2018-12-31 | Oak Hill | Substation | 1 | 69 | 69 |  | New 69kV/dist sub | IA |  |  | Under Construction | 2812626 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3055 | 2018-05-04 | CR 34kV Plan | 5283 | 2018-05-04 | LN | 2019-04-01 | Oak Hill | Marion | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) | IA | 8 |  | M3_Long Lead Materials | 4638000 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3055 | 2018-05-04 | CR 34kV Plan | 5282 | 2018-05-04 | LN | 2018-12-31 | PCI | Oak Hill | 1 | 69 | 69 |  | Rebuild 34kV to 69kV(operate at 34kV until 69kV/dist subs are ready) | IA | 5 |  | M4_Pre-Construction | 2351425 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5301 | 2018-06-29 | LN | 2020-05-12 | Moscow | Moscow Tap | 1 | 69 | 69 | 77 MVA | Build a new 3.75 mile 69kV tap to Moscow & retire 7 mile 34kV tap. | IA | 0 | 3.75 | M3_Long Lead Materials | 66000 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 6419 | 2017-10-11 | LN | 2020-12-31 | New Liberty | New Liberty Tap | 1 | 34 | 34 |  | Retire the New Liberty 34kV 9.4 mile tap | IA |  |  | M1_Final SPM or OOC | 282000 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 6418 | 2018-06-29 | LN | 2020-12-31 | Moscow Tap | Moscow | 1 | 34 | 34 |  | Retire the Moscow 34kV 7 mile tap | IA |  |  | M1_Final SPM or OOC | 210000 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5306 | 2017-10-11 | LN | 2020-12-31 | New Liberty Tap | Dixon Jct | 1 | 69 | 69 |  | Tap the Bennett Switch Station to Dixon Jct 69kV line for a new 69kV tap to New Liberty. | IA | 0 | 0 | M1_Final SPM or OOC | 0 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5305 | 2017-10-11 | LN | 2020-12-31 | Bennett | New Liberty Tap | 1 | 69 | 69 |  | Tap the Bennett Switch Station to Dixon Jct 69kV line for a new 69kV tap to New Liberty. | IA | 0 | 0 | M1_Final SPM or OOC | 0 | Planning |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5304 | 2017-10-11 | LN | 2020-12-31 | New Liberty | New Liberty Tap | 1 | 69 | 69 | 77 MVA | Build a new 2 mile 69kV tap to New Liberty & retire 9.4 mile 34kV tap. | IA | 0 | 2 | M1_Final SPM or OOC | 700000 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5303 | 2018-06-29 | LN | 2020-05-12 | Moscow Tap | Magmet T | 1 | 69 | 69 |  | Tap the Muscatine Switch Station to Magmet T69kV line for new tap to Moscow. | IA | 0 | 0 | M3_Long Lead Materials | 0 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | ITCM | 3057 | 2010-06-28 | WB 34kV Shift | 5302 | 2018-06-29 | LN | 2020-05-12 | Muscatine Switch Station | Moscow Tap | 1 | 69 | 69 |  | Tap the Muscatine Switch Station to Magmet T69kV line for new tap to Moscow. | IA | 0 | 0 | M3_Long Lead Materials | 0 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | MP | 2761 | 2009-11-13 | Dunka Rd | 4780 | 2018-04-03 | SUB | 2020-12-31 | Northmet | Substation Equipment |  | 138 | 14 |  | Substation Equipment & Transformer | MN |  |  | Planned | 3242847 | Engineering |  | N | N | N | Y
A in MTEP10 | A | West | NWEC | 3092 | 2009-11-16 | 2012-02 | 5410 | 2018-04-04 | LNrb | 2021-06-01 | Lake 26 | Webb Lake |  | 69 |  | 15 | Rebuild 34.5KV line to Webb Lake at 69KV with horizontal post construction and #4/0 ACSR | WI | 2.6 | 0 | Planned | 425000 |  |  | N | N | N | Y
A in MTEP09 | A | Central | AmerenIL | 2273 | 2010-04-05 |  | 4187 | 2016-03-09 | LN | 2020-06-01 | LaFarge | 161 kV Supply to Customer Substation |  | 161 |  |  | Provide 161 kV supply to customer substation | IL |  |  | Planned | 570000 | Engineering |  | N | N | N | Y
A in MTEP09 | A | Central | DEM | 2154 | 2011-09-27 | AMIN0360 | 2942 | 2018-09-27 | SUB | 2019-06-01 | Carmel Rohrer Rd. | distribution sub |  | 69 | 12 |  | Carmel Rohrer Rd 69/12-22.4MVA sub to looped through the 6989 ckt. at or near the existing Carmel Shell Oil tap | IN | 0.4 | 0.4 | M3_Long Lead Materials | 591143 | Engineering |  | N | N | N | NT
A in MTEP09 | A | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4362 | 2017-10-02 | LNrb | 2018-12-31 | Anita-Wiota | Adair | 1 | 34 |  | 39/39 MVA | Rebuild 1.2 miles of the Anita-Wiota-Adair line. | IA | 1.2 |  | Planned | 2194248 |  |  | N | N | N | NT
A in MTEP09 | A | West | ITCM | 2367 | 2009-04-01 | ITCM-08-033 | 4361 | 2017-10-02 | LNrb | 2018-12-31 | Anita 161kV | Anita-Wiota | 1 | 34 |  | 39/39 MVA | Rebuild the 34kV line to 69kV (operate at 34kV). | IA | 3.5 |  | Planned | 2695790 |  |  | N | N | N | NT
A in MTEP09 | A | East | METC | 2478 | 2017-06-30 |  | 4466 | 2018-03-27 | TAP | 2020-06-01 | Capital Ave | Battle Creek | 1 | 138 |  |  | Capital Ave taps the Battle Creek-Verona 138kV circuit #2. | MI |  |  | M2a_Pre-Project Approval | 89094 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2478 | 2017-06-30 |  | 4467 | 2018-03-27 | TAP | 2020-06-01 | Capital Ave | Battle Creek | 1 | 138 |  |  | Capital Ave taps the Battle Creek-Verona 138kV circuit #2. | MI |  |  | M2a_Pre-Project Approval | 89094 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2481 | 2016-06-08 |  | 4470 | 2016-06-08 | TAP | 2018-05-31 | Forest Grove | Campbell | 1 | 138 |  |  | Forest Grove taps the Campbell-Hudsonville (toward Ransom) 138kV circuit | MI |  |  | Planned | 85000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2481 | 2016-06-08 |  | 4471 | 2016-06-08 | TAP | 2018-05-31 | Forest Grove | Hudsonville | 1 | 138 |  |  | Forest Grove taps the Campbell-Hudsonville (toward Ransom) 138kV circuit | MI |  |  | Planned | 85000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2482 | 2018-06-27 |  | 4472 | 2018-06-27 | TAP | 2020-06-01 | Hawthorne | Four Mile | 1 | 138 |  |  | Hawthorne taps the Four Mile-Pingree (toward Blendon) 138kV circuit | MI |  |  | M2a_Pre-Project Approval | 85000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2482 | 2018-06-27 |  | 4473 | 2018-06-27 | TAP | 2020-06-01 | Hawthorne | Pingree | 1 | 138 |  |  | Hawthorne taps the Four Mile-Pingree (toward Blendon) 138kV circuit | MI |  |  | M2a_Pre-Project Approval | 85000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2485 | 2016-06-08 |  | 4478 | 2016-06-08 | RLY | 2019-06-01 | Ransom | Buck Creek | 1 | 138 |  |  | Relay modifications | MI |  |  | Planned | 12000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2486 | 2018-03-27 |  | 4479 | 2018-03-27 | TAP | 2023-06-01 | Haakwood | Rondo | 1 | 138 |  |  | Haakwood taps the Rondo-Vanderbilt section of the Riggsville-Livingston 138kV line. | MI |  |  | Planned | 85000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2486 | 2018-03-27 |  | 4480 | 2018-03-27 | TAP | 2023-06-01 | Haakwood | Vanderbilt | 1 | 138 |  |  | Haakwood taps the Rondo-Vanderbilt section of the Riggsville-Livingston 138kV line. | MI |  |  | Planned | 85000 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2501 | 2015-02-26 |  | 4501 | 2015-02-26 | CAP | 2030-06-01 | Plum | [5 empty] | Install 25.2 MVAR capacitor | MI |  |  | Planned | 435484 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2501 | 2015-02-26 |  | 4500 | 2015-02-26 | CAP | 2030-06-01 | Keystone | [5 empty] | Install 50.4 MVAR capacitor | MI |  |  | Planned | 740323 |  |  | N | N | N | Y
A in MTEP09 | A | East | METC | 2501 | 2015-02-26 |  | 4499 | 2015-02-26 | CAP | 2030-06-01 | New site (Wexford prime) | [5 empty] | Install 25.2 MVAR capacitor | MI |  |  | Planned | 1524194 |  |  | N | N | N | Y
A in MTEP09 | A | Central | Vectren | 2466 | 2017-06-30 | SIGE7 | 4430 | 2017-09-29 | SUB | 2025-12-31 | Roesner Rd 138/12kV Substation |  | 1 | 138 | 12.47 | 16/20 | New 138/12kV Substation for load growth | IN |  |  | M2a_Pre-Project Approval | 5000000 | Budgetary |  | N | N | N | NT
A in MTEP09 | A | East | WPSC | 2770 | 2009-02-03 |  | 4832 | 2015-09-15 | TAP | 2017-12-31 | Hersey | Gilmore | 1 | 69 |  |  | Gilmore Taps the Hersey to Vestaburg 69kV circuit | MI |  |  | Planned | 250000 | Planning |  | N | N | N | Y
A in MTEP09 | A | East | WPSC | 2770 | 2009-02-03 |  | 4833 | 2015-09-15 | TAP | 2017-06-01 | Gilmore | Vestaburg | 1 | 69 |  |  | Gilmore Taps the Hersey to Vestaburg 69kV circuit | MI |  |  | Planned | 250000 | Planning |  | N | N | N | Y
A in MTEP08 | A | Central | HE | 1929 | 2008-01-10 | None Yet | 3808 | 2011-01-11 | SUB | 2012-09-01 | Georgetown Primary |  | 1 | 138 |  | 2000 AMP | Rebuild | IN |  |  | Planned | 1250000 |  |  | N | N | N | Y
A in MTEP08 | A | West | ITCM | 1744 | 2009-09-25 | GM-MAQ | 3546 | 2018-06-25 | LNrc | 2018-12-31 | Maquoketa | Grand Mound | 1 | 161 |  | 326/326 MVA | Reconductor | IA | 14.5 |  | Under Construction | 12800161 | Planning |  | N | N | N | Y
A in MTEP08 | A | East | METC | 1448 | 2018-04-04 | 196 | 2452 | 2015-09-29 | Dist | 2019-12-31 | Simpson 138kV |  |  | 138 | 12.5 |  | Install a second distribution transformer at Simpson (Simpson) | MI |  |  | Planned | 2200000 |  |  | N | N | N | Y
A in MTEP08 | A | West | NWEC | 2016 | 2018-04-04 | 2011-02 | 3997 | 2018-09-14 | LNrb | 2020-06-01 | Frederic | Coffee Cup |  | 69 |  | 84 | Rebuild 69KV Dbl Ckt from DPC Tie to Hwy 35 with 477ACSR | WI | 1.5 | 0 | Planned | 450000 |  |  | N | N | N | Y
A in MTEP08 | A | Central | Vectren | 1784 | 2018-04-04 |  | 3574 | 2017-03-31 | SUB | 2025-12-31 | Jasper#3 Sub Exp-Victory Line | Victory | 1 | 69 |  |  | Extend existing Victory line to new term at existing sub | IN |  |  | M2a_Pre-Project Approval | 3625000 | Budgetary |  | N | N | N | NT
A in MTEP08 | A | Central | Vectren | 1789 | 2018-09-13 |  | 3579 | 2018-09-13 | SUB | 2020-12-31 | Boonville Sub | Boonville Pioneer Sub | 56 | 69 |  |  | New 69kV line from Boonville Sub to Boonville Pioneer Sub | IN |  |  | M3_Long Lead Materials | 6600000 | Budgetary |  | N | N | N | NT
A in MTEP06 | A | Central | AmerenIL | 739 | 2018-04-04 |  | 1432 | 2012-10-12 | LN | 2020-11-01 | Line 4561 Tap | Franklin County Power Plant | 1 | 345 |  |  | 345 kV connection (new ring bus) to new generation | IL |  |  | Proposed | 6410900 | Engineering | Interconnection | N | N | N | Y
B in MTEP18 | B | Central | AmerenIL | 13689 | 2018-09-27 |  | 22763 | 2018-09-27 | LNrb | 2030-06-01 | Louisville South | Newton | 1 | 138 |  |  | Increase ground clearance for 20.49 miles of 954 ACSR rail in order to permit operation at 120 degrees C. Replace 954 ACSR rail bus conductor at both Louisville South and Newton. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 13705 | 2017-09-07 |  | 22773 | 2017-10-18 | SUB | 2021-12-01 | North Nashville | Install 138 kV ring bus |  | 138 |  |  | Install initial 3-position (ultimate 4-position) 138 kV ring bus at North Nashville Substation. | IL |  |  | Proposed | 7810000 | Budgetary |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 13708 | 2018-10-03 |  | 22776 | 2017-10-18 | SUB | 2021-12-01 | New Athens Dutch Hill | Install 138 kV ring bus |  | 138 |  |  | Add 138 kV ring Bus. Initial 3-position (ultimate 4-position) | IL |  |  | Proposed | 8376000 | Budgetary |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 13709 | 2018-10-03 |  | 22777 | 2017-10-18 | SwSta | 2020-06-01 | Putnam | BAAH Substation |  | 138 |  |  | Install new 138kV BAAH substation on new site near Hennepin. | IL |  |  | Proposed | 24868000 | Budgetary |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 13709 | 2018-10-03 |  | 23288 | 2017-10-18 | LN | 2020-06-01 | Hennepin | Putnam |  | 138 |  |  | Install new 138 kV lines between the new Putnam Substation and Hennepin Substation | IL |  |  | Proposed | 7624000 | Budgetary |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 13793 | 2018-10-03 |  | 22855 | 2017-09-26 | SUB | 2022-12-01 | El Paso | Install 138 kV ring bus |  | 138 |  |  | Install initial 4-position ring bus at El Paso Substation for in/out supply. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 13797 | 2017-09-08 |  | 22859 | 2017-09-26 | LNcnv | 2020-06-01 | Albion South | Norris City North | 1 | 345 | 138 |  | Rebuild the existing 138 kV circuit to 2000A. Double circuit the line for new 3000A 345 kV circuit. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | Central | AmerenIL | 14062 | 2018-10-03 |  | 23196 | 2017-09-22 | LN | 2023-06-01 | Hutsonville | Robinson Marathon |  | 138 |  |  | Install 2nd line between Hutsonville and Robinson Marathon. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | Central | AmerenMO | 4075 | 2017-10-03 |  | 7724 | 2017-09-15 | LN | 2023-06-01 | Sioux | Huster | 3 | 138 |  | 314 | Reconductor 5.9 miles of 954 kcmil ACSR with conductor capable of carrying 1600 A under summer emergency conditions. Replace 1200 A terminal equpment (dixconnect switches, CT's, bus conductor) at Huster with equipment capable of carrying 1600 A or better. | MO | 5.9 |  | Proposed | 5900000 | Planning |  | N | N | N | Y
B in MTEP18 | B | West | ATC | 13739 | 2018-02-05 | F4580 | 22807 | 2018-09-14 | LNrb | 2029-12-31 | South Fond Du Lac |  |  | 69 |  |  | Y133 SFDL SPB 69kV Rebuild | WI |  |  | Proposed | 31000000 | Planning |  | N | N | N
B in MTEP18 | B | West | ATC | 14187 | 2018-02-05 | PR07829 | 23281 | 2017-09-22 | IND | 2019-06-01 | Arnold |  |  | 345 |  |  | This project consists of installing a new 345 kV, 80 MVAR, oil-filled inductor bank at the Arnold substation to an open 345 kV bay position. | MI |  |  | Conceptual | 5000000 | Planning |  | N | N | N
B in MTEP18 | B | West | ATC | 14907 | 2018-05-23 |  | 23478 | 2018-05-22 | SUB | 2024-06-30 | NA |  |  | 138 | 69 |  | Distribution Interconnection 2021 | WI,MI |  |  | Proposed | 7350000 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14909 | 2018-05-23 |  | 23464 | 2018-05-22 | SUB | 2024-06-30 | NA |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal 2021 | WI,MI |  |  | Proposed | 32969227 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14911 | 2018-05-30 |  | 23467 | 2018-05-22 | COM | 2024-06-30 | NA |  |  | 345 | 69 |  | Communication Reliability Upgrades 2021 | WI,MI |  |  | Proposed | 1741667 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14913 | 2018-05-23 |  | 23470 | 2018-05-22 | LNup | 2024-06-30 | NA |  |  | 345 | 69 |  | Line Clearance Mitigation Projects 2021 | WI,MI |  |  | Proposed | 14000000 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14915 | 2018-05-30 |  | 23473 | 2018-05-22 | SUB | 2024-06-30 | NA |  |  | 345 | 69 |  | Physical Security 2021 | WI,MI |  |  | Proposed | 9629152 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14964 | 2018-05-23 |  | 23465 | 2018-05-22 | SUB | 2025-06-30 | NA |  |  | 345 | 69 |  | Small Capital Project and Asset Renewal 2022 | WI,MI |  |  | Proposed | 30489835 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14965 | 2018-05-30 |  | 23468 | 2018-05-22 | COM | 2025-06-30 | NA |  |  | 345 | 69 |  | Communication Reliability Upgrades 2022 | WI,MI |  |  | Proposed | 8851667 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14966 | 2018-05-23 |  | 23471 | 2018-05-22 | LNup | 2025-06-30 | NA |  |  | 345 | 69 |  | Line Clearance Mitigation Projects 2022 | WI,MI |  |  | Proposed | 7100000 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14967 | 2018-05-30 |  | 23474 | 2018-05-22 | SUB | 2025-06-30 | NA |  |  | 345 | 69 |  | Physical Security 2022 | WI,MI |  |  | Proposed | 9165536 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 14968 | 2018-05-30 |  | 23479 | 2018-05-22 | SUB | 2025-06-30 | NA |  |  | 138 | 69 |  | Distribution Interconnection 2022 | WI,MI |  |  | Proposed | 38475000 |  |  | N | N | N
B in MTEP18 | B | West | ATC | 15125 | 2018-05-24 |  | 23448 | 2018-05-14 | Dist | 2020-06-01 | New Sub |  |  | 138 |  |  | Load addition in Marquette County, MI | MI |  |  | Proposed |  | Scoping |  | N | N | N
B in MTEP18 | B | South | CLECO | 13874 | 2017-12-05 |  | 23298 | 2017-10-04 | SUB | 2020-05-01 | Ball |  |  | 230 |  |  | Tap a new 230 kV substation into and out of the current Donahue to Sherwood 230 kV line. Move 16 MW of load from Beaver Creek to be served out of this new substation | LA |  |  | Proposed | 8130000 | Planning |  | N | N | N
B in MTEP18 | B | South | CLECO | 13875 | 2017-09-25 |  | 23296 | 2017-10-04 | LN | 2020-12-01 | Bayou Sale | North Bend | 2 | 138 |  |  | Build a new 138 kV line from Bayou Sale to North Bend. This line will become Teche to North Bend when Bayou Sale is removed from service. | LA |  | 3.8 | Proposed | 8000000 | Planning |  | N | N | N
B in MTEP18 | B | South | CLECO | 13875 | 2017-09-25 |  | 23297 | 2017-10-04 | SUB | 2020-12-01 | North Bend |  |  | 138 |  |  | Rebuild North Bend substation to a 4 terminal ring bus with traditional 34.5 low side | LA |  |  | Proposed | 6461000 |  |  | N | N | N
B in MTEP18 | B | South | CLECO | 13876 | 2017-09-25 |  | 23295 | 2017-10-04 | LNrc | 2025-05-01 | Madisonville | Mandeville | 1 | 230 |  |  | Reconductor existing 9.9 Mile line with 954. Line will have to be rebuilt. | LA | 9.9 | 0 | Proposed | 15803000 | Planning |  | N | N | N
B in MTEP18 | B | South | CLECO | 14404 | 2018-08-20 |  | 23319 | 2017-10-27 | SUB | 2026-05-01 | Oakdale |  |  | 230 |  |  | Expand Oakdale Substation for 230 kV expansion. Including a 500 MVA 230/138 Auto | LA |  |  | Proposed | 8890000 | Planning |  | N | N | N
B in MTEP18 | B | South | CLECO | 14404 | 2018-08-20 |  | 23320 | 2017-10-27 | LN | 2026-05-01 | Rork | Oakdale |  | 230 |  |  | Build a 57.7 mile 230 kV line from Rork to Oakdale. | LA |  | 57.7 | Proposed | 78800000 |  |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 12670 | 2018-08-07 | 17-EAI-015 | 22470 | 2018-08-07 | SUB | 2025-06-01 | Hall 115kV |  |  | 115 | 34.5 |  | Construct a new substation with a single 40 MVA 115/34.5 kV LTC transformer. Extend the transmission line 5.5 miles from Mt. Ida substation to this new station. | AR |  |  | Proposed | 38093408 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 12670 | 2018-08-07 | 17-EAI-015 | 22471 | 2018-08-07 | LN | 2025-06-01 | Mt Ida 115kV | Hall 115kV |  | 115 |  |  | Build a 5.5 mile 115kV transmission line from Mt Ida station to the new Hall station. | AR |  | 5.5 | Proposed |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13605 | 2017-09-13 | 18-EAI-025 | 22694 | 2018-08-01 | SUB | 2025-12-01 | Carmel 115kV |  |  | 115 |  |  | Build a 115kV breaker station at the existing Carmel 115kV Switching Station. | AR |  |  | Conceptual | 10493407 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13606 | 2017-09-13 | 18-EAI-032 | 22695 | 2018-08-01 | SUB | 2024-06-01 | Maumelle East 115kV |  |  | 115 |  |  | Install a breaker station at the Maumelle East 115kV Tap station. | AR |  |  | Conceptual | 11499529 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13607 | 2017-09-21 | 18-EAI-034-6 | 22696 | 2018-08-01 | TEQ | 2023-12-01 | LR South | LR West |  | 115 |  |  | Upgrade all station equipment along the LR South - LR West 115kV line to provide full conductor capacity. | AR |  |  | Conceptual | 5356512 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13609 | 2017-09-21 | 18-EAI-034-5 | 22697 | 2018-08-01 | LNrb | 2022-12-01 | LR Pinnacle | LR Walton Heights |  | 115 |  |  | Rebuild 5.3 miles of the LR Pinnacle - LR Walton Heights 115kV line to a minimum of 1950 Amps. | AR | 5.3 |  | Conceptual | 7796854 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13610 | 2017-09-21 | 18-EAI-034-4 | 22698 | 2018-08-01 | LNrb | 2022-12-01 | LR Gaines | NLR Westgate |  | 115 |  |  | Rebuild 0.7 miles to a minimum of 1950 Amps | AR | 0.7 |  | Conceptual | 3921272 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13616 | 2017-09-13 | 18-EAI-022 | 22706 | 2018-08-01 | TEQ | 2027-12-01 | Walnut Ridge | Black Rock |  | 161 |  |  | Upgrade the line bay bus and substation equipment to a minimum of 800 Amps. | AR |  |  | Conceptual | 710127 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13627 | 2018-05-23 | 18-EAI-004 | 22717 | 2018-08-03 | LN | 2025-06-01 | El Dorado EHV | El Dorado West |  | 115 |  |  | Construct a new 10 mile line. | AR |  | 10 | Proposed | 41226266 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13627 | 2018-05-23 | 18-EAI-004 | 22720 | 2018-08-03 | SUB | 2025-06-01 | El Dorado West |  |  | 115 |  |  | Convert El Dorado West station to a breaker station. | AR |  |  | Proposed |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13627 | 2018-05-23 | 18-EAI-004 | 22719 | 2018-08-03 | LN | 2025-06-01 | El Dorado Parker's Chapel | El Dorado West |  | 115 |  |  | Tap the El Dorado Lion - El Dorado Parker's Chapel 115kV line into El Dorado West 115kV. | AR |  |  | Proposed |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13627 | 2018-05-23 | 18-EAI-004 | 22718 | 2018-08-03 | LN | 2025-06-01 | El Dorado Lion | El Dorado West |  | 115 |  |  | Tap the El Dorado Lion - El Dorado Parker's Chapel 115kV line into El Dorado West 115kV. | AR |  |  | Proposed |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-AR | 13633 | 2018-05-22 | 18-EAI-009 | 22726 | 2018-09-13 | LNrb | 2023-06-01 | Quitman | Bee Branch |  | 161 |  |  | Rebuild the line and upgrade all station equipment to a minimum of 1300 Amps. | AR | 8.8 |  | Proposed | 11901686 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13894 | 2017-09-25 | 18-ELB-002 | 22965 | 2018-05-15 | LN | 2027-06-01 | Addis | Tiger | 2 | 230 |  |  | The construction will include 5 miles of new 230 kV line on separate structures and additional 1 mile of river crossing. This includes breakers at Addis and Tiger. | LA |  |  | Conceptual | 63530000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13904 | 2017-09-25 | 18-ELS-002 | 22983 | 2018-09-04 | LN | 2026-06-01 | Valentine | Golden Meadow | 2 | 115 |  |  | 1) Construct a new ~22 mile long 230 kV line from Valentine to Golden Meadow. This line will initially be operated at 115 kV. | LA |  | 22 | Conceptual | 82800000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13904 | 2017-09-25 | 18-ELS-002 | 22987 | 2018-09-04 | SUB | 2026-06-01 | Valentine |  |  | 115 |  |  | 3) At Valentine 115 kV station, extend the bus work to the east and add two new breakers. | LA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13904 | 2017-09-25 | 18-ELS-002 | 22986 | 2018-09-04 | BUS | 2026-06-01 | Golden Meadow |  |  | 115 |  |  | 4) Reconfigure the Golden Meadow 115 kV station into a ring bus with the ability to expand to breaker and a half. | LA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13904 | 2017-09-25 | 18-ELS-002 | 22985 | 2018-09-04 | LNrb | 2026-06-01 | Clovelly | Golden Meadow |  | 115 |  |  | 2) Rebuild the existing Clovelly to Golden Meadow 115 kV line to double circuit 230 kV and 115 kV, ~7.2 miles. Operate the line at 115 kV initially and tie both circuits together at Clovelly and Golden Meadow. | LA | 7.2 | 7.2 | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13905 | 2017-09-25 | 18-ELS-003 | 22988 | 2018-09-10 | SUB | 2024-06-01 | Burnside |  |  | 230 |  |  | 1) Construct a 3 breaker 230 kV ring bus at Burnside, Minimum of 2000 Amp equipment. 2) Cut in and out the Conway to Panama 230 kV line. 3) Install 300 MVA 230-115 kV Autotransformer, similar to the current Sorrento 230-115 kV Autotransformer. 4) Install 115 kV low side breaker at Burnside | LA |  |  | Conceptual | 17000000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13907 | 2018-08-30 | 18-ELS-004 | 22990 | 2018-09-04 | CB | 2023-06-01 | Adams Creek |  |  | 230 |  |  | Install three new breakers at the empty line bay in breaker and half configuration, such that Adams Creek – North Slidell 230 kV and Adams Creek – Bogalusa 230 kV line B are accommodated in the same bay. | LA |  |  | Conceptual | 5200000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13907 | 2018-08-30 | 18-ELS-004 | 22992 | 2018-09-04 | LN | 2023-06-01 | Adams Creek | Bogalusa-North Slidell |  | 230 |  |  | Construct ~.6 miles from the Adams Creek 230 kV to a point before the North Slidell to Bogalusa 230 kV line enters the Bogalusa 230 kV station. | LA |  | 0.6 | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13910 | 2018-08-06 | 18-ELN-002 | 22996 | 2017-12-07 | Dist | 2026-06-01 | Calhoun |  |  | 230 |  |  | 230 kV distribution substation | LA |  |  | Conceptual | 38330000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13910 | 2018-08-06 | 18-ELN-002 | 22997 | 2017-09-13 | LN | 2026-06-01 | Choudrant | Calhoun | 1 | 230 |  | 519 | Construct approximately 10 miles of 230 kV transmission line from the new substation that terminates into the Choudrant substation. | LA |  | 10 | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13925 | 2018-08-06 | 18-ELN-004 | 23000 | 2017-12-07 | Dist | 2023-06-01 | Choudrant |  |  | 230 |  |  | 230 kV distribution substation | LA |  |  | Conceptual | 47500000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13925 | 2018-08-06 | 18-ELN-004 | 23001 | 2017-09-13 | LN | 2023-06-01 | Mt Olive | Choudrant | 1 | 230 |  | 519 | Construct approximately 14 miles of 230 kV transmission line from the new substation that terminates into the existing Mt Olive substation. | LA |  | 14 | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13927 | 2017-09-25 | 18-ELN-003 | 23006 | 2017-12-07 | LN | 2026-06-01 | Calhoun | Cadeville | 1 | 230 |  | 519 | Construct approximately 6 miles of 230 kV transmission line from the Calhoun substation (MISO ID 13910) to the Cadeville substation (MISO ID 9684). | LA |  | 6 | Conceptual | 20700000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13927 | 2017-09-25 | 18-ELN-003 | 23010 | 2017-09-13 | LNcnv | 2026-06-01 | Cotton | Cadeville | 1 | 230 |  | 519 | Convert the Cotton - Cadeville line section to 230 kV operation. | LA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13927 | 2017-09-25 | 18-ELN-003 | 23009 | 2017-09-13 | LNcnv | 2026-06-01 | Rilla | Cotton | 1 | 230 |  | 519 | Convert the Rilla - Cotton line section to 230 kV operation. | LA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13936 | 2018-08-06 | 18-ELN-007 | 23016 | 2017-12-07 | Dist | 2025-06-01 | Dubach |  |  | 115 |  |  | Construct a new distribution substation near the town of Dubach, LA that cuts into the Vienna - Bernice 115 kV line section. | LA |  |  | Conceptual | 12100000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13937 | 2018-08-06 | 18-ELN-008 | 23019 | 2017-12-07 | Dist | 2027-06-01 | Homer |  |  | 115 |  |  | Construct a new distribution substation near the town of Homer, LA that cuts into the Haynesville - Minden East 115 kV line (MISO ID 12068). | LA |  |  | Conceptual | 27100000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13937 | 2018-08-06 | 18-ELN-008 | 23022 | 2017-09-15 | TAP | 2027-06-01 | Minden East | Homer | 1 | 115 |  | 259 | Construct approximately 6 miles of 115 kV line and utilize a portion of the Haynesville - Minden East 115 kV line section (MISO ID 12068) to create a new Minden East - Homer 115 kV line. | LA |  | 6 | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13937 | 2018-08-06 | 18-ELN-008 | 23021 | 2017-09-15 | TAP | 2027-06-01 | Haynesville | Homer | 1 | 115 |  | 259 | Construct approximately 6 miles of 115 kV line and utilize a portion of the Haynesville - Minden East 115 kV line section (MISO ID 12068) to create a new Haynesville - Homer 115 kV line. | LA |  | 6 | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13938 | 2017-09-25 | 18-ELN-005 | 23023 | 2017-09-13 | SUB | 2023-12-01 | Cheniere |  |  | 115 |  |  | Cheniere 115 kV substation breaker installation | LA |  |  | Conceptual | 3400000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13954 | 2018-08-06 | 18-ELB-004 | 23056 | 2018-05-15 | Dist | 2024-06-01 | Northline |  |  | 230 |  |  | Cohen Area (Northline) substation will cut in between Addis and Cohen 230 kV stations. | LA |  |  | Conceptual | 14500000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13969 | 2018-08-06 | 18-ELC-004 | 23080 | 2018-05-15 | Dist | 2023-06-01 | Pine Hill |  |  | 138 |  |  | Pine Hill substation will cut in on the Lowe Grout to Jennings 138 kV line section. | LA |  |  | Conceptual | 10800000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13970 | 2018-08-06 | 18-ELC-005 | 23081 | 2018-05-15 | Dist | 2026-12-01 | Vinton |  |  | 138 |  |  | Vinton substation will cut in on the Marshall to Toomey 138 kV line section. Depending on the location of the station, three or more miles of transmission may need to be constructed to the new station. | LA |  |  | Conceptual | 11500000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13971 | 2018-08-06 | 18-ELB-005 | 23084 | 2018-05-15 | Dist | 2025-12-01 | South Baton Rouge |  |  | 230 |  |  | The station may be cut in between the Tiger and Willow Glen 230 kV stations and will include ~8 miles of new 230 kV line. Mileage and exact location of the station is still TBD. | LA |  |  | Conceptual | 14650000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13971 | 2018-08-06 | 18-ELB-005 | 23086 | 2017-09-13 | LN | 2025-12-01 | South Baton Rouge | WGlenn Tiger 230 cut in point |  | 230 |  |  | The station may be cut in between the Tiger and Willow Glen 230 kV stations and will include ~8 miles of new 230 kV line. Mileage and exact location of the station is still TBD. | LA |  | 8 | Conceptual |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13984 | 2017-09-25 | 18-ELF-001 | 23087 | 2017-09-14 | Dist | 2024-06-01 | Labit Road |  |  | 230 |  |  | Labit Road 230 kV substation will cut in on the Cecelia to Lake Peigneur 230 kV line section. | LA |  |  | Conceptual | 12000000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13986 | 2018-08-06 | 18-ELF-003 | 23093 | 2017-12-07 | Dist | 2027-06-01 | Milton |  |  | 230 |  |  | Milton 230 kV substation may be cut in on the Segura to Sellers Road 230 kV CLECO line section. | LA |  |  | Conceptual | 13400000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13988 | 2018-08-06 | 18-ELF-005 | 23094 | 2017-09-14 | Dist | 2025-12-01 | Ambassador |  |  | 230 |  |  | Ambassador 230 kV substation may be served on a radial out of Labit Road230 kV station. Approximately 6 miles of 230 kV line will need to be constructed from Labit Road to the new station | LA |  |  | Conceptual | 19600000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13988 | 2018-08-06 | 18-ELF-005 | 23095 | 2017-09-14 | LN | 2025-12-01 | Labit Road | Ambassador |  | 230 |  |  | Ambassador 230 kV substation may be served on a radial out of Labit Road230 kV station. Approximately 6 miles of 230 kV line will need to be constructed from Labit Road to the new station | LA |  | 6 | Conceptual |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13989 | 2017-09-25 | 18-ELF-004 | 23096 | 2017-09-14 | Dist | 2025-12-01 | Sugar |  |  | 230 |  |  | Sugar 230 kV substation will be cut in on the Cecelia to Labit Road 230 kV line section. | LA |  |  | Conceptual | 5500000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-LA | 13991 | 2018-08-30 | 18-ELS-005 | 23097 | 2018-09-04 | Dist | 2023-06-01 | Ascension |  |  | 230 |  |  | Gonzales Area 230 kV substation will be cut in on the Sorrento to Demco Airline 230 kV line section. | LA |  |  | Conceptual | 8600000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13892 | 2018-09-13 | 18-EMI-004 | 22968 | 2018-09-13 | BUS | 2027-06-01 | Moon Lake |  |  | 230 |  |  | Expand the Moon Lake 230 kV substation to accommodate the cut in of the Ritchie to Tunica line. | MS |  |  | Conceptual | 8600000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13906 | 2017-09-15 | 18-EMI-012 | 22989 | 2017-09-15 | LN | 2027-06-01 | Byhalia | Cockrum |  | 230 |  | 500 | 6.5mi of 230kV line rated at least 500MVA from Byhalia to Cockrum | MS |  | 6.5 | Conceptual | 14000000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13906 | 2017-09-15 | 18-EMI-012 | 22991 | 2017-09-12 | SUB | 2027-06-01 | Cockrum |  |  | 230 |  |  | New 230kV substation to serve load in the Cockrum, MS area | MS |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13951 | 2017-09-15 | 18-EMI-007 | 23053 | 2017-12-27 | LN | 2026-06-01 | Franklin | Wynndale |  | 230 |  |  | 50 mile 230kV line from Franklin to Wynndale | MS |  | 50.12 | Conceptual | 99000000 |  |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13951 | 2017-09-15 | 18-EMI-007 | 23064 | 2017-09-13 | TX |  | Franklin |  |  | 500 |  |  | Install 500/230 kV Auto at Franklin | MS |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13951 | 2017-09-15 | 18-EMI-007 | 23062 | 2017-09-13 | TX |  | Wynndale |  |  | 230 |  |  | 230/115 kV Auto at Wynndale | MS |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13987 | 2017-09-15 | 18-EMI-014 | 23092 | 2017-09-14 | SUB | 2022-12-01 | Rankin | S. Jackson |  | 230 |  |  | Tap Rankin to S. Jackson 230kV line and the Brandon to Whitfield 115kV line to construct a substation with a 230/115kV auto | MS |  |  | Conceptual | 19300000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13987 | 2017-09-15 | 18-EMI-014 | 23156 | 2017-09-15 | TX | 2022-12-01 | East Metro |  |  | 230 | 115 | 392 | Install a 230-115 kV autotransformer at the new substation | MS |  |  | Conceptual |  |  |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13994 | 2017-10-04 | 18-EMI-017 | 23101 | 2017-09-14 | SUB | 2022-06-01 | S. Jackson |  |  | 115 |  |  | Tap S. Jackson to Georgetown 115kV line and construct new 115kV substation to serve load in Cleary, MS. | MS |  |  | Planned | 7600000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-MS | 13995 | 2017-09-14 | 18-EMI-017 | 23102 | 2017-09-14 | SUB | 2025-06-01 | Tinnin | Bozeman |  | 230 |  |  | New 230kV Substation cutting in on the Tinnin to Bozeman 230kV line | MS |  |  | Planned | 8700000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13930 | 2017-09-13 | 18-ETI-003 | 23005 | 2017-09-13 | Dist | 2023-06-01 | Knatson |  |  | 138 |  |  | Knatson substation will cut into L825 between Stilson and Gordon. | TX |  |  | Conceptual | 12800000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13931 | 2017-09-13 | 18-ETI-004 | 23007 | 2017-09-13 | Dist | 2024-06-01 | Crenshaw |  |  | 138 |  |  | Construct a 138 kV line from Himex to Crenshaw and convert Blue Water to Crenshaw 138 kV substation. | TX |  |  | Conceptual | 65300000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13931 | 2017-09-13 | 18-ETI-004 | 23008 | 2017-09-13 | LN | 2024-06-01 | Himex | Crenshaw |  | 138 |  |  | Construct a 138 kV line from Himex to Crenshaw and convert Blue Water to Crenshaw 138 kV substation. | TX |  | 22 | Conceptual |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13933 | 2017-09-13 | 18-ETI-005 | 23011 | 2017-09-13 | Dist | 2024-06-01 | Brownwater |  |  | 138 |  |  | Convert Sandy Shores to Brownwater 138 kV and cut in and out of Himex to Crenshaw line. | TX |  |  | Conceptual | 22000000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13939 | 2017-09-13 | 18-ETI-006 | 23024 | 2017-09-13 | Dist | 2024-06-01 | Hatcherville |  |  | 138 |  |  | Construct a new Hatcherville 138 kV substation and feed radial from Knatson substation. | TX |  |  | Conceptual | 22200000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13939 | 2017-09-13 | 18-ETI-006 | 23025 | 2017-09-13 | LN | 2024-06-01 | Knatson | Hatcherville | 1 | 138 |  |  | Construct a new Hatcherville 138 kV substation and feed radial from Knatson substation. | TX |  | 7 | Conceptual |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13940 | 2017-09-13 | 18-ETI-007 | 23026 | 2017-09-13 | Dist | 2025-06-01 | Wolf Island |  |  | 138 |  |  | Construct a new Wolf Island 138 kV substation that cuts into emergency Dayton - Crosby 138 kV tie. Operate Wolf Island - Crosby as normally open emergency tie. | TX |  |  | Conceptual | 12300000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13943 | 2017-09-13 | 18-ETI-010 | 23030 | 2017-09-13 | Dist | 2023-06-01 | Southern Point |  |  | 138 |  |  | Construct a new 138 kV substation that replaces the existing Speedway 138 kV substation. | TX |  |  | Conceptual | 11900000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13945 | 2018-08-16 | 18-ETI-014 | 23032 | 2017-09-13 | Dist | 2024-12-01 | Fairview |  |  | 138 |  |  | Construct a new 138 kV substation on the Dayton Bulk to New Caney 139 kV line near Road 624. | TX |  |  | Conceptual | 14400000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13946 | 2017-09-13 | 18-ETI-015 | 23033 | 2017-09-13 | LN | 2026-06-01 | Intersection | Wolf Island |  | 138 |  |  | Construct a new Intersection 138 kV substation and feed radial (3.5 miles) from Wolf Island 138 kV substation. | TX |  | 3.5 | Conceptual | 19000000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13946 | 2017-09-13 | 18-ETI-015 | 23034 | 2017-09-13 | Dist | 2026-06-01 | Intersection |  |  | 138 |  |  | Construct a new Intersection 138 kV substation and feed radial (3.5 miles) from Wolf Island 138 kV substation. | TX |  |  | Conceptual |  | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 13947 | 2017-09-13 | 18-ETI-016 | 23035 | 2017-09-13 | Dist | 2027-12-01 | Texaco Road |  |  | 138 |  |  | Construct a new 138 kV substation on the Colony to Eastgate 138 kV line near Texaco Road. | TX |  |  | Conceptual | 12800000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 14944 | 2018-04-05 | 17-ETI-016 | 23411 | 2018-04-03 | Dist | 2023-06-01 | Tuscany |  |  | 230 |  |  | Build a new substation on teh China to Porter 230 kV line. | TX |  |  | Proposed | 36990000 | Planning |  | N | N | N
B in MTEP18 | B | South | Entergy-TX | 15104 | 2018-05-10 | 18-ETI-020 | 23443 | 2018-05-10 | CAP | 2024-06-01 | Dobbin |  |  | 138 |  |  | Install a 25.1 MVAR capacitor bank with a breaker at the Dobbin 138 kV substation by the summer of 2024. | TX |  |  | Proposed | 730000 | Planning |  | N | N | N
B in MTEP18 | B | South | LAFA | 14105 | 2018-07-27 |  | 23255 | 2017-09-22 | BUS | 2019-12-31 | Bonin 69kV |  |  | 69 |  |  | Replace bus work | LA |  |  | Proposed | 700000 |  |  | N | N | N
B in MTEP18 | B | South | LAFA | 14105 | 2018-07-27 |  | 23257 | 2017-09-22 | RLY | 2019-12-31 | Bonin 69kV |  |  | 69 |  |  | Relaying, communications, and control building | LA |  |  | Proposed | 2200000 |  |  | N | N | N
B in MTEP18 | B | South | LAFA | 14105 | 2018-07-27 |  | 23256 | 2017-09-22 | SUB | 2019-12-31 | Bonin 69kV |  |  | 69 |  |  | Replace breakers and associated equipment. | LA |  |  | Proposed | 3500000 |  |  | N | N | N
B in MTEP18 | B | West | MDU | 14106 | 2018-07-10 |  | 23254 | 2017-09-18 | CB | 2019-03-31 | Heskett |  |  | 115 |  |  | Add 115 kV bus tie breaker | ND |  |  | Planned | 500000 | Budgetary |  | N | N | N
B in MTEP18 | B | West | MEC | 2938 | 2018-08-31 | G0104 | 5113 | 2018-08-31 | LNrb | 2023-12-01 | Sub 39 | Cordova | 1 | 345 |  | 1471 | Replace a limited number of existing 345 kV line structures to increase line conductor clearances. This Project will allow higher conductor operating temperatures and result in higher ratings on the Sub 39-MEC Cordova 345 kV line. | IL | 0.2 |  | Planned | 325000 | Planning |  | N | N | N | Y
B in MTEP18 | B | East | METC | 14050 | 2017-09-18 |  | 23185 | 2017-09-15 | RLY |  | Gallagher 345 kV |  |  | 345 |  |  | Modify relay scheme at the Gallagher 345 kV station to terminate line or transformer faults at the site. | MI |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16069 | 2018-09-18 |  | 24195 | 2018-09-18 | SwSta | 2021-12-31 | Dunka |  |  | 115 |  |  | Build new Dunka switching station with five transmission line connections | MN |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16069 | 2018-09-18 |  | 24198 | 2018-09-18 | CAP | 2021-12-31 | Dunka |  |  | 115 |  |  | New 2x20 MVAR cap banks at Dunka | MN |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16069 | 2018-09-18 |  | 24197 | 2018-09-18 | LNrb | 2021-12-31 | Embarrass | Babbitt |  | 115 |  |  | Rebuild existing Embarrass - Babbitt 115 kV Line | MN | 20 |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16069 | 2018-09-18 |  | 24196 | 2018-09-18 | LN | 2021-12-31 | Dunka | Babbitt |  | 115 |  |  | Extend existing Embarrass - Babbitt 115 kV Line to new Dunka Switching Station | MN |  | 8 | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16070 | 2018-09-18 |  | 24191 | 2018-09-18 | SwSta | 2021-12-31 | Hoyt Lakes |  |  | 115 |  |  | New switching station with six transmission line positions | MN |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16070 | 2018-09-18 |  | 24194 | 2018-09-18 | CAP | 2021-12-31 | Hoyt Lakes |  |  | 115 |  |  | New 2x20 MVAR cap banks at Hoyt Lakes | MN |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16070 | 2018-09-18 |  | 24193 | 2018-09-18 | LNrb | 2021-12-31 | Embarrass | Babbitt |  | 115 |  |  | Rebuild existing Embarrass - Babbitt 115 kV Line | MN | 5.5 |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MP | 16070 | 2018-09-18 |  | 24192 | 2018-09-18 | LN | 2021-12-31 | Hoyt Lakes | Babbitt |  | 115 |  |  | Extend existing Embarrass - Babbitt 115 kV Line 5.5 miles to new Hoyt Lakes Switching Station | MN |  |  | Proposed |  |  |  | N | N | N
B in MTEP18 | B | West | MPC, OTP | 971 | 2018-07-18 | OTP1 | 235 | 2018-07-19 | TX | 2022-10-01 | Winger 230-115 kV | transformer | 1 | 230 | 115 | 187 | Final Design not complete - Either add 2nd 230/115 kV TX or replace existing 187 MVA transformer with something larger | MN |  |  | Proposed | 4458420 | Planning Preliminary |  | N | N | N | Y
B in MTEP18 | B | West | MPC, OTP | 4232 | 2018-08-29 | OTP | 7985 | 2017-09-15 | SUB | 2024-11-15 | Winger 230 kV | Winger 230 kV |  | 230 |  |  | Winger Sub Expansion, Add 230 kV Breakers & Termination for New Line | MN |  |  | Planned | 2000000 | Planning Preliminary |  | N | N | N | Y
B in MTEP18 | B | West | MPC, OTP | 4232 | 2018-08-29 | OTP | 7988 | 2017-09-15 | LN | 2024-11-15 | Winger 230 kV | Thief River 230 kV | 1 | 230 |  | 452 | Winger-Thief River 230 kV New Transmission Line | MN |  | 47 | Planned | 22000000 | Planning Preliminary |  | N | N | N | Y
B in MTEP18 | B | West | MPC, OTP | 4232 | 2018-08-29 | OTP | 7987 | 2017-09-15 | TX | 2024-11-15 | Thief River 230 kV | Thief River 230 kV |  | 230 | 115 | 187 | Thief River 230/115 kV Add New 187 MVA Transformer | MN |  |  | Planned | 5000000 | Planning |  | N | N | N | Y
B in MTEP18 | B | West | MPC, OTP | 4232 | 2018-08-29 | OTP | 7986 | 2017-09-15 | SUB | 2024-11-15 | Thief River 230 kV | Thief River 230 kV |  | 230 |  |  | Thief River Sub Expansion, Add 230 kV Breakers & Termination for New Line | MN |  |  | Planned | 1000000 | Planning Preliminary |  | N | N | N | Y
B in MTEP18 | B | East | WPSC | 9916 | 2017-09-14 | Fairview Station Upgrade | 21330 | 2018-02-22 | SwSta | 2020-06-01 | Fairview |  |  | 138 |  |  | Construct new ring bus station | MI |  |  | Proposed | 3250000 | Planning |  | N | N | N
B in MTEP18 | B | East | WPSC | 9916 | 2017-09-14 | Fairview Station Upgrade | 23110 | 2018-02-22 | LNrl | 2020-06-01 | Fairview |  |  | 138 |  |  | Fairview station line modifications | MI |  |  | Proposed | 750000 | Planning |  | N | N | N
B in MTEP18 | B | East | WPSC | 14004 | 2017-09-14 |  | 23120 | 2017-09-14 | LN | 2022-12-31 | Haggensville Junction | Haggensville |  | 138 |  |  | Install new 138kV line | MI |  | 0.25 | Planned | 260000 | Budgetary |  | N | N | N
B in MTEP18 | B | East | WPSC | 14005 | 2017-09-14 |  | 23121 | 2017-09-14 | LNrb | 2022-12-31 | Hammond Bay Junction | Hammond Bay |  | 138 |  |  | Rebuild line | MI |  | 2 | Proposed | 900000 | Budgetary |  | N | N | N
B in MTEP18 | B | East | WPSC | 14328 | 2017-10-13 |  | 23316 | 2017-10-12 | LINE | 2022-12-22 | TBD |  |  | 69 |  |  | Install approximately 100 miles of fiber | MI | 100 |  | Proposed | 6000000 | Budgetary |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11925 | 2018-09-07 |  | 21877 | 2018-06-20 | TX | 2023-06-01 | Massac |  |  | 345 | 161 | 560 | Install 345/161 kV, 560 MVA transformer | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11925 | 2018-09-07 |  | 21878 | 2018-06-20 | LNcnv | 2023-06-01 | Massac | Jordan | 1 | 345 |  | 1206 | Rebuild from 230 kV to 345 kV use. | IL | 47.62 |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11926 | 2017-03-10 |  | 21879 | 2018-08-24 | TX | 2023-12-01 | Jordan |  |  | 345 | 138 | 560 | Install 345/138 kV, 560 MVA transformer | IL |  |  | Planned |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11926 | 2017-03-10 |  | 21880 | 2018-08-24 | LNcnv | 2023-12-01 | Jordan | Derby |  | 345 |  | 1200 | Rebuild line from 230 kV to 345 kV use. | IL | 19.9 |  | Planned |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11927 | 2017-08-23 |  | 21881 | 2017-03-10 | TX | 2022-12-01 | Derby |  |  | 345 | 138 | 560 | Install 345/138 kV, 560 MVA transformer | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11927 | 2017-08-23 |  | 21884 | 2017-03-10 | LN | 2022-12-01 | Derby | St. Johns | 1 | 138 |  | 240 | Extend 138 kV line from 345 kV bus to 138 kV Sub | IL |  | 0.1 | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11927 | 2017-08-23 |  | 21883 | 2017-03-10 | LNcnv | 2022-12-01 | Derby | Pinckneyville | 1 | 345 |  | 1200 | Rebuild 230 kV line for use at 345 kV. | IL | 9.88 |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11927 | 2017-08-23 |  | 21882 | 2016-09-07 | TX | 2022-12-01 | St. Johns |  |  | 138 | 69 | 76 | Replace 230/69 kV transformer with a 138/69 kV transformer. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11969 | 2017-01-18 |  | 21937 | 2016-09-09 | LN | 2020-12-01 | Miles | Mississippi | 1 | 138 |  | 399 | Construct new 138 kV line | IL |  | 1.7 | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11969 | 2017-01-18 |  | 21939 | 2016-09-09 | CB | 2020-12-01 | Mississippi |  |  | 138 |  | 478 | Install 138 kV breaker | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 11969 | 2017-01-18 |  | 21938 | 2016-09-09 | CB | 2020-12-01 | Miles |  |  | 138 |  | 478 | Install 138 kV breaker | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 12172 | 2017-01-18 |  | 22289 | 2016-09-15 | CAP | 2020-06-01 | Miles |  |  | 138 |  | 120 | Install 120 Mvar, 138 kV capacitor bank | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 12176 | 2017-01-18 |  | 22295 | 2016-09-15 | IND | 2020-12-01 | West Frankfort, East |  |  | 345 |  | 50 | Install 345 kV shunt reactor | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenIL | 12179 | 2017-03-10 |  | 22297 | 2017-03-10 | IND | 2020-12-01 | Massac |  |  | 345 |  | 50 | Install 345 kV shunt reactor | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenMO | 11905 | 2017-01-18 |  | 21859 | 2016-09-06 | TEQ | 2025-06-01 | Watson |  |  | 138 |  | 382 | Upgrade terminal equipment in Bus-Tie 2-3 position | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenMO | 12173 | 2017-02-23 |  | 22292 | 2016-09-15 | CAP | 2020-06-01 | Gasco |  |  | 138 |  |  | Install 138 kV capacitor bank (size TBD) | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenMO | 12181 | 2017-02-23 |  | 22299 | 2016-09-15 | LN | 2022-12-01 | Bland | Gasco |  | 138 |  | 240 | Construct 138 kV line | MO |  | 8 | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenMO | 12426 | 2017-12-19 |  | 22430 | 2017-12-19 | CB | 2030-12-01 | Meramec |  |  | 138 |  | 478 | Replace CTG 1-2 138 kV breaker | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | Central | AmerenMO | 12428 | 2017-01-18 |  | 22434 | 2016-10-18 | CB | 2021-12-01 | Stoddard | Morley | 1 | 161 |  | 280 | Replace 161 kV breaker at Stoddard terminal | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | West | ATC | 12143 | 2018-03-26 | PR05000 | 22266 | 2016-09-14 | LNrb | 2021-12-31 | Sobieski | Bayport |  | 69 |  | 79 | Rebuild Sobieski - Bayport 69kV (T-98) | WI | 10.3 |  | Proposed | 14990000 | Planning |  | N | N | N
B in MTEP17 | B | West | ATC | 12144 | 2018-03-26 | PR05000 | 22272 | 2016-09-14 | LNrb | 2021-12-31 | Pioneer | Sobieski |  | 69 |  | 79 | Rebuild Pioneer - Sobieski 69kV (E-83) | WI | 10.7 |  | Proposed | 14390000 | Planning |  | N | N | N
B in MTEP17 | B | West | ATC | 12175 | 2016-09-15 | PR07213, F4738, WO601705 | 22293 | 2017-01-31 | LNrb | 2023-12-31 | West Middleton | Stagecoach |  | 69 |  |  | Rebuild West Middleton - Stagecoach 69KV | WI | 4 |  | Proposed | 3754320 | Planning |  | N | N | N
B in MTEP17 | B | Central | BREC | 12703 | 2016-12-15 |  | 22496 | 2016-12-15 | LNrc |  | Bryan Road | McCracken | 1 | 161 |  |  | Reconductor 15.6 miles of existing 795 ACSR with 795 ACSS | KY |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | South | CLECO | 12984 | 2017-09-18 | CLEC | 22550 | 2017-02-20 | LINE | 2019-12-31 | Beaver Creek | Donahue | 1&2 | 138 |  |  | Rebuild the 2 lines on separate Structures so that the line is not on common structures for greater than a mile. | LA | 2.7 |  | Proposed | 3700000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-AR | 12026 | 2017-09-13 | 17-EAI-009 | 22099 | 2018-08-03 | LNcnv | 2025-06-01 | Woodward | Pine Bluff South |  | 230 |  |  | Cut Woodward - AECC Pinebergen in to Pine Bluff South and operate to 230kV. Install 230/115 auto transformer at Pine Bluff South. Build Pine Bluff South to AECC Pinebergen to 230kV standards and operate at 115kV. | AR |  |  | Conceptual | 30582348 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-AR | 12026 | 2017-09-13 | 17-EAI-009 | 22110 | 2016-11-08 | LN | 2025-06-01 | Pine Bluff South | AECC Pinebergen |  | 115 |  |  | Build Pine Bluff South to AECC Pinebergen to 230 kV standards, and operate at 115 kV. | AR |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-AR | 12026 | 2017-09-13 | 17-EAI-009 | 22109 | 2016-11-08 | TX | 2025-06-01 | Pine Bluff South |  |  | 230 |  |  | Install 230/115 kV auto transformer at Pine Bluff South. | AR |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-AR | 12055 | 2017-09-13 | 17-EAI-008 | 22136 | 2018-08-03 | SUB | 2024-06-01 | Gum Springs |  |  | 115 |  |  | Create a new substation by tapping the Arkadelphia North – Richwood 115kV and the Arkadelphia West – Dalark 115kV line sections. | AR |  |  | Conceptual | 10513196 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-AR | 12671 | 2018-08-01 | 17-EAI-021 | 22472 | 2018-08-07 | SUB | 2026-12-01 | Timbo 161kV |  |  | 161 |  |  | Construct a new substation on Highway 66 east of Timbo, AR. Install one 40 MVA 161/13.8 kV LTC transformer and four feeder breakers. Build 6 miles of transmission line from the Mt. View station to the new Timbo station. | AR |  |  | Conceptual | 41213740 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-AR | 12671 | 2018-08-01 | 17-EAI-021 | 22473 | 2018-08-07 | LN | 2026-12-01 | Mt. View 161kV | Timbo 161kV |  | 161 |  |  | Build 6 miles of transmission line from the Mt. View station to the new Timbo station. | AR |  | 6 | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12068 | 2017-09-15 | 17-ELN-007 | 22149 | 2018-09-13 | LN | 2026-06-01 | Haynesville | Minden East | 1 | 115 |  | 260 | New 115 kV-260 MVA circuit | LA |  | 25 | Conceptual | 39900000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12068 | 2017-09-15 | 17-ELN-007 | 22984 | 2017-09-12 | SwSta | 2026-06-01 | Minden East |  |  | 115 |  |  | Install a 115 kV switching substation to cut into the LAGEN Minden - Aracadia 115 kV line and terminate new line from Haynesville. | LA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12084 | 2016-09-14 | 17-ELB-003 | 22170 | 2018-05-15 | LNrc | 2027-06-01 | Dixie Baker | Zachary |  | 69 |  |  | The ~3.3 mile long line should be upgraded to a minimum rating of 143 MVA. If any station equipment is rated lower than 143 MVA (1200 Amps), it should be upgraded as well. | LA | 3.3 |  | Conceptual | 4700000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12088 | 2018-09-04 | 17-ELB-005 | 22176 | 2018-05-15 | LN | 2027-06-01 | Big Cajun | Coly |  | 500 |  |  | Build a new 500 kV station near Big Cajun or expand LaGN owned Big Cajun 500 kV substation to connect new 500 kV line. Similarly, expand at the existing Coly 500 kV station to a 5 breaker ring bus configuration to terminate the other end of the 500 kV line with an ongoing project to install second Coly 500-230 kV, 1200 MVA auto. Installation of 2nd 500-230 kV auto at Coly is a MTEP Appendix A project 14-EGL-026. Construct an approx. 37 miles of new Big Cajun to Coly 500 kV line. The new 500 kV line will be constructed to a minimum of 3000 A using a triple bundled conductor. | LA |  | 37 | Conceptual | 129850000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12098 | 2017-09-12 | 17-ELB-007 | 22204 | 2018-05-15 | LNrc | 2026-06-01 | Delmont | Hazel |  | 230 |  |  | Upgrade the Delmont to Hazel kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. | LA |  |  | Conceptual | 3900000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12098 | 2017-09-12 | 17-ELB-007 | 22206 | 2016-09-14 | TEQ | 2026-06-01 | Delmont | Hazel |  | 230 |  |  | Upgrade the Delmont to Hazel kV conductor, bus work at both the stations, line bay bus ,jumpers and any station equipment to a minimum of 1600 A to increase the final rating on Delmont to Hazel 230 kV circuit to a minimum of 1600 A. | LA |  |  | Conceptual |  | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-LA | 12771 | 2017-01-05 |  | 22518 | 2017-01-31 | Dist | 2023-06-01 | Arnaudville |  |  | 230 |  |  | New substation | LA |  |  | Proposed | 9850000 |  |  | N | N | N
B in MTEP17 | B | South | Entergy-MS | 4613 | 2017-05-17 | 11-EMI-007 | 8765 | 2017-10-02 | SUB | 2022-12-01 | Strait |  |  | 115 |  | N/A | Construct new substation | MS |  |  | Proposed | 12235047 | Planning |  | N | N | N | Y
B in MTEP17 | B | South | Entergy-MS | 4613 | 2017-05-17 | 11-EMI-007 | 8766 | 2017-05-17 | CB | 2022-12-01 | Hollandale 115 kV substation |  |  | 115 |  | N/A | Add breakers at existing substation | MS |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP17 | B | South | Entergy-MS | 12218 | 2017-05-04 |  | 22346 | 2016-12-01 | SwSta |  | Whitfield |  |  | 115 |  |  | Add (3) 115kV breakers to the EMI Whitfield switching station. | MS |  |  | Proposed | 2200000 |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12069 | 2018-09-04 | 17-ETI-012 | 22150 | 2018-09-04 | SwSta | 2025-06-01 | War Eagle |  |  | 138 |  |  | Construct a new War Eagle 138 kV (4) breaker ring bus substation approximately 0.3 miles north of the Oak Ridge 138 kV substation that cuts into the Oak Ridge – Metro 138 kV L-169. | TX |  |  | Conceptual | 32600000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12069 | 2018-09-04 | 17-ETI-012 | 22152 | 2018-09-04 | LNrb | 2025-06-01 | Forest | War Eagle | 1 | 138 |  |  | Energize the abandoned 138 kV L-403 by terminating into the War Eagle and Forest 138 kV substations and rebuilding to a minimum of 1950 A. | TX |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12069 | 2018-09-04 | 17-ETI-012 | 22151 | 2018-09-04 | LN | 2025-06-01 | Porter | War Eagle | 1 | 138 |  |  | Construct a new 138 kV line from Porter to the new War Eagle substation using a conductor rated a minimum of 1950 A and a line route approximately 8 miles. | TX |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12086 | 2016-09-14 | 17-ETI-001 | 22172 | 2016-09-14 | SUB | 2023-06-01 | Caldwell |  |  | 69 |  |  | Construct a new (4) breaker 69 kV ring bus substation named Caldwell just East of the existing Caldwell Industrial 69 kV substation. Move the City of Caldwell 69-13.8 kV distribution transformer to the new substation. | TX |  |  | Conceptual | 32900000 |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12086 | 2016-09-14 | 17-ETI-001 | 22174 | 2016-09-14 | LN | 2023-06-01 | Bryan | Caldwell | 1 | 69 |  |  | Construct an approximately 24 mile line to 161 kV specifications from Bryan to the new 69 kV substation and operate to 69 kV. | TX |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12087 | 2017-05-17 | 17-ETI-002 | 22175 | 2017-05-17 | LNrb | 2024-06-01 | Texas Eastern Spindletop | Gladys | 1 | 69 |  |  | Rebuild the portion of 69 kV L114 between Texas Eastern Spindletop – Gulf Lucas – Gladys to achieve a minimum through path rating of 880 A. | TX |  |  | Proposed | 5900000 |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12087 | 2017-05-17 | 17-ETI-002 | 22177 | 2017-05-17 | BUS | 2024-06-01 | Gladys |  |  | 69 |  |  | Install (2) breakers at Gladys 69 kV substation. | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12089 | 2018-09-04 | 17-ETI-004 | 22178 | 2018-09-04 | SUB | 2026-06-01 | Pony |  |  | 230 |  |  | Construct a new 230-138 kV substation named “Pony” adjacent to the existing Dayton 138 kV substation that cuts into the China - Ranch 230 kV line. The 138 kV bus should be constructed as a (4) bay breaker-and-a-half configuration (8 line bays). The 230 kV bus should be constructed as a (4) breaker ring bus with the ability to expand to a breaker-and-a-half. Move the Parkway, Long John, Petry Woods, Liberty and Rolke Road 138 kV lines to the new Pony substation. Install a 230-138 kV, 400 MVA autotransformer at the new Pony substation. | TX |  |  | Conceptual | 17000000 | Planning |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12089 | 2018-09-04 | 17-ETI-004 | 22180 | 2018-09-04 | LN | 2026-06-01 | Pony | Dayton | 2 | 138 |  |  | Construct a second 138 kV line between the existing Dayton substation and the new Pony substation. | TX |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12089 | 2018-09-04 | 17-ETI-004 | 22179 | 2018-09-04 | LN | 2026-06-01 | Pony | Dayton | 1 | 138 |  |  | Construct a 138 kV line between the existing Dayton substation and the new Pony substation. | TX |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12765 | 2017-05-17 | 17-ETI-018 | 22512 | 2017-05-17 | Dist | 2024-06-01 | Double Bayou |  |  | 138 |  |  | New Substation | TX |  |  | Proposed | 30200000 |  |  | N | N | N
B in MTEP17 | B | South | Entergy-TX | 12766 | 2017-01-05 | 17-ETI-015 | 22513 | 2017-08-17 | Dist | 2023-05-01 | Junction |  |  | 230 |  |  | New Substation | TX |  |  | Proposed | 13200000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 8202 | 2016-09-12 | SHECO_02_MTEP17 | 20585 | 2016-09-12 | LN | 2020-08-01 | 334281 | TBD | 1 | 138 |  |  | Construct new radial 138 kV line from Fork Creek to new 138 kV Fred substation | TX |  |  | Proposed | 22200000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 8202 | 2016-09-12 | SHECO_02_MTEP17 | 20673 | 2016-09-12 | SUB | 2020-08-01 | 334281 |  |  | 138 |  |  | Substation upgrades at Fork Creek to accommodate new 138kV transmission line to Fred | TX |  |  | Proposed | 1500000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 8202 | 2016-09-12 | SHECO_02_MTEP17 | 20586 | 2016-09-12 | SUB | 2020-08-01 | TBD |  |  | 138 |  |  | Construct new 138 kV Fred substation. | TX |  |  | Proposed | 4000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12225 | 2017-06-01 | ETEC_01_MTEP17 | 22364 | 2017-01-31 | LN | 2021-08-01 | 334069 | 334088 | 1 | 230 |  | 780 | New 230kV transmission line Lewis Creek - Ponderosa | TX |  | 12 | Proposed | 22000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12225 | 2017-06-01 | ETEC_01_MTEP17 | 22366 | 2017-01-31 | SwSta | 2021-08-01 | 334088 |  |  | 230 |  |  | Upgrade 230kV bus and install terminal equipment at Ponderosa substation | TX |  |  | Proposed | 1000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12225 | 2017-06-01 | ETEC_01_MTEP17 | 22365 | 2017-01-31 | SwSta | 2021-08-01 | 334069 |  |  | 230 |  |  | Upgrade 230kV bus and install terminal equipment at Lewis Creek substation | TX |  |  | Proposed | 1000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22367 | 2017-01-31 | LN | 2021-08-01 | 334069 | 334088 | 1 | 230 |  | 780 | New 230kV transmission line Lewis Creek - Ponderosa | TX |  | 12 | Proposed | 22000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22373 | 2017-01-31 | LN | 2021-08-01 | 334034 | 334049 | 1 | 345 |  | 1326 | New 345kV transmission line Quarry - Rivtrin | TX |  | 10 | Proposed | 20000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22372 | 2017-01-31 | SUB | 2021-08-01 | 334049 | 334055 |  | 345 | 138 | 525 | Construct 345kV Rivtrin substation, install 345/138kV AT - 525 MVA | TX |  |  | Proposed | 10000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22371 | 2017-01-31 | LNrb | 2021-08-01 | 334028 | 509241 | 1 | 345 |  | 1121 | Cut into the existing 345kV Crockett - Grimes line to connect the new 345kV Quarry switching station | TX |  |  | Proposed | 1000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22370 | 2017-01-31 | SwSta | 2021-08-01 | 334034 |  |  | 345 |  |  | Construct 345kV Quarry switching substation | TX |  |  | Proposed | 7500000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22369 | 2017-01-31 | SwSta | 2021-08-01 | 334088 |  |  | 230 |  |  | Upgrade 230kV bus and install terminal equipment at Ponderosa substation | TX |  |  | Proposed | 1000000 |  |  | N | N | N
B in MTEP17 | B | South | ETEC | 12226 | 2017-06-01 | ETEC_02_MTEP17 | 22368 | 2017-01-31 | SwSta | 2021-08-01 | 334069 |  |  | 230 |  |  | Upgrade 230kV bus and install terminal equipment at Lewis Creek substation | TX |  |  | Proposed | 1000000 |  |  | N | N | N
B in MTEP17 | B | East | ITC, ITCT | 2933 | 2017-09-14 | ITC_16_023 | 5105 | 2016-12-01 | LNrc | 2020-12-31 | Superior | Wayne | 1 | 120 |  |  | Reconductor a ~10.5 mile-long portion of the Superior – Wayne 120 kV line that is comprised of 477 ACSR conductor only utilizing 795 ACSR conductor and replace the 477 ACSR line entrance at Wayne station. | MI | 10.5 |  | Proposed | 6500000 | Engineering |  | N | N | N | Y
B in MTEP17 | B | East | ITC, ITCT | 4501 | 2017-09-14 | ITC_16_019 | 8625 | 2016-09-14 | LNrb | 2020-12-31 | Bunce Creek | Menlo | 1 | 120 |  | 305 MVA | Rebuild 8.6 miles from the Bunce Creek - Menlo 120 kV circuit using 954 ACSR and OPGW on new 120 kV single circuit structures. Also replace limiting terminal equipment at both Bunce Creek and Menlo 120 kV stations. | MI | 8.6 |  | Proposed | 9772000 | Engineering |  | N | N | N | Y
B in MTEP17 | B | East | ITC, ITCT | 4501 | 2017-09-14 | ITC_16_019 | 8626 | 2016-09-14 | TEQ | 2020-12-31 | Menlo |  |  | 120 |  |  | Upgrade limiting terminal equipment at the Menlo 120 kV station. | MI |  |  | Proposed | 14000 | Engineering |  | N | N | N | Y
B in MTEP17 | B | West | ITCM | 10784 | 2016-10-12 |  | 21664 | 2016-02-18 | CAP | 2018-12-31 | 8th Street | Subustation |  | 69 | 69 | 10 MVAR | Add a 10 MVAR cap on the 69kV | IA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP17 | B | West | ITCM | 13712 | 2017-09-27 | BvrChnl T3 TEQ | 22780 | 2017-09-27 | TEQ | 2026-12-31 | Beaver Channel | Tranformer | T3 | 161 | 69 | 150 MVA | Upgrade the terminal equipment on the Beaver Channel T3 transformer. | IA |  |  | Planned |  |  |  | N | N | N
B in MTEP17 | B | East | ITCT | 4501 | 2017-09-14 | ITC_16_019 | 21944 | 2016-09-14 | TEQ | 2020-12-31 | Bunce Creek |  |  | 120 |  |  | Upgrade limiting terminal equipment at the Bunce Creek 120 kV station. | MI |  |  | Proposed | 14000 | Engineering |  | N | N | N
B in MTEP17 | B | West | MEC | 10002 | 2017-05-25 |  | 21425 | 2017-05-25 | TX | 2022-06-01 | Sub 39 |  |  | 161 | 69 | 125 | Install a second 125 MVA Sub 39 161-69 kV transformer. | IA |  |  | Planned | 960000 | Planning |  | N | N | N
B in MTEP17 | B | West | MP | 12564 | 2016-11-17 | 51 Line Upgrade | 22456 | 2018-08-30 | LNup |  | Riverton | Merrifield |  | 115 |  |  | Increase operating temp of 51 Line. | MN |  |  | Proposed |  |  |  | N | N | N
B in MTEP17 | B | West | MP | 12684 | 2016-12-09 | Boswell 230 Fast-Switched Cap Bank | 22475 | 2018-08-30 | CAP | 2020-07-01 | Boswell |  |  | 230 |  |  | New fast-switched capacitor bank (size TBD) | MN | 0 | 0 | Proposed | 1000000 | Planning Preliminary |  | N | N | N
B in MTEP17 | B | West | OTP | 4813 | 2018-06-29 | OTP | 9093 | 2017-10-23 | LN | 2026-01-01 | Clearbrook 115 kV | Bagley West 230 kV | 1 | 115 |  | 240 | Clearbrook 115 kV to Bagley West 230 kV Build new 115 kV Tranmission Line (22 miles) | MN |  | 22 | Proposed | 9000000 | Planning Preliminary |  | N | N | N | Y
B in MTEP17 | B | West | OTP | 4813 | 2018-06-29 | OTP | 9095 | 2018-06-29 | SUB | 2026-01-01 | Bagley West 230/115 kV Tap | 230 kV Tap |  | 230 | 115 |  | Bagley West 230 kV tap, add 230/115 kV transformer and breakers. Transformer 140 MVA and EM Rating 175 MVA | MN |  |  | Proposed | 3300000 | Planning Preliminary |  | N | N | N | Y
B in MTEP17 | B | South | SMEPA | 12210 | 2016-09-15 |  | 22357 | 2017-01-31 | Dist | 2020-12-01 | South Hattiesburg GOAB | South Hattiesburg |  | 69 |  |  | In order to serve the South Hattiesburg delivery point economically and reliably, service will be established by rebuilding SMEPA’s exiting 69kV Line 87 (South Hattiesburg GOAB - South Hattiesburg Sub) with 795 ACSR conductor and installing a new 3-way remote controlled GOAB north of Purvis on Line 39B (Purvis – Okahola GOAB). A new 69/26.4kV, 15/20/25 MVA transformer will be installed at the South Hattiesburg substation to accommodate the 69 kV service feed. | MS |  |  | Proposed | 3090000 |  |  | N | N | N
B in MTEP17 | B | South | SMEPA | 12212 | 2016-09-15 |  | 22356 | 2017-01-31 | Dist | 2021-12-01 | Oak Grove 161/69 | Oak Grove |  | 69 |  |  | In order to serve the Oak Grove delivery point economically and reliably, SMEPA’s Line 91 (Okahola GOAB – Oak Grove) will be rebuilt with 795 ACSR conductor and extended 0.5 miles to the proposed Oak Grove 161/69kV substation. A new 69/26.4kV, 15/20/25 MVA transformer will be installed at the Oak Grove substation to accommodate the 69kV service. | MS |  |  | Proposed | 2323000 |  |  | N | N | N
B in MTEP17 | B | South | SMEPA | 12222 | 2016-09-15 |  | 22353 | 2017-01-31 | Dist | 2022-09-01 | Maxie |  |  | 69 |  |  | In order to serve the Maxie delivery point economically and reliably from SMEPA’s transmission, a short 161kV looped service feed consisting of 795 ACSR conductor will connect the Maxie substation with SMEPA Lines 37 and 38. A 161kV breaker and a dual voltage high side 69-161/26.4kV, 15/20/25 MVA transformer will complete the substation upgrades. | MS |  |  | Proposed | 1135000 |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9723 | 2015-12-14 |  | 21107 | 2015-09-11 | SUB | 2018-12-31 | Fishhook |  |  | 138 | 138 | 240 | Construct 138 kV breaker station in East Quincy-Meredosia-2 138 kV lline. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9734 | 2017-12-19 |  | 21119 | 2017-12-19 | SUB | 2022-12-01 | North Utica |  |  | 138 | 34.5 | 255 | Construct 138 kV breaker station in North LaSalle-Fox River-1646 138 kV line. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9738 | 2016-09-16 |  | 21125 | 2016-09-16 | LNrc | 2025-06-01 | Grand Tower | Carbondale, Northwest | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability. | IL | 16.66 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9739 | 2016-09-16 |  | 21126 | 2016-09-16 | LNrc | 2025-06-01 | Carbondale, Northwest | West Frankfort | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability. | IL | 3.18 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9740 | 2016-09-16 |  | 21127 | 2016-09-16 | LNrc | 2025-06-01 | Grand Tower | Campbell Hill | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability. | IL | 7.94 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9743 | 2015-09-11 |  | 21130 | 2016-05-23 | LNrc | 2021-06-01 | Pana, North | Route 51D | 1 | 138 | 138 | 399 | Reconductor to 2000 A summer emergency capability | IL | 1.43 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9832 | 2015-09-14 |  | 21208 | 2015-09-14 | LNrc | 2027-06-01 | Casey | Kansas | 1 | 345 | 345 | 1793 | Reconductor to 3000 A summer emergency capability. | IL | 21.16 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9838 | 2017-09-15 |  | 21215 | 2017-09-15 | TEQ | 2020-06-01 | Kincaid | Austin | 1 | 345 | 345 | 1195 | Upgrade terminal equipment to minimum 2600 A summer emergency capability | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9840 | 2015-09-14 |  | 21216 | 2015-09-14 | SUB | 2020-05-01 | Washington Street |  |  | 138 | 138 | 478 | Establish 138 kV ring bus | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenIL | 9844 | 2017-03-10 |  | 21221 | 2017-03-10 | LN | 2021-12-01 | Hershey | McLean | 1 | 138 | 138 | 399 | Construct 138 kV Line | IL |  | 10 | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9717 | 2016-05-23 |  | 21099 | 2016-05-23 | TEQ | 2040-06-01 | Moberly | Thomas Hill | 1 | 161 | 161 | 314 | Upgrade terminal equipment at Moberly Substation. | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9721 | 2015-10-14 | AMRN46 | 21104 | 2015-10-14 | LNrc | 2020-06-01 | Tegeler | Franklin | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability | MO | 18.25 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9721 | 2015-10-14 | AMRN46 | 21105 | 2015-10-14 | LNrc | 2020-06-01 | Bland | Tegeler | 1 | 138 | 138 | 240 | Reconductor to 1200 A summer emergency capability | MO | 16.75 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9730 | 2016-02-29 |  | 21114 | 2017-03-10 | SUB | 2019-12-01 | Gray | Wildwood | 1 | 138 | 138 | 240 | Replace overstressed breaker at Gray Summit | MO |  |  | Planned |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9732 | 2016-05-20 |  | 21116 | 2016-09-13 | SUB | 2021-12-01 | Mason |  |  | 138 | 138 | 717 | Replace overstressed Bus 1-2 tie breaker | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9733 | 2016-05-23 | AMRN47 | 21117 | 2016-09-13 | SUB | 2021-12-01 | Page | Warson | 5 | 138 | 138 | 399 | Replace overstressed breaker at Page. | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9733 | 2016-05-23 | AMRN47 | 21118 | 2016-09-13 | SUB | 2021-12-01 | Page | Berkeley | 1 | 138 | 138 | 240 | Replace overstressed breaker at Page. | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9735 | 2016-05-23 | AMRN48 | 21120 | 2016-09-13 | SUB | 2021-12-01 | Tyson | Marshall | 1 | 138 | 138 | 399 | Replace overstressed breaker at Tyson | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9735 | 2016-05-23 | AMRN48 | 21122 | 2016-09-13 | SUB | 2021-12-01 | Tyson | Arnold | 3 | 138 | 138 | 240 | Replace overstressed breaker at Tyson | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9735 | 2016-05-23 | AMRN48 | 21121 | 2016-09-13 | SUB | 2021-12-01 | Tyson | Marshall | 2 | 138 | 138 | 399 | Replace overstressed breaker at Tyson. | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9825 | 2015-09-14 |  | 21200 | 2015-09-14 | TEQ | 2021-06-01 | Tegeler | Osage | 1 | 138 | 138 | 128 | Upgrade terminal equipment at Osage. | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | AmerenMO | 9830 | 2016-05-23 |  | 21206 | 2016-05-23 | LNrc | 2022-06-01 | Meramec | Joachim | 2 | 138 | 138 | 322 | Reconductor to 1600 A summer emergency capability. | MO | 15.91 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | West | ATC | 9925 | 2018-03-26 | MTEP ID 10183 | 21337 | 2016-01-26 | SUB | 2018-06-01 | Pershing |  |  | 345 |  |  | Loop Stone Lake - Gardner Park 345-kV line into new Pershing 345-kV Substation. | WI |  |  | Proposed | 15000000 |  |  | N | N | N
B in MTEP16 | B | West | ATC | 10590 | 2018-03-26 | PR06462, F4830 | 21620 | 2018-09-14 | LNrb | 2023-12-31 | Academy | Columbus Tap | 1 | 69 |  | 79 | Rebuild Academy - Columbus 69kV. | WI | 1 |  | Conceptual | 3000000 | Planning |  | N | N | N
B in MTEP16 | B | West | ATC | 10590 | 2018-03-26 | PR06462, F4830 | 21621 | 2016-01-12 | LNrb | 2023-12-31 | Columbus Tap | Columbus | 1 | 69 |  | 79 | Rebuild Academy - Columbus 69kV. | WI | 1.13 |  | Conceptual |  |  |  | N | N | N
B in MTEP16 | B | West | ATC, XEL | 10183 | 2016-08-18 |  | 21485 | 2016-06-15 | SUB | 2018-06-01 | Pershing |  |  | 345 | 115 |  | New Pershing 345/115 kV substation. | WI |  |  | Planned | 10000000 |  |  | N | N | N
B in MTEP16 | B | East | CETO | 9879 | 2015-09-14 |  | 21264 | 2016-05-04 | LN | 2019-06-01 | Moore Road | Vrooman | 1 | 138 |  |  | Construct a new approximately 22 mile 138 kV line between Moore Road and Vrooman Substations, utilizing existing 46 kV line route. | MI |  | 22 | Conceptual | 20600000 | Budgetary |  | N | N | N
B in MTEP16 | B | East | CETO | 9879 | 2015-09-14 |  | 21266 | 2016-05-04 | SUB | 2019-06-01 | Vrooman |  |  | 138 |  |  | Add a 138 kV circuit breaker to the existing ring bus and install other supporting terminal equipment for the Moore Road-Vrooman 138 kV Line. | MI |  |  | Conceptual | 700000 | Budgetary |  | N | N | N
B in MTEP16 | B | East | CETO | 9879 | 2015-09-14 |  | 21265 | 2016-05-04 | SUB | 2019-06-01 | Moore Road |  |  | 138 |  |  | Add a 138 kV circuit breaker to the existing ring bus and install other supporting terminal equipment for the Moore Road-Vrooman 138 kV Line. | MI |  |  | Conceptual | 700000 | Budgetary |  | N | N | N
B in MTEP16 | B | South | Entergy-LA | 9764 | 2015-09-13 | 16-EGL-005 | 21138 | 2018-05-15 | LNrc | 2026-06-01 | Dixie Baker | Baker | 1 | 69 |  |  | Upgrade line | LA |  |  | Proposed | 3200000 | Planning |  | N | N | N
B in MTEP16 | B | South | Entergy-TX | 9821 | 2018-09-04 | 16-ETI-020 | 21196 | 2015-09-14 | LN | 2024-06-01 | Bryan | College Station Area | 1 | 138 |  |  | New line | TX |  |  | Proposed | 31500000 | Planning |  | N | N | N
B in MTEP16 | B | South | Entergy-TX | 10080 | 2016-05-12 | HCEC_01_MTEP16 | 21452 | 2015-11-12 | SUB |  | 334126 |  |  | 138 |  |  | Magnolia Groveton station upgrades to support addition of new transmission line | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10080 | 2016-05-12 | HCEC_01_MTEP16 | 21450 | 2015-11-12 | LN |  | 334126 | TBD | 1 | 138 |  |  | Construct new 138 kV line from existing Magnolia Groveton station to new Weldon station | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10080 | 2016-05-12 | HCEC_01_MTEP16 | 21454 | 2015-11-12 | SUB |  | 509325 |  |  | 138 |  |  | Mustang Prairie station upgrades to support addition of new transmission line | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10080 | 2016-05-12 | HCEC_01_MTEP16 | 21453 | 2015-11-12 | SUB |  | TBD |  |  | 138 |  |  | New Weldon station to support load growth | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10080 | 2016-05-12 | HCEC_01_MTEP16 | 21451 | 2015-11-12 | LN |  | 509325 | TBD | 1 | 138 |  |  | Construct new 138 kV line from existing Mustang Prairie station to new Weldon station | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10081 | 2015-09-18 | SHECO_01_MTEP16 | 21455 | 2015-11-12 | SwSta |  | TBD |  |  | 138 |  |  | New switching station on Dogwood-Warren 138 kV line | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10081 | 2015-09-18 | SHECO_01_MTEP16 | 21459 | 2015-11-12 | SUB |  | 334304 |  |  | 138 |  |  | North Buna station upgrades to support addition of new transmission line | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10081 | 2015-09-18 | SHECO_01_MTEP16 | 21458 | 2015-11-12 | LN |  | 334304 | TBD |  | 138 |  |  | Construct new 138 kV line from the new Fred substation to the existing North Buna substation | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10081 | 2015-09-18 | SHECO_01_MTEP16 | 21457 | 2015-11-12 | SUB |  | TBD |  |  | 138 |  |  | Construct new 138 kV Fred substation | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10081 | 2015-09-18 | SHECO_01_MTEP16 | 21456 | 2015-11-12 | LN |  | TBD | TBD |  | 138 |  |  | Construct new 138 kV line from the new Fred switching station to new Fred substation. | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10082 | 2015-09-18 | SHECO_02_MTEP16 | 21460 | 2015-11-12 | SUB |  | TBD |  |  | 138 |  |  | Construct new 138 kV Fred substation | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10082 | 2015-09-18 | SHECO_02_MTEP16 | 21464 | 2015-11-12 | SUB |  | 334281 |  |  | 138 |  |  | Fork Creek station upgrades to support addition of new transmission line | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10082 | 2015-09-18 | SHECO_02_MTEP16 | 21463 | 2015-11-12 | SUB |  | 334304 |  |  | 138 |  |  | North Buna station upgrades to support addition of new transmission line | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10082 | 2015-09-18 | SHECO_02_MTEP16 | 21462 | 2015-11-12 | LN |  | 334281 | TBD |  | 138 |  |  | Construct new 138 kV line from the new Fred substation to the existing Fork Creek substation | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | South | ETEC | 10082 | 2015-09-18 | SHECO_02_MTEP16 | 21461 | 2015-11-12 | LN |  | 334304 | TBD |  | 138 |  |  | Construct new 138 kV line from the new Fred substation to the existing North Buna substation | TX |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | Central | IPL | 10786 | 2016-02-18 |  | 21666 | 2016-02-18 | SUB | 2017-12-31 | Stout Substation |  |  | 138 | 13.8 |  | Stout Battery Energy Storage System interconnection at the existing Stout 138 kV Substation. Connected through existing 13.8 kV Bus/Breaker and existing 138/13.8 kV step-up transformer. | IN |  |  | Planned |  |  |  | N | N | N
B in MTEP16 | B | Central | IPL | 10786 | 2016-02-18 |  | 21721 | 2016-05-02 | RLY | 2017-12-31 | Lilly South |  |  | 138 |  |  | Change relay tap settings at Lilly South to increase Lilly South-Southwest ckt 10 line rating to 345 MVA. Line rating increase due to MISO J401 NRIS Constraint mitigation on the Lilly South-Southwest ckt 10 line. | IN |  |  | Planned | 4000 | Planning |  | N | N | N
B in MTEP16 | B | West | ITCM | 9100 | 2015-05-28 | Burlington Area 69kV | 20813 | 2015-05-28 | BUS | 2019-12-19 | Burlington | South Burlington | 1 | 69 |  | 103 MVA | Upgrade terminal equipment above the conductor rating. | IA |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | West | ITCM | 9100 | 2015-05-28 | Burlington Area 69kV | 20814 | 2015-05-28 | LNrb | 2019-12-31 | Burlington 4th Street | Agency | 1 | 69 |  | 101 MVA | Rebuild the 4th Street-Agency 69kV line to T2-477. | IA | 2.51 |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | East | ITCT | 9885 | 2016-09-30 | ITC_15_017 | 21273 | 2015-10-01 | LNup | 2019-12-31 | Jewell | St.Clair | 1 | 345 |  |  | Raise the Sag Limit on Jewell-St.Clair 345 kV to 1965 MVA (3288 Amp) | MI |  |  | Proposed | 5380000 | Engineering |  | N | N | N
B in MTEP16 | B | West | MDU | 9122 | 2015-06-10 |  | 20818 | 2015-06-10 | TEQ | 2020-06-01 | East Bismarck |  |  | 115 |  | 191 | Replace switch 7114, 7115 & 7117 and line jumpers. | ND |  |  | Planned | 125000 | Engineering Preliminary |  | N | N | N
B in MTEP16 | B | West | MDU | 9140 | 2015-06-12 |  | 20822 | 2015-06-12 | LNrc | 2020-09-01 | Coyote Jct | NACO | 1 | 115 |  | 120 | Reconductor line with 477 ACSS | ND | 7 |  | Proposed | 1270000 | Planning Preliminary |  | N | N | N
B in MTEP16 | B | West | MDU | 9180 | 2015-06-16 |  | 20830 | 2015-06-16 | CAP | 2020-10-01 | Green River Jct |  |  | 115 |  |  | Increase existing 15 Mvar capacitors to 20 Mvar | ND |  |  | Proposed | 400000 | Planning |  | N | N | N
B in MTEP16 | B | East | METC | 9880 | 2016-09-30 | METC_15_025 | 21267 | 2015-11-24 | LNup | 2018-12-31 | Claremont | Manning | 1 | 138 |  |  | Remediate the sag limit on the Portsmouth Tap – Manning 138 kV section of the Claremont – Manning 1 138 kV line to a minimum of 378 MVA / 1581 Amps and remediate the sag limit on the Claremont – Portsmouth Tap 138 kV section of the Claremont – Manning 1 138 kV line to a minimum of 362 MVA / 1514 Amps | MI |  |  | Proposed |  |  |  | N | N | N
B in MTEP16 | B | East | METC | 9880 | 2016-09-30 | METC_15_025 | 21268 | 2015-11-24 | TEQ | 2018-12-31 | Claremont |  |  | 138 |  |  | Upgrade terminal equipment at Claremont | MI |  |  | Proposed | 330000 | Engineering |  | N | N | N
B in MTEP16 | B | East | METC | 9929 | 2016-09-30 | METC_15_29 | 21339 | 2015-12-04 | LN | 2019-12-31 | Donaldson Creek | Pere Marquette | 1 | 138 |  |  | Build new ~21 mile circuit from Donaldson Creek to Pere Marquette using 954 ACSR and OPGW | MI |  |  | Proposed | 7400000 | Engineering |  | N | N | N
B in MTEP16 | B | East | METC | 9929 | 2016-09-30 | METC_15_29 | 21341 | 2015-12-04 | TEQ | 2019-12-31 | Pere Marquette |  |  | 138 |  |  | Upgrade terminal equipment at Pere Marquette | MI |  |  | Proposed | 760000 | Engineering |  | N | N | N
B in MTEP16 | B | East | METC | 9929 | 2016-09-30 | METC_15_29 | 21340 | 2015-12-04 | TEQ | 2019-12-31 | Donaldson Creek |  |  | 138 |  |  | Upgrade terminal equipment at Donaldson Creek | MI |  |  | Proposed | 540000 | Engineering |  | N | N | N
B in MTEP16 | B | West | MP | 9643 | 2015-09-11 | Little Falls Tie Breaker | 20956 | 2015-09-08 | CB | 2017-06-01 | Little Falls |  |  | 115 |  |  | New 115 kV tie breaker at Little Falls & associated bus modifications | MN | 0 | 0 | Proposed | 1000000 | Planning |  | N | N | N
B in MTEP16 | B | West | OTP | 9997 | 2018-08-21 |  | 21422 | 2018-08-21 | SUB | 2021-12-31 | Rolette 230/69/41.6 kV |  |  | 230 | 41.6 |  | Install three 230 kV Breakers, one 69 kV Breaker and one 41.6 kV Breaker. Install one 230/69/41.6 kV Transformer (60 MVA) | ND |  |  | Proposed | 9000000 | Planning Preliminary |  | N | N | N
B in MTEP16 | B | West | OTP | 10001 | 2018-08-21 |  | 21424 | 2018-08-21 | SUB | 2021-12-31 | Voltaire 115/41.6 kV |  |  | 115 | 41.6 |  | Build a new 115/41.6 kV substation in the Voltaire area. Install one 56 MVA Transformer 115/41.6 kV. Install four 41.6 kV Breakers. | ND |  |  | Proposed | 5000000 | Planning Preliminary |  | N | N | N
B in MTEP16 | B | West | OTP | 10043 | 2015-09-17 |  | 21445 | 2015-09-18 | CB | 2020-12-31 | Jamestown 345 |  |  | 345 |  |  | Add an additional 345 kV breaker to create a 4 breaker ring bus. | ND |  |  | Planned | 2000000 | Planning |  | N | N | N
B in MTEP16 | B | West | OTP | 10903 | 2018-08-21 |  | 21686 | 2018-08-21 | SUB | 2021-12-31 | Rugby 230 kV |  |  | 115 |  |  | Install one 115 kV breaker. | ND |  |  | Proposed | 500000 | Planning Preliminary |  | N | N | N
B in MTEP16 | B | West | OTP | 10903 | 2018-08-21 |  | 21687 | 2018-08-21 | LN | 2021-12-31 | Rugby 230 kV | Harvey 230 kV |  | 115 |  | 243 | Construct 2 miles of 115 kV line out of the Rugby 230 kV Substation. Conductor T2 - 266 ACSR with Summer Ratings 192 & Emergency 212. Winter Ratings 243 & Emergency 267. | ND |  | 2 | Proposed | 1000000 | Planning Preliminary |  | N | N | N
B in MTEP16 | B | Central | PPI | 9563 | 2017-06-02 | 2016-13 | 20928 | 2015-09-01 | LN | 2017-12-01 | 4TUSCOLA W (348350) | 4CRONUS W | 1 | 138 |  | 229 | 2.7 mile 138 kV transmission line | IL |  | 2.7 | Planned | 1620000 | Budgetary |  | N | N | N
B in MTEP16 | B | Central | PPI | 9563 | 2017-06-02 | 2016-13 | 20929 | 2015-09-01 | LN | 2017-12-01 | 4TUSCOLA W (348350) | 4CRONUS E | 1 | 138 |  | 229 | 3.3 mile 138 kV transmission line | IL |  | 3.3 | Planned | 1980000 | Budgetary |  | N | N | N
B in MTEP16 | B | Central | Vectren | 9943 | 2016-05-18 | 2016SIGE14 | 21387 | 2016-05-18 | TX | 2023-12-31 | LEONARD ROAD |  |  | 138 | 69 |  | 138/69kV transformer addition at existing Leonard Road switching station | IN |  |  | Proposed | 3000000 | Budgetary |  | N | N | N
B in MTEP16 | B | Central | Vectren | 9943 | 2016-05-18 | 2016SIGE14 | 21388 | 2016-05-18 | LN | 2023-12-31 | AB BROWN | FARM BUREAU | Z94 | 138 |  |  | Z94 138kV line loop from AB Brown Sub to Farm Bureau Sub for load growth | IN |  |  | Proposed | 100000 | Budgetary |  | N | N | N
B in MTEP16 | B | East | WPSC | 10264 | 2015-10-28 | Pellston to Cross Village | 21507 | 2016-09-15 | LNrb | 2022-12-31 | Pellston | Cross Village |  | 138 |  |  | Pellston to Cross Village line rebuild | MI | 9.08 |  | Proposed | 3600000 | Budgetary |  | N | N | N
B in MTEP16 | B | East | WPSC | 10265 | 2015-10-28 |  | 21508 | 2015-10-28 | RLY | 2019-12-31 | Gaylord |  |  | 138 |  |  | Gaylord relay replacement - 138kV Livingston line | MI |  |  | Planned | 35000 | Budgetary |  | N | N | N
B in MTEP16 | B | West | XEL | 10183 | 2016-08-18 |  | 21486 | 2016-06-15 | TX | 2018-06-01 | Pershing |  |  | 345 | 115 | 448 MVA | New Pershing 345/115 kV 448 MVA transformer | WI |  |  | Planned | 4500000 |  |  | N | N | N
B in MTEP15 | B | Central | AmerenIL | 3010 | 2015-03-19 | AMRN13 | 5219 | 2014-09-11 | LN | 2030-06-01 | Baldwin | Heritage | 1 | 345 |  | 1793 | Baldwin-Grand Tower-N.W. Cape (Heritage) 345 kV - Construct 69 miles of 3000 A summer emergency capability. Install a 560 MVA, 345/138 kV transformer at Grand Tower | IL |  | 69 | Proposed | 0 | Planning |  | N | N | N | Y
B in MTEP15 | B | Central | AmerenIL | 3010 | 2015-03-19 | AMRN13 | 5220 | 2014-08-27 | TX | 2030-06-01 | Grand Tower Plant | Install 345/138 kV Xfmr | 1 | 345 | 138 | 560 | Install a 560 MVA, 345/138 kV transformer at Grand Tower | IL |  |  | Proposed | 5000000 | Planning |  | N | N | N | Y
B in MTEP15 | B | Central | AmerenIL | 7802 | 2015-11-24 |  | 20089 | 2015-11-24 | LNrc | 2026-06-01 | West Frankfort, East | West Frankfort | 1 | 138 |  | 322 | Reconductor 5.25 miles of 1272 kcmil ACSR conductor with conductor capable of carrying 1600 A under summer emergency conditions. Replace bus conductor at West Frankfort, East with conductor having capability equal to or greater than the new line conductor. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP15 | B | Central | AmerenIL | 7821 | 2016-06-02 |  | 20091 | 2016-06-02 | CAP | 2020-06-01 | Kickapoo |  |  | 34.5 |  |  | Install --2-7.2 Mvar, 34.5 kV capacitor banks and PCBs. | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP15 | B | Central | AmerenIL | 7861 | 2015-03-19 |  | 20101 | 2017-03-10 | CB | 2019-06-01 | Effingham Northwest |  |  | 138 |  |  | Install 2-138 kV, 2000 A, 40 kA PCBs, one on each 138 kV line position. Upgrade bus conductor to 2000 A continuous capability. | IL |  |  | Planned |  |  |  | N | N | N
B in MTEP15 | B | Central | AmerenMO | 7862 | 2014-12-05 |  | 20102 | 2016-09-09 | SUB | 2020-12-01 | Buick Smelter |  |  | 161 | 4 |  | Relocate substation. Remove existing substation, install 2 motor-operated 161 kV switches and 2 customer owned and installed 161 kV circuit switchers. Make provisions for the addition of a third 161-4 kV transformer. | MO |  |  | Proposed |  |  |  | N | N | N
B in MTEP15 | B | West | ATC | 8082 | 2018-04-24 | PR07197, F5291 | 20407 | 2014-09-19 | LNrc | 2020-12-01 | Highway V | Preble | 1 | 138 |  | 220 | Reconductor X154 Highway V - Preble 138 kV line | WI | 2 |  | Conceptual | 6000000 | Planning |  | N | N | N
B in MTEP15 | B | Central | BREC | 3440 | 2014-09-16 | LRP6 | 6343 | 2010-11-15 | TX | 2024-12-31 | Reid EHV 161 kV | Reid EHV 69 kV |  | 161 | 69 | 56 MVA | new transformer | KY |  |  | Proposed | 5000000 | Planning |  | N | N | N | Y
B in MTEP15 | B | South | CLECO | 7993 | 2015-04-01 |  | 20267 | 2015-07-09 | LNrc | 2024-05-01 | Rodemacher | East Leesville | 1 | 230 |  | 628 | Reconductor Rodemacher to East Leesville 230 kV line with Cardinal 954 ACSS/TW/HS285 | LA | 38.28 |  | Proposed | 10000000 | Planning |  | N | N | N
B in MTEP15 | B | South | Entergy-TX | 4799 | 2017-09-13 | 13-ETI-021 | 9067 | 2017-08-17 | SUB | 2023-05-01 | Dishman 230 kV Substation |  |  | 230 |  |  | Construct new substation | TX |  |  | Proposed | 10500000 |  |  | N | N | N | Y
B in MTEP15 | B | West | GRE | 2632 | 2014-12-19 | 20385 | 4643 | 2014-12-19 | LN | 2022-11-30 | Onigum | Birch Lake | 1 | 115 |  | 140 | Onigum 115 kV conversion, Birch Lake 115 kV breaker and deadend | MN | 9.45 |  | Proposed | 5300000 |  |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8652 | 2016-10-06 | SUB | 2020-12-31 | Mortar Creek |  |  | 345 |  | N/A | The Mortar Creek 345 kV switching substation. | MI |  |  | Proposed | 17100000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8658 | 2016-10-06 | LN | 2020-12-31 | Mortar Creek | Monroe | 2 | 345 |  | 1748 MVA | Loop the Monroe #2 circuit into Mortar Creek. | MI |  |  | Proposed | 1000000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8657 | 2016-10-06 | LN | 2020-12-31 | Mortar Creek | Lenawee - Milan | 1 | 345 |  | 1814 MVA | Loop the Lenawee - Milan circuit into Mortar Creek. | MI |  |  | Proposed | 1000000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8656 | 2016-10-06 | LN | 2020-12-31 | Mortar Creek | Majestic | 1 | 345 |  | 953 MVA | Loop the Majestic circuit into Mortar Creek. | MI |  |  | Proposed | 1000000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8655 | 2016-10-06 | LN | 2020-12-31 | Mortar Creek | Lemoyne | 1 | 345 |  | 953 MVA | Loop the Lemoyne circuit into Mortar Creek. | MI |  |  | Proposed | 1000000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8654 | 2016-10-06 | LN | 2020-12-31 | Mortar Creek | Monroe | 1 | 345 |  | 1315 MVA | Loop Monroe circuit into Mortar Creek. | MI |  |  | Proposed | 1000000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | ITC, ITCT | 4520 | 2016-10-06 | ITC_14_001 | 8653 | 2016-10-06 | LN | 2020-12-31 | Mortar Creek | Bayshore | 1 | 345 |  | 1262 MVA | Loop the Bayshore circuit into Mortar Creek. | MI |  |  | Proposed | 1000000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | West | ITCM | 8842 | 2015-03-19 | Quad-Rock Ck 345 | 20759 | 2016-01-08 | LN | 2024-12-31 | Quad Cities | Rock Creek | 2 | 345 |  | 1246 MVA | Build the Quad Cities to Rock Creek 345kV line to double circuit and add 345kV terminals at both substations. | IA,IL |  |  | Conceptual |  |  |  | N | N | N
B in MTEP15 | B | West | ITCM | 8843 | 2015-03-19 | Rock Creek 2nd 345/161kV | 20760 | 2016-01-08 | TX | 2024-12-31 | Rock Creek |  |  | 345 | 161 | 450 MVA | Add a 2nd 345/161kV 450MVA transformer at Rock Creek. | IA |  |  | Conceptual |  |  |  | N | N | N
B in MTEP15 | B | West | ITCM | 8844 | 2015-03-19 | Albany-Galena 161kV Rebuild | 20761 | 2015-03-13 | LNrb | 2024-12-31 | Albany | York | 1 | 161 |  | 446 MVA | Rebuild Albany-York161kV to 446MVA. | IL | 15.04 |  | Conceptual |  |  |  | N | N | N
B in MTEP15 | B | West | ITCM | 8844 | 2015-03-19 | Albany-Galena 161kV Rebuild | 20763 | 2015-03-13 | LNrb |  | Savanna | Galena | 1 | 161 |  | 446 MVA | Rebuild Savanna to Galena 161kV to 446 MVA. | IL | 29.16 |  | Conceptual |  |  |  | N | N | N
B in MTEP15 | B | West | ITCM | 8844 | 2015-03-19 | Albany-Galena 161kV Rebuild | 20762 | 2015-03-13 | LNrb |  | York | Savanna | 1 | 161 |  |  | Rebuild York to Savanna 161kV to 446 MVA. | IL | 8.65 |  | Conceptual |  |  |  | N | N | N
B in MTEP15 | B | East | ITCT | 3943 | 2014-12-02 |  | 7505 | 2015-04-29 | TEQ | 2018-12-31 | Navarre |  | 1 | 230 | 120 |  | Increase the CT ratio on the low-side breaker of the Navarre 230/120 kV Transformer #201. | MI |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP15 | B | East | ITCT | 4520 | 2016-10-06 | ITC_14_001 | 20382 | 2016-10-06 | RLY | 2020-12-31 | Majestic |  |  | 345 |  |  | Upgrade relays at the Majestic station. | MI |  |  | Proposed | 450000 | Engineering |  | N | N | N
B in MTEP15 | B | East | ITCT | 4520 | 2016-10-06 | ITC_14_001 | 20383 | 2016-10-06 | RLY | 2020-12-31 | Monroe |  |  | 345 |  |  | Upgrade relays at Monroe station. | MI |  |  | Proposed | 400000 | Engineering |  | N | N | N
B in MTEP15 | B | East | ITCT | 8068 | 2015-04-22 | ITC_13_061 | 20384 | 2014-09-15 | LNup | 2017-12-31 | Brownstown | Monroe | 2 | 345 |  | 1756 MVA | Remediate the sag limit on the Brownstown to Monroe 2 345 kV line to increase its summer emergency rating to a minimum of 1793 MVA / 3000 Amps. | MI | 18.2 | 0 | Planned | 1200000 | Engineering |  | N | N | N
B in MTEP15 | B | East | ITCT | 8069 | 2015-04-22 | ITC_13_056 | 20385 | 2014-09-15 | LNup | 2018-12-31 | Lemoyne | Majestic | 1 | 345 |  |  | Remediate the sag limit on the Lemoyne - Majestic 345 kV line. | MI |  |  | Proposed | 2500000 | Engineering |  | N | N | N
B in MTEP15 | B | East | ITCT | 8099 | 2015-04-22 | ITC_14_014 | 20442 | 2014-09-15 | LNrb | 2018-12-31 | Lincoln | Northeast/Northwest | 1 | 120 |  |  | Rebuild 2.95 miles of 477 ACSR to 1431 ACSR on new Double circuit towers. | MI |  |  | Proposed | 4000000 | Engineering |  | N | N | N
B in MTEP15 | B | East | ITCT | 8099 | 2015-04-22 | ITC_14_014 | 20443 | 2014-09-15 | TEQ | 2018-12-31 | Lincoln |  |  | 120 |  |  | Replace 2 line enterences at Lincoln Substation. | MI |  |  | Proposed | 200000 | Engineering |  | N | N | N
B in MTEP15 | B | West | MEC | 8023 | 2015-04-09 |  | 20297 | 2015-03-10 | LNrc |  | Hills | Sub E (Iowa City) | 1 | 161 |  | 410 MVA | Reconductor 161 kV line | IA | 6.6 |  | Proposed | 4000000 | Planning |  | N | N | N
B in MTEP15 | B | West | MEC | 8114 | 2015-04-09 |  | 20451 | 2016-09-14 | LNup | 2018-06-01 | SubA | Sub 84 |  | 69 |  | 72 | Replace structures to increase line clearance and rating. | IA | 8.6 |  | Proposed | 225000 | Planning |  | N | N | N | NT
B in MTEP15 | B | East | METC | 1804 | 2014-12-02 |  | 3620 | 2014-11-17 | TEQ | 2018-12-31 | Marquette | Substation Equipment |  | 138 |  |  | upgrade station equipment (relaying at Marquette) | MI |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP15 | B | East | METC | 3927 | 2015-07-22 | METC_14_026 | 7489 | 2014-11-14 | TEQ | 2017-12-31 | Karn | Saginaw River | 1 | 138 |  |  | Replace limiting equipment from the Saginaw River 138 kV station. | MI |  |  | Proposed | 2800000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | METC | 4525 | 2017-05-22 | METC_14_015 | 8666 | 2017-05-22 | TX | 2021-12-31 | Goss |  |  | 345 | 138 |  | Install a second 345/138 kV transformer at Goss | MI |  |  | Planned | 4490000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | METC | 4525 | 2017-05-22 | METC_14_015 | 8667 | 2017-05-22 | SUB | 2021-12-31 | Goss |  |  | 345 | 138 |  | Install new and upgrade existing station equipment at Goss. | MI |  |  | Planned | 4810000 | Engineering |  | N | N | N | Y
B in MTEP15 | B | East | METC | 8123 | 2015-04-22 | METC_14_028 | 20475 | 2014-12-05 | TX | 2018-12-31 | Weeds Lake |  |  | 345 | 138 |  | Add a 2nd 345/138 kV transformer at Weeds Lake substation | MI |  |  | Proposed | 4500000 | Engineering |  | N | N | N
B in MTEP15 | B | East | METC | 8123 | 2015-04-22 | METC_14_028 | 20681 | 2015-07-13 | RLY | 2018-12-31 | Argenta |  |  | 345 |  |  | Upgrade line relaying at Argenta 345 kV station. | MI |  |  | Proposed | 250000 | Engineering |  | N | N | N
B in MTEP15 | B | East | METC | 8123 | 2015-04-22 | METC_14_028 | 20483 | 2014-12-05 | SUB | 2018-12-31 | Weeds Lake |  |  | 345 | 138 |  | Add 345 and 120 kV station equipment required to accomodate the new 345/138 kV transformer #2 and looping in the Argenta to Twin Branch 345 kV line. | MI |  |  | Proposed | 11750000 | Engineering |  | N | N | N
B in MTEP15 | B | East | METC | 8123 | 2015-04-22 | METC_14_028 | 20481 | 2014-12-05 | LN | 2018-12-31 | Weeds Lake | Twin Branch | 1 | 345 |  |  | Install approx 0.1 miles of new 345 kV double circuit structures, and use 2x954 ACSR to loop Agenta-Twin Branch 345 kV into Weeds Lake to create the Twin Branch(AEP) to Weeds Lake #1 circuit | MI |  | 0.1 | Proposed | 500000 | Engineering |  | N | N | N
B in MTEP15 | B | East | METC | 8123 | 2015-04-22 | METC_14_028 | 20479 | 2014-12-05 | LN | 2018-12-31 | Weeds Lake | Argenta | 2 | 345 |  |  | Install approx 0.1 miles of new 345 kV double circuit structures, and use 2x954 ACSR to loop Agenta-Twin Branch 345 kV into Weeds Lake to create the Argenta to Weeds Lake #2 circuit | MI |  | 0.1 | Proposed | 500000 | Engineering |  | N | N | N
B in MTEP15 | B | East | METC | 8130 | 2016-11-10 | METC_13_049 | 20497 | 2016-11-10 | TX | 2020-12-31 | Pere Marquette |  |  | 345 | 230 |  | Install a 345/230 kV transformer at Pere Marquette substation. | MI |  |  | Proposed | 4655000 | Engineering Preliminary |  | N | N | N
B in MTEP15 | B | East | METC | 8130 | 2016-11-10 | METC_13_049 | 20505 | 2016-11-10 | LN | 2020-12-31 | Keystone | Pere Marquette | 1 | 230 |  |  | Construct the new, approx. 75 mile, 230 kV transmission line between Pere Marquette and Keystone Substations | MI | 29.4 | 46.4 | Proposed | 66020000 | Engineering Preliminary |  | N | N | N
B in MTEP15 | B | East | METC | 8130 | 2016-11-10 | METC_13_049 | 20504 | 2016-11-10 | SUB | 2020-12-31 | Pere Marquette |  |  | 345 | 230 |  | Install all 230 and 345 kV terminal equipment associated with the new 345/230 kV transformer and the new 230 kV Pere Marquette to Keystone line. | MI |  |  | Proposed | 11561000 | Engineering Preliminary |  | N | N | N
B in MTEP15 | B | East | METC | 8130 | 2016-11-10 | METC_13_049 | 20503 | 2016-11-10 | SUB | 2020-12-31 | Keystone |  |  | 230 | 138 |  | Install all 230 and 138 kV terminal equipment associated with the new 230/138 kV transformer and the new 230 kV Pere Marquette to Keystone line. | MI |  |  | Proposed | 5595000 | Engineering Preliminary |  | N | N | N
B in MTEP15 | B | East | METC | 8130 | 2016-11-10 | METC_13_049 | 20499 | 2016-11-10 | TX | 2020-12-31 | Keystone |  |  | 230 | 138 |  | Install a 230/138 kV transformer at Keystone substation. | MI |  |  | Proposed | 2367000 | Engineering Preliminary |  | N | N | N
B in MTEP15 | B | East | NIPS | 8026 | 2014-12-01 |  | 20299 | 2014-11-26 | TX | 2017-12-31 | 17DEKALB 138 | 17DEKALB 69 | 1 | 138 | 69 | 112 | Upgrade to 112 MVA Transformer | IN |  |  | Planned | 2700000 | Planning |  | N | N | N
B in MTEP15 | B | East | NIPS | 8026 | 2014-12-01 |  | 20301 | 2014-11-26 | LNup | 2017-12-31 | 17DEKALB | 05AUBURN | 1 | 138 |  | 54 | Rating Increase | IN |  |  | Planned | 0 | Actual |  | N | N | N
B in MTEP15 | B | West | OTP | 8085 | 2016-09-14 |  | 20432 | 2015-03-20 | LN | 2020-11-15 | GRE Kerkhoven 115kV | OTP Kerkhoven 115 kV | 1 | 115 | 12.5 | 102 | Add a new 115 kV - 1 mile - 266 ACSR transmission line from GRE Kerkhoven to OTP Kerkhoven Town. | MN |  | 1 | Proposed | 600000 | Planning Preliminary |  | N | N | N | Y
B in MTEP15 | B | West | OTP | 8085 | 2016-09-14 |  | 20433 | 2015-03-20 | SUB | 2020-11-15 | GRE Kerkhoven 115 kV | OTP Kerkhoven 115/12.5 |  | 115 | 12.5 | 10MVA | Building new substation due to town conversion from existing 41.6 kV line to 115 to 12.5kV. Transformer 10MVA | MN |  | 4 | Proposed | 1100000 | Planning Preliminary |  | N | N | N | Y
B in MTEP15 | B | Central | PPI | 7888 | 2017-09-22 | 2015-19,20,41 | 20120 | 2015-07-09 | LN | 2016-12-31 | Geneseo Plant | JCE Geneseo |  | 69 | 69 | 50 | Construct 0.2 mile 69 kV transmission line to connect Geneseo plant substation to the Geneseo Jo-Carroll Energy substation to provide a network connection. | IL |  | 0.2 | Planned | 289300 |  |  | N | N | N
B in MTEP15 | B | Central | PPI | 7888 | 2017-09-22 | 2015-19,20,41 | 20797 | 2015-11-05 | LN |  | MEC Sub 39 | JCE Ladwig | 1 | 69 |  | 50 | New 11 mile 69 kV line to provide network feed for Jo-Carroll Energy and the City of Geneseo | IL |  |  | Proposed |  |  |  | N | N | N
B in MTEP15 | B | Central | PPI | 7888 | 2017-09-22 | 2015-19,20,41 | 20122 | 2015-07-09 | LNcnv | 2016-12-31 | Ladwig | JCE Geneseo | 1 | 69 | 69 | 35 | Convert existing 34.5 kV line to 69 kV. Existing line is built to 69 kV specifications. | IL | 7.62 |  | Planned | 0 |  |  | N | N | N
B in MTEP15 | B | South | SMEPA | 8141 | 2015-04-03 |  | 20510 | 2014-09-15 | LNrb | 2026-06-01 | Hoy | Sharon GOAB | 1 | 69 |  | 126 | Rebuild L16 (Hoy - Sharon GOAB 69kV) using 795 ACSR with 161kV insulation and double circuit provisions. | MS | 3.98 |  | Conceptual | 1273600 | Planning |  | N | N | N
B in MTEP15 | B | South | SMEPA | 8143 | 2015-04-03 |  | 20515 | 2014-09-15 | LNrb | 2026-06-01 | Foxworth | Pickwick GOAB | 1 | 69 |  | 126 | Rebuild L45A (Foxworth - Pickwick GOAB) using 795 ACSR conductor. | MS | 7.07 |  | Conceptual | 2050300 | Planning |  | N | N | N
B in MTEP15 | B | Central | Vectren | 4397 | 2014-10-06 | 2013SIGE11 | 8414 | 2014-10-01 | LNrb | 2020-12-31 | Leonard Rd. 69 | St. Phillips 69 | 31 | 69 |  | 103 MVA | Rebuild and reconductor approx. 6.8 miles | IN | 6.78 | 0 | Planned | 5100000 | Planning |  | N | N | N | Y
B in MTEP15 | B | Central | Vectren | 4399 | 2016-05-19 | 2013SIGE13 | 8416 | 2016-05-19 | SUB | 2023-12-31 | Newtonville 161 | Bus reconfig. |  | 161 |  | 335 MVA | Convert existing 161 kV bus to a ring bus configuration | IN | 0 | 0 | Planned | 1000000 | Planning |  | N | N | N | Y
B in MTEP15 | B | East | WPSC | 8360 | 2015-03-30 | Alba New Station | 20649 | 2016-09-15 | SUB | 2022-12-31 | Alba |  |  | 138 | 69 |  | The Alba transmission tie station represents the oldest tie on the Wolverine system. It is located on a small parcel of leased property with limited expansion capability. The existing station shall be replaced with a new in/out transmission line design, three (3) breaker substation, modern control house, metering, protection relaying and a 50 or 90MVA, 138/69kV tie transformer, dependent upon load requirements. | MI |  |  | Proposed | 4000000 | Budgetary |  | N | N | N
B in MTEP15 | B | East | WPSC | 8361 | 2015-03-30 | Alba Line Mods | 20650 | 2016-09-15 | LN | 2022-12-31 | Alba |  |  | 138 | 69 |  | This project will address 138kV transmission line and structure reconfiguration costs associated with construction of the new Alba transmission substation, so that the 138kV ITC/METC looped transmission line segments can successfully enter and leave the substation | MI |  |  | Proposed | 1000000 | Budgetary |  | N | N | N
B in MTEP14 | B | Central | AmerenMO | 4498 | 2014-12-17 | AMRN45 | 8611 | 2013-09-13 | LN | 2020-06-01 | Berntie | Jim Hill | 1 | 161 |  | 399 | Construct approximately 20 miles of 161 kV line between Jim Hill Plant and Berntie Substation in southeast, Missouri. The new line should have a 2000 A summer emergency rating. | MO |  | 20 | Proposed | 24000000 | Planning |  | N | N | N | Y
B in MTEP14 | B | Central | AmerenMO | 4498 | 2014-12-17 | AMRN45 | 8613 | 2013-09-13 | CB | 2020-06-01 | Jim Hill | Install 161 kV Breaker |  | 161 |  |  | Install 161 kV Breaker at Jim Hill | MO |  |  | Proposed | 500000 | Planning |  | N | N | N | Y
B in MTEP14 | B | Central | AmerenMO | 4498 | 2014-12-17 | AMRN45 | 8612 | 2013-09-13 | CB | 2020-06-01 | Berntie | Install 161 kV Ring Bus |  | 161 |  |  | Construct 161 kV ring bus at Berntie Substation | MO |  |  | Proposed | 6000000 | Planning |  | N | N | N | Y
B in MTEP14 | B | West | ATC, MP | 3832 | 2015-05-07 | Iron Range - Arrowhead 345 kV | 7203 | 2013-07-24 | LN | 2025-12-31 | Blackberry | Transformer | 1 | 500 | 345 | 1200 | Blackberry 1200 MVA 500/345 kV transformer | MN |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP14 | B | West | ATC, MP | 3832 | 2015-05-07 | Iron Range - Arrowhead 345 kV | 7206 | 2013-07-24 | LN | 2025-12-31 | Blackberry | Arrowhead | 2 | 345 |  | 1219 | Blackberry - Arrowhead 345 kV line (Ckt 2) | MN |  | 60 | Proposed |  |  |  | N | N | N | Y
B in MTEP14 | B | West | ATC, MP | 3832 | 2015-05-07 | Iron Range - Arrowhead 345 kV | 7205 | 2013-07-24 | LN | 2025-12-31 | Blackberry | Arrowhead | 1 | 345 |  | 1219 | Blackberry - Arrowhead 345 kV line (Ckt 1) | MN |  | 60 | Proposed | 220481656.22 | Planning |  | N | N | N | Y
B in MTEP14 | B | West | ATC, MP | 3832 | 2015-05-07 | Iron Range - Arrowhead 345 kV | 7204 | 2013-07-24 | LN | 2025-12-31 | Blackberry | Transformer | 2 | 500 | 345 | 1200 | Blackberry 1200 MVA 500/345 kV transformer | MN |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP14 | B | West | GRE | 4376 | 2016-06-30 | 202496 | 8381 | 2016-06-30 | LNrc | 2020-04-29 | Parkwood | Crooked Lake | 1 | 115 |  | 300+ | Reconductor line | MN | 3.36 |  | Proposed | 500000 | Planning |  | N | N | N | Y
B in MTEP14 | B | West | MDU | 3082 | 2017-01-16 | NW Bism | 5362 | 2017-01-16 | CB | 2020-06-01 | NW Bismarck | 3 PCB |  | 115 |  |  | Create a ring bus | ND |  |  | Planned | 3050000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | East | METC | 1795 | 2016-12-20 | METC_13_037 | 3604 | 2016-12-20 | LNrb | 2023-12-31 | David Jct. | Bingham | 1 | 138 |  | 303 MVA | Rebuild approximately 19miles of 336.4 ACSR from the Bingham - David Jct. 138 kV section to 954 ACSR on new 138 kV future double circuit structures. | MI | 19 |  | Proposed | 19000000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | East | METC | 3922 | 2016-11-10 | METC_13_039 | 7484 | 2016-11-10 | LNrb | 2023-12-31 | Alpine Jct. | Cannon Jct. | 1 | 138 |  | 257 MVA | Rebuild 8.4 miles of 336 ACSR utilizing 954 ACSR on new 138 kV structures. | MI | 8.4 |  | M1_Final SPM or OOC | 8200000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | East | METC | 4510 | 2014-12-17 | METC_13_044 | 8639 | 2014-06-13 | LNrb | 2017-12-31 | Morrow | Battle Creek | 1 | 138 |  | 388 MVA | Rebuild 22 miles of Morrow - Battle Creek138kV to 954 ACSR on future double circuit 138kV towers. | MI | 22 | 0 | Proposed | 24200000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | East | METC | 4510 | 2014-12-17 | METC_13_044 | 8640 | 2014-06-13 | TEQ | 2017-12-31 | Morrow |  |  | 138 |  |  | Upgrade terminal equipment at Morrow. | MI |  |  | Proposed | 440000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | East | METC | 4511 | 2016-07-05 | METC_13_046 | 8641 | 2016-07-05 | LNrb | 2019-12-31 | Verona | Foundry | 1 | 138 |  | 287 MVA | Rebuild 21 miles of the Verona - Foundry 38kV circit to 1431 ACSR. | MI | 21 | 0 | Proposed | 16000000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | East | METC | 4511 | 2016-07-05 | METC_13_046 | 8642 | 2016-07-05 | TEQ | 2019-12-31 | Verona |  |  | 138 |  |  | Upgrade terminal equipment at Verona. | MI |  |  | Proposed | 21000 | Engineering |  | N | N | N | Y
B in MTEP14 | B | West | MP | 2548 | 2014-12-17 | Duluth 230 kV Project | 4564 | 2014-09-12 | TX | 2026-12-31 | Hilltop |  | 2 | 230 | 115 | 187 | Hilltop Transformer #2 | MN | 0 | 0 | Proposed | 3000000 | Planning Preliminary | Network | N | Y | N | Y
B in MTEP14 | B | West | MP | 2548 | 2014-12-17 | Duluth 230 kV Project | 4565 | 2014-09-12 | LNcnv | 2026-12-31 | Arrowhead | Hilltop | 1 | 230 |  | 470 | Upgrade 115 kV line to 230 kV | MN | 9 |  | Proposed | 3000000 | Planning Preliminary | Network | N | Y | N | Y
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 7379 | 2015-06-10 | LNup | 2020-12-31 | Square Butte | Arrowhead | 1 | 250 |  | 750 | Structure upgrades on existing +/- 250 V HVDC line to achieve 750 MW capacity | ND,MN | 465 |  | Proposed | 10000000 | Planning |  | N | N | N | Y
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 20820 | 2015-06-10 | HVDC | 2020-12-31 | Square Butte |  |  | 250 |  | 750 | Replace valve hall at Square Butte HVDC terminal +/-250kV HVDC | ND |  |  | Proposed | 37500000 | Planning |  | N | N | N
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 20819 | 2015-06-10 | HVDC | 2020-12-31 | Arrowhead |  |  | 250 |  | 750 | Replace valve hall at Arrowhead HVDC terminal +/-250kV HVDC | MN |  |  | Proposed | 37500000 | Planning |  | N | N | N
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 7383 | 2015-06-10 | TEQ | 2020-12-31 | Arrowhead | HVDC Terminal Equipment | 1 | 250 |  |  | Arrowhead HVDC terminal equipment upgrades; +/- 250 V | MN |  |  | Proposed | 15000000 | Planning |  | N | Y | N | Y
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 7382 | 2015-06-10 | TX | 2020-12-31 | Arrowhead | Converter Transformers | 1 | 250 | 230 | 750 | Twelve 75 MVA converter transformers at Arrowhead; +/- 250 V | MN |  |  | Proposed | 42500000 | Planning |  | N | N | N | Y
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 7381 | 2015-06-10 | TEQ | 2020-12-31 | Square Butte | HVDC Terminal Equipment | 1 | 250 |  |  | Square Butte HVDC terminal equipment upgrades; +/- 250 V | ND |  |  | Proposed | 15000000 | Planning |  | N | N | N | Y
B in MTEP14 | B | West | MP | 3856 | 2015-06-10 | HVDC 750 MW | 7380 | 2015-06-10 | TX | 2020-12-31 | Square Butte | Converter Transformers | 1 | 250 | 230 | 750 | Twelve 75 MVA converter transformers at Square Butte; +/- 250 V | ND |  |  | Proposed | 42500000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4439 | 2015-04-03 | LRTPS11-RP2102 | 8475 | 2014-09-22 | LN | 2021-06-01 | Tap Point | Morrow | 1 | 161 |  | 296 | New 161kV Line (Tap existing Purvis - Lumberton 161kV Line) w/OPGW | MS |  | 3 | Conceptual | 1050000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4439 | 2015-04-03 | LRTPS11-RP2102 | 8479 | 2014-09-22 | TEQ | 2021-06-01 | Morrow |  |  | 161 |  |  | Add 161kV Breaker @ Morrow | MS |  |  | Conceptual | 165000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4439 | 2015-04-03 | LRTPS11-RP2102 | 8478 | 2014-09-22 | LNup | 2021-06-01 | Purvis | Lumberton | 1 | 161 |  |  | Uprate Purvis to Lumberton 161kV line to 296MVA w/OPGW | MS | 1 |  | Conceptual | 123200 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4439 | 2015-04-03 | LRTPS11-RP2102 | 8477 | 2014-09-22 | TAP | 2021-06-01 | Tap Point |  |  | 161 |  |  | New 161kV Switching Station @ Tap Point w/ 3 breakers | MS |  |  | Conceptual | 1950000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4439 | 2015-04-03 | LRTPS11-RP2102 | 8476 | 2015-07-13 | LN | 2021-06-01 | Tap Point | Morrow |  | 161 |  |  | New 161kV Transmission Line Right of Way | MS |  | 3 | Conceptual | 210000 | Planning | Generator | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8480 | 2014-09-22 | TEQ | 2021-06-01 | Lumberton |  |  | 161 |  |  | Add 161kV breaker at Lumberton 161kV substation | MS |  |  | Conceptual | 180000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8490 | 2014-09-22 | SwSta | 2021-06-01 | Big Level |  |  | 161 |  |  | Big Level 161kV switching station w/3 breakers | MS |  |  | Conceptual | 1950000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8489 | 2014-09-22 | SwSta | 2021-06-01 | Stillmore |  |  | 161 |  |  | Stillmore 161kV switching station w/3 breakers | MS |  |  | Conceptual | 1950000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8488 | 2014-09-22 | Dist | 2021-06-01 | Big Level |  |  | 161 |  |  | Convert Big Level distribution substation to 161kV | MS |  |  | Conceptual | 1600000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8487 | 2014-09-22 | Dist | 2021-06-01 | Stillmore |  |  | 161 |  |  | Convert Stillmore distribution substation to 161kV | MS |  |  | Conceptual | 1600000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8486 | 2014-09-22 | LNrb | 2021-06-01 | Stillmore | Wiggins GOAB | 1 | 161 |  | 296 | Rebuild Line 37C (Stillmore - Wiggins GOAB) at 161kV w/OPGW | MS | 7.22 |  | Conceptual | 2093800 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8485 | 2014-09-22 | LNrb | 2021-06-01 | Benndale GT | Benndale | 1 | 161 |  | 296 | Rebuild Line 35A (Benndale GT - Benndale) at 161kV w/OPGW | MS | 1.3 |  | Conceptual | 377000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8484 | 2014-09-22 | LNrb | 2021-06-01 | Wiggins GOAB | Big Level | 1 | 161 |  | 296 | Rebuild Lines 37A & 37B (Wiggins GOAB - Big Level) at 161kV w/OPGW | MS | 8.5 |  | Conceptual | 2465000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8483 | 2014-09-22 | LN | 2021-06-01 | Wiggins GOAB | Stillmore |  | 161 |  |  | New 161kV Transmission Line Right of Way | MS |  | 8 | Conceptual | 560000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8482 | 2014-09-22 | LN | 2021-06-01 | Wiggins | Stillmore | 1 | 161 |  | 296 | New 161kV line to Stillmore w/OPGW | MS |  | 8 | Conceptual | 2800000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4440 | 2015-04-03 | LRTPS11-RP2106 | 8481 | 2014-09-22 | TEQ | 2021-06-01 | Benndale |  |  | 161 |  |  | Add 161kV breaker at Benndale 161kV substation | MS |  |  | Conceptual | 180000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8491 | 2014-09-22 | TAP | 2026-06-01 | Tap Point |  |  | 161 |  |  | New 161kV Switchyard (Tap L171) w/ breakers | MS |  |  | Conceptual | 1950000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8498 | 2014-09-22 | TEQ | 2026-06-01 | State Line |  |  | 69 |  |  | Additional 69kV breaker | MS |  |  | Conceptual | 120000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8497 | 2014-09-22 | TEQ | 2026-06-01 | State Line |  |  | 69 |  |  | Additional 69kV bay w/ breaker | MS |  |  | Conceptual | 440000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8496 | 2014-09-22 | TX | 2026-06-01 | State Line |  |  | 161 | 69 | 50 | New 161/69kV, 100 MVA transformer | MS |  |  | Conceptual | 1810000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8495 | 2014-09-22 | TEQ | 2026-06-01 | State Line |  |  | 161 |  |  | New 161kV bay w/ breaker | MS |  |  | Conceptual | 1635000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8494 | 2014-09-22 | SwSta | 2026-06-01 | State Line |  |  | 161 |  |  | New 161kV Switchyard at State Line | MS |  |  | Conceptual | 315000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8493 | 2014-09-22 | LN | 2026-06-01 | Tap Point | State Line |  | 161 |  | 296 | New 161kV Transmission Line Right of Way | MS |  | 19 | Conceptual | 1330000 | Planning |  | N | N | N | Y
B in MTEP14 | B | South | SMEPA | 4441 | 2015-04-03 | LRTPS11-RP2607 | 8492 | 2014-09-22 | LN | 2026-06-01 | Tap Point | State Line | 1 | 161 |  | 296 | New 161kV Transmission Line w/ OPGW adder | MS |  | 19 | Conceptual | 6650000 | Planning |  | N | N | N | Y
B in MTEP13 | B | Central | AmerenIL | 4071 | 2014-11-17 | AMRN31 | 7718 | 2014-11-17 | LN | 2025-06-01 | Cottage Hills | Wanda | 1 | 138 |  | 160 | Increase clearances to ground on 5.63 miles of 477 kcmil ACSR between Cottage Hills and Wanda to permit operation at 120 degrees C. in the Wood River-Stallings 138 kV Line. | IL | 5.63 |  | Proposed | 4504000 | Planning |  | N | N | N | Y
B in MTEP13 | B | Central | AmerenIL | 4071 | 2014-11-17 | AMRN31 | 7720 | 2014-11-17 | SUB | 2025-06-01 | Cottage Hills | Upgrade terminal equipment on Cottage Hills-Wanda |  | 138 |  | 160 | Replace or reconnect 600 A CTs and replace an 800 A PCB at Cottage Hills with equipment capable of carrying 1200 A continuously. | IL |  |  | Proposed | 500000 | Planning |  | N | N | N | Y
B in MTEP13 | B | Central | AmerenIL | 4071 | 2014-11-17 | AMRN31 | 7719 | 2014-11-17 | LN | 2025-06-01 | Stallings | Wanda |  | 138 |  | 314 | Reconductor 6.01 miles of 477 kcmil ACSR in the Stallings-Wanda section with conductor capable of carrying 1600 A under summer emergency conditions. | IL | 6.01 |  | Proposed | 6000000 | Planning |  | N | N | N | Y
B in MTEP13 | B | West | GRE | 4012 | 2016-06-30 | 20326 | 7645 | 2016-06-30 | Dist | 2020-12-31 | Hardy Lake |  |  | 115 |  |  | GRE will build new Crow Wing Power 115 KV Hardy Lake Substation | MN |  | 0.1 | Proposed | 207500 | Planning |  | N | N | N | Y
B in MTEP13 | B | West | GRE | 4013 | 2012-09-11 | 20334 | 7646 | 2016-06-30 | Dist | 2026-05-02 | Air Lake |  |  | 115 |  |  | GRE will build new Dakota Electric 115 kv South Air Lake substation. | MN |  | 0 | Proposed | 864000 | Planning |  | N | N | N | Y
B in MTEP13 | B | West | GRE | 4016 | 2016-06-30 | 20507 | 7649 | 2016-06-30 | Dist | 2022-05-31 | Cashel |  |  | 115 |  |  | GRE will convert Agralite Cashel 41.6 kV distribution sub to 115 kV | MN | 1 |  | Proposed | 625000 | Planning |  | N | N | N | Y
B in MTEP13 | B | West | MEC | 4252 | 2012-09-15 | G4083 | 8001 | 2012-09-15 | SUB | 2015-06-30 | Neal North | Breaker |  | 161 |  |  | Neal North:161 kV Breaker Replacements | IA |  |  | Planned | 325000 | Planning |  | N | N | N | Y
B in MTEP13 | B | East | METC | 4346 | 2015-11-13 |  | 8321 | 2016-07-14 | LNrb | 2018-12-31 | Karn | Garfield | 1 | 138 |  | 330 | Rebuild the 33.5 mile copper portion of the Karn to Garfield circuit using single circuit 138kV structures and 954 ACSR conductor. Mitigate several additional points of interest on the remaining portions (795 and 1431 ACSR). Replace station equipment at | MI | 33.5 |  | Proposed | 39500000 | Engineering |  | N | N | N | Y
B in MTEP13 | B | West | MP | 3756 | 2015-05-07 | Wrenshall | 7021 | 2015-06-10 | SUB | 2020-12-31 | Wrenshall | Substation Equipment |  | 115 | 69 | 28 | Add breakers and a 115/69 kV transformer | MN |  |  | Proposed | 3000000 | Planning |  | N | N | N | Y
B in MTEP13 | B | West | MP | 4295 | 2015-06-10 | HVDC Valve Hall Replacement | 8219 | 2015-06-10 | HVDC | 2020-12-31 | Arrowhead | Valve hall upgrade |  | 250 |  | 550 | Replace valve hall at Arrowhead terminal, +/- 250 kV | MN |  |  | Proposed | 37500000 | Planning |  | N | N | N | Y
B in MTEP13 | B | West | MP | 4295 | 2015-06-10 | HVDC Valve Hall Replacement | 8220 | 2015-06-10 | HVDC | 2020-12-31 | Square Butte | Valve hall upgrade |  | 250 |  | 550 | Replace valve hall at Square Butte terminal, +/- 250 kV | ND |  |  | Proposed | 37500000 | Planning |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenIL | 2290 | 2015-09-11 |  | 4206 | 2015-09-11 | LN | 2023-06-01 | Joppa | 2nd. 345/161 kV Transformer |  | 345 | 161 | 560 | Install 2nd. 345/161 kV, 560 MVA Transformer | IL |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenIL | 3336 | 2012-03-06 |  | 6201 | 2013-09-13 | LN | 2020-06-01 | Gilman | Watseka | 1 | 138 |  | 322 | Reconductor to 1600 A summer emergency capability | IL | 15.21 |  | Proposed | 4763000 | Planning |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenIL | 3342 | 2017-09-15 |  | 6207 | 2017-09-15 | LN | 2020-06-01 | Diamond Star | McClean County Sw. Station | 1 | 138 |  | 160 | Diamond Star Tap-McClean County section of McClean-Washington Street 138 kV Line 1544 - Verify hardware capable of operations at 120 degrees C on 5.04 miles of 477 kcmil ACSR conductor. | IL | 5.04 |  | Proposed | 240000 | Planning |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenIL | 3703 | 2016-08-15 |  | 6953 | 2016-08-15 | SUB | 2022-12-01 | New Berlin Sub. |  |  | 138 | 69 | 112 | Install new 112 MVA, 138-69 kV Substation. Connect to Auburn, North-Jacksonville Industrial 138 kV Line 1306. | IL |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenMO | 3701 | 2012-03-06 | AMRN25 | 6946 | 2013-09-13 | LN | 2023-06-01 | Joachim | Cotter Creek | 1 | 138 |  | 240 | Extend 138 kV line from Joachim to Cotter Creek 138-34.5 kV substation as initial 138 kV supply to Cotter Creek sub. | MO |  |  | Proposed | 11880110 | Engineering |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenMO | 3701 | 2012-03-06 | AMRN25 | 6948 | 2013-09-13 | LN | 2023-06-01 | Olympian Village | Cotter Creek | 1 | 138 |  | 240 | Extend 138 kV line from Olympian Village to Cotter Creek 138-34.5 kV Substation | MO |  |  | Proposed | 13385390 | Engineering |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenMO | 3701 | 2012-03-06 | AMRN25 | 6947 | 2013-09-13 | SUB | 2023-06-01 | Olympian Village Sub |  |  | 138 |  | 478 | Olympian Village Switching Station - Establish 138 kV Breaker Station in Joachim-St. Francois-2 138 kV line (3-2000 A PCBs) as source of second 138 kV supply to Cotter Creek Substation. | MO |  |  | Proposed | 5965140 | Engineering |  | N | N | N | Y
B in MTEP12 | B | Central | AmerenMO | 3708 | 2017-12-19 |  | 6960 | 2016-10-17 | TX | 2030-06-01 | Fountain Lake Sub. | Install 2nd. 138-12.5 kV Xfmr |  | 138 | 12.5 | 45 | Fountain Lake Substation - Install 2nd. 138-12.5 kV Transformer. | MO |  |  | Proposed |  |  |  | N | N | N | Y
B in MTEP12 | B | East | ITC, ITCT | 1295 | 2014-01-31 |  | 2124 | 2014-01-31 | LN | 2018-06-01 | Quaker 120 | To Drexel to Southfield 120 |  | 120 |  |  | Rebuild the existing Quaker to Drexel to Southfield circuit utilizing 1431 ACSR conductor on double circuit 230 kV towers and add a second Quaker to Southfield circuit on this new tower line | MI | 7.35 |  | Proposed | 25500000 |  |  | N | N | N | Y
B in MTEP12 | B | East | ITC, ITCT | 1295 | 2014-01-31 |  | 5485 | 2014-01-31 | LN | 2018-06-01 | Quaker 120 | Southfield 120 |  | 120 |  |  | Rebuild the existing Quaker to Drexel to Southfield circuit utilizing 1431 ACSR conductor on double circuit 230 kV towers and add a second Quaker to Southfield circuit on this new tower line | MI |  | 7.35 | Proposed | 25550000 |  |  | N | N | N | Y
B in MTEP12 | B | East | ITC, ITCT | 3589 | 2014-01-31 |  | 6683 | 2014-01-31 | LNrb | 2018-06-01 | Lee | Lake Huron Pumping Jct. | 1 | 120 |  |  | Rebuild approximately 5.4 miles of 267 ACSR conductor to 954 ACSR | MI | 5.4 |  | Proposed | 5000000 |  |  | N | N | N | Y
B in MTEP12 | B | East | ITC, ITCT | 3589 | 2014-01-31 |  | 6684 | 2014-06-13 | LNrb | 2018-06-01 | Lake Huron Pumping Jct. | Menlo | 1 | 120 |  |  | Rebuild approximately 6.4 miles of 267 ACSR conductor to 954 ACSR | MI | 6.4 |  | Proposed | 6200000 |  |  | N | N | N | Y
B in MTEP12 | B | East | METC | 3137 | 2014-01-31 |  | 5515 | 2014-01-31 | LN | 2017-12-31 | Bard Road | Warren | 1 | 138 |  |  | Rebuild approximately 19.6 miles of the Warren to Bard Road 138 kV circuit to 230 kV double circuit construction using 954 ACSR. One side would be energized at 138kV, with the other side left vacant for future use. | MI | 19.6 |  | Planned | 27800000 |  |  | N | N | N | Y
B in MTEP12 | B | East | METC | 3582 | 2014-01-31 |  | 6675 | 2014-01-31 | LNrb | 2017-06-01 | Bullock | Summerton | 1 | 138 |  |  | Rebuild the entire circuit between Bullock and Summerton to 954 ACSR on single-circuit, 138 kV steel pole structures | MI | 25.5 |  | Proposed | 20000000 | Planning |  | N | N | N | Y
B in MTEP12 | B | East | METC | 3594 | 2014-11-04 |  | 6693 | 2014-11-04 | TEQ | 2018-12-31 | Tittabawassee |  |  | 345 |  |  | Replace 345kV station equipment in rows 34 and 36 at Tittabawassee. | MI |  |  | Proposed | 3500000 |  |  | N | N | N | Y
B in MTEP11 | B | Central | AmerenMO | 2973 | 2014-11-17 |  | 5174 | 2014-11-17 | SUB | 2022-12-01 | Mason-Carrollton-8 | Connection to Howard Bend 138-12 kV Sub | 1 | 138 |  | 478 | Howard Bend 138-12 kV Substation - Provide 138 kV ring bus connection from Mason-Carrollton-8 138 kV line to new Howard Bend Substation. Install 1-138 kV, 2000 A PCB at Carrollton Substation as a bus-tie. | MO |  |  | Proposed | 1371000 | Planning |  | N | N | N | Y
B in MTEP11 | B | West | MEC | 3215 | 2016-09-14 | T6242 | 6089 | 2016-09-14 | CAP | 2030-06-01 | Sub 49 | Capacitor |  | 161 |  | 50 | Sub 49 161 kV 50 MVAr Capacitor | IL |  |  | Proposed | 840000 | Planning |  | N | N | N | Y
B in MTEP11 | B | West | MEC | 3266 | 2013-09-15 | T6164 | 6085 | 2013-09-15 | LNrb | 2024-06-01 | Sub 56 | Sub 89 | 1 | 161 |  | 314 | Sub 56-89 161 kV line uprate | IA | 22 |  | Proposed | 680000 | Planning |  | N | N | N | Y
B in MTEP11 | B | East | METC | 1815 | 2014-01-31 |  | 3649 | 2014-01-31 | LNrb | 2020-06-01 | Chase | Mecosta | 1 | 138 |  | 108 | Rebuild 7.2 miles (230 kV construction, operate at 138 kV) | MI | 7.2 |  | Planned | 8900000 | Planning |  | N | N | N | Y
B in MTEP10 | B | East | ITC, ITCT | 1856 | 2014-01-31 |  | 3743 | 2016-03-17 | LN | 2030-12-31 | Jewell | Pontiac | 1 | 345 |  |  | Cut Pontiac-Greenwood-Belle River into Jewell creating Pontiac-Jewell and Jewell-Belle River-Greenwwod | MI |  |  | Proposed | 2600000 |  |  | N | N | N | Y
B in MTEP10 | B | East | ITC, ITCT | 1856 | 2014-01-31 |  | 3744 | 2016-03-17 | LN | 2030-12-31 | Jewell | Belle River - Greenwood Jct | 1 | 345 |  |  | Cut Pontiac-Greenwood-Belle River into Jewell creating Pontiac-Jewell and Jewell-Belle River-Greenwwod | MI |  |  | Proposed | 2600000 |  |  | N | N | N | Y
B in MTEP10 | B | East | ITC, ITCT | 2932 | 2015-03-25 |  | 5104 | 2015-03-25 | LN | 2020-06-01 | St Antoine | Essex | 1 | 120 |  |  | Construct 2nd underground cable from St Antoine to Essex (5.1 miles). | MI |  | 5.1 | Proposed | 54800000 |  |  | N | N | N | Y
B in MTEP10 | B | West | ITCM | 1746 | 2011-12-13 |  | 3549 | 2012-03-26 | LNrb | 2014-12-31 | Fox Lake | Rutland | 1 | 161 |  | 446/446 MVA | Rebuild existing line | MN | 17 |  | Proposed | 11900000 | Planning |  | N | N | N | Y
B in MTEP10 | B | West | ITCM | 1746 | 2011-12-13 |  | 3553 | 2012-03-26 | LNrb | 2018-12-31 | Hayward | Adams | 1 | 161 |  | 446/446 MVA | Rebuild existing line | MN | 36.39 |  | Proposed | 25480000 | Planning |  | N | N | N | Y
B in MTEP10 | B | West | ITCM | 1746 | 2011-12-13 |  | 3552 | 2012-03-26 | LNrb | 2016-12-31 | Winnebago | Hayward | 1 | 161 |  | 446/446 MVA | Rebuild existing line | MN | 49.09 |  | Proposed | 34370000 | Planning |  | N | N | N | Y
B in MTEP10 | B | West | ITCM | 1746 | 2011-12-13 |  | 3551 | 2012-03-26 | LNrb | 2017-12-31 | Lakefield Jct | Fox | 1 | 161 |  | 446/446 MVA | Rebuild existing line | MN | 22.3 |  | Proposed | 15610000 | Planning |  | N | N | N | Y
B in MTEP10 | B | West | ITCM | 1746 | 2011-12-13 |  | 3550 | 2012-03-26 | LNrb | 2015-12-31 | Rutland | Winnebago | 1 | 161 |  | 446/446 MVA | Rebuild existing line | MN | 14.6 |  | Proposed | 10220000 | Planning |  | N | N | N | Y
B in MTEP10 | B | East | METC | 3210 | 2014-01-31 |  | 5953 | 2014-01-31 | LN | 2016-06-01 | Vanderbilt | Riggsville |  | 138 |  |  | Rebuild 30.3 miles of 138 kV 266 ACSR to 954 ACSR FDC 230 kV construction. | MI | 30.3 |  | Proposed | 33254000 |  |  | N | N | N | Y
Note on T3: Upgraded or on existing rights of way