## MTEP24 Appendix A
MTEP24 Appendix A - New Local Reliability Projects
Planning Region | MTEP Project ID | Project Name | Project Description | State(s) | Submitting TO | Project Type | Other Type | Expected ISD | Max kV | Current Cost
West | 25141 | Arrowhead 115kV SPF Upgrade | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Arrowhead 115kV buses. | MN | MINNESOTA POWER INC. | BRP |  | 2024-12-31 | 115 | 250000
West | 25142 | Forbes 115kV SPF Upgrade | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Forbes 115kV buses. | MN | MINNESOTA POWER INC. | BRP |  | 2024-12-31 | 115 | 250000
West | 25200 | J1190 GIA NU Calamus East 161 kV Bus Expansion | A 161 kV straight bus expansion at the Calamus East station will be constructed for the interconnection of project J1190. | IA | ITC MIDWEST | GIP |  | 2026-10-01 | 161 | 155146
West | 50113 | J1716 Eldorado SS Network Upgrades | J1716 is a solar facility located in Fond du Lac County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-03-19 | 345 | 225000
West | 25201 | J1325 GIA TOIF Magnolia 161 kV Terminal Addition | TOIF includes facilities and equipment dedicated to the Generating Facility including; dead-end, switch, relay panel, CCVTs, etc. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | MN | ITC MIDWEST | GIP |  | 2025-06-30 | 161 | 417240
West | 25182 | J1313 GIA TOIF Karma 161 kV Terminal Addition | The Karma 161 kV substation will be expanded to accommodate the J1313 terminal, including the addition of a new breaker position and switches. New equipment should be capable of 2000A. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | ITC MIDWEST | GIP |  | 2025-06-30 | 161 | 427809
Central | 50089 | Aetna Synchronous Condenser | Synchronous Condenser placed at Aetna 138kV substation. +360/-180 MVAR capabilities. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2024-05-01 | 138 | 91000000
West | 25184 | J1365 GIA TOIF Traer 161 kV Terminal Addition | TOIF includes surge arrestors, switch, current transformers, and relay dedicated to J1365 radial line and generating facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | ITC MIDWEST | GIP |  | 2024-09-06 | 161 | 462831
South | 25544 | JCWL - Commerce to Ringier 69kV Rebuild | Rebuild the Commerce - Ringier 69kV line | AR | CITY WATER AND LIGHT PLANT OF JONESBORO ARKANSAS | Other | Age and Condition | 2024-07-01 | 69 | 873580
South | 25312 | J1832 Plaisance Expansion | Expand Plaisance Substation to interconnect J1832 Solar | LA | CLECO POWER LLC | GIP |  | 2024-07-15 | 138 | 6512000
West | 25202 | J1325 GIA NU Magnolia 161 kV Bus Expansion | Expand Magnolia 161 kV substation from a 4-terminal, 4 breaker, ring-bus substation to a 5 terminal ring bus substation. | MN | ITC MIDWEST | GIP |  | 2025-06-30 | 161 | 486788
Central | 25144 | Y52-3 Oakland City - Duke Oakland City Rebuild | Rebuild ~2.76 miles of 69kV line due to aging infrastructure and pole condition | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2024-08-01 | 69 | 3882590
Central | 25304 | HE_J1396_Ratts_3_Solar | Engineering labor is to be required to modify protection settings to comply with increased load flow | IN | HOOSIER ENERGY | GIP |  | 2024-08-20 | 161 | 10000
West | 25183 | J1313 GIA NU Karma 161 kV Ring Bus Expansion | The Facilities Study for J1313 identified Network Upgrades and TOIF necessary for the interconnection of project J1313 to ITCM’s Karma 161 kV station. Project J1313’s impact to the transmission system was evaluated as part of the DPP 2019 April West Area Study. | IA | ITC MIDWEST | GIP |  | 2025-06-30 | 161 | 556081
West | 25197 | J1734 GIA TOIF New Wever 161 kV Terminal | Perform TOIF upgrades for J1734 per the GIA. The J1734 TOIF upgrades will include dead-end, disconnect switch, arresters, PT’s, line relay panel, and associated equipment dedicated to the generating facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | ITC MIDWEST | GIP |  | 2024-06-01 | 161 | 562250
West | 25221 | J1432 GIA TOIF New Bryant 345 kV Terminal | TOIF includes facilities and equipment at the Bryant 345 kV switching station dedicated to the 345 kV radial line and Generating Facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | ITC MIDWEST | GIP |  | 2028-09-01 | 345 | 716244
Central | 25261 | HE_J1028_Ratts1_Solar | Transmission Owner Upgrades consist of filling and leveling the site for the proposed Apollo Substation and constructing on it the new 161kV switchyard in a ring bus arrangement with proposed dimensions of 250’ x 275’ for the fenced area. The station will have an initial build out of 3 positions along with accommodations for a fourth future position. The initial terminals shall connect to the IC’s facilities, Victory Substation, and Petersburg Substation. | IN | HOOSIER ENERGY | GIP |  | 2024-09-06 | 161 | 11424620
West | 25181 | J1190 GIA TOIF Calamus East 161 kV Terminal Addition | TOIF includes facilities including, 161 kV breaker, switches, dead-end, and equipment at Calamus East substation dedicated to the 161 kV radial line and Generating Facility. TOIF costs estimates are funded by the customer and ITC costs will be $0 as it will be a CIAC project for ITCM. | IA | ITC MIDWEST | GIP |  | 2026-10-01 | 161 | 803119
Central | 25148 | Posey Solar Gen Interconnection (J1308) | New interconnection substation for Posey Solar generation project J1308 | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | GIP |  | 2024-10-01 | 345 | 20000000
Central | 25145 | Lynnville 69kV OCB Replacement | Replace two 69kV oil breakers with gas breakers at Lynnville substation | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2024-11-01 | 69 | 872319
West | 22487 | OTP Audubon and Erie 230/115 kV Transformer Tap Adjustments | Adjust Audubon 230/115 kV transformer #1, Audubon 230/115 kV transformer #2, and Erie 230/115 kV transformer taps. | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-11-30 | 230 | 3000
West | 50009 | OTP Winger 41.6 kV Line Reroute | Reconductor and reroute small portion of 41.6 kV line between Winger 41.6 kV and Winger Town 41.6 kV. | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-12-31 | 42 | 115000
Central | 25146 | Fairlawn 69kV Switch Replacement | Replacement of several 69kV switches at Fairlawn substation due to aging infrastructure. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2024-12-01 | 69 | 1000000
West | 25357 | BYN-NRH Pilot Channel Replacement | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2023-12-15 | 345 | 200000
Central | 25353 | Replace Southwest 138 kV #1 Breaker | Replacement of 1 138 kV breaker at Southwest. Breaker #1. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2024-12-05 | 138 | 900000
West | 25356 | CNC-BUL-SHC Pilot Channel Replacement | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-01-15 | 345 | 300000
West | 25319 | Sheas Lake Pilot Channel Replacement | Replace secondary pilot communication circuit from SLL - WLM 345 kV. Install a modern Ethernet circuit and associated communication equipment for this protection system. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-04-01 | 345 | 300000
East | 24693 | Milan - J799 Amended Generation Interconnection - TOIF | Milan- J799 TOIF - Install line at position HD | MI | ITC | GIP |  | 2024-12-31 | 120 | 0
West | 25376 | Line 0876 Redwood Falls Tap Switch Replacement | Line 0876 Switch 278 replacement at SMMPA Redwood Falls tap. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-01 | 115 | 350000
West | 25317 | Wakefield Protection Upgrade | Upgrade system protection equipment at Wakefield 115 kV substation. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2024-09-30 | 115 | 450000
West | 50008 | OTP Oklee Rebuild 41.6 kV Tap | Rebuild and relocate 41.6 kV line near Oklee 41.6 kV. | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-12-31 | 42 | 450000
West | 25377 | DPC North Wal Interconnection | Build 3 way switching structure on line W3421 between Rice Lake - Barron 69 kV to accommodate DPC North Wal interconnection. | WI | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2024-12-01 | 69 | 500000
West | 25368 | W3418 Insulator Replacement And Refurb | W3418 line refurb on 2.8 miles from structures 716-762. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-31 | 69 | 500000
West | 25369 | W3410 Ellsworth Switch Replacement | Replace 3-way switch at Ellsworth substation tap with two 1-way switches. | WI | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2024-12-31 | 69 | 500000
South | 25413 | Retirement of Golden Meadow to Barataria 115 kV line | Retirement of Golden Meadow to Barataria 115 kV line. | LA | ENTERGY SERVICES, LLC. | Other | Local Needs | 2024-12-31 | 115 | 1
West | 25302 | Hills 69 kV Breaker Replacement | Replace the 69 kV breaker 514 at Hills Substation with a breaker that has interrupting rating of 40 kA. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-12-01 | 69 | 500000
East | 25365 | ITCT Line Relocation - 2024 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | ITC | Other | Local Needs | 2024-12-31 | 345 | 2500000
West | 25439 | Sub G 69 kV Line Taps | Install two 69 kV line taps terminating at Sub G 69 kV line breakers. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2030-12-31 | 69 | 600000
East | 25278 | METC Line Relocation - 2024 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | METC | Other | Local Reliability | 2024-12-31 | 345 | 2500000
South | 25214 | Virlilia 230 kV Substation | The Virlilia 230 kV breaker and a half substation will be fed out of the existing Catlett 230 kV substation. The existing Catlett substation will be reconfigured into a breaker and a half substation with two additional bays to connect to (2) 230 kV lines to the Virlilia 230 kV substation. A 108 MVAR capacitor bank will also be added to the new Virlilia 230 kV substation. Customer load will be fed out of (3) 150 MVA 230/34.5 kV transformers. | MS | ENTERGY MISSISSIPPI, LLC. | Other | Load Growth | 2025-01-01 | 230 | 79500003
West | 25295 | 2023 Line Clearance Mitigations | Replace structures at five different faclities to mitigate clearance limitations. Facilities include Raptor-Red Rock, Wilmarth-Swan Lake, St Augusta-Wakefield, North Rochester-Prairie Island, and Monticello-Oakwood. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2023-09-30 | 345 | 625000
West | 25380 | OTP Erie Junction Interconnection | Build two deadend structures to accommodate in-and-out Erie Junction interconnection (MTEP ID 15344). | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2023-11-01 | 230 | 650000
South | 24959 | Kolbs to Port Acres 230 kV upgrade project | Upgrade station equipment at Port Acres and conductor to achieve an upgrade on the Kolbs to Port Acres Bulk 230 kV line. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2025-02-01 | 230 | 17300000
West | 50147 | Frederic To Lewis - 69 KV - Clam Falls Drive Section | Upgrade Conductor and Structure from Crossarm 1/0 ACSR to Horizontal Post 477 ACSR. | WI | NORTHWESTERN WISCONSIN ELECTRIC CO. | Other | Local Reliability | 2027-05-01 | 69 | 660000
East | 25227 | Dowling Junction-Knowles Sag Remediation (J1658) - Network Upgrade | Remediate Knowles-Dowling Junction sag limit to achieve a rating of at least 240 MVA SN and 266 MVA WN. | MI | METC | GIP |  | 2025-03-03 | 138 | 1098750
Central | 25088 | Givens 69/12kV T1 Replacement | Replacement of transformer T1 at Givens substation due to age and condition | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-04-01 | 69 | 3500000
East | 24538 | J1635 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect at the new Lukesport substation. | MI | METC | GIP |  | 2025-04-01 | 138 | 0
West | 25257 | W3419 Str 162 Switch Replacement | Replace damaged 3-way switch with new 3-way switch on steel pole. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-31 | 69 | 700000
South | 50013 | Grand Prairie 115kV: New substation | Construct a new 115 kV substation with two 115/4.16 kV 33.3 MVA transformers to serve the planned motors at the pumping station. Cut into the Devalls Bluff – Brinkley East 115kV line and build ~.20 circuit mile (.40 total circuit mile) of “in and out” 115kV line. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2025-04-01 | 115 | 15626062
East | 24537 | J1635 Generator Interconnection Network Upgrades | Install new Lukesport 138 kV substation. Install three 138 kV breakers and associated disconnects rated at 40 kA and two new bus sections. Cut the Michigan Ave - Newton 138 kV circuit into the new Lukesport station. | MI | METC | GIP |  | 2025-04-03 | 138 | 9608322
Central | 25383 | Replace South 138 kV Breakers | Replace 3 138 kV breakers at South. Breakers #1, #2, and #3. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-04-28 | 138 | 2700000
Central | 25384 | Replace East 138 kV Breakers | Replace 5 138 kV breakers at East. Breakers #1, #2, #4, #5, and #7. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-04-29 | 138 | 4500000
South | 50034 | J1437 Nimbus Wind FCA | Facilities Construction Agreement for the upgrade of relays and protection schemes at Osage Creek, Berryville, Green Forest, Green Forest South, Harrison West and Harrison East station. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2025-04-30 | 161 | 1869029
East | 24444 | Barton Lake-Batavia - J1550 Generator Interconnection (Dorrance) TOIF | Install a line entrance structure and a switch for the generator to connect at position BM14. | MI | METC | GIP |  | 2025-05-01 | 138 | 0
South | 50035 | Doylestown 115kV: Cut in Switching Station (J1577 & J1607) | New three breaker ring bus switching station for J1577 (100 MW solar) and J1607 (25 MW battery) GIA projects on the Hardin West SS - Sheridan 115kV line section. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2025-05-01 | 115 | 3797000
West | 50075 | Raun-Remsen 345 kV Structure Replacement | The project will replace some line structures on MidAmerican's Raun to Remsen 345 kV line. This project will increase the line rating of the Raun to Remsen 345 kV line. | IA | MIDAMERICAN ENERGY CO. | Other | Local Needs | 2025-06-01 | 345 | 700000
South | 50011 | WeeksIsland Sub | Tap the existing Ivanhoe to Bayou Warehouse 138 kV line with a new 3 breaker ring substation 2 miles form Ivanhoe to serve a new industrial load. | LA | CLECO POWER LLC | Other | Local Reliability | 2025-05-16 | 138 | 21224064
Central | 25355 | Replace Northwest 138 kV Breakers | Replace 4 138 kV breakers at Northwest. Breakers #1, #4, #21, and #22. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-05-21 | 138 | 3600000
Central | 25354 | Replace Parker 138 kV Breakers | Replace 3 138 kV breakers at Parker. Breakers #1, #2, and #3. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-05-21 | 138 | 2700000
Central | 25402 | Replace Petersburg 138 kV #4 Breaker | Replace 1 138 kV breaker at Petersburg. Breaker #4. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-05-28 | 138 | 900000
East | 24515 | J1553 Generator Interconnection TOIF | Install required entrance structures and 138 kV disconnect switch at the METC Bingham Substation. | MI | METC | GIP |  | 2025-05-30 | 138 | 0
East | 24535 | J1553 Generator Interconnection Network Upgrades | Extend White Bus and move capacitor to make room for a third row at Bingham. Add Row 4, install 2-138 kV breakers and associated disconnects rated at 40 kA. Re-terminate the Cornell circuit at position WM4. Complete row 8, install 2-138 kV breakers and associated disconnects rated at 40 kA. | MI | METC | GIP |  | 2025-05-30 | 138 | 6200531
Central | 25080 | J1323 J1392 Network Upgrades | Relocate one existing 138kV line, create new position on LaGrange ring bus for generating lead line, replace control enclosure | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2025-06-01 | 138 | 5431638
Central | 25153 | New Moyer 138 kV Ring Bus for One Earth Energy Interconnection | This project will interconnect the One Earth Energy 30 MW ethanol plant. It will construct a new 138 kV substation called Moyer and a new AIC 138/12 kV substation called Gibson City One Earth. | IL | AMEREN ILLINOIS | Other | Load Growth | 2025-06-01 | 138 | 16700000
West | 25293 | 0725 Tracy Switching Station to 5535 Str 191 Rebuild | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-31 | 69 | 750000
West | 50101 | Hodges Substation Tap | Install a 3-way manual load break 115 kV, 2000 A switch on GRE’s Walden – Morris 115 kV line (near structure 89) and construct about 2 spans of 115 kV line with 477 ACSR conductor to the high side of Agralite’s new Hodges area distribution substation. Install metering/telecom and a new EEE for the distribution substation. | MN | GREAT RIVER ENERGY | Other | Load Growth | 2025-07-31 | 115 | 750116
Central | 25225 | Maurer Lake 161 Aging Infrastructure | Replace breaker H9 Bus Tie (G735) and associated switches (G734 and G736) Add disconnect switch and breaker to XFMR 1 and 2 | MO | AMEREN MISSOURI | Other | Local Reliability | 2025-06-01 | 161 | 4000000
South | 25465 | Paincourtville 115 kV Capacitor Bank Split | Split the current Paincourtville 115 kV 32.4 MVAR capacitor bank into two smaller banks, by reducing the size of the current bank and installing a second smaller bank, | LA | ENTERGY SERVICES, LLC. | BRP |  | 2025-06-01 | 115 | 4400000
South | 25480 | Port Hudson 230-138 kV AT4 & 5 SPOF | Ensure Port Hudson 230/138 kV AT4 and AT5 both have redundant high-speed protection. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2025-06-01 | 230 | 4400000
West | 20030 | LSPI Cap Bank Asset Renewal | Replace the problematic LSPI capacitor bank with capacitor cans that are the new standard size. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2024-12-31 | 115 | 800000
West | 50007 | OTP Omemee Rebuild 41.6 kV Line | Rebuild and relocate 41.6 kV line between Rugby 41.6 kV and Bottineau 41.6 kV. | ND | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-11-01 | 42 | 800000
Central | 25367 | New 138 kV Hawthorne Substation | New 138 kV 3 breaker, 2 40 MVA transformer straight-bus substation to serve customer load. Looped-in on 132-28 Prospect to Ford line. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Load Growth | 2025-06-25 | 138 | 15000000
West | 50005 | OTP Donaldson 41.6 kV CB 215 Reconductor | Rebuild 41.6 kV line between Donaldson 41.6 kV and Drayton 41.6 kV. | MN | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2025-12-31 | 42 | 800000
West | 50002 | Overstress Breaker Replacement | End of Life replacement and upgrade of breakers identified in MTEP23 Short-Circuit Analysis. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-05-01 | 115 | 800000
West | 25467 | Substation P Iowa City Transformer Breakers | Add two 161 kV breakers at Substation P to separate the distribution transformers from the substation's line terminals | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-12-01 | 161 | 900000
West | 25370 | W3401 Insulator Replacement And Refurb | W3401 line refurb on 18.8 miles from Alma Center to Blair. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-31 | 69 | 1000000
West | 25375 | W3415 EGA-DUR-ARK Insulator Replacement and Refurbishment | Line W3415 refurb and insulator replacement on 5.9 miles between Eau Galle - Durand and 5.5 miles between Durand - Arkansas. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-01 | 69 | 1000000
West | 25273 | Bateman Substation Breaker Upgrade | Project to convert 69kV switch 4E442 to a circuit breaker and upgrade and bus relaying scheme at the Bateman substation. | WI | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-12-31 | 69 | 1000000
Central | 25401 | New 138-34.5 kV Northwest Transformer | New 138/34.5 kV 66.7 MVA transformer and 1 new 138 kV east bus tie breaker to create double breaker position at Northwest | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Local Reliability | 2025-06-30 | 138 | 4000000
South | 50087 | J1673&J1759 Ft. Jessup Substation | Tap the future Marthaville to Belmont 230 kv line 6.8 miles from Marthaville for a new Ft. Jessup 230 kV substation. This substation will serve as the POI for J1673 and J1759 generators. | LA | CLECO POWER LLC | GIP |  | 2025-07-01 | 230 | 4070667
Central | 25336 | Greensburg Washington St. 69kV Breaker upgrades | Replace (3) 69kV oil CBs with SF6 gas circuit breakers (GCBs) – 6937, 6964, 69119; replace relays on (3) 69kV lines; replace (12) 69kV switches. | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-07-24 | 69 | 2141580
West | 25311 | Stinson PST Retirement | Retire Stinson Phase Shifting Transformer (PST) due to age and increased maintenance costs. | WI | MINNESOTA POWER INC. | Other | Age and Condition | 2028-12-31 | 115 | 1000000
West | 25251 | J1734 GIA NU Wever 161 kV Bus Expansion | ITC Midwest will add a 161 kV breaker to expand the Wever 161 kV bus to allow for the interconnection of J1734 and the new 161 kV gen-tie line. | IA | ITC MIDWEST | GIP |  | 2025-07-31 | 161 | 1086141
East | 24440 | Van Tyle - J1603 NU - Install breaker 4B7 and switches 4M5 and 4B3 | Install breaker 4B7 and switches 4M5 and 4B3 | MI | METC | GIP |  | 2025-08-01 | 138 | 1122500
East | 24442 | Van Tyle-J1603 TOIF-Install position BM4 and switch 177 | Install BM4 line entrance structure and disconnect switch 177 for generator interconnection. | MI | METC | GIP |  | 2025-08-01 | 138 | 0
Central | 24939 | J1407 Network Upgrades | South Valparaiso substation 138kV yard will be expanded by one breaker to accommodate the Generating Facility lead line. Additionally, existing 13820 terminal pole 1008845 will be relocated | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2025-08-01 | 138 | 5401744
Central | 25521 | J992 Appleseed Solar POI | J992 - 200MW AppleSeed Solar (NextERA) Gen Intercon - Expand Walton 230 kV ring bus and add line terminal | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-08-15 | 230 | 7327980
South | 25313 | J1599 Daspit Substation | Build a new Daspit Substation on the Hopkins and Morbihan 138 kV line to allow J1599 Solar Generator | LA | CLECO POWER LLC | GIP |  | 2025-09-01 | 138 | 16236000
West | 25391 | Mud Lake to Riverton 230 kV Upgrade | The Riverton – Mud Lake “MR” 230 kV line is temperature rated at 189 degrees and is limited by seven spans. Make the necessary upgrades, six H-frame pole replacements, to get the Riverton – Mud Lake “MR” 230 kV line up to 212°F operating temperature and achieve a rating of 384.8/515.8 (summer/winter) MVA. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-06-01 | 230 | 1146876
Central | 25335 | Add new Thorntown 69kV ckt and rebuild 6943 ckt | Rebuild 6943 line from Thorntown Substation to Lebanon Substation with 954ACSR@120C - approx. 10 miles; Rebuild the double circuit section of 69134/6943; upgrade line terminals at Thorntown and Lebanon Enterprise; Thorntown substation: Add a 69kV 2000 amp line terminal and line to existing radial line off of the 6943 serving the Boone County REMC Pike 69kV substation (and new proposed WVPA Eli Lilly load). | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-09-04 | 69 | 31200000
Central | 25385 | Replace Petersburg 345 kV Breakers | Replace 6 345 kV breakers at Petersburg. Breakers #3A, #3B, #3C, #4A, #4B, and #4C. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-09-11 | 138 | 5400000
West | 25405 | Lakeville Area Projects | GRE will be adding a second radial circuit tap (double circuit) into Lakeville substation for the addition of a second transformer and switchgear to Lakeville substation. Dakota Electric Association (DEA) is responsible for the high side structures and associated transmission side substation equipment. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2025-09-30 | 115 | 1200000
South | 50043 | J1834 NRIS/ERIS Sabine to Neches L5 & L-172 upgrade to Double Bus Double Breaker | Add two additional 138 kV breakers at the Sabine 138 kV station to convert the Sabine to Neches lines to double bus double breaker configuration. | TX | ENTERGY SERVICES, LLC. | GIP |  | 2025-09-30 | 138 | 10000000
Central | 25542 | J1357 Williams Power POI | J1357 - 150MW Williams Power - battery storage: Madison 138 - add breaker (straight bus config) and line terminal | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-09-30 | 138 | 5680572
East | 25196 | Beecher-Dowling Junction Sag Remediation (J1550, J1635, J1658) - Network Upgrade | Remediate the Beecher-Dowling Junction sag limit to achieve a rating of at least 219 MVA SN and 249 MVA WN. | MI | METC | GIP |  | 2025-09-30 | 138 | 258750
West | 25464 | CBEC Upgrade Sync Check Relaying | Retire existing sync check relaying panel at CBEC and incorporate sync check into existing relays or replace relays where necessary | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-12-01 | 345 | 1200000
Central | 25089 | New Harmony 69/12kV T2 and CB's Replacement | Replacement of transformer T2 and breakers at New Harmony substation due to age and condition | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-10-01 | 69 | 5300000
South | 25416 | Lucedale 69kV Switching Station | In order to serve the member delivery points of North Lucedale and South Lucedale economically and reliably a new 69kV switching will be constructed at near Lucedale, MS. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2025-10-01 | 69 | 2860000
Central | 25347 | WVPA Lebanon Industrial 69/12kV Sub | WVPA Lebanon Industrial 69kV Sub - Construct a new 69/12kV substation to serve a new Eli Lilly facility, the substation will have a high side 69kV ring bus | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-10-01 | 69 | 12215000
South | 50099 | Lewisville West Capacity Increase | Add 2nd transformer at existing Lewisville West substation. New transformer will be 115/69 kV, 100 MVA. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Load Growth | 2025-10-01 | 115 | 4500000
Central | 25303 | HE_J1027_Ratts2_Solar | Network Upgrades include upgrades to bay 4 at Petersburg Substation in order to tie in the IC’s new generator lead line from the solar PV plant. Switches 29-463 and 29-461 will be replaced as well as all existing conductor. All existing structures and breaker 52-462 will be reused. New CTs, CCVTs, and arresters will be added on the line side of switch 29-463. | IN | HOOSIER ENERGY | GIP |  | 2025-10-01 | 161 | 3636500
West | 25505 | J1314/S1039 Generation Interconnection Upgrades | J1314/S1039 will require substation modifications at the existing Apple River 161 kV substation for the interconnection | WI | DAIRYLAND POWER COOPERATIVE | GIP |  | 2025-06-30 | 161 | 1263371
West | 25388 | Cleveland Breaker Replacement | Cleveland – replace breaker 4S100 and 4S99. Replace GE JVS-350 PTs and any other type PTs in poor condition (verify during scoping which PTs are this type, possibly replace all 5 depending on age/condition/type – Maximo data is incomplete). Add missing 69 kV breaker to complete topology. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2025-10-01 | 69 | 1311954
West | 25373 | Salem Breaker Station | Expand the existing Salem transmission site to include line breakers for each of the three lines that tie into the site. Boy River, circuit to Deer River and Blind Lake circuit would have breakers. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2025-10-17 | 69 | 1342821
West | 25453 | Medina Breaker Addition and Replacement | Replace 55WB2 and breaker addition | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2026-11-30 | 115 | 1400052
West | 50006 | OTP Marvin - Corona Area 41.6 kV Rebuild | Rebuild 41.6 kV line between Wilmot 41.6 kV and Summit 41.6 kV in the Marvin/Corona 41.6 kV area. | SD | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-12-31 | 42 | 1500000
Central | 25021 | J1387 Network Upgrades | Network Upgrades work consists of: • installation of three (3) new class H1direct-embed wood poles, • 336 kcmil ‘Merlin’ ACSR conductor to interconnect the 6958 line into the new 69kV tap substation’s • two (2) 69kV 1200 ampere disconnect switches. Transmission Owner will also install direct transfer trip relay equipment at Transmission Owner’s Thayer substation on 6958 breaker to communicate with the new station. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2025-10-16 | 69 | 1066894
Central | 25090 | Northwest CB's Replacement | Replacement of breakers at Northwest substation due to age and condition | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-10-17 | 138 | 5000000
Central | 50068 | HE Taylorsville 69/12kV Sub | HE Taylorsville 69/12kV Sub: construct new 22MVA sub at the same location as existing HE Taylorsville sub; to be served radially off the DEI 69146 ckt.; load at HE Taylorsville will be transferred from Edinburgh sub 69/12kV bank #2 = 3MW+/- | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-10-17 | 69 | 900000
West | 25204 | J1365 GIA NU Traer 161 kV Ring Bus Expansion | A new 161 kV, breaker, and ring-bus expansion at the station will be constructed for J1365. | IA | ITC MIDWEST | GIP |  | 2024-07-26 | 161 | 1574200
Central | 25463 | Glenwood to Rushville 69kV Line Rebuild | TDSIC 69kV Line Rebuild: Glenwood -(6920 / 5.72 mi.)- Rushville East -(69192 / 1.85 mi.)- Rushville; replace approx. 150 single poles; conductor size = 477ACSR45X7@120C; replace (2) line switches at Glenwood Jct; reroute 6920 around Glenwood area | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2025-10-31 | 69 | 24685000
East | 25245 | Coldwater-Ash Road Junction Sag Remediation (J1550) - Network Upgrade | Remediate the Coldwater-Ash Road Junction sag limit to achieve a minimum rating of 200 MVA Summer Emergency. | MI | METC | GIP |  | 2025-10-31 | 138 | 335000
West | 24413 | Richer-Littlefork 230 kV Line Rebuild | 230 kV transmission structure replacement from Richer to Littlefork. | MN | MINNKOTA POWER COOPERATIVE, INC | Other | Age and Condition | 2025-02-28 | 230 | 1590000
West | 25411 | Second 69 kV Line into Rock Valley Town Substation | Construct a second 69 kV line into Rock Valley Town Substation and retire a section of existing Rock Valley Town Tap-NIPCO K218 69 kV line | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-12-01 | 69 | 1600000
Central | 25280 | HE_J1354_Decatur_Battery | Decatur County 138kV Switching Station upgrades to accommodate interconnection of Decatur Battery Storage project J1354. Modifications in the switching station will include relocation of the capacitor bank to make available a terminal position for connection of the new transmission line from the battery storage facility. Upgrades also include CCVTs, CTs, Disconnect Switches, Arrestors, etc. | IN | HOOSIER ENERGY | GIP |  | 2025-11-15 | 138 | 3248872
East | 24461 | Grassmere - J1525 Gen Network Upgrade | Install breakers AT, BF, CT and CM and install switches AV, BD, CV, CR, CO, and CK. | MI | ITC | GIP |  | 2025-11-17 | 345 | 7602430
East | 24462 | Grassmere - J1525 TOIF - Install Position CQ and switch CQA | Install a CQ line entrance structure and disconnect switch CQA for generator interconnection. | MI | ITC | GIP |  | 2025-11-17 | 345 | 0
West | 25466 | Maynard Substation: Replace Three 69 kV Breakers and Relaying | Replace oil breakers, bus differential relaying, and breaker failure relaying. | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2029-12-31 | 69 | 1600000
South | 25472 | 2025 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. | AR | ENTERGY ARKANSAS, LLC | Other | Age and Condition | 2025-12-01 | 161 | 32893800
South | 25417 | Line 34 Rebuild | To ensure reliable service a complete rebuild of L34 (Lucedale – Rocky Creek 7.97 miles) is recommended. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2025-12-01 | 69 | 5000000
West | 25421 | Sand Lake Area Projects | Add approximately .75 mile to the Sand Lake tap (LP Line) and add new metering to a new substation site. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2024-11-20 | 69 | 1630051
Central | 22951 | Upgrade Rantoul 138 kV substation | Reconfigure 138kV into ring bus | IL | AMEREN ILLINOIS | Other | Age and Condition | 2025-12-01 | 138 | 7100000
Central | 25091 | Replace 345/138kV Transformer 2 at Norris City North | Replace the existing Transformer 2 at Norris City North with a new 345/138kV 700 MVA unit | IL | AMEREN ILLINOIS | Other | Age and Condition | 2025-12-01 | 345 | 7000000
Central | 25193 | Turkey Hill - Transformer 1 Replacement | Replace Turkey Hill XFMR 1 with a new 345/138kV 700 MVA transformer. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2025-12-01 | 345 | 6700000
Central | 50148 | Havana-Puro 138 kV1422 MPFCA | Rebuild the 138 kV Havana-Puro 1422 transmission line with new wood H frame structures, steel structures, OPGW and 1200 A conductor. Affected J#s include: J1408, J1453, J1454 | MO | AMEREN ILLINOIS | GIP |  | 2025-12-01 | 138 | 13200000
West | 25199 | Fairmont 10th St 69kV Substation Modernization | Current breakers were installed in 1985, and they have become unreliable and difficult to maintain with their age. Along with these breakers, the associated switches and relays will also be replaced with newer and more reliable equipment. The new equipment includes new PTs, arresters, and new solid-state relay panels. | MN | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Other | Age and Condition | 2025-02-01 | 69000 | 1800000
Central | 25043 | Moose 138 kV Substation for Albion PV1 (J1422) | This project will install a new 138 kV line position to serve as the Point of Interconnection for Albion PV 1, LLC under GIA J1422, within the new 3-position ring bus named Moose. | IL | AMEREN ILLINOIS | GIP |  | 2025-12-01 | 138 | 8400000
Central | 25545 | J1390 Lowland Solar Park POI | J1390 - 150MW Lowland Solar Park - Oversite of Self-Build Switching Station by developer (3-CB ring); inserted in the 23004 Gallagher to Columbus ckt; includes relay upgrades on the remote ends, 23004 loop-through line work; and reroute of the 23005 around the new switching station | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-12-01 | 230 | 6843406
Central | 25499 | Reconductor HMPL Sub 2 to HMPL Sub 5 69kV line | Reconductor line from HMPL Sub 2 to HMPL Sub 5 69 kV line | KY | CITY OF HENDERSON, KY, UTILITY COMMISSION, DBA HENDERSON MUNICIPAL POWER AND LIGHT (BA) | Other | Age and Condition | 2025-12-01 | 69 | 1036568
West | 25260 | Loon Lake 69kV Substation Modernization | Current breakers were installed in 1985, and they have become unreliable and difficult to maintain with their age. Along with these breakers, the associated switches and relays will also be replaced with newer and more reliable equipment. The new equipment includes new PTs, arresters, and new solid-state relay panels. | MN | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Other | Age and Condition | 2025-02-01 | 69000 | 1800000
South | 25540 | State Line 69kV Delivery Point | In order to serve the member delivery point, tap L32 (State Line - Leakesville) with a 69kV Goab and construct a new line to the delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2025-12-01 | 69 | 725000
South | 50164 | Woodberry Load Addition | AECC has received a request for a 26 MW load addition served out of the Summerville delivery point. This new load will require a 69kV substation to be built off of the 69kV Summerville system as well as load additions to existing substations served out of Summerville. Two (2) 15.3 MVAR capacitor banks will also be needed for voltage support during contingencies. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Load Growth | 2025-12-01 | 69 | 10200000
Central | 23151 | Rebuild East Quincy-Hamilton-4 138 kV line | Rebuild the 30.5 mile East Quincy-Hamilton-4 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | 46000000
Central | 24738 | Rebuild Hull-Herleman-1682 138 kV Transmission Line | Rebuild the Hull-Herleman-1682 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | 24000000
Central | 24737 | Rebuild Woodhall-Hallock-1570 138 kV Transmission Line | Rebuild the Woodhall-Hallock-1570 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | 16000000
Central | 25349 | Labadie-Montgomery 345kV Aging Infrastructure | Address aging infrastructure issues on the Labadie-Montgomery 345kV line. | MO | AMEREN MISSOURI | Other | Local Reliability | 2025-12-01 | 345 | 10500000
South | 25481 | Arklahoma 115kV Bus Relay Improvement SPOF | Construct redundant high speed protection for the Arklahoma 115kV bus. All elements of the auto protection scheme should have high-speed redundancy including redundant DC supply such that loss of any component of the auto protection scheme would not result in delayed fault clearing. All single points of failure should be avoided, and the following should be accounted for: Independent and redundant communication for each relay. Dual station batteries with separate DC system feeding each relay or monitoring sufficient to FERC 754 guidelines. Independent CT and PT winding inputs for each relay. | AR | ENTERGY ARKANSAS, LLC | Other | Local Reliability | 2025-12-01 | 115 | 2525674
South | 25485 | Champs 115kV: New Substation Phase 1 | Build a new 115kV operating and transfer bus substation with one 40 MVA 115/13.8kV transformer in Maumelle, AR. | AR | ENTERGY ARKANSAS, LLC | Other | Local Reliability | 2025-12-01 | 115 | 10804929
Central | 24717 | Rebuild Edwards-Keystone-1397 138 kV Transmission Line | Rebuild Edwards-Keystone-1397 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | 5500000
Central | 25092 | Zachary 161 kV BAAH Addition | Add six breakers at Zachary 161 kV station to complete a breaker-and-a-half arrangement | MO | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Other | Local Reliability | 2025-12-01 | 161 | 3000000
South | 25487 | Frazier Pike 115kV: New Substation | Build a new 115kV operating and transfer bus substation with a single 50 MVA 115/13.8kV transformer that will include a 0.5 mile in and out 115kV transmission line in Little Rock, AR. | AR | ENTERGY ARKANSAS, LLC | Other | Local Reliability | 2025-12-01 | 115 | 18007302
Central | 24739 | Rebuild Greenback-Lanesville 138 kV Line | Rebuild the Greenback-Lanesville-1314 138 kV line from Str. 159-Lanesville Substation with conductors capable of carrying 2000 amps under Summer Emergency conditions at 2 OPGW's. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | 2200000
West | 25452 | Dickinson Breaker Replacement | Replace 62WB1, WB2 and WB4 and replace BPRO | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-06-01 | 115 | 1845219
Central | 25093 | Zachary 161 kV Terminal Addition | Add one 161 kV breaker and line terminal for Locust Creek (AECI) | MO | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Other | Local Reliability | 2025-12-01 | 161 | 1500000
West | 25306 | ITCM Burlington 4th Street Control Enclosure & 69 kV Tie Breaker Addition | IPL has notified ITC that they will be rebuilding their Burlington 4th Street sub and installing a 2nd 20/26/33 MVA transformer; as well as, replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Burlington 4th Street sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | IA | ITC MIDWEST | Other | Load Growth | 2026-12-31 | 69 | 1984333
West | 25446 | Willmar System Upgrades | Willmar is upgrading SCADA, relays, RTUs, and replacing 69 kV poles due to age. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Age and Condition | 2025-12-05 | 230 | 2000000
West | 50020 | 0711 Redwing - Str 11 Rebuild | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-31 | 69 | 2000000
Central | 24987 | Mason-IL 138 kV Upgrade for Glacier Sands Wind II (J1454) | MISO project J1454, a 40.90 MW Wind Generating Facility, will interconnect to the Ameren Illinois Transmission System. Project No. J1454 is an expansion of J1055 Generating Facility. Transmission Owner will modify the 138 kV bus at its existing Mason substation | IL | AMEREN ILLINOIS | GIP |  | 2025-12-01 | 138 | 100000
Central | 25039 | Taum Sauk 138 kV Upgrade for 60MW Hydro (J1213) | MISO project J1213, will add 60 MW to the existing Hydro Energy Generating Facility, Transmission Owner will modify the 138 kV bus at its existing Taum Sauk 138 kV substation. | MO | AMEREN MISSOURI | GIP |  | 2025-12-01 | 138 | 100000
Central | 25081 | J1450 Webster County Switching Station for POI | Construction of a new switching station called Webster County to accommodate a POI per the executed GIA for project J1450. This will be constructed 4.23 miles from BREC's existing Hopkins County substation on the existing Hopkins-Reid EHV 161 kV line. OPGW will be ran for the length of the existing Hopkins-Reid EHV 161 kV line for remote end communications. Relaying will be upgraded at both Hopkins and Reid EHV. | KY | BIG RIVERS ELECTRIC CORPORATION | GIP |  | 2025-12-01 | 161 | 0
Central | 25120 | J1466 Reid EHV 161 kV Terminal Addition | Add a 161 kV terminal for POI for project J1466, which has an executed GIA. | KY | BIG RIVERS ELECTRIC CORPORATION | GIP |  | 2025-12-01 | 161 | 0
West | 50109 | J1814 Nordic SS Network Upgrades and Interconnection Facilities | J1814 is a solar facility located in Dickinson County, MI. | MI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-09-10 | 138 | 2150000
West | 25253 | ITCM Flint Ridge Control Enclosure & 69 kV Tie Breaker Addition | IPL has notified ITCM that they will be rebuilding their Flint Ridge sub and installing a 2nd 20/26/33 MVA transformer. This rebuild will also be replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Flint Ridge sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | IA | ITC MIDWEST | Other | Load Growth | 2026-12-31 | 69 | 2160171
West | 23851 | Stanton Breaker Replacement | Replace Stanton oil breakers 31RB1, 2, 3, 4 & 6. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2026-11-05 | 230 | 2179821
West | 25294 | Reinforce Tracy Switching Station TR01 | Upgrade existing transformer at Tracy Switching Station to 14 MVA. Convert town of Tracy to 13.8 kV and retire Tracy (TRA) substation. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-10-15 | 69 | 2200000
Central | 25386 | Replace North 138 kV Breakers | Replace 2 138 kV breakers at North. Breakers #3 and #4. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-12-22 | 138 | 1800000
Central | 25389 | Replace Northeast 138 kV Breakers | Replace 2 138 kV breakers at Northeast. Breakers #1 and #3. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-12-22 | 138 | 1800000
Central | 25390 | Replace Brookwood 138 kV Breakers | Replace 2 138 kV breakers at Brookwood. Breakers #1 and #2. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-12-22 | 138 | 1800000
Central | 25387 | Replace Prospect 138 kV #2 Breaker | Replace 1 138 kV breaker at Prospect. Breaker #2. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-12-22 | 138 | 900000
Central | 25334 | Kokomo Webster St Ckt Brkr Replacements | Kokomo Webster St Ckt Brkr Replacements - 230kV: replace (2) oil CBs (23022-20 and 230B2-22) and their disconnect switches (motorize); replace all 230kV relays; install SCADA controlled line disconnect switches (23016, 23020 & 23022) and upgrade wave traps as needed; Upgrade RTU and DC power supply systems; 69kV: Replace (4) oil CBs (69173, 69174, 6912-1 and 69230-2) and their disconnect switches as needed; replace all 69kV relays | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-12-22 | 230 | 6300000
Central | 25414 | Rebuild 138kV Line from Speed to Jeffersonville | (1) Rebuild entire 13898 ckt from Speed to Jeffersonville with 954ACSS@200C; (2) upgrade very short 13882 tie with LGE at Jeffersonville to 954ACSS@200C and have LGE add ATO switches at the junction just outside Jeffersonville sub; (3) rebuild 6955 ckt where double circuited with 13898 ckt; (4) upgrade line terminals and substation buses as needed | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2025-12-31 | 138 | 38300000
West | 25447 | Forest & Vermont Breaker Replacements | Replace four (4) overdutied 69 kV breakers | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-12-01 | 69 | 2400000
West | 50091 | Milwaukee County, New DIC | ATC will tap 138 kV line 836 (Oak Creek-Oakview) to serve new interconnection request. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-01 | 138 | 2600000
West | 50108 | J1573 Plover SS Network Upgrades and Interconnection Facilities | J1573 is a solar facility located in Portage County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-09-10 | 115 | 2633000
West | 25241 | ITCM Newton 8th St Control Enclosure, Relay, and SCADA Replacement | Replace the existing relaying and SCADA at Leon by ITC installing a new ITC owned control building. IPL owns and maintains this building. Separating the buildings by owner lines up with the current substation standards. | IA | ITC MIDWEST | Other | Age and Condition | 2026-12-31 | 161 | 2655119
West | 25431 | Dakota Dunes: Install 69 kV Capacitor Bank | Install a 69 kV, 14.7 MVAR capacitor bank at Dakota Dunes Substation | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-06-01 | 69 | 2800000
South | 25484 | 2025 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2025. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized | TX | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2025-12-31 | 500 | 38300000
Central | 25151 | Y67/Z78 Junction - Jasper South Rebuild | Replacement of poles from Y67/Z78 Junction to Jasper South (no conductor change) and several switches. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-12-31 | 69 | 10000000
Central | 25152 | Z99 AB Brown - Wolf Road Rebuild | Replacement of poles along Z99 from AB Brown to Wolf Road (no conductor change) | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-12-31 | 138 | 8500000
West | 25307 | ITCM State Center Rural 69 kV Interconnection | IPL will construct a new 69/24.9kV - 10/12.5MVA w/ LTC substation, State Center Rural. This new substation is due to the 69kV conversion of the Maxwell North to Timbercreek line. ITC will install two 69kV line breakers in both directions from the sub, and tap and reroute the Nevada North-Timber Creek line in and out of the new State Center Rural sub. | IA | ITC MIDWEST | Other | Load Growth | 2026-12-15 | 69 | 2910514
Central | 25150 | Y52-2 Mackey - Oakland City Rebuild | Replacement of poles along Y52-2 due to age and condition (conductor no changing) | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-12-31 | 69 | 8000000
Central | 25441 | Z91-2 Pigeon Creek - Heidelbach Rebuild | Rebuilding ~2 miles of 138kV line from 795 to 954 | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-12-31 | 138 | 5500000
Central | 25149 | County Line 69/12kV T1 Replacement | Replacement of transformer T1 at County Line substation due to age and condition | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2025-12-31 | 69 | 3000000
South | 25482 | 2025 ELL Asset Renewal Program | This project is for the ELL Asset Renewal Program that will be executed in 2025. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized | LA | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2025-12-31 | 500 | 87900000
South | 25486 | 2025 EML Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. | MS | ENTERGY MISSISSIPPI, LLC. | Other | Age and Condition | 2025-12-31 | 500 | 47800000
South | 25483 | 2025 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2025. The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized | LA | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2025-12-31 | 230 | 9600000
East | 24559 | J1658 Generator Interconnection TOIF | Install required line entrance structure and 138 kV disconnect at new Cronk Station. | MI | METC | GIP |  | 2025-12-31 | 138 | 0
East | 24561 | J1614 Generator Interconnection TOIF | Install required line entrance structures and disconnect at the new Aphis station. | MI | METC | GIP |  | 2025-12-31 | 138 | 0
Central | 25331 | WVPA Blacketor 69/12kV Sub | WVPA Blacketor 69kV Sub - Construct a new 69/12kV substation to serve load fed from an existing meter point | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-12-31 | 69 | 8753000
West | 50014 | West Grand Add 161 kV Line Breakers | Install two 161 kV line breakers and associated relaying at West Grand Substation. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2025-06-30 | 161 | 3000000
West | 25379 | Rebuild Wabasha Substation | Rebuild Wabasha substation at a nearby location due to flooding concerns. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-31 | 69 | 3000000
West | 50136 | Baraboo SS, DIC, Substation Relocation | The LDC is planning to relocate the Baraboo substation from its current location to a nearby site. To accommodate this ATC will install 2x new T-Line structures and replace one T-Line structure to reroute the Kirkwood-Dam Heights 69kV (Y-75) line. This will require roughly 0.04 miles of new conductor. Additionally, a new 3 way tap structure to the new substation will be required. A new ATC control house will be required to retain supervisory control of the tap switches. Lastly, ATC to retire 9x T-Line poles and the substation equipment at the current Baraboo location. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-01 | 69 | 3000000
West | 25425 | Metro East Substation 161 kV line breakers | Install 161 kV line breakers and relaying | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2027-12-01 | 161 | 3000000
East | 25500 | METC Line Relocation - 2025 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | METC | Other | Local Needs | 2025-12-31 | 345 | 2500000
East | 25478 | ITCT Line Relocation - 2025 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI | ITC | Other | Local Needs | 2025-12-31 | 345 | 2500000
Central | 25408 | Fort Branch 69kV Capacitor Bank | Install 69kV 15.6MVAR capacitor bank at Fort Branch | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Local Reliability | 2025-12-31 | 69 | 3000000
West | 25454 | East Chain Tie Line Projects | Construct a tie line between East Chain municipal and GRE’s FE-WB (East Chain to Wilbert) line. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2028-10-06 | 69 | 3000000
West | 25213 | ITC Midwest SCADA Controlled Motor Operated Switch Addition Program 2025 | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be utilized to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | IA; IL; MN | ITC MIDWEST | Other | Local Needs | 2025-12-31 | 69 | 3125000
West | 50107 | J1513 Clintonville Swt St Network Upgrades and Interconnection Facilities | J1513 is a solar facility in Waupaca County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-09-10 | 138 | 3168000
West | 50120 | J1615 Morgan SS Network Upgrades and Interconnection Facilities | J1615 is a solar facility located in Oconto County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-09-10 | 138 | 3342000
West | 25285 | 0891 West St Cloud - Crossroads Rebuild | Rebuild 4.1 miles 115 kV from West St. Cloud - Crossroads with new structures and new OPGW shield wire. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-15 | 115 | 3500000
South | 25229 | Costas 230 kV Substation | The Costas 230 kV breaker and a half substation will cut into the existing Lake Castle – North Park 230 kV transmission line. A 108 MVAR capacitor bank will also be added to the new Costas 230 kV substation. Customer load will be fed out of (3) 150 MVA 230/34.5 kV transformers. | MS | ENTERGY MISSISSIPPI, LLC. | Other | Load Growth | 2026-01-01 | 230 | 44500002
Central | 50057 | Vessel Bulk Sub - Add 2nd 138/34 kV Transformer | At Vessel Bulk Sub Install the second 84 MVA transformer | MO | AMEREN MISSOURI | Other | Load Growth | 2026-01-01 | 138 | 4000000
South | 25438 | Pickens - South Canton 230 kV Line Rebuilds | Rebuild the Pickens – Canton – South Canton 230 kV line with new conductor and through–path rating no lower than 779 MVA. | MS | ENTERGY MISSISSIPPI, LLC. | BRP |  | 2026-01-01 | 230 | 55200001
Central | 50032 | New Pike County Energy Storage 345kV (R1021 & R1022) | Generator Project R1021 Interconnection Customer shall install a 117.6 MVA battery storage system. Generator Project R1022 Interconnection Customer shall install a 117.6 MVA battery storage system. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | GIP |  | 2026-01-15 | 345 | 3000000
South | 24958 | Sandling 230 kV Customer Load Addition Project | Entergy is proposing to construct a new 230 kV transmission station called Sandling 230 kV which will serve a new industrial customer’s load near Port Arthur, TX. Sandling 230 kV station will be cut into the Legend to Keith Lake 230 kV line and the Keith Lake to Port Acres Bulk 230 kV line. Two capacitor banks will also be installed in the new Sandling 230 kV station. | TX | ENTERGY SERVICES, LLC. | Other | Load Growth | 2026-01-30 | 230 | 114200000
East | 25210 | Replace Moore Road WM33 Trainer (J1658) - Network Upgrade | Replace Moore Road WM33 477 ACSR 26/7 trainer with 1590 to raise rating to 209 MVA SN and 237 MVA SE. | MI | METC | GIP |  | 2026-01-30 | 138 | 27635
East | 24558 | J1658 Generator Interconnection Network Upgrades | Install new Cronk 138 kV Substation. Install three 138 kV breakers rated at 40 kA and two new bus sections. Cut the Coldwater - Moore 138 kV line to loop in the new station. Island at Ash Road will need to be mitigated. | MI | METC | GIP |  | 2026-02-02 | 138 | 19660970
East | 25194 | Cronk-Moore Road Rebuild & Station Equipment Upgrades (J1550, J1635, J1658) - Network Upgrade | Rebuild the Cronk - Moore Rd circuit utilizing conductor rated at least that of 1431 ACSR. Replace Moore Road conductor and equipment to achieve a rating at least that of 348 MVA SE. Any new towers should be 230 kV double circuit structures to be operated at 138 kV. Structures in spans entering the new Cronk station do not need to be 230 kV structures. | MI | METC | GIP |  | 2026-02-02 | 138 | 11323126
Central | 50086 | Load addition at Montgomery 161 kV Substation | This project will facilitate the connection of a 250 MW datacenter load at Montgomery (161 kV) Substation with a new straight bus and terminal | MO | AMEREN MISSOURI | Other | Load Growth | 2026-03-01 | 161 | 2500000
East | 24560 | J1614 Generator Interconnection Network Upgrades | Install new Aphis substation. Install three 138 kV breakers and associated disconnects rated at 40 kA and two new bus sections. Cut the Cobb – Meyer line into the new Aphis station. Fiber will be needed to mitigate an island at White Road. | MI | METC | GIP |  | 2026-03-03 | 138 | 11805174
West | 25301 | Leola load addition | MDU has new customer requesting service on our 41.6 kV system near our Leola substation of 50 MW. MDU will need to add 2-10 Mvar capacitors and add additional 41.6 kV breaker to the Leola substation. | SD | MONTANA-DAKOTA UTILITIES CO. | Other | Load Growth | 2024-09-01 | 115 | 3600000
East | 24478 | Kenowa - J1527 Gen Network Upgrade | Add Row 35, install 2-345kV breakers and associated disconnects at positions 35H9, 35F7 with minimum 40kA interrupting capability. | MI | METC | GIP |  | 2026-04-01 | 345 | 5567500
Central | 25504 | J1481 Emerald Green Solar POI | J1481 - 200MW Emerald Green Solar: Greentown 230 - Expand 230 kV sub by adding a new CB that will share the existing ring bus terminal of the 23022 line and add line terminal equipment | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2026-04-01 | 230 | 8535044
South | 50040 | Morrilton East 161kV: POI for J1559 | A new point of interconnection at the existing Morrilton East 161kV substation for the J1559 200 MW ERIS solar project. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-04-01 | 161 | 3175000
East | 24553 | J1659 Generator Interconnection Network Upgrades | Install 120 kV breaker HG rated at 40 kA. | MI | ITC | GIP |  | 2026-04-01 | 120 | 922579
East | 24554 | J1659 Generator Interconnection TOIF | Install required line entrance structures and 120 kV disconnect at Dorset Substation. | MI | ITC | GIP |  | 2026-04-01 | 120 | 0
South | 50039 | J1561 Generator Interconnection at Richard138 kV | Facilities required for the interconnection of J1561 at the Richard 138kV | LA | ENTERGY SERVICES, LLC. | GIP |  | 2026-04-01 | 138 | 8263000
South | 50094 | Northstar | Interconnect Entergy's Monticello South to Wilmar transmission line east of Wilmar and construct a 115/13.2 kV, 20 MVA substation. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Load Growth | 2026-04-01 | 115 | 7000000
South | 50004 | J1670 Crooked Lake 2 GIA upgrades | This project is to install power quality metering panel and remove current transformers. Also, revenue meters, telecom equipment, and a digital disturbance recorder panel will be installed. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-04-03 | 161 | 1296000
East | 24443 | Tallmadge-Argenta - J1663 Generator Interconnection (Gordon) - Network Upgrade | Build a new 345 kV 3 Breaker ring substation cut in from the Tallmadge-Argenta 345 kV line. System changes will require relay upgrades at Argenta and Tallmadge 345 kV stations. | MI | METC | GIP |  | 2026-05-01 | 345 | 14811052
East | 24479 | Gordon-J1663 TOIF-Install position RH29 and switch 177 | Install RH29 line entrance structure and disconnect switch 177 for generator interconnection. | MI | METC | GIP |  | 2026-05-01 | 345 | 0
West | 25309 | Substation Technology Package #2 - 2024 | The Substation Technology Package #2 (SSTP#2) program of work will set the stage for the future of the digital substation field worker by providing enhanced Business Capabilities over ATC’s substation fiber network infrastructure. The SSTP#2 – 2024 project scope will include the following technology enhancements: • The installation of Wireless Access Points and enhanced Cyber Security fortifications at ~75 ATC substations. • Wireless connectivity will provide field workers with secure access from the substation ATC’s corporate data centers. • Cyber Security fortifications will introduce substation communication equipment protections in the event of a rogue device breach by pro-actively monitoring data activity between the substation router and switch. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2024-12-31 | 0 | 3600000
East | 24533 | J1526 Generator Interconnection Network Upgrades | Install 345 kV breaker KT rated at 63 kA. | MI | ITC | GIP |  | 2026-05-13 | 345 | 1364741
East | 24534 | J1526 Generator Interconnection TOIF | Install required line entrance structure and 345 kV disconnect switch at the ITCT Greenwood Substation. | MI | ITC | GIP |  | 2026-05-13 | 345 | 0
Central | 25546 | J1388 Galea Springs SPV POI | J1388 - 150MW Galea Springs SPV - solar farm - construct new switching station (3-CB ring) in the radial Oakland City 13862 ckt. - includes Oakland City relay upgrades and rebuilding 6.75 miles of 138kV line from POI to Oakland City | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2026-06-01 | 138 | 52928159
Central | 22878 | Upgrade Cat Mapleton 138 kV substation | New ring bus across road with two lead lines back to Cat Mapleton. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-06-01 | 138 | 8700000
South | 25459 | Line 35 Rebuild | To ensure reliable service a complete rebuild of L35 (Lucedale – Benndale 11.37 miles) is recommended. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2026-06-01 | 69 | 7100000
West | 25272 | MNN MOD Installation | Install new MOD transmission line switches at Monticello. Potential for new pole and substation fence expansion. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-06-13 | 345 | 3600000
Central | 22950 | Upgrade Watson 161 kV substation | Add line breakers to Pos. V & W Remove HSGS' and Add CS/PCB on the XFMRs 1,2,3 | MO | AMEREN MISSOURI | Other | Age and Condition | 2026-06-01 | 138 | 6200000
Central | 25523 | J1348 Brouilletts Creek Solar POI | J1348 - 200MW Brouilletts Creek Solar: Provide construction oversite for new switching station constructed by the IPP; relaying upgrades at Cayuga CT and Sugar Creek (34513 ckt); Loop 34513 in and out of new substation | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2026-06-01 | 345 | 8372617
Central | 22969 | Upgrade Decatur East Main St. 138 kV substation | Add line breaker to the L1522 line. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-06-01 | 138 | 2250000
West | 25211 | ITCM Customer Interconnects with short lead time 2026 | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA | ITC MIDWEST | Other | Load Growth | 2026-12-31 | 345 | 3750000
West | 50012 | OTP Buffalo Area 41.6 kV Rebuild | Rebuild 41.6 kV line between Buffalo 41.6 kV and Colgate 41.6 kV | ND | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2028-12-31 | 42 | 3770000
Central | 22949 | Rebuild Stoddard 161 kV substation | Rebuild Stoddard substation into a ring bus configuration, including replacement of aging/overstressed/broken equipment. | MO | AMEREN MISSOURI | Other | Local Reliability | 2026-06-01 | 161 | 15900000
Central | 24921 | New Steamboat 138 kV Ringbus for Babylon 138 kV Sub for PPI Connection | Prairie Power Incorporated (PPI) 138 kV delivery point substation to supply a new bulk distribution transformer at the PPI Ellisville tap on the Ameren Castro-Galesburg Monmouth Blvd-1427 138 kV line | IL | AMEREN ILLINOIS | Other | Local Reliability | 2026-06-01 | 138 | 9700000
Central | 22880 | Zion 161 kV Substation Add High Side Interrupter | Add high side interrupting device on 161/69 kV transformer #1 | IL | AMEREN MISSOURI | Other | Local Reliability | 2026-06-01 | 161 | 2000000
South | 25436 | Bobville 230-138 kV Station | Cut a new 230 kV station called Bobville into the Castle to Ponderosa 230 kV line. Install a 230-138 kV Autotransformer. Cut Bobville 138 kV station into the Dobbin to Spring Branch 138 kV line. Bobville 230 kV and 138 kV stations will both be three breaker ring. Upgrade the short section between the Dobbin and Bobville 138 kV stations. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2026-06-01 | 230 | 48600001
West | 25160 | Weston - Morrison Ave 115kV (Z-52), Reconductor | Reconfigure Weston - Sherman Street (O-41) line terminal to new position on West bus and relocate the Weston - Morrison Ave (Z-52) line terminal to the vacated position. Z-52 to be reconductored from Weston to Morrison Ave. Install upgraded communication equipment at remote ends. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2026-06-01 | 115 | 3800000
West | 24980 | Pioneer SS Breaker Relay and Remote Ends Asset Renewal | At Pioneer SS: Replace 3 breakers and remove free standing CTs and replace relaying. Install arrestors as required for the new breakers. Replace CCVT on line F-58. Replace GPS clock. Replace three Bus 1 potential transformers and one bus station power transformer. Replace two disconnect switches. At Stiles SS: Replace relaying on line 64442. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-31 | 138 | 3800000
South | 50048 | MPFCA J1644, J1686, J1832: Upgrade of Champagne – East Opelousas – Colton 138 kV line | Upgrade of of Champagne – East Opelousas – Colton 138 kV line. | LA | ENTERGY SERVICES, LLC. | GIP |  | 2026-06-09 | 138 | 9105556
West | 50031 | Maffitt Lake Add 161 kV Breakers | Install four 161 kV breakers and associated equipment at Maffitt Lake Substation. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2025-06-01 | 161 | 4000000
Central | 25525 | Kokomo Project Fusion Phase 2 - 230/69kV Sub | Kokomo Fusion Phase 2 (StarPlus Energy) - 155MW/51MVAR load addition; relocate 23022, 69172, and 69174 lines away from Phase 2 facilities; add (1) 150MVA 230/69kV transformer; add (2) 230CBs; add (4) 60MVA 69/34kV transformers | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-06-30 | 230 | 14000000
West | 25324 | Downing Substation | Install new distribution substation in the Downing area. | WI | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-10-15 | 69 | 4000000
West | 50137 | Line ILKY31 and 6912 Grounding Improvement | Test all of 138kV and 69kV Line ILKD31/6912 double circuit structures with 3-point ground test method (356) structures). Install additional grounding on an estimated and assumed 190 each of the steel structures to meet ATC Construction Specifications. Retest and install additional 4-150 ft runs of counterpoise system grounding with Ground Enhancing. Counterpoise will likely need to be installed after initial ground rod installation and retesting between structures 106635 and 106765 (Boring B-20 to B-53) due to bedrock located less than 10 feet from the surface. Replace broken ground connection on approximately 24 structures per ATC specification as required. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-01 | 138 | 4000000
Central | 25041 | Virden 138 kV Substation for Virden Wind (J1408) | This project will install a new 138 kV line position to serve as the Point of Interconnection for Virden Wind, LLC under GIA J1408, within the new 3-position ring bus named Virden. | IL | AMEREN ILLINOIS | GIP |  | 2026-07-01 | 138 | 8000000
East | 24450 | J1516 Generator Interconnection Network Upgrades | Install 120 kV breaker HF and associated disconnects rated at 40 kA. | MI | ITC | GIP |  | 2026-08-03 | 120 | 912475
East | 24451 | J1516 Generator Interconnection TOIF | Install required line entrance structure and 120 kV disconnect switch at the ITCT Fitz Substation. | MI | ITC | GIP |  | 2026-08-03 | 120 | 0
East | 50038 | Project Phoenix-Husky Substation | Install line tap on the Murphy-Orr Rd 1 138 kV line for the temp load. Expand Orr Rd station and constructs a new Murphy to Orr Rd 345 kV line and 345/138 kV transformer at Orr Road to support CE’s transformers and METC’s new transformer at Orr Rd. | MI | METC | Other | Local Needs | 2026-08-19 | 345 | 50252000
South | 50067 | J1686 Generator Interconnection on Coughlin - Plaisance 138 kV | J1686 Generator Interconnection of 100 MW solar facility on the Coughlin -Plaisance 138 kV line section. | LA | CLECO POWER LLC | GIP |  | 2026-09-01 | 138 | 18175765
South | 50090 | Wheatley 500kV: New POI J1710 J1819 J1820 J1821 | A new 500kV point of interconnection for GIA projects J1710, J1819, J1820, and J1821. This is for 300 MW of solar and 100 MW of Battery. The project will include a new 500kV interconnection substation that will be cut in on the KEO - Heth 500kV line. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-09-13 | 500 | 32354000
South | 50093 | Galet 500/230kV New Substation | Construct a new 500/230kV substation to serve a new customer on the West Memphis - Heth 500kV line. The substation will include two 1200 MVA autotransformers and a four 500kV breaker ring bus new 230kV lines extending to the customer 230kV station. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2026-09-30 | 500 | 142000000
Central | 50095 | Upgrade Stout CT - CT 4 and 5 Relaying | Upgrading the protection packages for generating units CT 4 and 5 and GSUs at Stout CT substation. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Local Reliability | 2026-09-30 | 138 | 300000
Central | 50096 | Upgrade Stout CT - CT Bus Relaying | Upgrading the protection packages for the bus section at Stout CT substation. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Local Reliability | 2026-09-30 | 138 | 150000
West | 25322 | 0890 Granite City - Crossroads Rebuild | Rebuild 3.7 miles 115 kV line from Granite City - Crossroads with new structures and new OPGW shield wire. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-15 | 115 | 4000000
West | 25289 | 0821 Highbridge - Miriam Park Refurb | Rebuild 3.3 miles 115 kV with new structures and new OPGW shield wire. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-31 | 115 | 4000000
West | 25434 | J1218/J1229 Network Upgrades at Sub 92 | Expand Substation 92 to interconnect generators J1218 and J1229 | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2027-06-30 | 345 | 4000000
Central | 25543 | J1381 Locomotive Solar POI | J1381 - 200MW Locomotive Solar: Greentown 230 - Expand 230 kV ring bus and add line terminal equipment | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2026-10-01 | 230 | 6666686
South | 50059 | Kinder 161kV: New POI J1558 | New 161kV switching station for the J1558 200 MW solar interconnection on the Moreland - St. Vincent 161kV line. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-10-01 | 161 | 14012000
West | 25358 | Burnsville Area Projects | Replace and relocate EEE (all new panels/relays/etc.). Soil correction at new EEE site, northwest fence line expansion, replacement of 5M197, addition of breakers with new 115 kV ring bus configuration on north end of substation. This ring bus configuration will prepare site for Pilot Knob to Burnsville line conversion to 115 kV in the future. | MN | GREAT RIVER ENERGY | Other | Local Needs | 2028-05-31 | 115 | 4000000
West | 25296 | Install Lawrence LAW TR02 | Install second 115/34.5 kV transformer with LTC at Lawrence substation. | SD | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-06-15 | 115 | 4158000
West | 50061 | CAPX Fargo-TC OPWG Replacement | Replacement of the existing OPGW on the Fargo line with. In conjunction with the LRTP 2 project the spans from MNN-ALS will also be replaced. | MN; ND | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-15 | 345 | 4280000
West | 25188 | ITCM Boone South 69 kV Substation Interconnection | Once ITC has converted the Grand Junction to Doud line from 34.5kV to 69kV through the work in ITCMW_16_60, IPL will retire its current Boone South substation and transfer its load to a new IPL Boone South station at a site ~0.7 miles away. IPL is requesting ITC to install a double bus with a two transformer template. IPL will initially install one 69/26.1kV 20/26/33 MVA transformer. ITC will install two line breakers and a bus tie breaker at the new site. ITC will also retire the tap to the old Boone South sub as well as retire pole top switches 2055 and 2057. | IA | ITC MIDWEST | Other | Load Growth | 2025-12-01 | 69 | 4363663
West | 25346 | ITCM Walcott 80 Substation Interconnection | IPL has notified ITC that they will be constructing a new Walcott 80 Substation which will replace their existing Walcott and Walcott North substations. The new substations will initially connect at 34.5 kV and then be converted to 69 kV as part of the Fulton – Dixon 69 kV conversion. IPL has requested ITC install two 69 kV busses with two line breakers and a bus tie breaker. New line taps for Walcott 80 substation to be constructed with T2-4/0 ACSR conductor. While operating at 34.5 kV, one new breaker looking toward Calamus 3350 should be operated as the new normal open point, with PTS 3372 becoming normally closed to allow the Walcott 80 load to be switched between the two 34.5 kV sources. Existing taps to Walcott and Walcott North to be retired under separate future EI Sketches prior to 69 kV conversion. | IA | ITC MIDWEST | Other | Local Needs | 2029-12-30 | 69 | 4475472
South | 50065 | J1576 Generator Interconnection on the Adams Creek - Angie 230 kV | Facilities required for the interconnection of J1576 on the Adams Creek - Angie 230 kV. | LA | ENTERGY SERVICES, LLC. | GIP |  | 2026-11-15 | 230 | 19725228
West | 25469 | Silver Lake Transformer Replacement | Replace existing 230/41.6 kV transformer with XXX MVA and replace associated breakers | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-12-31 | 230 | 4646984
Central | 22886 | Reconfigure Berkeley 138 kV substation | Age and condition maintenance: Replace Breakers: BERK-138 Pos. F; BERK-138 BT 1-2; BERK-138 BT 2-3 Add high side interrupting devices. Add line BRKs to Pos. D & J. | MO | AMEREN MISSOURI | Other | Age and Condition | 2026-12-01 | 138 | 39200000
Central | 25042 | Supernova 345 kV Substation for Perry County Solar (J1306) | This project will install a new 345 kV line position to serve as the Point of Interconnection for Perry County under GIA J1306, within the new 3-position ring bus named Supernova. | IL | AMEREN ILLINOIS | GIP |  | 2026-12-01 | 345 | 11000000
Central | 50044 | Hull-Marion-7324 Rebuild | Rebuild the 7 mile Hull-Marion-1690 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-01 | 138 | 5500000
Central | 24034 | Coffeen N. XFMR 2 Replacement | Replace Existing XFMR 2 at Coffeen North Substation with a new 345/138kV 700 MVA unit. | IL | AMEREN ILLINOIS | Other | Load Growth | 2026-12-01 | 345 | 6000000
South | 25501 | County Line 115kV Delivery Point | In order to serve the member delivery point, tap the Olive Oil Loop line with a 115kV Goab and construct a new line to the new delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2026-12-01 | 115 | 2160000
West | 25471 | St. Clair Tap Rebuild | BE-SC line - St. Clair 69-kV tap rebuild (4.5 miles) | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-12-30 | 69 | 4728756
Central | 25243 | Rockwood 138kV Aging Infrastructure and Line Breaker Addition | At Rockwood 138/34.5 kV substation, install three 138 kV line breakers on the Rockwood-Big River-1 line position H2, Gray-Rockwood-3 position H6, Gray-Rockwood-4 position H10 having a 2000 A continuous capability. | MO | AMEREN MISSOURI | Other | Local Reliability | 2026-12-01 | 138 | 3500000
South | 50197 | West Memphis 500/161kV Auto Replacement MPFCA | The existing 500/161kV autotransformer at West Memphis EHV will be replaced with a 600MVA rated autotransformer. Also, the 161kV breaker B2600 will also be replaced. All new relay panels will be installed. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-12-05 | 500 | 25506000
South | 25283 | Dolet Solar Replacement R1004 | Upgrade Dolet Substation for replacement generation interconnection for R1004 | LA | CLECO POWER LLC | GIP |  | 2026-12-15 | 345 | 19687305
West | 25205 | ITCM Meservey 69 kV Tap Rebuild | Rebuild the 6.9 mile Meservey Tap 69 kV line. New line should be rebuilt with T2-4/0 ACSR conductor. | IA | ITC MIDWEST | Other | Age and Condition | 2027-12-31 | 69 | 4766250
West | 50102 | University – Whitewater 138 kV (UNIG51), Partial Reconductor & OPGW | • Reconductor 3.54 miles of UNIG51 (University-Whitewater 138-kV line), increasing UNIG51’s ratings. This increase allows continuous operation of University generation at full capability after the University – Mukwonago 138-kV line contingency, prepares the corridor for future needs, and enhances operational flexibility in the area. • Install OPGW (24-strand retrofit) in the roughly 6.3 miles of UNIG51, contingent upon no structure replacements needed. OPGW addition completes the communication circuit and create a self-healing optical ring between University and Whitewater substations, leveraging both pre-existing fiber and the future OPGW. • Replace the two bus-side disconnect switches at University SS on both Line UNIG51 and Line UNIG52 • Project to be done in parallel with MTEP ID 24782 J1304 J1305 J1460 MPFCA Network Upgrades, which optimizes ATC’s expenditures and local generation outages. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2025-12-31 | 138 | 4825000
West | 25308 | ITCM Leon Rodeo 69 kV Substation Interconnection | IPL will construct a new 69/26.2kV substation, Leon Rodeo, west of the town of Leon and north of the existing Leon substation. For the ITC owned portion of Leon Rodeo, ITC will build a 69kV substation with two single boxes, two 69 kV line breakers, and a 69 kV bus tie breaker. ITC will also take the cap bank from the J2 bus of the Leon sub and relocate it to the Grand River bus section of the new Leon Rodeo substation. ITC will also build the line taps to connect Leon Rodeo to the Grand River-Leon and Leon-Saling circuits. Once the Leon Rodeo sub is put in-service, the existing Leon substation will be retired. | IA | ITC MIDWEST | Other | Load Growth | 2028-12-31 | 69 | 4860742
West | 25475 | Merricourt Reactor | Adding a 50 MVar reactor at Merricourt to support high voltages on the 230 kV when wind and load are low. | ND | MONTANA-DAKOTA UTILITIES CO. | BRP |  | 2026-12-31 | 230 | 5000000
West | 25378 | Gaylord Substation Rebuild | Rebuild Gaylord substation at a new location, converting 4.16kV feeders to 13.8kV. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-10-15 | 69 | 5100000
Central | 25279 | Replace Pole and Insulator Program - MTEP24 | Miscellaneous replacements requested by maintenance. Missouri and Illinois. | IL; MO | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-31 | 345 | 20000000
Central | 25403 | Newtonville T3, T2 and CB's Replacement | Replacing 161/138kV T3 transformer, 138/69kV T2 transformers, and several circuit breakers. Breaker replacements result in 138/69kV T1 transformers rating to increase. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 161 | 18500000
West | 23951 | Line Clearance Mitigation Program 2025 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2025. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2027-06-30 | 345 | 5400000
Central | 25442 | Z91-1 NW - Pigeon Creek Rebuild | Rebuilding ~3 miles of 138kV line from 795 to 954 | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 138 | 11000000
West | 25340 | Albany Second Transformer | Rebuild and relocate NSP's facilities on the west side of the Albany substation yard and install a second 69/12.5 kV transformer. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-10-15 | 69 | 5500000
West | 25206 | ITCM Lime Creek 161/69 kV Transformer Replacement | Replace the existing two 161/69 kV transformers T1 and T2 at Lime Creek with a new single 150 MVA 161/69 kV transformer with LTC. The new transformer will be installed at the current T2 location. T1 and its associated equipment will be retired. The existing high and low side breakers associated with T2 will be reused for the new transformer. | IA | ITC MIDWEST | Other | Age and Condition | 2026-12-31 | 161 | 5690194
West | 25422 | Airport Substation Breaker Addition | The Anoka County Highway Department is planning to expand Highway 65 and Great River Energy’s Highway 65 Switching Station is in the way and needs to be relocated. The switching station will be relocated just outside Connexus’ Airport Substation. This project will relocate the Highway 65 Switch to Connexus’ Airport substation by: 1. Building a breaker station at Connexus’ Airport substation 2. Rebuild the “CR” line from structures #158 (Highway 65 Switch) – #145 (CE Airport) to double circuit 69 kV – Will be a MN/DOT project | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2026-06-30 | 69 | 5692565
East | 24458 | Kenowa - J1527 TOIF - Install position FH35 and switch 177 | Install FH35 line entrance structure and disconnect switch 177 for generator interconnection. | MI | METC | GIP |  | 2026-12-31 | 345 | 0
East | 24516 | J1571 Generator Interconnection Network Upgrades | Install new Rouget 138 kV station. Install three 138 kV breakers rated at 40 kA and two new bus sections. Cut the Beecher - Pixley (Beecher - Morocco #1) 138 kV circuit into the new Rouget station. | MI | METC | GIP |  | 2026-12-31 | 138 | 8574899
Central | 25362 | Replace Breakers and Relays Program - MTEP24 | Miscellaneous breaker and relay replacements requested by maintenance. Missouri and Illinois. | IL; MO | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-31 | 345 | 5000000
West | 25381 | Long Siding - Princeton Area Projects | Rebuild OL line segment 1, BM line segment 3, and SS-2887 (Long Siding tap switch) | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-12-19 | 69 | 5728758
Central | 25393 | Chrisney 69/12kV T1 Replacement | Replacement of 69/12kV transformer at Chrisney substation | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 69 | 4000000
Central | 25397 | Tepe Park 138/15kV Transformer Addition | Adding 138/13.09kV 20MVA transformer and 15kV breakers | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 138 | 4000000
Central | 25444 | Y74 Azteca - VIP Pole Replacement | Replacing ~1 mile of poles for 69kV line from Azteca to VIP | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 69 | 4000000
East | 24536 | J1571 Generator Interconnection TOIF | Install required line entrance structures and 138 kV disconnect switch at the new Rouget station. | MI | METC | GIP |  | 2026-12-31 | 138 | 0
Central | 25407 | Angel Mounds CB and Switch Replacement | Replacing several 138kV circuit breakers and switches | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 138 | 3000000
Central | 25395 | Oakland City 69/15kV Xformer and CB Replacement | Replacing 69/15kV 5MVA transformer and several 69kV circuit breakers | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 69 | 2700000
East | 24557 | J1586 Generator Interconnection TOIF | Install required line entrance structures and 345 kV disconnect switch at the new Oxby station. | MI | METC | GIP |  | 2026-12-31 | 345 | 0
Central | 25404 | Winslow 69kV CB Replacement | Replacing 2 69kV circuit breakers at Winslow substation | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2026-12-31 | 69 | 1500000
Central | 50174 | New Customer X 138kV Substation | 200MW load is being looped into circuit 13853 Roxana to StatelineB circuit.(NIPSCO-CE) | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Load Growth | 2026-12-31 | 138 | 12000000
West | 25297 | Blue Heron Second Transformer | Install new 69/13.8 kV transformer with LTC at Blue Heron substation. Substation equipment at Blue Heron and Rich Spring will be reinforced to increase flow capacity on their feeders. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-10-15 | 69 | 5800000
West | 25190 | Badger SS Control House, Breaker, and Relay Asset Renewal | Asset Renewal of control house and contents, one circuit breaker, and replacement of various other relay panels to meet ATC standards. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-06-01 | 138 | 5900000
Central | 25333 | Westfield 156th St 69/12kV Sub | Westfield 156th St 69/12kV Sub (new sub) - Loop 69142 line through Sub; transfer 69155 wire to 5 new poles | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-12-31 | 69 | 3442000
West | 25286 | 0754 Buffalo - Maple Lake Rebuild | Rebuild 8.2 miles 69 kV from Buffalo - Maple Lake with new structures, new OPGW shield wire, and new conductor. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-15 | 69 | 6000000
East | 21786 | Vestaburg 69kV Relocation | The Vestaburg 69 kV Transmission Station was built in the late 1950s and is due for a major upgrade, including new ground grid and switches. To consolidate the transmission station, the transmission line terminations will be relocated across the road to the 138/69 kV transmission yard after expanding the 69 kV bus in the planned expansion area. As a part of this project the Vestaburg Distribution station will be moved from the Altona-Vestaburg line to the North Shade-Vestaburg line. The old Vestaburg 69 kV Transmission Station will be decommissioned. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2026-12-31 | 69 | 7500000
East | 25327 | METC Asset Replacement Program - 2026 | Replace aging and outdated equipment at a pace that will ensure each type of equipment is replaced near its projected end of life. | MI | METC | Other | Age and Condition | 2026-12-31 | 345 | 53960000
East | 25366 | ITCTransmission Asset Replacement Program - 2026 | Replace aging and outdated equipment at a pace that will ensure each type of equipment is replaced near its projected end of life. | MI | ITC | Other | Age and Condition | 2026-12-31 | 345 | 60700000
West | 25287 | W3402 Loyal - Spokesville Rebuild | Rebuild 8 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-31 | 69 | 6000000
West | 25288 | 0774 Goodview - Str 444 Rebuild | Rebuild 3 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-31 | 69 | 6000000
West | 50029 | SE Soteria Add 161 kV Breakers | Install six 161 kV breakers and associated equipment at SE Soteria Substation. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2026-06-01 | 161 | 6000000
South | 24694 | Coop Office Breaker Addition | AECC will be adding a sectionalizing breaker on Woodruff Electric's Coop Office to Colt 69kV line. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Local Reliability | 2026-12-31 | 69 | 2500000
West | 50030 | Johnson Creek Add 161 kV Breakers | Install six 161 kV breakers and associated equipment at Johnson Creek Substation. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2026-06-01 | 161 | 6000000
West | 25162 | Milwaukee Leased Dark Fiber Retirement Plan | Installation of 8+ miles of ATC Owned Underground (UG) Fiber to replace leased UG Fiber with Midwest Fiber Networks in Milwaukee Metro Area. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2027-12-31 | 0 | 6000000
East | 24574 | J1664 Generator Interconnection Network Upgrades | Expand Carrigan Substation and extend Bus 102 to start the J row. Install one 120 kV breaker and two disconnect switches rated at 40 kA. | MI | ITC | GIP |  | 2027-01-01 | 120 | 1969214
East | 25082 | J1664 Generator Interconnection TOIF | Install required line entrance structures and 120 kV disconnect switch at Carrigan Substation. | MI | ITC | GIP |  | 2027-01-01 | 120 | 0
East | 24556 | J1586 Generator Interconnection Network Upgrades | Install new Oxby 345 kV station. Install three 345 kV breakers and associated disconnects rated at 50 kA and two new bus sections. Cut the Argenta - Tompkins 345 kV circuit into the new Oxby station. | MI | METC | GIP |  | 2027-01-21 | 345 | 14487583
East | 25209 | Battle Creek-Oneida and Argenta-Tompkins Line Upgrades (J1586) - Network Upgrade | Install Row 31 by installing 3-345 kV breakers and associated disconnect. Install breakers 29R8 and 33F7 and associated disconnects. Cut the Battle Creek-Oneida 345 kV circuit into Oxby station using a conductor rated at least that of 2-1431 ACSR. Remediate the sag on the Oxby-Oneida 345 kV line to achieve a rating of at least 1327 MVA SN and 1327 MVA SE. Reconductor the Oxby-Tompkins 345 kV line with OPGW using 2-1431 ACSR conductor. | MI | METC | GIP |  | 2027-02-01 | 345 | 16178613
Central | 25526 | Terre Haute Project Tonic Water | Terre Haute Project Tonic Water new load: 130MW/43MVARs; located north of the Vigo Co. Industrial Park in the 13821 ckt; new 138kV line loop to be 954ACSS@200C; 138kV sub to be 7 breakers in a breaker and 1/2 layout; (2) dedicated customer-owned 138kV outlet lines to their load; (2) 36MVAR-138kV capacitors | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2027-03-01 | 138 | 35777500
West | 25165 | Glory Road - Oak St. 69 kV (GLNY41), Partial Rebuild | Rebuild and install OPGW on approximately 0.7 miles of line GLNY41 from Glory Rd SS towards Oak St SS. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-06-01 | 69 | 6000000
West | 24394 | Maple River-Buffalo River 69 kV Line Rebuild | Rebuild of 69 kV line from Maple River to Buffalo River. | MN; ND | MINNKOTA POWER COOPERATIVE, INC | Other | Age and Condition | 2024-12-31 | 69 | 6050000
West | 24922 | Forest Junction SS and Remote End Relay Asset Renewal | Scope of work combines work at Forest Junction with remote end work at Kaukauna Central, Lake Park, Melissa, and Tecumseh Rd. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-01 | 345 | 6480000
South | 25352 | J1833 Generator Interconnection | Interconnection of gas generator (J1833) at Leeville 115kV | LA | ENTERGY SERVICES, LLC. | GIP |  | 2027-04-01 | 115 | 17825000
West | 25424 | NE 6th St Substation and 161 kV line taps | Construct a new 161-13 kV substation and 161 kV taps | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-06-01 | 161 | 6500000
West | 25460 | Southridge Substation and 161 kV line taps | Construct a new 161-13 kV substation and 161 kV taps | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-06-01 | 161 | 6500000
South | 25215 | Andes 500/230 kV Substation | The Andes 500 kV four breaker ring bus station will cut into the existing Lakeover – McAdams 500 kV transmission line. Two 720 MVA autotransfomers (2 x 3 single phase 240 MVA autotransformers + 2 single phase spares) will connect the 500 kV ring bus to the 230 kV breaker and a half station. A 108 MVAR capacitor bank will also be added to the new 230 kV substation. Customer load will be fed out of (6) 150 MVA 230/34.5 kV transformers. | MS | ENTERGY MISSISSIPPI, LLC. | Other | Load Growth | 2027-06-01 | 500 | 158000005
West | 50026 | Kaukauna Central Tap - Melissa 138 kV (971K11), Rerate | Rerate line 971K11 to keep up with system demand. The thermal study identified issues that need to be fixed to bring the rating up to meet Operations and Planning needs. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2025-05-01 | 138 | 7000000
West | 25163 | Freeman - Presque Isle (X-118), OPGW Addition | Installation of 7.5 miles of OPGW to provide an alternate fiber path establishing two diverse fiber routes connecting into ATC larger OPGW Network Infrastructure. | MI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2026-12-31 | 138 | 7000000
West | 25437 | Substation 85: Convert to Ring Bus | Install 161 kV circuit breakers and bus work to convert Substation 85 to a ring bus configuration | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2027-12-31 | 161 | 7000000
West | 50017 | West Middleton - Str 36 69 kV (6967/6963), Rebuild Green Poles (CAC/CCA/SX) Replacements | Rebuild 2 miles of double circuit 6967/6963 from structure 36 to West Middleton. Install new structures, conductor, shield wire. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-10-01 | 69 | 7200000
West | 50112 | J1781 Hill Valley SS Network Upgrades and Interconnection Facilities | J1781 is a wind facility in Iowa and Lafayette County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2030-03-10 | 345 | 7219000
East | 21968 | Delaney 138 kV Station Rebuild | The new Delaney 138 kV station will be rebuilt as a compressed four breaker ring bus configuration. Install new control house. Install (3) 138 kV, 3000 A breakers with at least 40 kA interrupting. The summer emergency rating of all new equipment should be no less than 644 MVA/2693 amps. | MI | METC | Other | Age and Condition | 2027-06-01 | 138 | 8632000
South | 25455 | Amite South/DSG Reactive Support Project | •Addition of reactive support in the form of capacitor banks at 3 substations. ·Gypsy 230 kV – 2 x 81.4 MVAR ·Peters Road 230 kV – 1 x 81.4 MVAR ·Munster 230 kV – 1 x 81.4 MVAR | LA | ENTERGY SERVICES, LLC. | Other | Local Needs | 2027-06-01 | 230 | 21100000
East | 25522 | Oakland 138 kV Station Rebuild | The new Oakland 138 kV station will be rebuilt as a compressed four breaker ring bus configuration. Replace 50MVAR w/2x 25 MVAR cap banks on separate buses with new synchronous breakers. | MI | METC | Other | Age and Condition | 2027-06-01 | 138 | 8294000
East | 24998 | Pontiac 345 kV Station - Extend Buses and Add A Row | Extend bus 303 and construct a fifth breaker and a half row for terminating Transformer 301 and Transformer 303 into breaker and a half positions. All breakers should be 3000 A, 63 kA breakers. Fitz-Pontiac 345kV line termination will be moved from position BQ to position AQ. Transformer 301 will be terminated at Pos AI. Transformer 303 will be terminated at Pos BQ. Remove breakers from Row E, replacing disconnect switches, and upgrade replaying as necessary to accommodate new configuration. | MI | ITC | Other | Local Needs | 2027-06-01 | 345 | 8274000
South | 25457 | PCI 69 kV Breaker Upgrades | Replace PCI 69 kV Breakers 8220, 8225 and 8230 with 40kA breakers. | LA | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2027-06-01 | 69 | 2730000
South | 25470 | Sunrise 230 kV New Station | Cut a new 230 kV station named Sunrise on the Wells to Labbe 230 kV line. Install distribution facilities to serve load currently served from the existing Sunset 69 kV station. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2027-06-01 | 230 | 39600000
South | 25468 | Southline to Jacinto 138 kV New Line | Construct a new ~6 mile 138 kV line between Jacinto and Southline 138 kV stations. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2027-06-01 | 138 | 40700000
West | 25258 | Prior TR02 And Feeder | Install second 115/13.8 kV transformer and associated equipment. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2026-06-15 | 115 | 7280000
East | 25223 | Lulu - Construct 345 kV Station - Multiple Generator Interconnect Network Upgrade | Construct the Lulu 345 kV switchyard. Cut in the Lemoyne-Maple and Milan-Monroe-Morocco lines into the new station. | MI | ITC | GIP |  | 2027-06-11 | 345 | 29916928
East | 25244 | Morocco - Replace RH34 Relaying - Multiple Generator Network Upgrade | Construct the Lulu 345 kV switchyard. Cut in the Lemoyne-Maple and Milan-Monroe-Morocco lines into the new station. | MI | METC | GIP |  | 2027-06-11 | 345 | 319323
West | 25104 | 2nd St. Tap - 30th Ave. 69 kV (N-14), Partial Rebuild | Rebuild and install OPGW on approximately 1.5 miles of N-14 from Structure 145364 to 30th Ave. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-11-01 | 69 | 7500000
West | 24375 | Center-Maple River 345 kV Foundation Restoration | Replacement of aging structures and concrete foundations on the Center - Maple River 345 line. | ND | MINNKOTA POWER COOPERATIVE, INC | Other | Age and Condition | 2028-12-31 | 345 | 7550000
West | 25445 | Prairie Woods to Sunburg Rebuild | Rebuild Sunburg to Prairie Woods Switch 69 kV line. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-12-31 | 69 | 7649388
West | 25321 | Winnebago City Substation Interconnection | BENCO/GRE has notified ITC that they will be retiring the existing Winnebago Local substation and replacing it with a new Winnebago City substation which will consolidate all the BENCO load onto one substation. As part of this, ITC will be retiring the transmission portion of the Winnebago Local substation and constructing the transmission portion of the new Winnebago City substation. ITC will construct a new 4 line terminal bus with one BENCO transformer position, with provisions to accommodate a 2nd BENCO transformer and future bus tie breaker. | MN | ITC MIDWEST | Other | Local Needs | 2025-10-31 | 69 | 7915596
East | 24463 | Greenwood-Rapson#1 - J1557 Generator Interconnection (Cribbins) - Network Upgrade | Build a new 345 kV 3 breaker ring substation cut in from the Greenwood – Rapson #1 345kV line. | MI | ITC | GIP |  | 2027-07-01 | 345 | 13994489
East | 24494 | Cribbins-J1557 TOIF- Install position CQ and switch CQA | Install CQ line entrance structure and disconnect switch CQA for generator interconnection. | MI | ITC | GIP |  | 2027-07-01 | 345 | 0
South | 24960 | Legend to Sandling 230 kV Circuit 2 Project | Construct a new ~7.6 mile 230 kV Legend to Sandling Ckt 2. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2027-07-31 | 230 | 77320000
West | 16289 | Bemidji 115/12.5 kV Substation | New Bemidji 115/12.5 kV Substation design with express feeders and source transfer, one transformer 37MVA. This is a multi-year project. In the event that a new transformer will not fit in the original substation, the 115 kV line will be tapped just outside the substation. | MN | OTTER TAIL POWER COMPANY | Other | Load Growth | 2025-12-31 | 115 | 8000000
West | 24842 | Atlantic – Osceola 69kV (Laurium2), Re-insulate | Replace crossarms at ~140 structures with new insulators, replace select structures, obtain rights for gaps along existing corridor, and complete vegetation management activities. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-31 | 69 | 8100000
East | 50151 | Sphinx 138 kV Station | METC to build a new station as a 138 kV four-row breaker-and-a-half configuration to serve 255 MVA new load. Rebuild 2.5 mile of Gaines – Plaster Creek to DCT 1431 ACSS and install OPGW. Gaines 138 kV station rows 7 and 11 will be expanded. | MI | METC | Other | Load Growth | 2027-09-01 | 138 | 32810000
East | 24477 | Gaines - Thompson Road 138kV - J1292 GIA (Peddler) TOIF | Connect generator at position BM6 as TOIF. | MI | METC | GIP |  | 2027-09-29 | 138 | 0
West | 10001 | OTP Voltaire 115 kV Substation | Tap Xcel's 115 kV line between GRE McHenry and Magic City and build a new 115/41.6 kV substation in the Voltaire area. Install three 115 kV breakers and three 41.6 kV breakers. Install one 56 MVA 115/41.6 kV transformer. | ND | OTTER TAIL POWER COMPANY | Other | Local Needs | 2026-12-31 | 115 | 8100000
West | 25164 | Menominee - 30th Ave. 69 kV (Y-199), Rebuild | Rebuild and install OPGW on approximately 1.3 miles of line Y-199 from Menominee SS to 30th Ave. SS. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-06-01 | 69 | 8400000
West | 9997 | OTP Rolette 230 kV Substation | Tap Xcel's 230 kV line between Rugby and Peace Garden and install 230/115/69 kV Transformer - Install three 230 kV breakers and two 69 kV breakers, and install one 230/115/69 kV Transformer (140 MVA) leaving the 115 kV winding disconnected. | ND | OTTER TAIL POWER COMPANY | Other | Local Needs | 2026-12-31 | 230 | 8700000
West | 50041 | West Junction SS 138 kV Sectionalizing | • Add a 138 kV bus with two-line breakers and a bus tie breaker and associated facilities at West Junction substation to provide for the required sectionalizing facilities, • Retirement of the West Junction Tap to Bluemound portion of 138 kV line 5066 and associated facilities in coordination with the Milwaukee Area 230 kV conversion to 345 kV Project, • Modification of the protection scheme and implement required networking protection. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2026-12-31 | 138 | 8700000
Central | 50045 | Austin Transformer 3 Replacement | Replace transformer 3 at Austin Substation which is AIC owned. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2027-12-01 | 345 | 6800000
Central | 22872 | Upgrade Macomb NE 138 kV substation | Add line breaker on the Macomb West line | IL | AMEREN ILLINOIS | Other | Age and Condition | 2027-12-01 | 138 | 1800000
South | 25489 | North Lucedale 69kV Delivery Point | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2027-12-01 | 69 | 6399100
West | 25547 | Blind Lake Breaker Addition | Remove switch 58NSM4 and replace with a circuit breaker. Replace existing breakers B1 and B2. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-12-30 | 69 | 8777667
Central | 25276 | Conway 138kV Add Breakers and Aging Infrastructure | Add interrupting devices on XFMRs 1,2,3,4 Add Line BKRs to MASN-WLDW-1&2, CNWY-TYSN-3&4 Aging infrastructure replacements | MO | AMEREN MISSOURI | Other | Local Reliability | 2027-12-01 | 138 | 17500000
West | 25000 | Lakefront SW YD – Revere Dr 69 kV (D-104), Partial Rebuild | Rebuild and install OPGW on approximately 1.84 miles of D-104 form Lakefront to Revere Dr. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-10-01 | 69 | 9000000
West | 25342 | Missouri Creek Substation | Rebuild Eau Galle distribution substation as new Missouri Creek substation and convert existing Eau Galle distribution to 23.9kV. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2029-06-01 | 69 | 9000000
West | 50036 | J1304 Big Hill Park SS Network Upgrades and Interconnection Facilities | Solar farm in Rock County, Wisconsin. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2023-07-31 | 138 | 9112672
South | 25430 | Fairview to Madisonville 230 kV Upgrades | Upgrade Fairview to Madisonville 230 kV circuit to at least 2000 Amps. This includes conductor on this 0.2 mile facility. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2027-12-01 | 230 | 700000
South | 25410 | Winshire 69 kV Capacitor Banks | Install two 11 MVAR capacitor banks at the Winshire 69 kV station. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2027-12-01 | 69 | 7000000
West | 25338 | Victor to Woodland Rebuild Projects | Rebuild about 14.4 miles of 69 kV line from Victor to the DX line. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-12-01 | 69 | 9303114
South | 50160 | J1672 Network Upgrades: Gerald Andrus 230kV Auto | Install a second 230/115 kV 392 MVA Autotransformer. The second autotransformer bank install will also require installing new protection panels per current Entergy standards. Installation of a double bus double breaker bay scheme at the 230 kV yard and a transfer bus configuration bay scheme on the 115 kV yard will be required. This project will also require the removal of the existing oil circuit breaker J7202 and installation of a new 115 kV bus tie breaker. | MS | ENTERGY MISSISSIPPI, LLC. | GIP |  | 2027-12-15 | 230 | 19750000
West | 50110 | J1751 Young St SS Network Upgrades and Interconnection Facilities | J1751 is a solar facility in Wood County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-09-10 | 138 | 9703000
West | 25506 | Inver Grove – Inver Hills 115 kV Rebuild to Double Circuit 115 kV | Rebuild 2.2 miles 115 kV line 5507 to double circuit from Inver Grove - Inver Hills. Expand Inver Hills substation. Add 1 breaker at Umore substation. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-31 | 115 | 10000000
West | 25270 | 0760 Redwing - Lake City - Str 217 Rebuild | Rebuild 18 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-31 | 69 | 10000000
Central | 25443 | Z84-1 Culley - Dubois Rebuild | Replacing ~ 33 miles of poles for the 138kV line from Culley to Dubois | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2027-12-31 | 138 | 47500000
West | 25348 | Saratoga – 7 Mile Creek 138 kV, Construct New Line | Interim configuration: • Construct a new Saratoga – 7 Mile Creek (X-New) 138-kV line, double-circuiting it with existing Saratoga – ACEC Grant (Y-301) 69-kV line. • At 7 Mile Creek SS, relocate existing 7 Mile Creek – Sand Lake (X-11) 138-kV line to connect the new line at existing X-11’s terminal. In addition, construct a new section of approx. 0.05 miles on X-11 for its interconnection to bus 4, eliminating the need for 138-kV crossings. Finally, install new 138 kV substation equipment (breaker and switch) at 7 Mile Creek to complete its 4-position ring bus. • At Saratoga SS, install one 138-kV line circuit breaker with manual line and bus-side disconnect switches for the new line. In addition, install a new 138-kV bus-tie breaker and replace Saratoga – Badger West (X-43) 138-kV line jumpers, and buses 1 and 2 jumpers, to allow higher ratings on existing facilities. Finally, reroute X-159 line preventing it from being above the new line’s terminal. Final configuration: • After Northern Adams County Area Network Improvement Project is placed in service in 2027, retire Saratoga 138/69-kV T33 transformer and re-terminate the new line with this vacated position. This will prevent the new line passing over its existing box structure. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2027-12-31 | 138 | 10300000
West | 50042 | Substation Technology Package #2 - 2025 | The Substation Technology Package #2 (SSTP#2) program of work will set the stage for the future of the digital substation field worker by providing enhanced Business Capabilities over ATC’s substation fiber network infrastructure. The SSTP#2 – 2025 project scope will include the following technology enhancements: • Installation of Wireless Access Points (AP) at various ATC substations • Installation of Cyber Security fortifications for Rogue Device detection at various ATC substations • Convert select Telecom equipment to DC power at various ATC substations | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2025-12-31 | 0 | 10500000
West | 25247 | ITCM Abbott - Marshalltown 161 kV Rebuild | ITC will rebuild the Pheonix/SD and Rail portions of Abbott – Marshalltown 161kV circuit with T2-Grosbeak. | IA | ITC MIDWEST | Other | Age and Condition | 2028-12-31 | 161 | 10762500
West | 25220 | Cuba City South, DIC, Sub Expansion | • ATC will construct 0.63 miles of new 69 kV line. • ATC will rebuild 1.12 miles of the existing Cuba City South Tap as a new double circuit 69 kV line to provide a loop-through connection to the Cuba City South Substation. • ATC will construct a loop-through, straight bus substation with two 69 kV line breakers. • Cuba City will install a 69/12.47 kV transformer at Cuba City South. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-12-31 | 69 | 11000000
Central | 25450 | Rebuild Breiner-Spring Lake Jct. 69 kV Line | Rebuild Breiner-Spring Lake Jct. 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2027-12-31 | 69 | 5500000
West | 25226 | Union Townline, DIC, Sub Expansion | • ATC will construct an approximately 0.08 mile 69 kV transmission line extension from the Bass Creek-Sheepskin 69 kV line (Y-158) to the Union Townline substation for a networked substation feed. • ATC will construct a 69 kV loop-through straight bus with line breakers, associated switches, and space reserved for a potential bus-tie breaker. • Evansville Water & Light (WPPI) to install a second 69/12.47 kV transformer with high side circuit switcher protection and necessary low side bus equipment. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2026-11-01 | 69 | 11600000
West | 21767 | 13 Line Rebuild | Rebuild Portage Lake - Riverton ("13 Line") 115 kV Line. The project will also add shield wire and OPGW for operations and relay improvements. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2027-03-31 | 115 | 12000000
East | 25230 | Manning #2 345-138 kV Transformer Replacement | Replace the Manning #2 345/138 kV transformer with at least 650 MVA (2718 Amps) summer emergency rated transformer. Also install a new high side 3000 Amps disconnect switch. | MI | METC | Other | Age and Condition | 2027-12-31 | 345 | 7060000
East | 25208 | Brownstown #304 345-120 kV Transformer Replacement | Replace the Brownstown #304 transformer with a standard 345/120 kV, 560MVA (approx. 715MVA Summer-Emergency rated) transformer. | MI | ITC | Other | Age and Condition | 2027-12-31 | 345 | 6572000
East | 25218 | Sterling #201 230-120 kV Transformer Replacement | Replace the Sterling #201 230/120 kV transformer with a transformer of at least 728 MVA (3503 Amps) summer emergency rating. Install a breaker and associated equipment on the high side of the transformer. | MI | ITC | Other | Age and Condition | 2027-12-31 | 230 | 7950000
Central | 25290 | Sprott 69/12kV Substation | Construct New Sprott 69/12 kV Substation to serve new load and relieve nearby delivery points | MO | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2027-12-31 | 69 | 1200000
East | 25277 | METC Customer Interconnections - 2027 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI | METC | Other | Load Growth | 2027-12-31 | 345 | 2500000
West | 25337 | Meadowbrook to Side Lake Area Projects | Rebuild Meadowbrook to Side Lake line, replace Meadowbrook and Side Lake switches. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-12-01 | 69 | 12124891
East | 25364 | ITCT Customer Interconnections - 2027 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI | ITC | Other | Load Growth | 2027-12-31 | 345 | 2500000
Central | 25560 | Centerton-Wilbur New 69kV Line and Upgrades | Construct a new 5.8 mile 69kV line between Hoosier's Wilbur station and DEI's Centerton station. Upgrade approximately 18 miles of 69kV line around the Mooresville, IN area, including the following branches: 07Wilbur-07Nelson, 07Nelson-07WilburJct, 07WilburJct-07Moores, 07WilburJct-07HartLake, 07HartLake-08MoorJct, 07Moores-08ToytJct. | IN | HOOSIER ENERGY | Other | Local Reliability | 2027-12-31 | 69 | 34650000
Central | 23374 | New Babylon 138/69 kV Substation and Lines | 1) New 138 kV line to interconnect Babylon substation to a new Ameren Steamboat ring bus 2) New Babylon 138/69 kV substation 3) New Babylon-Canton 69 kV line 4) New Babylon-Ellisville/Smithfield double-circuit line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2027-12-31 | 138 | 18320000
Central | 23373 | New Industry-Ipava 69 kV Line | 1) New Industry-Table Grove 69 kV line 2) New Table Grove-Ipava 69 kV line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2027-12-31 | 69 | 15700000
West | 25423 | Fox Lake Area Upgrades | Rebuild FE-FD line, the Fox Lake switching station, and the Dunnell switch. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-09-30 | 69 | 12469907
West | 25429 | Liberty Substation 161-69 kV Expansion and Associated Lines | Construct second 69 kV line into Terra Substation, expand Liberty Substation to install a 161-69 kV, 125 MVA transformer and 69 kV bs and rebuild the existing Neal North-Terra 69 kV line. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2027-12-01 | 161 | 12500000
West | 50152 | Ellendale load 3 addition | MDU has a third load request at Ellendale, ND for an additional 125 MW. MDU will serve this load from the Ellendale Data Center Substation that is being built as part of MTEP project 50037. An additional 230 kV line will be added that will run from the Ellendale Substation to the Ellendale Data Center Substation. An additional 230/34.5 transformer, 230 kV breakers and 34.5 kV breakers will be added at the Ellendale Data Center Substation. | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Load Growth | 2025-09-01 | 230 | 12575738
West | 25222 | J1432 GIA NU New Bryant 345 kV Switch Station | A new Bryant 345 kV, 3 breaker, ring-bus switching station will be constructed for the interconnection of project J1432. The Salem to Rock Creek 345 kV line will be opened and 2 dead-end structures will be installed to allow the line to be looped through the Bryant 345 kV switching station and dual fiber will be needed to Rock Creek from the new substation.¿ And upgrades required to install fiber at Rock Creek. | IA | ITC MIDWEST | GIP |  | 2028-09-01 | 345 | 12787112
West | 25300 | Nobles County Third Transformer | Add third 345/115 kV transformer with tertiary reactor at Nobles County. | MN | NORTHERN STATES POWER COMPANY | BRP |  | 2028-05-01 | 345 | 13250000
South | 25520 | South Lucedale 69kV Delivery Point | In order to serve the member delivery point economically and reliably, a new 2.7-mile radial line will be constructed from the Lucedale 69kV Switching Station to the member delivery. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2028-03-01 | 69 | 6477100
West | 25448 | Browns Woods Substation and 161 kV lines | Construct a new 161-13 kV substation and 161 kV lines and retire 63rd & Park Substation and 69 kV lines | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2026-12-01 | 161 | 13400000
West | 25374 | Blackberry Area Rebuild Projects | Rebuild 69 kV lines in Blackberry area along with switch replacements. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-12-10 | 69 | 14260525
Central | 25350 | New Waynesville 345kV Station | A new transmission station South of Walesboro, IN will be built to support load growth and reliability in the Walesboro Area. The station will be a 345 kV to 69 kV station. The station will feature a 345 kV ring bus design with 4 breakers and two 345 kV :69 kV transformers. The project also includes new 69kV lines from the Waynesville Transmission Station to Ogilville, Walesboro Industrial Park, and Woodside. The existing 2-mile Ogilville tap line will be rebuilt to support the new 69kV transmission loop. | IN | HOOSIER ENERGY | Other | Local Reliability | 2028-05-31 | 345 | 58160000
East | 50060 | Bismarck - Macomb 120 kV Line | Construct a new 120 kV line (~6.7 miles) from Bismarck to Macomb. Approximately 3.9 miles of this new circuit will be using new 954 ACSR conductor, 2.7 miles of which will be strung on the vacant side of existing Lenox - Stephens 120 kV structures and the other 1.2 miles will be on new ROW. The remaining section from the west-to-east crossover point toward Macomb (2.8 miles) will utilize existing 795 ACSR conductor through undoing 6-wire on the Macomb - Stephens 120 kV circuit. This new 120 kV line will require installations of a new 120 kV breaker at Bismarck and Macomb stations. | MI | ITC | BRP |  | 2028-06-01 | 120 | 11160000
East | 20017 | Rebuild Alma (Cheesman) - Regal #1 138 kV | ITC is to rebuild approximately 1.34 miles of the Alma (Cheesman) – Regal #1 138kV with 954 ACSR 138kV double circuit standards with OPGW and upgrade terminal station equipment at Regal. | MI | METC | BRP |  | 2028-06-01 | 138 | 18031000
East | 15831 | Alma - Regal #2 138 kV Rebuild | Rebuild ~3.8 miles of the ~5.8 mile-long Alma – Regal 2 138 kV line to 138 kV double circuit standards construction by replacing the existing assets (all structures and 336 ACSR conductor) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. Relocate CE's 46kV circuit to the under-build and leave the vacant 138 kV side of the new structures for future transmission use. | MI | METC | BRP |  | 2028-06-01 | 138 | 11311000
East | 22015 | Blackstone – Leoni #1 and #2 138 kV Rebuild | Rebuild approximately 4.2 miles of circuits #1 and #2 from Blackstone 138 kV to Leoni 138 kV to 954 ACSR conductor using 138 kV double- circuit structures. Install OPGW. Upgrade station equipment at Blackstone to at least 431 MVA (1804 Amps) summer emergency rating. The Blackstone – Leoni #2 138 kV circuit currently shares towers with both the Blackstone – Leoni #1 and #3 138 kV circuits. This project moves the Blackstone – Leoni #2 138 kV circuit entirely on to the Blackstone – Leoni #1 138 kV double-circuit structures. | MI | METC | BRP |  | 2028-06-01 | 138 | 9840000
East | 22018 | Blackstone – Leoni #3 138 kV Rebuild | The proposed solution is to rebuild approximately 4.2 miles of the Blackstone – Leoni #3 138 kV line using 954 ACSR on double circuit structures constructed at 138kV Standards, with future double circuit on the northeast side of the towers. Install OPGW along the entire length from Blackstone to Leoni. | MI | METC | BRP |  | 2028-06-01 | 138 | 8405000
East | 25217 | Blendon 138 KV Capacitor | Install (1) 33.33 MVAR capacitor bank with associated 138kV, 40 kA synchronous breakers and disconnect switch at the Blendon 138kV substation. The proposed capacitor will be connected to bus 40 and Transformer 1 will be moved to Bus 50. Relocate the existing Blendon-Campbell 138kV line termination from bus 30 to the bus 60. Also, Relocate the existing Blendon-Fairview 138kV line termination from bus 60 to the section 30 bus. | MI | METC | BRP |  | 2028-06-01 | 138 | 4260000
East | 20034 | Sag Remediate Higgins - Mio Dam 138 kV | The proposed solution is to remediate sag limit on the 266.8 ACSR on the Higgins – Mio Dam 138kV line up to the conductor’s limit. | MI | METC | BRP |  | 2028-06-01 | 138 | 2800000
East | 20119 | Sag Remediate Claremont - Cornell #2 138 kV | METC is to raise the sag limit on the 477 ACSR to 257F and 795 ACSR to 178F on the Bell Road – Cornell section of the Claremont - Cornell #2 138 kV Line | MI | METC | BRP |  | 2028-06-01 | 138 | 1263000
East | 14344 | Airport - Hillman Tap 138 kV Sag Remediation | Remediate the sag limit on ~17.0 miles of 266 ACSR conductor of the ~21.3 mile-long Airport - Hillman Tap 138 kV section of the Airport - Mio 138 kV line to at least the planned target summer normal/summer emergency rating of 133 MVA/556 Amps. | MI | METC | BRP |  | 2028-06-01 | 138 | 1061250
East | 18072 | Sag Remediation Hubbard Lake – Spruce Road 138 kV | Remediate the sag on the Hubbard Lake – Spruce Road section of the Alpena – Iosco 138kV line to at least 124 MVA for summer emergency rating. | MI | METC | BRP |  | 2028-06-01 | 138 | 700000
East | 25216 | Gaines - Caledonia Jct. 138 kV Sag Remediation | Remediate sag on the 795 ACSS up to 153 MVA (summer ratings) on the Gaines – Caledon J. section of the Thompson Road – Gaines 138 kV circuit. | MI | METC | BRP |  | 2028-06-01 | 138 | 520000
West | 25325 | 0986 K Frame Replacement | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0986. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-31 | 345 | 15000000
West | 25341 | 0987 K Frame Replacement | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0987. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-31 | 345 | 15000000
East | 50121 | Iosco - Karn 138 kV Relocation (#50064 Alternative) | Utilizing the existing vacant side of the Twining – Whittemore and Shale - Twining to string East Tawas - Quarry and Quarry - Karn 138 kV circuits on these double-circuit structures with 954 ACSR and also install OPGW. Construct ~1.5 mile from Cottage Grove to a new location a new ROW. Replace station equipment East Tawas and Cottage Grove substations. CE to tap their existing Santiago and Seven Mile stations to the new conductor on Quarry – Cottage Grove 138 kV line. ITC’s Asset Management Department identified this line for rebuild due to the age and condition of the line. Rebuilding approximately 46 miles of the Iosco-Karn 138kV line would reduce equipment failures, unplanned outages and repair costs. Ultimately, increasing reliability of the system and bringing the line up to the current line design standards. Additionally, rebuilding this circuit with 954 ACSR conductor will increase system capacity to support the increasing load and renewable generator interconnections around the Arenac, Bay, and Iosco counties. | MI | METC | Other | Age and Condition | 2028-06-01 | 138 | 45060000
South | 13905 | Burnside 230-115 kV Autotransformer | 1) Construct a 3 breaker 230 kV ring bus at Burnside, Minimum of 2000 Amp equipment. 2) Cut in and out the Conway to Panama 230 kV line. 3) Install 230-115 kV Autotransformer 4) Install 115 kV low side breaker at Burnside. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2028-06-01 | 230 | 34260000
East | 25195 | MCV 345-138 kV Transformer Addition | Install six 345 kV breakers to convert the 345 kV side to ring-bus. Expand MCV 138 kV buses, replace 10 existing breakers, and install 3 additional breakers to the west as depicted in the diagram to accommodate the 3rd XFMR at MCV. Install a new 345/138 kV transformer and terminated it at the newly created 345 & 138 kV positions. | MI | METC | Other | Local Reliability | 2028-06-01 | 345 | 36750000
East | 25198 | Port Calcite 138 kV Station Rebuild | Rebuild Port Calcite into a four (4) position ring bus configuration that can be converted to Breaker and a half in the future. The new substation is located to the Northwest of existing station. | MI | METC | Other | Local Reliability | 2028-06-01 | 138 | 9811000
South | 50139 | J1818 Generator Interconnection at Moss 69kV Station | Interconnection Facilities required for the interconnection of J1818 at Moss 69 kV Station | LA | LAFAYETTE UTILITIES SYSTEM | GIP |  | 2028-06-30 | 69 | 993000
West | 25461 | Johnson Creek - Maffitt Lake 161 kV line | Construct a new 161 kV line | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-08-01 | 161 | 15300000
West | 50037 | Ellendale load 2 addition | MDU has an additional load request at Ellendale, ND for a total demand of 225 MW. MDU will serve the customer from its Ellendale 345 substation from the 230 kV. A 230 kV line will run to a new sub where a 230/34.5 transformer will be added along with the 34.5 kV breakers. | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Load Growth | 2024-09-01 | 230 | 16776939
West | 25449 | Norwoodville Substation and 69 kV lines | Construct a new 69 kV switching substation and lines | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2027-12-31 | 69 | 16900000
West | 25503 | MDU Network and Interconnection Upgrades - J1040 | A 250 MW wind project (J1040) is interconnecting at MDU's Wishek 230 kV substation as part of DPP 2018 study cycle. The project has been assigned the following network and interconnection upgrades. Wishek substation - terminal equipment to interconnect project (PCB, Disconnects, bus work) Mandan-Napoleon 230 kV line - terminal equipment (Re-tap CTs Mandan and jumpers at Napoleon) Wishek-Merricourt 230 kV line - reconductor and pole replacement Merricourt Substation - Add another breaker and re-terminate one of the 230 kV lines Ellendale Substation - 115 kV terminal equipment for line to Aberdeen | ND | MONTANA-DAKOTA UTILITIES CO. | GIP |  | 2026-10-01 | 230 | 18115000
West | 22911 | Load Interconnection Program 2025 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2025. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-30 | 345 | 19000000
West | 25428 | New Shenandoah Substation and 69 kV lines | Construct a new 69-13 kV substation and 69 kV lines | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-12-31 | 69 | 19100000
West | 25433 | J1270 POI New 345 kV Interconnection Substation and 345 kV Line Taps | Construct new 345 kV POI substation and 345 kV line taps for J1270 wind farm | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2025-09-18 | 345 | 19500000
West | 25498 | J898 Generation Interconnection Network Upgrades | J898 will require a 4-breaker, 161 kV ring bus for a POI | MN | DAIRYLAND POWER COOPERATIVE | GIP |  | 2027-09-01 | 161 | 19574516
West | 50111 | J1773 Edmund Swt St Network Upgrades and Interconnection Facilities | J1773 is a wind facility in Lafayette County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2030-03-10 | 345 | 19693000
South | 25419 | Hermanville 115kV Delivery Point | In order to serve the member delivery point, tap Utica Loop line with a 115kV Goab and construct a new line to the delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2028-11-01 | 115 | 700000
West | 25456 | Spring Creek Upgrade Projects | Spring Creek - transformer replacement and upgrade | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2029-12-31 | 161 | 19992124
South | 25432 | Cypress to Legend 500 kV line | Construct a new ~35 mile 500 kV line between Cypress and Legend 500 kV stations. Expand the Cypress and Legend stations to accommodate the new facilities. Build a 500 kV station at Legend, and install a 500-230 kV Autotransformer. Upgrade Kolbs 69 kV breakers 2870 and 209. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2028-12-01 | 500 | 405900001
South | 25435 | Serpent to Tupper 69 kV Upgrade | Upgrade 69 kV bus at Tupper. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2028-12-01 | 69 | 1200000
Central | 25284 | Rebuild Salem Bulk to Seminary 69kV Line T10 | Rebuild 29.54 miles of 69kV between Salem Bulk and Seminary. Voltage issue fix from Long Range Study. | MO | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Age and Condition | 2028-12-31 | 69 | 60000000
Central | 25458 | Gibson 345kV Ckt Brkr Upgrades | Gibson 345 CB upgrades - TPL-001 short ckt overduty - replace (18) 345kV-63kA interrupting rated CBs with 80kA; replace breaker disconnect switches and upgrade bus conductor as needed. ALTERNATIVE: add neutral to ground fault current limiting reactors on Gibson Units 1 and 2 GSUs (6 ohms) currently under consideration. | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2028-12-31 | 345 | 27000000
West | 25345 | ITCM Cleveland to Sheas Lake Rebuild | ITC will rebuild approximately 10 miles of the Cleveland to Sheas Lake 69 kV line. The line will be rebuilt to 115 kV or 161 kV Standards with T2-477 ACSR and OPGW. | MN | ITC MIDWEST | Other | Age and Condition | 2029-12-30 | 69 | 22306250
Central | 25268 | Replace 345-138 kV Petersburg East & West Autos | Replacement of the Petersburg 345/138 kV 300 MVA autotransformers with 500 MVA autotransformers. Project scope includes adding redundant relaying to each autotransformer. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2028-12-31 | 345 | 12000000
East | 50098 | Hagensville Junction Interconnection | Interconnect Wolverine's Hagensville Junction with METC's Rockport to Port Calcite line. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | BRP |  | 2028-12-31 | 138 | 17550000
West | 50184 | Elm Road Generation POI Relocation Project | Driven by WEC’s Generating Facility Modification Request to relocate Elm Road generation POIs, this project will expand Elm Road 345 kV substation breaker and a half configuration with three new rungs and six new 345kV breakers. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2026-06-30 | 345 | 22600000
West | 25399 | Congestion Mitigation Projects | The facilities included in this project are being upgraded to achieve higher ratings to mitigate market congestion caused by these facilities. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2028-02-01 | 230 | 23452560
Central | 25440 | Vigo Coal 69/12kV Xformer and CB Replacement | Replacing 69/12kV transformer and circuit breakers | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2028-12-31 | 69 | 6000000
West | 23706 | 158 Line Rebuild | Rebuild Portage Lake - Cromwell ("158 Line") 115 kV Line. The project will also add shield wire and OPGW for operations and relay improvements. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2027-03-31 | 115 | 25000000
Central | 25147 | Mead Johnson 69/12kV Transformer Replacement | Replacement of a 69/12kV distribution transformer and several breakers due to age and to support local load growth | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2028-12-31 | 69 | 3800000
Central | 25359 | Louis Allis Switch Replacement | Replacing several switches and distribution breakers | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2028-12-31 | 69 | 2300000
Central | 25394 | Midway 69/2.4kV Transformer Replacement | Replacing several 69/2.4kV transformers and switches | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2028-12-31 | 69 | 2000000
Central | 25406 | Santa Claus Switch Replacement | Replacing several 69kV switches | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2028-12-31 | 69 | 1500000
Central | 25332 | WVPA Pike 69kV Line Rebuild | WVPA Pike 69kV Line Rebuild - Rebuild 69kV line feeding Pike substation | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2028-12-31 | 69 | 15000000
West | 25507 | Umore Park 115 kV Substation | New 115kV load serving substation with in-and-out tap to existing Rosemount - Empire 115 kV line 0822. Build 6 miles new double circuit 115 kV line from Umore Park - Inver Grove. | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2025-12-31 | 115 | 35000000
West | 25396 | Otsego Area Rebuilds | Rebuild EMX to Maple Lake line. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2029-02-28 | 69 | 40078416
West | 22798 | Small Capital Project and Asset Renewal Program 2025 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2025. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-06-30 | 345 | 45000000
East | 25191 | Leroy to South Boardman DC Line Rebuild | Rebuild and upgrade 43 miles of 69 kV line from Cadillac to South Boardman to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2028-12-31 | 138 | 52100000
West | 25323 | St Croix Valley Upgrades | "New 115kV transmission line from the proposed Junction Mill substation in River Falls to a new South Hudson substation to Willow River Build a new South Hudson substation. Replace the two 70 MVA TR’s at Willow River. Add bus and breaker at Willow River to accommodate the new 115kV transmission line" | WI | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2029-09-30 | 115 | 45000000
East | 25228 | DBGEN 41 120 kV Station Rebuild | Rebuild the 120 kV DBGEN 41 station to five rows of breaker and a half station due to age/condition. | MI | ITC | Other | Age and Condition | 2029-03-31 | 120 | 64200000
East | 25363 | ITCT SPOF Blanket | Blanket for projects to address locations where single point of failure (SPOF) are identified that cause system issues. | MI | ITC | BRP |  | 2029-06-01 | 345 | 12100000
West | 25412 | Line Rebuilds Blanket 2025 - 2027 | Blanket project to rebuild 69 kV, 161 kV and 345 kV lines due to condition and to improve reliability and operational flexibility. | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2029-12-01 | 345 | 45000000
East | 25275 | METC SPOF Blanket | Blanket for projects to address locations where single point of failure (SPOF) are identified that cause system issues. | MI | METC | BRP |  | 2029-06-01 | 345 | 19500000
Central | 25372 | New 345-138 kV Monrovia Substation | New 2-bay 345/138 kV breaker-and-a-half substation. Looped-in on the 345-01 Petersburg-Thompson line. 1 300/400/500 MVA 345/138 kV autotransformer. 1 40 MVA 138 kV to serve load. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Load Growth | 2029-06-30 | 345 | 35348000
West | 24778 | Grant County, DIC, New Substation | New load interconnection request in SW Wisconsin. Project scope includes construction of a new 69-kV transmission line to network Hillman – Miners (Y-130) 69-kV line with a new 69-kV substation near the customer site. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2028-01-01 | 69 | 50100000
West | 25212 | ITC Midwest Asset Replacement Program 2026 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA; IL; MN | ITC MIDWEST | Other | Age and Condition | 2026-12-31 | 345 | 52625000
Central | 24555 | New - Waverly - 138 kV Substation | New 138 kV, one 13.5 MVA transformer, three-breaker ring bus substation to serve customer load | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Load Growth | 2029-12-01 | 138 | 6000000
West | 24983 | Hilltop – Council Creek 69 kV (Y-74), Rebuild & OPGW | Rebuild and install OPGW on approximately 29 miles of 69 kV line Y-74 from Hilltop Substation to Council Creek Substation and rebuild ~0.5 miles of Camp Douglas Tap. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-10-31 | 69 | 56000000
West | 3856 | HVDC 900MW Transmission Line Upgrades | Upgrade the capacity of the existing Square Butte – Arrowhead HVDC transmission line from 550 MW to 900 MW, generally by replacing existing structures with taller structures and reconductoring a short segment of line. | MN; ND | MINNESOTA POWER INC. | TDSP |  | 2028-12-31 | 250 | 58000000
West | 50106 | Big Cedar Interconnection | ITC Midwest will construct the new Big Cedar 345 kV Switching Station which will connect to the existing ITC Midwest Beverly - Morgan Valley 345 kV line and add a 2nd Beverly – Big Cedar 345 kV line on existing structures. The new switching station will be constructed in a breaker and ½ configuration and provide service/connections to multiple customer owned transformers/substations. | IA | ITC MIDWEST | Other | Load Growth | 2026-03-31 | 345 | 63743317
West | 21900 | Mullet River Area Reliability Project | Retire existing Mullet River and North Mullet River substations, retire Y-50 between North Mullet River substation and tap to new substation. Design and construct a new 138 kV / 69 kV switching station at a green field location, proposed site to be located south of County Road PP at the intersection of South Road. Tie X-97 and X-57 together near existing Mullet River substation using the south circuit on X-57. Tie X-89and X-57 together near the existing Mullet River substation using the north circuit on X-57. Reroute 8241, LYNG11, X-57, X-89, X-97, and Y-50 into new substation, including any OPGW fiber. Rebuild X-57 which currently is single circuit bifurcated as double circuit from existing Mullet River to location of taps to new site to accommodate extending X-89 and X-97 from existing Mullet River to new substation. | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2028-11-01 | 138 | 64600000
Central | 25318 | Upgrade Winchester 138/69 kV Transformer | Upgrade Winchester 138/69 kV Transformer with 140 MVA unit | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2029-12-31 | 138 | 3500000
Central | 24274 | New - 138 kV Maloney-Reservoir Loop | A new 138 kV loop with two substations to serve growing customer load including a rebuild of one existing 138 kV line. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Load Growth | 2029-12-31 | 138 | 71400000
Central | 25315 | New Forest City-St. David 69 kV Line | 1) New Forest City-Breeds 69 kV Line 2) New Breeds-Sky Rocket 69 kV Line 3) New Sky Rocket-St David 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2029-12-31 | 69 | 20130000
Central | 25316 | New Plymouth-Macomb 69 kV Line | 1) New Plymouth Breaker Station 2) New Plymouth-Colmar 69 kV Line 3) New Colmar-Fandon 69 kV Line 4) New Fandon-Colchester 69 kV Line 5) New Colchester-Macomb 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2029-12-31 | 69 | 19065000
Central | 23426 | New Rushville-Ipava 69 kV Line | 1) New Rushville-Astoria 69 kV line 2) New Astoria-Ipava 69 kV line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2029-12-31 | 69 | 16185000
Central | 23375 | Replace Babylon 138/69 kV XFMR | Replace the 56 MVA Delta-Wye Babylon 138/69 kV transformer with an 84 MVA Wye-Wye transformer. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2029-12-31 | 138 | 2600000
West | 23910 | Eden – Rock Branch 69kV (Y-106), Rebuild & OPGW | Rebuild of line Y-106 from Eden SS to Rock Branch SS. Full rebuild of line with enhanced 69 kV structures and OPGW. This project relieves economic congestion and serves as an asset renewal project. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2030-12-31 | 69 | 67900000
West | 25299 | Racine County, DIC, Nimbus Substation | A new 138/24.9 kV breaker-and-a-half substation named Nimbus and 4 short 138 kV transmission lines (less than 1.0 mile) from the existing Mount Pleasant Substation to the new Nimbus Substation. New bus positions at the Mount Pleasant Substation will need to be added to connect the new transmission lines. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2025-04-01 | 138 | 89000000
West | 50138 | Dodge County, DIC, New Substation | Construct one new 138 kV interconnection substation named Manhattan near the city of Beaver Dam. Also, expand and upgrade the exiting North Randolph 138 kV bus to support additional circuits to Manhattan. Rebuild the existing N Randolph – N Beaver Dam 138 kV line (X-47) forming a new North Randolph - Manhattan 138 kV line and construct a new double circuit 138 kV transmission line between North Randolph and Manhattan substations. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-01 | 138 | 161000000
West | 4295 | HVDC Modernization Project | Replace the existing Center (Square Butte) and Arrowhead high voltage direct current (HVDC) converter stations and associated assets with modern equipment. To modernize the terminals of the existing Square Butte HVDC Line and implement the latest VSC HVDC technology, new buildings and electrical infrastructure need to be constructed on a new site near the existing HVDC terminals. In Minnesota, to connect the new HVDC terminal to the existing AC system, the Project would require the construction of a new St. Louis County 345 kV/230 kV substation located less than one mile west of the current Arrowhead Substation. The new HVDC terminal would be connected to the St. Louis County Substation by less than one mile of 345 kV transmission line and the new St. Louis County Substation would be connected to the existing Arrowhead Substation by two parallel 230 kV transmission lines less than one mile in length. Additionally, a short portion of the existing ±250 kV HVDC Line in Minnesota will need to be reconfigured to terminate at the new HVDC terminal. Similar modifications will take place near the existing Center HVDC terminal in North Dakota. | MN; ND | MINNESOTA POWER INC. | TDSP |  | 2028-12-31 | 345 | 800000000

## MTEP24 Facilities
Target Appendix | App AB | Planning Region | Geographic Location by TO Member System | PrjID | Facility ID | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Description | State | Miles Upgrade | Miles New | Plan Status | Estimated Cost | Submitting Comp. | Cost Shared
A | B | East | MI | 24693 | 28059 | Substation | 2024-12-31 | Milan |  |  | 120 |  | Interconnect generator J799 to Milan line position HD. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
A | B | West | WI | 50107 | 50166 | Substation | 2028-09-10 | Werner West |  |  | 138 |  | 138kV Werner West Substation Remote End | WI |  |  | M1 - Proposed | 146000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IL | 25316 | 28412 | Substation | 2029-12-31 | Plymouth |  |  | 69 | 69 | New Plymouth Breaker Station | IL |  |  | M1 - Proposed | 3400000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | IA | 25182 | 28249 | Substation | 2025-06-30 | Karma | Subustation |  | 161 | 161 | Transmission Owner Interconnection Facilities include equipment (dead-end, insulators, switch, CCVTs, etc.) dedicated to the J1313 Generating Facility | IA |  |  | M1 - Proposed | 427809 | ITC MIDWEST | Not Shared
B | B | West | WI | 25259 | 28446 | Voltage Device | 2028-09-30 | Grassland |  |  | 69 |  | Add 2x10 MVAR caps | WI |  |  | M1 - Proposed | 2000000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | MN | 25282 | 28395 | Line New | 2027-09-30 | Sherco |  |  | 345 |  | ~140 radial double circuit 345kV line to wind collector substations and voltage support substation. | MN |  | 140 | M1 - Proposed | 800000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | South | LA | 25413 | 28703 | Misc. | 2024-12-31 | Golden Meadow | Barataria |  | 115 |  | Remove Barataria to Golden Meadow from the MISO models | LA |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 50106 | 50159 | Substation | 2026-03-31 | Beverly |  |  | 345 | 345 | Add line terminal for Big Cedar #2 line at Beverly substation, converting substation from ring bus to breaker and 1/2 configuration. | IA |  |  | M2 - Appendix A Approved | 5667950 | ITC MIDWEST | Not Shared
A | B | West | MN | 25295 | 28457 | Line Upgrade | 2023-09-30 | Monticello | Oakwood | 1 | 115 |  | Replace structures at 3 clearance limited span between Monticello - Oakwood. | MN |  |  | M1 - Proposed | 150000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | MO | 25243 | 28288 | Line Upgrade | 2026-12-01 | Rockwood |  |  | 138 |  | At Rockwood 138/34.5 kV substation, install three 138 kV line breakers on the Rockwood-Big River-1 line position H2, Gray-Rockwood-3 position H6, Gray-Rockwood-4 position H10 having a 2000 A continuous capability. | MO |  |  | M1 - Proposed | 3500000 | AMEREN MISSOURI | Not Shared
A | B | South | MS | 25214 | 28323 | Substation | 2025-01-01 | Virlilia |  |  | 230 |  | New Virlilia 230 kV breaker and a half substation fed out of Catlett 230 kV substation. | MS |  |  | M1 - Proposed | 79500000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | West | MN | 4295 | 28487 | Substation | 2028-12-31 | Arrowhead | 230kV Line Entrances |  | 230 |  | Upgrade existing 230kV HVDC bus and equipment from line entrances to existing Pole 1 & 2 line entrance positions. Capacity increased to 1000MVA | MN |  |  | M1 - Proposed | 5000000 | MINNESOTA POWER INC. | Not Shared
A | B | East | MI | 25209 | 28308 | Substation | 2027-02-01 | Oxby |  |  | 345 |  | Install Row 31, install 3-345 kV breakers and associated disconnects at positions 31R8, 31H9, and 31F7. Install breakers 29R8 and 33F7 and associated disconnects. | MI |  |  | M1 - Proposed | 8274863 | METC | Not Shared
A | B | South | AR | 50093 | 50139 | Substation | 2026-09-30 | Galet 500/230kV |  |  | 500 | 230 | A new 500/230kV four breaker ring bus substation with two 1200MVA autotransformers and two 230kV lines extending to the customer station. | AR |  |  | M1 - Proposed | 142000000 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | South | TX | 25410 | 28661 | Voltage Device | 2027-12-01 | Winshire |  |  | 69 |  | Install 2 - 11 MVAR cap banks | TX |  |  | M1 - Proposed | 7000000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | WI | 25287 | 28430 | Line Upgrade | 2025-12-31 | Loyal | Spokesville | 1 | 69 |  | Rebuild 8 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | WI | 8 |  | M1 - Proposed | 6000000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | MN | 25282 | 28605 | Substation | 2027-09-30 | Terminus |  |  | 345 |  | 4 wind collector substations connected to terminus substation to bring in wind generation. | MN |  |  | M1 - Proposed | 70000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 24553 | 28005 | Substation | 2026-04-01 | Dorset |  |  | 120 |  | Install tie-bkr HG at Dorset. | MI |  |  | M1 - Proposed | 922579 | ITC | Not Shared
A | B | West | MN | 24394 | 27849 | Line Upgrade | 2024-12-31 | Kragnes | Averil Switch |  | 69 |  | Kragnes - Averil Switch 69 kV | MN |  |  | M1 - Proposed | 1200000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | West | MN | 25506 | 28794 | Line Upgrade | 2025-12-31 | Inver Grove | Inver Hills | 1 | 115 |  | Rebuild 2.2 miles 115 kV line 5507 to double circuit from Inver Grove - Inver Hills. Expand Inver Hills substation. | MN | 2.2 |  | M1 - Proposed | 8000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25523 | 28735 | Misc. | 2026-06-01 | Brouilletts Creek Solar | J1348 POI |  | 345 |  | J1348 200MW Brouilletts Creek Solar, LLC: Provide construction oversite for new switching station constructed by the IPP; relaying upgrades at Cayuga CT and Sugar Creek (34513 ckt); Loop 34513 in and out of new substation | IN |  |  | M1 - Proposed | 8372617 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | East | MI | 24440 | 27931 | Substation | 2025-08-01 | Van Tyle |  |  | 138 |  | Complete Row 4, install 1-138kV breaker at position 4B7 with minimum 40kA interrupting capability. Install 138kV 3000A disconnect switches 4B3 and 4M5 | MI |  |  | M1 - Proposed | 1122500 | METC | Not Shared
A | B | West | ND | 50152 | 50253 | Line New | 2025-09-01 | Ellendale | Ellendale Data Center |  | 230 |  | This is a new 230 kV transmission line between the Ellendale sub and the Ellendale Data Center Sub. | ND |  | 1 | M1 - Proposed | 2265527 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | West | IA | 25306 | 28367 | Substation | 2026-12-31 | Burlington 4th Street | Substation |  | 69 | 69 | IPL has notified ITC that they will be rebuilding their Burlington 4th Street sub and installing a 2nd 20/26/33 MVA transformer; as well as, replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Burlington 4th Street sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | IA |  |  | M1 - Proposed | 1984333 | ITC MIDWEST | Not Shared
A | B | East | MI | 24443 | 27935 | Misc. | 2026-05-01 | Argenta |  |  | 345 |  | Upgrade position FH30 relaying at Argenta 345kV | MI |  |  | M1 - Proposed | 457185 | METC | Not Shared
B | B | West | WI | 25019 | 28177 | Line Upgrade | 2027-07-01 | Gran Grae | Hillside | Y-161 | 69 |  | Rebuild of line Y-161 from Gran Grae SS to Hillside SS. | WI |  |  | M1 - Proposed | 12000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | MS | 25459 | 28746 | Line Upgrade | 2026-06-01 | Benndale | Lucedale |  | 69 |  | To ensure reliable service a complete rebuild of L35 (Lucedale – Benndale 11.37 miles) is recommended. | MS |  |  | M1 - Proposed | 7100000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | WI | 21900 | 26490 | Substation | 2028-11-01 | Mullet River |  |  | 138 | 69 | • Retire existing Mullet River and North Mullet River. • Build new 138 kV / 69 kV substation. • 8 position 138 kV breaker and a half yard expandable to 10 positions. o 3 position segmented 69 kV straight bus expandable to 5 positions. o 138/69 kV LTC transformer o 69 kV cap bank o Provisions for series reactors or other flow control devices on the 8241 and LYNG11 line exits. | WI |  |  | M1 - Proposed | 32300000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 50008 | 50019 | Line Upgrade | 2025-12-31 | Oklee 41.6 kV |  |  | 42 |  | Rebuild and relocate 41.6 kV line near Oaklee 41.6 kV. | MN |  |  | M1 - Proposed | 450000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | East | MI | 25366 | 28498 | Substation | 2026-12-31 | ITCT Facilities |  |  | 345 | 120 | Replace aging and outdated equipment at a pace that will ensure each type of equipment is replaced near its projected end of life. | MI |  |  | M1 - Proposed | 60700000 | ITC | Not Shared
A | B | Central | IN | 25261 | 28359 | Substation | 2024-09-06 | Apollo 161 kV |  |  | 161 |  | Construct Transmission Owner's Interconnection Facilities at Apollo Station | IN |  |  | M1 - Proposed | 11424620 | HOOSIER ENERGY | Not Shared
A | B | East | MI | 24557 | 28021 | Substation | 2026-12-31 | Oxby |  |  | 345 |  | Install a line entrance structure and disconnect as TOIF. Install position RH31 at Oxby to interconnect J1586 generator. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | MN | 25374 | 28556 | Line Upgrade | 2025-10-31 | Blackberry | Enbridge Blackberry Tap | 1 | 69 |  | Rebuild 1.07 miles of the Blackberry to Enbridge Blackberry Tap line. | MN | 1.07 |  | M1 - Proposed | 1980680 | GREAT RIVER ENERGY | Not Shared
A | B | South | TX | 25436 | 28684 | Transformer | 2026-06-01 | Bobville |  |  | 230 | 138 | 230-138 kV Auto | TX |  |  | M1 - Proposed | 48600000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 25460 | 28626 | Line New | 2027-06-01 | Southridge | Greenfield Plaza | 1 | 161 |  | Tap SE Polk - Greenfield Plaza 161 kV | IA |  |  | M1 - Proposed | 1250000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 24560 | 28030 | Misc. | 2025-05-15 | Meyer |  |  | 138 |  | Upgrade position WM14 Relaying at Meyer 138kV station. | MI |  |  | M1 - Proposed | 176535 | METC | Not Shared
B | B | West | WI | 25002 | 50022 | Misc. | 2028-12-31 | Walworth | Williams Bay | Y-41 | 69 |  | OPGW installation and select aging structure replacement from Walworth SS to Williams Bay SS to align with the entire Y-41 rebuild project. | WI |  |  | M1 - Proposed | 8700000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 25401 | 28544 | Substation | 2025-06-30 | Northwest |  |  | 138 | 35 | Addition of 1 138/34.5 kV 66.7 MVA transformer and 1 138 kV breaker. | IN |  |  | M1 - Proposed | 4000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | WI | 50110 | 50174 | Substation | 2028-09-10 | Saratoga |  |  | 138 |  | Saratoga Substation remote end work | WI |  |  | M1 - Proposed | 235000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25338 | 28533 | Line Upgrade | 2027-12-01 | Victor | Woodland | 1 | 69 |  | Rebuild Victor to Woodland. | MN | 8.6 |  | M1 - Proposed | 5423955 | GREAT RIVER ENERGY | Not Shared
A | B | Central | MO | 50148 | 50242 | Line Upgrade | 2025-12-01 | Havana | Puro |  | 138 |  | Rebuild the 138 kV Havana-Puro 1422 transmission line with new wood H frame structures, steel structures, OPGW and 1200 A conductor. Affected J#s include: J1408, J1453, J1454 | MO |  |  | M1 - Proposed | 13200000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 50038 | 50080 | Misc. | 2026-08-19 | HSC | Murphy | 1 | 138 |  | Re-route OHL to accommodate Orr Road expansion | MI |  |  | M1 - Proposed | 2364000 | METC | Not Shared
A | B | South | LA | 50039 | 50069 | Substation | 2026-04-01 | Richard |  |  | 138 |  | Facilities required for the interconnection of J1561 at the Richard 138 kV station. | LA |  |  | M1 - Proposed | 1880000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | IN | 25268 | 28396 | Transformer | 2028-12-31 | Petersburg | Petersburg | E | 345 | 138 | Replace Petersburg E auto | IN |  |  | M1 - Proposed | 6000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | South | AR | 25485 | 28704 | Substation | 2025-12-01 | Champs 115kV |  |  | 115 |  | Build a new 115kV substation with a 40 MVA 115/13.8kV transformer. | AR |  |  | M1 - Proposed | 10804929 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 50121 | 50194 | Line Upgrade | 2028-06-01 | Quary | Cottage Grove | 1 | 138 |  | Relocate approximately ~39.04 miles from Quarry to Cottage Grove onto the vacant side of the recently-rebuilt Twining – Whittemore & Shale – Twining utilizing existing double- circuit structures, using 954 ACSR conductor and install OPGW. Construct ~1.5 mile from Cottage Grove to new location on a new ROW. Relocate existing PT switches at Santiago tap, at Saganing tap, and at Seven Mile tap De-energize old section after relocating to new location. | MI | 34.04 |  | M1 - Proposed | 26750000 | METC | Not Shared
A | B | Central | IN | 25394 | 28581 | Substation | 2028-12-31 | Midway |  |  | 69 | 2 | Replacing several 69/2.4kV transformers and switches | IN |  |  | M1 - Proposed | 2000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | SD | 25296 | 28458 | Transformer | 2025-06-15 | Lawrence |  |  | 115 | 35 | Install second 115/34.5 kV transformer with LTC at Lawrence substation. | SD |  |  | M1 - Proposed | 4158000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25525 | 28781 | Substation | 2026-06-30 | Kokomo Fusion - Phase 2 | xfmr and CBs |  | 230 | 69 | Kokomo Fusion Phase 2 (StarPlus Energy) - 155MW/51MVAR addition; relocate 23022, 69172, and 69174 lines away from StarPlus Energy Phase 2 facilities; add (1) 150MVA 230/69kV transformer; add (2) 230CBs; add (4) 60MVA 69/34kV transformers | IN |  |  | M1 - Proposed | 14000000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | IA | 25433 | 28668 | Substation | 2025-09-16 | J1270 Sub |  |  | 345 |  | Network Upgrades for J1270 Generator (Graettinger Marsh Sub) | IA |  |  | M1 - Proposed | 14500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | IN | 25334 | 28510 | Substation | 2025-09-03 | Kokomo Webster St | 230 CBs |  | 230 |  | Kokomo Webster St Ckt Brkr Replacements - 230kV: replace (2) oil CBs (23022-20 and 230B2-22) and their disconnect switches (motorize); replace all 230kV relays; install SCADA controlled line disconnect switches (23016, 23020 & 23022) and upgrade wave traps as needed; Upgrade RTU and DC power supply systems | IN |  |  | M1 - Proposed | 2800000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | Central | IN | 25397 | 28594 | Substation | 2026-12-31 | Tepe Park |  |  | 138 | 15 | Replacing 138/15kV transformer and breakers | IN |  |  | M1 - Proposed | 4000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
B | B | East | MI | 18040 | 50047 | Substation | 2028-06-01 | Cottage Grove |  |  | 138 |  | Upgrade all 336 ACSR buses at Cottage Grove substation. The new equipment must be rated at least 431 MVA for summer emergency rating. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | East | MI | 24516 | 27995 | Line Upgrade | 2026-12-31 | Beecher | Pixley |  | 138 |  | Loop in the Beecher – Pixley (Beecher – Morocco #1) 138kV circuit to the new J1571 station ~2.8 miles from Beecher 138kV station near structure 017B5283 utilizing conductor rated at least that of 954 ACSR 54/7. | MI |  |  | M1 - Proposed | 687500 | METC | Not Shared
A | B | West | IA | 25183 | 28250 | Voltage Device | 2025-06-30 | Karma | Substation |  | 161 | 161 | Add a 161 kV breaker position in the Karma Substation | IA |  |  | M1 - Proposed | 556081 | ITC MIDWEST | Not Shared
A | B | East | MI | 25244 | 28289 | Substation | 2027-06-11 | Morocco |  |  | 345 |  | Replace position RH34 relaying | MI |  |  | M1 - Proposed | 319323 | METC | Not Shared
A | B | East | MI | 25209 | 28309 | Line Upgrade | 2027-02-01 | Oxby | Oneida |  | 345 |  | Remediate the sag on the Oxby - Oneida 345 kV line to achieve a rating of at least 1327 MVA SN and 1327 MVA SE | MI |  |  | M1 - Proposed | 2196250 | METC | Not Shared
B | B | West | WI | 25254 | 28382 | Line New | 2027-06-01 | Morris Street |  |  | 69 |  | Retiring the Morris Street (MN1T) tap, removing the 1264-LB normal open between the North Fond Du Lac-Mercury Marine (Y-114) 69 kV line and South Fond Du Lac-Morris Street (Y-60) 69 kV line, and installing a loop-through configuration with 69 kV line breakers at the Morris Street substation. This will effectively provide network connection to the existing radial Y-114 and radial Y-60 lines. | WI |  |  | M1 - Proposed | 6500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | MS | 25419 | 28762 | Line New | 2028-11-01 | Hermanville GOAB |  |  | 115 |  | In order to serve the member delivery point, tap Utica Loop line with a 115kV Goab and construct a new line to the delivery point. | MS |  |  | M1 - Proposed | 200000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | East | MI | 24556 | 28018 | Line Upgrade | 2027-01-21 | Argenta | Tompkins |  | 345 |  | Extend the Argenta - Tompkins 345kV line 0.2 miles by adding 2-1431 ACSR to loop in J1586 POI 345kV station. | MI |  |  | M1 - Proposed | 1820400 | METC | Not Shared
A | B | South | AR | 50094 | 50143 | Substation | 2026-04-01 | New interconnection |  |  | 115 |  | Construct 115 kV main & transfer bus with line breakers as per Entergy standards to interconnect. | AR |  |  | M1 - Proposed | 3000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | B | West | MI | 50109 | 50171 | Substation | 2028-09-10 | Nordic |  |  | 138 |  | J1814 138kV Interconnection Facilities | MI |  |  | M1 - Proposed | 1091000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25323 | 28447 | Substation | 2029-09-30 | South Hudson |  |  | 115 | 24 | Build a new South Hudson substation. | WI |  |  | M1 - Proposed | 15000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25288 | 28431 | Line Upgrade | 2025-12-31 | Goodview | Goodview Tap | 1 | 69 |  | Rebuild 3 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | 3 |  | M1 - Proposed | 6000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25399 | 28606 | Line Upgrade | 2028-02-01 | Jamestown Tap GRE | Jamestown Tap Xcel | 1 | 69 |  | Rebuild from 2.8 miles of the GRE Jamestown Tap to the Xcel Jamestown Tap line. | MN | 2.8 |  | M1 - Proposed | 3265967 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 50151 | 50249 | Line Upgrade | 2027-09-01 | Sphinx | Plaster Creek | 1 | 138 |  | Redirect line from East Paris into the new station Sphinx utilizing 1431 ACSS conductor and replace OPGW. | MI |  |  | M1 - Proposed | 4400000 | METC | Not Shared
A | B | Central | IL | 23374 | 27075 | Substation | 2026-06-01 | Babylon |  |  | 138 | 69 | New Babylon 138/69 kV Substation | IL |  |  | M1 - Proposed | 7325000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | MN | 24394 | 27850 | Line Upgrade | 2024-12-31 | Averil Switch | Xcel Averil Switch |  | 69 |  | Averil Switch - Xcel Averil Switch 69 kV | MN |  |  | M1 - Proposed | 1000000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | Central | IL | 25316 | 28413 | Line New | 2029-12-31 | Plymouth | Colmar |  | 69 | 69 | New Plymouth-Colmar 336 ACSR 69 kV Line | IL |  | 7.2 | M1 - Proposed | 4680000 | PRAIRIE POWER, INC. | Not Shared
A | B | East | MI | 24554 | 28006 | Substation | 2026-04-01 | Dorset |  |  | 120 |  | Install an entrance structure, one BKR, and two disconnect switches as TOIF. Install position HK at Dorset to interconnect J1659 generator. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
A | B | Central | IL | 25042 | 28203 | Substation | 2026-12-01 | Supernova |  |  | 345 |  | This project will install a new 345 kV line position to serve as the Point of Interconnection for Perry County under GIA J1306, within the new 3-position ring bus named Supernova. | IL |  |  | M1 - Proposed | 11000000 | AMEREN ILLINOIS | Not Shared
A | B | South | MS | 25214 | 28324 | Line New | 2025-01-01 | Catlett | Virlilia | 1 | 230 |  | Short Transmission lines to interconnect new substation to Catlett | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 25429 | 28662 | Line Upgrade | 2027-12-01 | Neal North | Terra | 1 | 69 |  | Rebuild Neal North-Terra 69 kV line | IA | 0.5 |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25253 | 28368 | Substation | 2026-12-31 | Flint Ridge | Substation |  | 69 | 69 | IPL has notified ITC that they will be rebuilding their Flint Ridge sub and installing a 2nd 20/26/33 MVA transformer. This rebuild will also be replacing the existing transformer, T1, with a new one of the same size. As part of this, ITC will need to install a new bus tie breaker at the Flint Ridge sub. In addition, ITC will build a new control enclosure with all new relays and SCADA equipment. All new ITC owned equipment is to be rated minimum 1200 amps summer normal rating. | IA |  |  | M1 - Proposed | 2160171 | ITC MIDWEST | Not Shared
A | B | East | MI | 50151 | 50248 | Substation | 2027-09-01 | Gaines |  |  | 138 |  | Expand Gaines 138 kV station rows 7 and 11 to accommodate the new line. Install five 138 kV standard 3000 A 63 kA breakers. | MI |  |  | M1 - Proposed | 4900000 | METC | Not Shared
A | B | West | MN | 50009 | 50020 | Line Upgrade | 2025-12-31 | Winger 41.6 kV | Winger Town 41.6 kV | 1 | 42 |  | Reconductor and reroute small portion of 41.6 kV line from Winger 41.6 kV to Winger Town 41.6 kV. | MN |  |  | M1 - Proposed | 115000 | OTTER TAIL POWER COMPANY | Not Shared
B | B | West | ND | 24334 | 27824 | Line Upgrade | 2027-06-01 | Mapleton (620203) | Sheyenne (603018) | 1 | 115 |  | Rebuild OTP's 5.68 miles of the Mapleton - Sheyenne 115 kV line with a larger conductor. | ND |  |  | M1 - Proposed | 3500000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | East | MI | 24442 | 27932 | Substation | 2025-08-01 | Van Tyle |  |  | 138 |  | Install Van Tyle line position BM4 and switch 177 for generator interconnect. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | Central | IN | 25152 | 28234 | Line Upgrade | 2025-12-31 | AB BROWN | Northwest | 99 | 138 |  | Replacement of pole along Z99 from AB Brown to Wolf Road | IN |  |  | M1 - Proposed | 8500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | IA | 50030 | 50055 | Substation | 2026-06-01 | Johnson Creek |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25506 | 28795 | Substation | 2025-12-31 | Umore Park |  |  | 115 |  | Add 1 breaker at Umore substation. | MN |  |  | M1 - Proposed | 2000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25543 | 28747 | Misc. | 2026-10-01 | Greentown 230 | J1381 POI |  | 230 |  | J1381 200MW net Locomotive Solar, LLC: Greentown 230 - Expand 230 kV ring bus and add line terminal equipment between AEP Bk2 and 23021 (Peru SE) | IN |  |  | M1 - Proposed | 6666686 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | IA | 50106 | 50161 | Line New | 2026-03-31 | Big Cedar |  |  | 345 |  | New 345 kV feeds from Big Cedar Switching Station to customer owned substations | IA |  | 4 | M2 - Appendix A Approved | 16482500 | ITC MIDWEST | Not Shared
A | B | East | MI | 25275 | 28478 | Substation | 2029-06-01 | Throughout METC system |  |  | 345 | 120 | System violations throughout METC system that are caused by single point of failure (SPOF) contingencies. | MI |  |  | M1 - Proposed | 19500000 | METC | Not Shared
A | B | West | WI | 50036 | 50066 | Substation | 2023-07-31 | Big Hill Park |  |  | 138 |  | 605098 - J1304 Big Hill Park SS Interconnection Facilities | WI |  |  | M4 - Project in Service | 363168 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IL | 24034 | 27728 | Transformer | 2026-12-01 | Coffeen N |  |  | 345 | 138 | Replace Existing XFMR 2 at Coffeen North Substation with a new 345/138kV 700 MVA unit. | IL |  |  | M1 - Proposed | 6000000 | AMEREN ILLINOIS | Not Shared
B | B | West | WI | 24474 | 27901 | Substation | 2026-07-15 | Winnebago County DIC |  |  | 138 |  | WPS is proposing to construct a new T-D substation with two new 138/12.47 kV transformers with circuit breakers for high-side protection. The substation is located in Oshkosh, Wisconsin. ATC will construct a 138 kV loop-through straight bus with two-line breakers. ATC will also install two manual bus-tie switches and make provisions for a future bus-tie breaker. ATC will construct approximately 0.8 miles of a new 138 kV double-circuit transmission line extension from the Fitzgerald – Ellinwood 138 kV line (W-101) on new right-of-way to loop in and out of the proposed T-D substation. | WI |  |  | M1 - Proposed | 10500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | AR | 50164 | 50311 | Voltage Device | 2025-12-01 | Summerville |  |  | 69 |  | 2 new cap banks will be added to the Summerville 69kV substation to support contingency voltage issues. | AR |  |  | M1 - Proposed | 2000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | B | Central | IN | 25367 | 28499 | Substation | 2025-06-25 | Prospect | Ford | 28 | 138 | 13 | Straight bus, 3 breakers, 2 40 MVA transformers | IN |  |  | M1 - Proposed | 15000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | MN | 22487 | 27353 | Substation | 2025-11-30 | Audubon 230 kV (620336) | Audubon 115 kV (658112) | 1 | 230 | 115 | Adjust Audubon 230/115 kV transformer #1 tap. | MN |  |  | M1 - Proposed | 1000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | West | MN | 25374 | 28557 | Line Upgrade | 2025-11-10 | Enbridge Blackberry | Enbridge Blackberry Tap | 1 | 69 |  | Rebuild 0.76 miles of the Enbridge Blackberry to Enbridge Blackberry Tap line. | MN | 0.76 |  | M1 - Proposed | 726560 | GREAT RIVER ENERGY | Not Shared
B | B | West | MI | 24981 | 28169 | Substation | 2027-12-31 | Presque Isle |  |  | 138 |  | Breaker and Relay Asset Renewal | MI |  |  | M1 - Proposed | 10700000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24443 | 27936 | Misc. | 2026-05-01 | Tallmadge |  |  | 345 |  | Upgrade Position RH31 relaying at Tallmadge 345kV. | MI |  |  | M1 - Proposed | 457185 | METC | Not Shared
A | B | West | MN | 25272 | 28441 | Line Upgrade | 2025-06-13 | Monticello |  |  | 345 |  | Install new MOD transmission line switches at Monticello. Potential for new pole and substation fence expansion. | MN |  |  | M1 - Proposed | 3600000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MI | 25163 | 28227 | Misc. | 2026-12-31 | Freeman | Presque Isle | X-118 | 138 |  | Installation of 7.5 miles of OPGW to provide an alternate fiber path establishing two diverse fiber routes connecting into ATC larger OPGW Network Infrastructure. | MI |  |  | M1 - Proposed | 7000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 50029 | 50050 | Substation | 2025-05-01 | SE Soteria |  |  | 161 |  | Install 161 kV breakers and associated equpiment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | WI | 50111 | 50179 | Line Upgrade | 2030-03-10 | Hill Valley | Cardinal | W-18 | 345 |  | The W-18 345 kV Transmission Line Loop-In project will consist of two (2) vertical dead-end structures routing the line through the Transmission Owner’s new substation, segmenting W-18 between the Hill Valley and Cardinal substations. Line renaming will be required and determined in detailed design. | WI |  |  | M1 - Proposed | 2300000 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | South | AR | 50164 | 50310 | Substation | 2025-12-01 | Woodberry |  |  | 69 |  | New substation that is needed to serve a new 26MW load on the Summerville 69kV system. | AR |  |  | M1 - Proposed | 8200000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | B | West | MN | 25423 | 28572 | Line Upgrade | 2027-09-30 | Dunnel | Fox Lake Tap | 1 | 69 |  | Rebuild the Dunnel to Fox Lake tap line. | MN | 4 |  | M1 - Proposed | 5255229 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 24413 | 27843 | Line Upgrade | 2025-02-28 | Lund | Littlefork |  | 230 |  | Lund - Littlefork 230 KV | MN |  |  | M1 - Proposed | 540000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | Central | IN | 25304 | 28360 | Substation | 2024-08-20 | Apollo 161 kV |  |  | 161 |  | Develop Transmission Owner's Facilities necessary to interconnect project J1396. | IN |  |  | M1 - Proposed | 10000 | HOOSIER ENERGY | Not Shared
A | B | Central | IN | 25268 | 28397 | Transformer | 2028-12-31 | Petersburg | Petersburg | W | 345 | 138 | Replace Petersburg W autotransformer. | IN |  |  | M1 - Proposed | 6000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | South | AR | 25487 | 28705 | Substation | 2025-12-01 | Frazier Pike 115kV |  |  | 115 |  | Build a new 115kV substation with a single 50 MVA transformer | AR |  |  | M1 - Proposed | 18007302 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | West | ND | 50012 | 50025 | Line Upgrade | 2028-12-31 | Buffalo 41.6 kV | Colgate 41.6 kV | 1 | 42 |  | Rebuild 41.6 kV line from Buffalo 41.6 kV to Colgate 41.6 kV. | ND | 15.2 |  | M1 - Proposed | 3770000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | West | IA | 25460 | 28627 | Line New | 2027-06-01 | Southridge | SE Polk | 1 | 161 |  | Tap SE Polk - Greenfield Plaza 161 kV | IA |  |  | M1 - Proposed | 1250000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | West | MI | 25003 | 28178 | Line Upgrade | 2027-12-31 | Laurium2 South Riser | Laurium2 North Riser | Laur2 | 69 |  | Replace underground cable on line Laurium2. | MI | 0.35 |  | M1 - Proposed | 9000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25338 | 28534 | Line Upgrade | 2027-12-01 | Woodland | DX Line | 1 | 69 |  | Rebuild Woodland to DX line. | MN | 5.8 |  | M1 - Proposed | 3879159 | GREAT RIVER ENERGY | Not Shared
A | B | West | IA | 25433 | 28669 | Line New | 2025-09-18 | Graettinger Marsh | Palo Alto | 1 | 345 |  | Network Upgrades for J1270 Generator (345 kV line taps) | IA |  |  | M1 - Proposed | 2500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25396 | 28595 | Line Upgrade | 2029-02-28 | Black Lake Tap | Maple Lake | 1 | 69 |  | Rebuild 5 miles of the Black Lake tap to Maple Lake line. | MN | 5 |  | M1 - Proposed | 8182839 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 25209 | 28310 | Line Upgrade | 2027-02-01 | Oxby | Tompkins |  | 345 |  | Reconductor Oxby-Tompkins 345 kV line with OPGW using 2-1431 ACSR conductor. Approximately 15.7 miles of this reconductor will be completed under LRTP. | MI |  |  | M1 - Proposed | 3443750 | METC | Not Shared
A | B | West | WI | 50036 | 50064 | Substation | 2023-07-31 | Town Line Road |  |  | 138 |  | 605096 - Town Line Road SS Relay Panel Improvements | WI |  |  | M4 - Project in Service | 209597 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | Central | KY | 25499 | 28782 | Line Upgrade | 2025-12-01 | HMPL Sub 2 | HMPL Sub 5 | 1 | 69 |  | Reconductor 69kV line | KY |  |  | M1 - Proposed | 1036568 | CITY OF HENDERSON, KY, UTILITY COMMISSION, DBA HENDERSON MUNICIPAL POWER AND LIGHT (BA) | Not Shared
A | B | Central | MO | 25225 | 28290 | Line Upgrade | 2025-06-01 | Maurer Lake |  |  | 161 |  | Replace breaker H9 Bus Tie (G735) and associated switches (G734 and G736) Add disconnect switch and breaker to XFMR 1 and 2 | MO |  |  | M1 - Proposed | 4000000 | AMEREN MISSOURI | Not Shared
A | B | South | TX | 50043 | 50074 | Substation | 2025-09-30 | Sabine | Neches |  | 138 |  | Add two 138 kV breakers at Sabine to convert both lines going to Neches to double bus double breaker | TX |  |  | M1 - Proposed | 10000000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 50038 | 50082 | Misc. | 2026-08-19 | Murphy | Orr Road | 1 | 138 |  | CE to install flying taps to the existing Murphy-Orr Road 1 138 kV line for their connection to serve up to 95 MW Consumers Energy's new dedicated customer substation. | MI |  |  | M1 - Proposed | 182000 | METC | Not Shared
A | B | West | MN | 25399 | 28607 | Line Upgrade | 2027-04-22 | St. Thomas Tap | Sheas Lake | 1 | 69 |  | Rebuild 3.43 miles from the St. Thomas Tap (AKA ITC Le Center Tap) switch to the Sheas Lake double circuit line. | MN | 3.43 |  | M1 - Proposed | 3293491 | GREAT RIVER ENERGY | Not Shared
A | B | South | AR | 50197 | 50345 | Transformer | 2026-12-05 | West Memphis EHV |  |  | 500 | 161 | The existing 500/161kV autotransformer at West Memphis will be replaced with a new 600MVA rated autotransformer. Also, the existing 161kV breaker B2600 will be replaced. | AR |  |  | M1 - Proposed | 25506000 | ENTERGY ARKANSAS, LLC | Shared
A | B | West | MN | 25297 | 28459 | Transformer | 2025-10-15 | Blue Heron |  |  | 69 | 14 | Install new 69/13.8 kV transformer with LTC at Blue Heron substation. | MN |  |  | M1 - Proposed | 5800000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | East | MI | 50064 | 50129 | Line Upgrade | 2028-06-01 | Cottage Grove | East Tawas | 1 | 138 |  | Rebuild approximately ~32.79 miles from Quarry - Cottage Grove circuits to 954 ACSR conductor utilizing standard 138 kV double- circuit structures with OPGW. Leave the west side of the double-circuit structures vacant. | MI | 32.79 |  | M1 - Proposed | 50870000 | METC | Not Shared
A | B | West | MN | 25471 | 28722 | Line Upgrade | 2027-12-30 | St. Clair | St. Clair Tap | 1 | 69 |  | Rebuild 4.5 miles from St. Clair to the St. Clair Tap. | MN | 4.5 |  | M1 - Proposed | 4728756 | GREAT RIVER ENERGY | Not Shared
A | B | West | IA | 25251 | 28521 | Substation | 2025-07-31 | Wever | Substation |  | 161 | 161 | Perform the required by the GIA for J1734 including 161 kV breaker, switches, etc. to allow a new 161 kV gen-tie line to the customer substation. | IA |  |  | M1 - Proposed | 701639 | ITC MIDWEST | Not Shared
A | B | West | MN | 24394 | 27851 | Line Upgrade | 2024-12-31 | Xcel Averil Switch | Buffalo River |  | 69 |  | Xcel Averil Switch - Buffalo River 69 kV | MN |  |  | M1 - Proposed | 1850000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | Central | IL | 25316 | 28414 | Line New | 2029-12-31 | Colmar | Fandon |  | 69 | 69 | New Colmar-Fandon 336 ACSR 69 kV Line | IL |  | 7 | M1 - Proposed | 4550000 | PRAIRIE POWER, INC. | Not Shared
A | B | Central | IN | 25334 | 28511 | Substation | 2025-12-22 | Kokomo Webster St | 69 CBs |  | 69 |  | Kokomo Webster St Ckt Brkr Replacements - 69kV: Replace (4) oil CBs (69173, 69174, 6912-1 and 69230-2) and their disconnect switches as needed; replace all 69kV relays | IN |  |  | M1 - Proposed | 3500000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | IA | 25411 | 28663 | Line New | 2027-12-01 | Rock Valley Town | NIPCO K218 | 1 | 69 |  | Construct a second 69 kV line into Rock Valley Town Substation and retire a section of the Rock Valley Town Tap-NIPCO K218 69 kV line | IA |  | 0.6 | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 24443 | 27933 | Substation | 2026-05-01 | Argenta | Tallmadge |  | 345 |  | Construct J1663 as a 345kV breaker and half station with three 50kA breakers. | MI |  |  | M1 - Proposed | 12721682 | METC | Not Shared
A | B | West | MI | 24842 | 28135 | Line Upgrade | 2025-12-31 | Atlantic | Osceola | Laurium2 | 69 |  | Replace crossarms at ~140 structures with new insulators, replace select structures, obtain rights for gaps along existing corridor, and complete vegetation management activities. | MI |  |  | M1 - Proposed | 8100000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25289 | 28432 | Line Upgrade | 2025-12-31 | Highbridge | Miriam Park | 1 | 115 |  | Rebuild 3.3 miles 115 kV with new structures and new OPGW shield wire. | MN | 3.3 |  | M1 - Proposed | 4000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25251 | 50352 | Substation | 2024-07-31 | BGS | Wever | 1 | 161 |  | Relays at Wever on BGS terminal | IA |  |  | M1 - Proposed | 205358 | ITC MIDWEST | Not Shared
A | B | East | MI | 24560 | 28031 | Misc. | 2026-03-03 | Tanner |  |  | 138 |  | Install fiber Jumpers at Tanner. | MI |  |  | M1 - Proposed | 36223 | METC | Not Shared
A | B | West | MN | 25202 | 28251 | Substation | 2025-06-30 | Magnolia | Substation |  | 161 | 161 | Expand Magnolia 161 kV substation from a 4-terminal, 4 breaker, ring-bus substation to a 5 terminal ring bus substation. | MN |  |  | M1 - Proposed | 486788 | ITC MIDWEST | Not Shared
A | B | West | IA | 25307 | 28369 | Line New | 2026-12-15 | State Center Rural | State Center Rural | 1 | 69 | 69 | Line Taps for new State Center Rural Substation Interconnection | IA |  | 0.1 | M1 - Proposed | 297500 | ITC MIDWEST | Not Shared
A | B | West | MI | 25104 | 28235 | Line Upgrade | 2027-11-01 | 2nd St. Tap | 30th Ave. | N-14 | 69 |  | Rebuild and install OPGW on approximately 1.5 miles of N-14 from Structure 145364 to 30th Ave. | MI |  |  | M1 - Proposed | 7500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IL | 25043 | 28204 | Substation | 2025-12-01 | Moose |  |  | 138 |  | This project will install a new 138 kV line position to serve as the Point of Interconnection for Albion PV 1, LLC under GIA J1422, within the new 3-position ring bus named Moose. | IL |  |  | M1 - Proposed | 8400000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 50098 | 50152 | Substation | 2028-12-31 | Hagensville Junction |  |  | 138 |  | Build a 3 terminal station with 138/69kV stepdown transformer. One terminal will connect to new Hagensville Junction to Hagensville 138kV line. One terminal will connect to the 69kV line to the the Airport station. One terminal will connect to the 69 kV line to the Tower station. | MI |  |  | M1 - Proposed | 9000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | East | MI | 24558 | 28022 | Substation | 2025-12-31 | Cronk |  |  | 138 |  | Construct J1658 Interconnection 138kV station as a breaker and half station with three 40kA breakers in a ring bus configuration. | MI |  |  | M1 - Proposed | 6800964 | METC | Not Shared
A | B | West | WI | 25323 | 28448 | Substation | 2029-09-30 | Willow River |  |  | 115 |  | Add bus and breaker at Willow River to accommodate the new 115kV transmission line | WI |  |  | M1 - Proposed | 2000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | A | West | ND | 4295 | 28489 | Substation | 2028-12-31 | Nelson Lake | 345-230kV Sub Expansion |  | 345 | 230 | Expand planned Nelson Lake Substation to include 345/230kV transformer (1000MVA) and 1x 345 kV line entrance | ND |  |  | M1 - Proposed | 30000000 | MINNESOTA POWER INC. | Not Shared
B | B | East | MI | 50062 | 50102 | Line New | 2028-06-01 | Charge | Mud Lake | 1&2 | 138 |  | Construct new 138 kV, double-circuit lines (approximately 7.5 miles) from Charge to Mud Lake substation. The new lines are to use 1431 ACSR conductor and pre-built to 230 kV standard. New right-of-way will be required for the construction of this 138 kV double-circuit. | MI |  | 7.5 | M1 - Proposed | 37350000 | METC | Not Shared
A | B | Central | IN | 25402 | 28545 | Substation | 2025-05-28 | Petersburg |  |  | 138 |  | Replace 1 138 kV breaker. #4 | IN |  |  | M1 - Proposed | 900000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | Central | IL | 23374 | 27226 | Line New | 2026-06-01 | Ameren Steamboat | Babylon | 1 | 138 | 138 | New Ameren Interconnection to Babylon 138 kV Line | IL |  | 1.4 | M1 - Proposed | 1400000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | MN | 25507 | 28796 | Substation | 2025-08-31 | Umore Park |  |  | 115 |  | New 115kV load serving substation. | MN |  |  | M1 - Proposed | 17000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 22015 | 26679 | Line Upgrade | 2028-06-01 | Blackstone |  |  | 138 |  | Upgrade terminal equipment at Blackstone. | MI |  |  | M1 - Proposed | 481000 | METC | Not Shared
A | B | South | AR | 25544 | 28748 | Line Upgrade | 2024-07-01 | Commerce | Ringier | 1 | 69 |  | Rebuild the Commerce - Ringier 69kV line due to Aging Infrastructure | AR |  |  | M4 - Project in Service | 873580 | CITY WATER AND LIGHT PLANT OF JONESBORO ARKANSAS | Not Shared
A | B | West | WI | 50108 | 50168 | Substation | 2028-09-10 | Plover |  |  | 115 |  | Existing Plover Substation will add one (1) new 138kV bus tie breaker and three (3) bus VTs to the existing bus configuration. Three (3) new relay panels will be added to the existing control house for protecting the new buses and Generator Lead Line. | WI |  |  | M1 - Proposed | 1735000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24450 | 27987 | Substation | 2026-08-03 | Fitz |  |  | 120 |  | Install breaker position HF and disconnect switches HH and HD. | MI |  |  | M1 - Proposed | 912475 | ITC | Not Shared
A | B | West | MN | 25356 | 28558 | Misc. | 2024-01-15 | Coon Creek | Bunker Lake | 1 | 345 |  | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | 6.5 |  | M1 - Proposed | 50000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | South | MS | 25438 | 28686 | Line Upgrade | 2026-01-01 | Canton | South Canton |  | 230 |  | Rebuild/reconductor Canton - South Canton 230 kV line to at least 779 MVA. | MS |  |  | M1 - Proposed | 55200000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | South | MS | 25214 | 28325 | Line New | 2025-01-01 | Catlett | Virlilia | 2 | 230 |  | Short transmission lines to interconnect Virlilia to Catlett 230 kV substation. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | KY | 25081 | 28196 | Substation | 2025-12-01 | Webster County |  |  | 161 |  | new switching station | KY |  |  | M1 - Proposed | 0 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | B | South | LA | 50011 | 50024 | Substation | 2025-05-16 | Ivanhoe | Bayou Warehouse | 1 | 138 | 138 | Construct a new 3 terminal ring bus substation tapped into the Ivanhoe to Bayou Warehouse 138 kV line to serve a new customer load. | LA |  |  | M1 - Proposed | 21224064 | CLECO POWER LLC | Not Shared
A | B | Central | IN | 50032 | 50058 | Line New | 2026-01-15 | Petersburg | R1021 |  | 345 |  | Transmission line to serve new energy center. Shares Gen lead line with R1022 (MTEP 50033) | IN |  | 1 | M1 - Proposed | 3000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | South | AR | 25472 | 28706 | Line Upgrade | 2025-12-01 | Greenbrier |  |  | 161 |  | New equipment | AR |  |  | M1 - Proposed | 32893800 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | West | MN | 25345 | 28500 | Line Upgrade | 2029-12-30 | Cleveland | Sheas Lake | 1 | 69 | 69 | The ITCM portion of the Cleveland – Sheas Lake 69 kV line was originally constructed in the 1960’s and is at end of life and is approaching eminent failure condition. In addition, this line has been identified as needing to have it’s thermal rating increased and also due to it connecting between two areas with 115 kV infrastructure, it should be built to allow for future conversion to 115 kV operation if/as needed. | MN |  |  | M1 - Proposed | 22306250 | ITC MIDWEST | Not Shared
A | B | Central | IN | 25444 | 28596 | Line Upgrade | 2026-12-31 | Azteca | VIP | 74 | 69 |  | Replacing ~1 mile of poles | IN | 1 |  | M1 - Proposed | 4000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
B | B | East | MI | 50064 | 50130 | Line Upgrade | 2028-06-01 | Cottage Grove | Karn | 1 | 138 |  | Rebuild approximately ~7.86 miles from Cottage Grove to structure #5M4282 138 kV circuits to 954 ACSR conductor utilizing standard 138 kV double- circuit structures with OPGW. Leave the west side of the double-circuit structures vacant. | MI | 38.34 | 7.8 | M1 - Proposed | 13000000 | METC | Not Shared
A | B | West | WI | 50113 | 50183 | Substation | 2027-03-19 | Eldorado |  |  | 345 |  | ATC System Protection and supporting activities, potential ground grid mitigation | WI |  |  | M1 - Proposed | 225000 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | East | MI | 24479 | 27937 | Substation | 2026-05-01 | Gordon |  |  | 345 |  | Install Gordon line entrance structure at position RH29 and switch 177 for generator interconnection. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | MN | 25446 | 28670 | Line Upgrade | 2024-12-31 | 69 kV system |  |  | 69 |  | Replace 69 kV poles due to condition | MN |  |  | M1 - Proposed | 400000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A | B | East | MI | 20017 | 25698 | Line Upgrade | 2028-06-01 | Alma | Regal | 1 | 138 |  | Rebuild approximately 1.34 miles of the Cheesman – Regal #1 138kV with 954 ACSR 138kV double circuit standards with OPGW | MI | 6 |  | M1 - Proposed | 17785000 | METC | Not Shared
A | B | East | MI | 25210 | 28311 | Substation | 2026-01-30 | Moore Road |  |  | 138 |  | Replace Moore Road WM33 477 ACSR 26/7 trainer with 1590 ACSR to raise rating to 209 MVA SN and 237 MVA SE. | MI |  |  | M1 - Proposed | 27635 | METC | Not Shared
A | B | East | MI | 25245 | 28291 | Line Upgrade | 2025-10-31 | Coldwater | Ash Road Junction |  | 138 |  | Remediate the Coldwater-Ash Road Junction sag limit to achieve a minimum rating of 200 MVA Summer Emergency. | MI |  |  | M1 - Proposed | 335000 | METC | Not Shared
B | B | South | LA | 50092 | 50138 | Misc. | 2027-12-31 | Cocodrie |  |  | 230 |  | Relay Upgrades for Cocodrie Substation | LA |  |  | M1 - Proposed | 1550000 | CLECO POWER LLC | Not Shared
A | B | West | MN | 22487 | 27354 | Substation | 2025-11-30 | Audubon 230 kV (620336) | Audubon 41.6 kV (658113) | 2 | 230 | 42 | Adjust Audubon 230/115 kV transformer #2 tap. | MN |  |  | M1 - Proposed | 1000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | Central | IL | 24717 | 28068 | Line Upgrade | 2025-12-01 | edwards | Keystone |  | 138 |  | Rebuild Edwards-Keystone-1397 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL |  |  | M1 - Proposed | 5500000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 24536 | 27996 | Substation | 2026-12-31 | Beecher | Pixley |  | 138 |  | Install required entrance structures and disconnect switch as TOIF. Install position BM8 at Rouget to interconnect J1571 generator. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | Central | IN | 25144 | 28216 | Line Upgrade | 2024-08-01 | Oakland City | Duke Oakland City | Y52-3 | 69 |  | Rebuild ~2.76 miles of 69kV due to aging infrastructure (conductor size not changing) | IN | 2.78 |  | M1 - Proposed | 3882590 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | Central | IN | 25395 | 28582 | Substation | 2026-12-31 | Oakland City |  |  | 69 | 15 | Replacing 69/15kV transformer and 69kV circuit breakers | IN |  |  | M1 - Proposed | 2700000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | MN | 25317 | 28415 | Misc. | 2024-09-30 | Wakefield |  |  | 115 |  | Upgrade system protection equipment at Wakefield 115 kV substation. | MN |  |  | M1 - Proposed | 450000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | MI | 24924 | 28170 | Substation | 2027-12-01 | Straits |  |  | 138 | 69 | Straits SS Power Transformer Asset Renewal | MI |  |  | M1 - Proposed | 10800000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | MO | 25276 | 28479 | Line Upgrade | 2027-12-01 | Conway |  |  | 138 |  | Add interrupting devices on XFMRs 1,2,3,4 Add Line BKRs to MASN-WLDW-1&2, CNWY-TYSN-3&4 Aging infrastructure replacements | MO |  |  | M1 - Proposed | 17500000 | AMEREN MISSOURI | Not Shared
A | B | West | IA | 25411 | 28664 | Misc. | 2027-12-01 | Rock Valley Town Tap | NIPCO K218 | 1 | 69 |  | Retire a section of the Rock Valley Town Tap-NIPCO K218 69 kV line (~0.25 miles) | IA |  |  | M1 - Proposed | 100000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25461 | 28628 | Substation | 2027-08-01 | Johnson Creek |  |  | 161 |  | Install Johnson Creek 161 kV line terminal | IA |  |  | M1 - Proposed | 3400000 | MIDAMERICAN ENERGY CO. | Not Shared
A | A | West | MN | 3856 | 20819 | Line Upgrade | 2028-12-31 | HVDC Line | MN Structure Upgrades |  | 250 |  | Structure Upgrades in Minnesota to increase capacity | MN |  |  | M1 - Proposed | 26000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | MN | 50020 | 50034 | Line Upgrade | 2026-12-31 | Red Wing | GRE Spring Creek | 1 | 69 |  | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. | MN |  |  | M1 - Proposed | 2000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25447 | 28608 | Substation | 2025-12-01 | Forest & Vermont |  |  | 69 |  | Replace overdutied 69 kV breakers | IA |  |  | M1 - Proposed | 2400000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25308 | 28370 | Substation | 2028-12-31 | Leon Rodeo | Substation |  | 69 | 69 | ITCM will build the 69 kV portion of a new Leon Rodeo sub with 2 line breakers and a bus tie breaker. | IA |  |  | M1 - Proposed | 4118979 | ITC MIDWEST | Not Shared
B | B | West | WI | 25020 | 28179 | Line Upgrade | 2028-03-01 | Lost Dauphin | Oak St | E-31 | 69 |  | Partial rebuild of line E-31 from Lost Dauphin SS to Oak St SS. | WI |  |  | M1 - Proposed | 11400000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 23910 | 27599 | Line Upgrade | 2030-12-31 | Eden | Rock Branch | Y-106 | 69 |  | Eden – Rock Branch 69kV (Y-106), Rebuild | WI |  |  | M1 - Proposed | 67900000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MI | 25164 | 28236 | Line Upgrade | 2028-06-01 | Menominee | 30th Ave. | Y-199 | 69 |  | Rebuild and install OPGW on approximately 1.3 miles of line Y-199 from Menominee SS to 30th Ave. SS. | MI |  |  | M1 - Proposed | 8400000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25340 | 28460 | Transformer | 2025-10-15 | Albany |  |  | 69 | 13 | Install new Albany TR3 69/12.5 kV transformer and replace existing TR2 both with 14 MVA transformers on the West side of the Albany substation yard. | MN |  |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 15831 | 23880 | Line Upgrade | 2028-06-01 | Alma | Regal | 2 | 138 |  | Rebuild the entire ~5.8 mile-long Alma – Regal 2 138 kV line by replacing the existing assets (all structures, 336 ACSR conductor, and the 336 ACSR line entrance at Alma) with new structures that are designed for 954 ACSR conductor and install this conductor along with OPGW. | MI | 3.8 |  | M1 - Proposed | 10617000 | METC | Not Shared
A | B | Central | IL | 23375 | 27077 | Transformer | 2029-12-31 | Babylon |  | 1 | 138 | 69 | Upgrade Babylon 138/69 kV XFMR | IL |  |  | M1 - Proposed | 2600000 | PRAIRIE POWER, INC. | Not Shared
A | B | East | MI | 50121 | 50197 | Substation | 2028-06-01 | Cottage Grove |  |  | 138 |  | Replace station equipment at Cottage Grove | MI |  |  | M1 - Proposed | 660000 | METC | Not Shared
A | B | South | MS | 25540 | 28764 | Line New | 2025-12-01 | State Line GOAB | State Line |  | 69 |  | In order to serve the member delivery point, tap L32 (State Line - Leakesville) with a 69kV Goab and construct a new line to the delivery point. | MS |  |  | M1 - Proposed | 600000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | Central | MO | 25039 | 28188 | Substation | 2025-12-01 | Taum Sauk |  |  | 138 |  | MISO project J1213, will add 60 MW to the existing Hydro Energy Generating Facility, Transmission Owner will modify the 138 kV bus at its existing Taum Sauk 138 kV substation. | MO |  |  | M1 - Proposed | 100000 | AMEREN MISSOURI | Not Shared
A | B | Central | IN | 25526 | 28783 | Substation | 2027-03-01 | Terre Haute Tonic Water | new switching station |  | 138 |  | Terre Haute new load - Tonic Water: located north of the Vigo Co. Industrial Park in the 13821 ckt; new 138kV line loop to be 954ACSS@200C - 3.26 mi. west side / 2.17 mi. east side; 138kV sub to be 7 breakers in a breaker and 1/2 layout; (2) dedicated customer-owned 138kV outlet lines to their load; Load ramp: 33MW/11MVAR each step - 7/1/25; 7/1/26; 11/1/26; 31MW/10MVAR - 3/1/27; (2) 36MVAR - 138kV capacitors | IN |  | 5.43 | M1 - Proposed | 35777500 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | WI | 25273 | 28442 | Substation | 2025-12-31 | Bateman |  |  | 69 |  | Project to convert 69kV switch 4E442 to a circuit breaker and upgrade and bus relaying scheme at the Bateman substation. | WI |  |  | M1 - Proposed | 1000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25201 | 28252 | Substation | 2025-06-30 | Magnolia | Substation |  | 161 | 161 | TOIF includes facilities and equipment dedicated to the Generating Facility including; dead-end, switch, relay panel, CCVTs, etc. | MN |  |  | M1 - Proposed | 417240 | ITC MIDWEST | Not Shared
A | B | East | MI | 50038 | 50078 | Line New | 2026-08-19 | Murphy | Orr Road | 1 | 345 |  | Construct a new ~ 4-mile 345 kV line from Murphy 345 kV to Orr Road with OPGW using 2-1431 ACSR 45/7 on standard double circuit structures and leave the south side vacant. | MI |  |  | M1 - Proposed | 16000000 | METC | Not Shared
A | B | Central | IN | 25403 | 28573 | Substation | 2026-12-31 | Newtonville |  |  | 161 |  | Replacing 161/138kV transformer, 138/69kV transformer and circuit breakers. | IN |  |  | M1 - Proposed | 18500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | South | MS | 25520 | 28749 | Line New | 2028-03-01 | Lucedale | South Lucedale |  | 69 |  | In order to serve the member delivery point economically and reliably, a new 2.7-mile radial line will be constructed from the Lucedale 69kV Switching Station to the member delivery. | MS |  |  | M1 - Proposed | 4000000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | Central | IN | 25149 | 28228 | Substation | 2025-12-31 | County Line |  | T1 | 69 |  | Replacement of 69/12kv transformer T1 at County Line substation | IN |  |  | M1 - Proposed | 3000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | MN | 25507 | 28797 | Line New | 2025-08-31 | Rosemount | Empire | 1 | 115 |  | In-and-out tap to existing Rosemount - Empire 115 kV line 0822. | MN |  |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25335 | 28512 | Line Upgrade | 2025-09-04 | Thorntown | Lebanon |  | 69 |  | Rebuild 6943 line from Thorntown Substation to Lebanon Substation with 954ACSR@120C - approx. 10 miles; Rebuild the double circuit section of 69134/6943; upgrade line terminals at Thorntown and Lebanon Enterprise | IN | 10 |  | M1 - Proposed | 28200000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | East | MI | 22015 | 26680 | Line Upgrade | 2028-06-01 | Leoni |  |  | 138 |  | Upgrade terminal equipment at Leoni. | MI |  |  | M1 - Proposed | 127000 | METC | Not Shared
A | B | West | MN | 25356 | 28559 | Misc. | 2024-01-15 | Bunker Lake | Sherco | 1 | 345 |  | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | 37 |  | M1 - Proposed | 250000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | ND | 50152 | 50254 | Substation | 2025-09-01 | Ellendale Data Center Sub |  |  | 230 | 34 | Additions to the Ellendale Data Center Sub for the additional load. Add transformer, breakers and switches. | ND |  |  | M1 - Proposed | 7310211 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | West | WI | 50120 | 50192 | Substation | 2028-09-10 | Morgan |  |  | 138 |  | J1615 138kV Interconnection Facilities | WI |  |  | M1 - Proposed | 433000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 50184 | 50321 | Substation | 2026-06-30 | Elm Road |  |  | 345 |  | Driven by WEC’s Generating Facility Modification Request to relocate Elm Road generation POIs, this project will expand Elm Road 345 kV substation breaker and a half configuration with three new rungs and six new 345kV breakers. | WI |  |  | M1 - Proposed | 22600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 50026 | 50045 | Line Upgrade | 2025-05-01 | Kaukauna Central Tap | Melissa | 971K11 | 138 |  | Rerate line 971K11. | WI |  |  | M1 - Proposed | 7000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24561 | 28032 | Substation | 2025-12-31 | Aphis |  |  | 138 |  | Install a line entrance structure and disconnect as TOIF. Install position WM13 at Aphis to interconnect J1614 generator. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | WI | 50036 | 50065 | Line Upgrade | 2023-07-31 | Big Hill Park | Paddock | X-39 | 138 |  | 605097 - X39 (138kV) Sectionalization The X-39/X-155 138 kV Transmission Line Loop-In Network Upgrade will consist of multiple double circuit dead-end poles, multiple double circuit tangent poles, one single circuit dead end pole and two OPGW lines through the Transmission Owner’s new J1304 switchyard, segmenting the line into X-39 towards Paddock and X-155 towards Townline Road. | WI |  |  | M4 - Project in Service | 2205217 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | West | IA | 50106 | 50156 | Substation | 2026-03-31 | Big Cedar |  |  | 345 | 345 | New Big Cedar 345 kV Switching Station | IA |  |  | M2 - Appendix A Approved | 33106789 | ITC MIDWEST | Not Shared
A | B | South | AR | 50004 | 50015 | Misc. | 2026-04-03 | Crooked Lake 161kV |  |  | 161 |  | Upgrades consist of power quality metering panel, CT removal, revenue metering install, new telcom equipment, and installation of digital disturbance recorder panel. | AR |  |  | M1 - Proposed | 1296000 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | East | MI | 25227 | 28312 | Line Upgrade | 2025-03-03 | Beecher | Knowles |  | 138 |  | Remediate Knowles - Dowling Junction sag limit to achieve a rating of at least 240 MVA SN and 266 MVA SE. | MI |  |  | M1 - Proposed | 1098750 | METC | Not Shared
A | B | East | MI | 24444 | 27938 | Substation | 2025-05-01 | Dorrance |  |  | 138 |  | Install position BM14 as TOIF for the J1550 generator to connect. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | East | MI | 50060 | 50098 | Line New | 2028-06-01 | Bismarck | Macomb | 1 | 120 |  | Construct a new 120 kV circuit (~6.7 miles) from Bismarck to Macomb. | MI | 2.8 | 3.9 | M1 - Proposed | 8700000 | ITC | Not Shared
A | B | West | MN | 25445 | 28597 | Line Upgrade | 2027-12-31 | Prairie Woods Tap | Sunburg | 1 | 69 |  | Rebuild 7.2 miles of the Prairie Woods tap to Sunburg line. | MN | 7.2 |  | M1 - Proposed | 7649388 | GREAT RIVER ENERGY | Not Shared
B | B | East | MI | 25249 | 50042 | Line Upgrade | 2028-06-01 | Stephens | Stephens |  | 120 |  | Relocate Bismarck - Stephens 2 120kV line structure #8086 from current location to applicable location for accommodating more space for the 120kV substation work. | MI |  |  | M1 - Proposed | 820000 | ITC | Not Shared
B | B | West | SD | 24335 | 27825 | Line Upgrade | 2027-06-01 | Big Stone (620314) | Hwy. 12 (620215) | 1 | 115 |  | Rebuild GRE's 2.03 miles of the Big Stone - Hwy 12 115 kV line with a larger conductor. | SD |  |  | M1 - Proposed | 1500000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | West | ND | 24375 | 27844 | Line Upgrade | 2028-12-31 | Center | Jamestown |  | 345 |  | Center - Jamestown 345 KV | ND |  |  | M1 - Proposed | 4400000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | South | MS | 25215 | 28333 | Line Upgrade | 2027-06-01 | Andes | Soldiers |  | 230 |  | 2x230 kV short transmission lines will interconnect the Soldiers 230 kV substation to the Andes 500/230 kV station. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | MN | 20030 | 25725 | Voltage Device | 2024-12-31 | LSPI |  |  | 115 |  | Replace the problematic LSPI capacitor bank. | MN |  |  | M1 - Proposed | 800000 | MINNESOTA POWER INC. | Not Shared
A | B | West | IA | 25197 | 28522 | Substation | 2025-07-31 | Wever | Substation |  | 161 | 161 | The J1734 TOIF upgrades will include dead-end, disconnect switch, arresters, PT’s, line relay panel, and associated equipment dedicated to the generating facility. | IA |  |  | M1 - Proposed | 562250 | ITC MIDWEST | Not Shared
A | B | West | MN | 25399 | 28633 | Line Upgrade | 2025-09-26 | Jamestown Tap GRE |  |  | 69 |  | Upgrade Jamestown Tap switches (SS2824) to 1200 A. | MN |  |  | M1 - Proposed | 600000 | GREAT RIVER ENERGY | Not Shared
A | B | West | IA | 25307 | 50322 | Substation | 2026-12-15 | State Center Rural | State Center Rural |  | 69 | 69 | Construct transmission portion of new State Center Rural substation | IA |  |  | M1 - Proposed | 2613014 | ITC MIDWEST | Not Shared
A | B | Central | MO | 25290 | 28433 | Substation | 2027-12-31 | Sprott 69kV |  |  | 69 | 12 | New 5/7MVA 69-12kV Substation | MO |  |  | M1 - Proposed | 1200000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A | B | Central | IL | 25316 | 28416 | Line New | 2029-12-31 | Fandon | Colchester |  | 69 | 69 | New Fandon-Colchester 336 ACSR 69 kV Line | IL |  | 5.2 | M1 - Proposed | 3380000 | PRAIRIE POWER, INC. | Not Shared
B | B | Central | IN | 25473 | 28707 | Substation | 2030-06-01 | Gibson | line terminals |  | 345 |  | (1) Insert 1% impedance / 3000A series reactors at the Gibson terminal of the 34516 line to SIGE Francisco; (2) Upgrade bus conductor from 2500AL to (2)1590AL at the Gibson terminal of the 34507 line to IPL Petersburg | IN |  |  | M1 - Proposed | 16500000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | East | MI | 21786 | 28292 | Misc. | 2026-12-31 | Vestaburg |  |  | 69 |  | In conjunction with the planned relocation of the Vestaburg 69kV station, redesign and install new line exits | MI |  |  | M1 - Proposed | 1000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | West | IA | 25433 | 28671 | Line New | 2025-09-16 | Graettinger Marsh | Trumbull Lake | 1 | 345 |  | Network Upgrades for J1270 Generator (345 kV line taps) | IA |  |  | M1 - Proposed | 2500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | South | AR | 50013 | 50026 | Substation | 2025-04-01 | Grand Prairie |  |  | 115 |  | Construct a new 115 kV substation with two 115/4.16 kV 33.3 MVA transformers to serve the planned motors at the pumping station. Cut into the Devalls Bluff – Brinkley East 115kV line and build ~.20 circuit mile (.40 total circuit mile) of “in and out” 115kV line. | AR |  |  | M3 - Under Construction | 15626062 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | South | MS | 25214 | 28326 | Voltage Device | 2025-01-01 | Virlilia |  |  | 230 |  | 108 MVAR capacitor bank at Virlilia 230 kV substation. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | South | LA | 25430 | 28665 | Line Upgrade | 2027-12-01 | Fairview | Madiosnville |  | 230 |  | Upgrade short 230 kV line | LA |  |  | M1 - Proposed | 700000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | IN | 25440 | 28583 | Substation | 2028-12-31 | Vigo Coal |  |  | 69 | 12 | Replacing 69/12kV transformer and circuit breakers | IN |  |  | M1 - Proposed | 6000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | South | TX | 24958 | 28143 | Substation | 2026-01-30 | Sandling |  |  | 230 |  | Station cut in on the Port Acres to Keith Lake and Legend to Keith Lake 230 kV lines | TX |  |  | M1 - Proposed | 114200000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 21786 | 26362 | Substation | 2025-12-31 | Vestaburg 69kV Station |  |  | 69 |  | Rebuild and relocate station | MI |  |  | M1 - Proposed | 6500000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | East | MI | 24451 | 27988 | Substation | 2026-08-03 | Fitz |  |  | 120 |  | Install line entrance structure and disconnect switch. Install position HI at Fitz to interconnect J1516 generator. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
A | B | Central | IL | 24737 | 28069 | Line Upgrade | 2025-12-01 | Woodhall | Hallock |  | 138 |  | Rebuild the Woodhall-Hallock-1570 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL |  |  | M1 - Proposed | 16000000 | AMEREN ILLINOIS | Not Shared
A | A | West | ND | 3856 | 20820 | Line Upgrade | 2028-12-31 | HVDC Line | ND Structure Upgrades |  | 250 |  | Structure Upgrades in North Dakota to increase capacity | ND |  |  | M1 - Proposed | 26000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | IA | 50030 | 50053 | Substation | 2025-05-01 | Johnson Creek |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25461 | 28629 | Substation | 2027-08-01 | Maffitt Lake |  |  | 161 |  | Install Maffitt Lake 161 kV line terminal | IA |  |  | M1 - Proposed | 3400000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | South | MS | 25540 | 28765 | Line New | 2025-12-01 | State Line GOAB |  |  | 69 |  | In order to serve the member delivery point, tap L32 (State Line - Leakesville) with a 69kV Goab and construct a new line to the delivery point. | MS |  |  | M1 - Proposed | 125000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | WI | 25165 | 28237 | Line Upgrade | 2028-06-01 | Glory Road | Oak St | GLYN4 | 69 |  | Rebuild and install OPGW on approximately 0.7 miles of line GLNY41 from Glory Rd SS towards Oak St SS. | WI |  |  | M1 - Proposed | 6000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25308 | 28371 | Line New | 2028-12-31 | Grand River | Leon Rodeo | 1 | 69 | 69 | ITCM will construct new line taps for the new Leon Rodeo sub and retire any existing 69 kV line no longer needed. | IA |  |  | M1 - Proposed | 130000 | ITC MIDWEST | Not Shared
A | B | Central | IN | 25385 | 28546 | Substation | 2025-09-11 | Petersburg |  |  | 138 |  | Replace 6 345 kV breakers. #3A, #3B, #3C, #4A, #4B, and #4C. | IN |  |  | M1 - Proposed | 5400000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | IA | 25448 | 28609 | Substation | 2026-12-01 | Browns Woods |  |  | 161 |  | Construct new 161-13 kV substation | IA |  |  | M1 - Proposed | 3500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | KY | 25081 | 28197 | Line Upgrade | 2025-12-01 | Hopkins County | Webster County | 1 | 161 |  | 4.23 mile of OPGW and related equipment. | KY |  |  | M1 - Proposed | 0 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | B | East | MI | 50060 | 50099 | Substation | 2028-06-01 | Bismarck |  |  | 120 |  | Install a new 120 kV breaker at Bismarck position "JK" to terminate the new Bismarck - Macomb 120 kV line. | MI |  |  | M1 - Proposed | 1100000 | ITC | Not Shared
A | B | Central | IN | 25542 | 28737 | Misc. | 2025-09-30 | Madison 138 |  |  | 138 |  | J1357 150MW Williams Power, LLC battery storage (600MWh): Madison 138 - add breaker (straight bus config) and line terminal on bus section #1 | IN |  |  | M1 - Proposed | 5680572 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | WI | 25323 | 28449 | Transformer | 2029-09-30 | Willow River |  |  | 115 | 24 | Replace the two 70 MVA TR’s at Willow River. | WI |  |  | M1 - Proposed | 8000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25145 | 28217 | Substation | 2024-11-01 | Lynnville |  |  | 69 |  | Replace two 69kV oil breakers with gas breakers. | IN |  |  | M1 - Proposed | 872319 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | East | MI | 24461 | 27948 | Substation | 2025-11-17 | Grassmere |  |  | 345 |  | Install BKRs AT, BF, CT, CM, and associated disconnect switches at Grassmere. Install OrionLX and IOs. Install CCVTs for CQ, Bus 301, and Bus 303. | MI |  |  | M1 - Proposed | 7602430 | ITC | Not Shared
A | B | West | MN | 25374 | 28560 | Line Upgrade | 2027-04-30 | Enbridge Blackberry Tap | Warba | 1 | 69 |  | Rebuild 3.76 miles of the Enbridge Blackberry Tap to Warba line. | MN | 3.76 |  | M1 - Proposed | 4726830 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 25507 | 28798 | Line New | 2025-12-31 | Umore Park | Inver Grove | 1 | 115 |  | Build 6 miles new double circuit 115 kV line from Umore Park - Inver Grove. | MN |  | 6 | M1 - Proposed | 13000000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | WI | 25259 | 28443 | Substation | 2028-09-30 | Grassland |  |  | 69 |  | Add 3 transmission breakers at Grassland substation | WI |  |  | M1 - Proposed | 3000000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | WI | 25004 | 28180 | Line Upgrade | 2027-08-01 | South Lake Geneva | North Lake Geneva | Y-152 | 69 |  | Partial rebuild of line Y-152 from South Lake Geneva SS to North Lake Geneva SS. | WI |  |  | M1 - Proposed | 11000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | MS | 25520 | 28750 | Substation | 2028-03-01 | South Lucedale |  |  | 69 |  | Upgrade member high side substation equipment to accommodate the 69kV service. | MS |  |  | M1 - Proposed | 2477100 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | MN | 25340 | 28461 | Substation | 2025-10-15 | Albany |  |  | 69 |  | Rebuild and relocate NSP's facilities on the west side of the Albany substation yard. | MN |  |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25346 | 28501 | Substation | 2026-12-30 | Walcott 80 | Substation |  | 69 | 34 | IPL has notified ITC that they will be constructing a new Walcott 80 Substation which will replace their existing Walcott and Walcott North substations. The new substations will initially connect at 34.5 kV and then be converted to 69 kV as part of the Fulton – Dixon 69 kV conversion. IPL has requested ITC install two 69 kV busses with two line breakers and a bus tie breaker. New line taps for Walcott 80 substation to be constructed with T2-4/0 ACSR conductor. While operating at 34.5 kV, one new breaker looking toward Calamus 3350 should be operated as the new normal open point, with PTS 3372 becoming normally closed to allow the Walcott 80 load to be switched between the two 34.5 kV sources. Existing taps to Walcott and Walcott North to be retired under separate future EI Sketches prior to 69 kV conversion. | IA |  |  | M1 - Proposed | 3685151 | ITC MIDWEST | Not Shared
A | B | West | WI | 21900 | 26496 | Line Upgrade | 2028-11-01 | Mullet River |  | X-57 | 138 |  | • Rebuild X-57 from the existing Mullet River site to the new substation site as a double circuit to route X-89 and X-97 into the new yard. • Build new double circuit taps to tie 8241 and LYNG11 into the new site. • Build new segment for Y-50 to tie it into the new site. • Build new double circuit connection for X-57 operated as a bifurcated single circuit to the new site. • Retire Y-50 from North Mullet River to connection with new tap to the new site | WI |  |  | M1 - Proposed | 32300000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | ND | 9997 | 21422 | Substation | 2026-12-31 | Rolette 230 kV |  |  | 230 | 69 | Install one 230 kV breaker, two 230 kV line switches, and one 69 kV breaker. Install one 230/115/69 kV Transformer (140 MVA) leaving the 115 kV winding disconnected. | ND |  |  | M1 - Proposed | 8700000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | Central | IN | 25088 | 28229 | Substation | 2025-04-01 | Givens |  | T1 | 69 |  | Replacement of 69/12kV transformer T1 at Givens substation | IN |  |  | M1 - Proposed | 3500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
B | B | East | MI | 50062 | 50104 | Substation | 2028-06-01 | Mud Lake |  |  | 138 |  | Add two rows and install six (6) 138 kV breakers to terminate the two new lines at Mud Lake station. | MI |  |  | M1 - Proposed | 6270000 | METC | Not Shared
A | B | West | MI | 50137 | 50217 | Line Upgrade | 2025-12-01 | Indian Lake | Hiawatha | ILKD31/6912 | 138 |  | Test all of 138kV and 69kV Line ILKD31/6912 double circuit structures with 3-point ground test method (356) structures). Install additional grounding on an estimated and assumed 190 each of the steel structures to meet ATC Construction Specifications. Retest and install additional 4-150 ft runs of counterpoise system grounding with Ground Enhancing. Counterpoise will likely need to be installed after initial ground rod installation and retesting between structures 106635 and 106765 (Boring B-20 to B-53) due to bedrock located less than 10 feet from the surface. Replace broken ground connection on approximately 24 structures per ATC specification as required. | MI |  |  | M1 - Proposed | 4000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | AR | 50094 | 50144 | Substation | 2026-04-01 | New interconnection |  |  | 115 |  | Construct 115/13.2 kV, 20 MVA substation. | AR |  |  | M1 - Proposed | 4000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | B | East | MI | 21968 | 26596 | Line New | 2026-06-01 | New Station | Delaney | 1 | 138 |  | Construct ~1.1 miles of line through new right-of-way, using 1431 ACSR conductor, to connect Delaney distribution substation to the new 138 kV station. | MI |  | 1.1 | M1 - Proposed | 0 | METC | Not Shared
A | B | West | MN | 25454 | 50142 | Line New | 2028-10-06 | East Chain | East Chain Tap |  | 69 | 69 | Construct a tie line between East Chain municipal and GRE’s FE-WB (East Chain to Wilbert) line. | MN |  | 1.75 | M1 - Proposed | 3000000 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IN | 25335 | 28513 | Line New | 2025-09-04 | Thorntown | 6943 tap |  | 69 |  | Thorntown substation: Add a 69kV 2000 amp line terminal and line to existing radial line off of the 6943 serving the Boone County REMC Pike 69kV substation (and new proposed WVPA Eli Lilly load). New Line = 69211. | IN |  | 0.5 | M1 - Proposed | 3000000 | DUKE ENERGY INDIANA, LLC | Not Shared
B | B | East | MI | 50064 | 50132 | Substation | 2028-06-01 | Cottage Grove | Karn | 1 | 138 |  | Replace station equipment at Cottage Grove | MI | 38.34 | 7.8 | M1 - Proposed | 660000 | METC | Not Shared
A | B | West | WI | 25000 | 28171 | Line Upgrade | 2028-10-01 | Lakefront | Revere Dr | D-104 | 69 |  | Rebuild and install OPGW on approximately 1.84 miles of D-104 from Lakefront to Revere Dr. | WI | 1.84 |  | M1 - Proposed | 9000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 25195 | 28313 | Substation | 2028-06-01 | MCV |  |  | 345 | 138 | Install six 345 kV breakers to convert the 345 kV side to ring-bus. Expand MCV 138 kV buses, replace 10 existing breakers, and install 3 additional breakers to the west as depicted in the diagram to accommodate the 3rd XFMR at MCV. | MI |  |  | M1 - Proposed | 28000000 | METC | Not Shared
A | B | West | IA | 25205 | 28268 | Line Upgrade | 2027-12-31 | Meservey Tap | Meservey | 1 | 69 | 69 | The radial 6.9 miles Meservey Tap 69 kV line is at the end of its useful life and needs to be rebuilt for continued use. | IA | 6.9 |  | M1 - Proposed | 4766250 | ITC MIDWEST | Not Shared
A | B | West | WI | 50138 | 50218 | Substation | 2027-06-01 | Manhattan |  | X-47 | 138 |  | Construct one new 138 kV interconnection substation named Manhattan near the city of Beaver Dam. Also, expand and upgrade the exiting North Randolph 138 kV bus to support additional circuits to Manhattan. Rebuild the existing N Randolph – N Beaver Dam 138 kV line (X-47) forming a new North Randolph - Manhattan 138 kV line and construct a new double circuit 138 kV transmission line between North Randolph and Manhattan substations. | WI |  |  | M1 - Proposed | 161000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 22018 | 26681 | Line Upgrade | 2028-06-01 | Blackstone |  |  | 138 |  | Upgrade terminal equipment at Blackstone. | MI |  |  | M1 - Proposed | 297000 | METC | Not Shared
A | B | West | WI | 25311 | 28385 | Misc. | 2028-12-31 | Stinson |  |  | 115 |  | Retire Stinson 115 kV PST. | WI |  |  | M1 - Proposed | 1000000 | MINNESOTA POWER INC. | Not Shared
A | B | Central | MO | 22949 | 26911 | Substation | 2026-06-01 | Stoddard |  |  | 161 |  | Rebuild Stoddard substation into a ring bus configuration, including replacement of aging/overstressed/broken equipment. | MO |  |  | M1 - Proposed | 15900000 | AMEREN MISSOURI | Not Shared
A | B | West | WI | 50036 | 50063 | Substation | 2023-07-31 | Paddock |  |  | 138 |  | 605094 - Paddock SS Relay Panel Improvements | WI |  |  | M4 - Project in Service | 209851 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | Central | IL | 24987 | 28189 | Substation | 2025-12-01 | Mason (IL) |  |  | 138 |  | MISO project J1454, a 40.90 MW Wind Generating Facility, will interconnect to the Ameren Illinois Transmission System. Project No. J1454 is an expansion of J1055 Generating Facility. Transmission Owner will modify the 138 kV bus at its existing Mason substation | IL |  |  | M1 - Proposed | 100000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 24537 | 27997 | Substation | 2025-04-01 | Lukesport |  |  | 138 |  | Construct Lukesport station as a 138kV station with three 40 kA breakers in a ring bus configuration. | MI |  |  | M1 - Proposed | 6414229 | METC | Not Shared
A | B | West | MN | 25399 | 28634 | Line Upgrade | 2025-10-23 | St. Thomas Tap |  |  | 69 |  | Upgrade St. Thomas Tap (SS265) switch to 1200 A. | MN |  |  | M1 - Proposed | 691822 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IN | 25463 | 28649 | Line Upgrade | 2025-10-31 | Glenwood | Rushville |  | 69 |  | TDSIC 69kV Line Rebuild: Glenwood -(6920 / 5.72 mi.)- Rushville East -(69192 / 1.85 mi.)- Rushville; replace approx. 150 single poles; conductor size = 477ACSR45X7@120C; replace (2) Glenwood Jct line switches | IN | 7.57 |  | M1 - Proposed | 24685000 | DUKE ENERGY INDIANA, LLC | Not Shared
B | B | West | ND | 25474 | 28708 | Line Upgrade | 2028-06-01 | Merricourt | tatanka north | 1 | 230 |  | Reconductor or rebuild the line with larger conductor. | ND |  |  | M1 - Proposed | 2250000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | Central | IN | 24274 | 28784 | Substation | 2025-12-31 | Brownsburg East |  |  | 138 |  | New WVPA 138kV, 4 position ring bus substation to serve load | IN |  |  | M1 - Proposed | 8600000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | East | MI | 25191 | 28293 | Line Upgrade | 2027-12-31 | Cadillac | South Boardman | 1 | 138 |  | Rebuild and upgrade 23 miles of 69 kV line from Cadillac to South Boardman to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | MI | 23 |  | M1 - Proposed | 27600000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | South | TX | 25432 | 28672 | Line New | 2028-12-01 | Cypress | Legend |  | 500 |  | New ~35 mile 500 kV line | TX |  |  | M1 - Proposed | 405900000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 25466 | 28688 | Substation | 2029-12-31 | Maynard |  |  | 69 |  | Replace oil breakers, bus differential relaying, and breaker failure relaying. | IA |  |  | M1 - Proposed | 1600000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25431 | 28666 | Voltage Device | 2026-06-01 | Dakota Dunes |  | 1 | 69 |  | Expand Dakota Dunes Substation to install a 14.7 MVAR 69 kV capacitor bank | IA |  |  | M1 - Proposed | 2800000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | West | MN | 25282 | 28598 | Substation | 2027-09-30 | MNEC |  |  | 345 |  | Voltage Support Substation for radial generation | MN |  |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 24558 | 28023 | Line Upgrade | 2025-12-01 | Coldwater | Moore Road |  | 138 |  | Extend the Coldwater - Moore Road line and loop in the J1658 Station. Extend fiber path to J1658 POI, Coldwater, and Moore Rd stations. | MI |  |  | M1 - Proposed | 12137500 | METC | Not Shared
A | B | West | WI | 25220 | 28253 | Substation | 2027-12-31 | Cuba City South |  |  | 69 |  | • ATC will construct 0.63 miles of new 69 kV line around the space-constrained Gro Alliance area. • ATC will rebuild 1.12 miles of the existing Cuba City South Tap as a new double circuit 69 kV line to provide a loop-through connection to the Cuba City South Substation. • ATC will construct a loop-through, straight bus substation with two 69 kV line breakers. • Cuba City will install a 69/12.47 kV transformer at Cuba City South. | WI |  |  | M1 - Proposed | 11000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25461 | 28630 | Line New | 2027-08-01 | Johnson Creek | Maffitt Lake | 1 | 161 |  | Johnson Creek - Maffitt Lake 161 kV line | IA |  |  | M1 - Proposed | 8500000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | Central | MO | 50074 | 50114 | Line Upgrade | 2027-12-01 | Moro | Laclede |  | 138 |  | DPP studies have identified the need for the Moro – Laclede N Tap rebuild project | MO |  |  | M1 - Proposed | 26000000 | AMEREN ILLINOIS | Not Shared
A | B | Central | IL | 25153 | 28238 | Substation | 2025-06-01 | Moyer |  |  | 138 |  | This project will interconnect the One Earth Energy 30 MW ethanol plant. It will construct a new 138 kV substation called Moyer and a new AIC 138/12 kV substation called Gibson City One Earth. | IL |  |  | M1 - Proposed | 16700000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 20017 | 25700 | Line Upgrade | 2028-06-01 | Regal |  |  | 138 |  | Upgrade terminal station equipment | MI |  |  | M1 - Proposed | 246000 | METC | Not Shared
A | B | South | MS | 25229 | 28327 | Substation | 2026-01-01 | Coastas |  |  | 230 |  | New Costas 230 kV substation to serve customer load. | MS |  |  | M1 - Proposed | 44500000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | South | MS | 25215 | 28334 | Transformer | 2027-06-01 | Andes |  |  | 500 | 230 | 2x230 kV Autotransformers will be installed at the new Andes 500/230 kV station. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 50106 | 50160 | Misc. | 2026-03-31 | Morgan Valley |  |  | 345 | 345 | Upgrade relays at Morgan Valley on terminal for line to Big Cedar Switching Station. | IA |  |  | M2 - Appendix A Approved | 97328 | ITC MIDWEST | Not Shared
A | B | Central | IN | 25441 | 28584 | Line Upgrade | 2025-12-31 | Pigeon Creek | Heidelbach | 91-1 | 138 |  | Rebuilding ~2miles of 138kV line from 795 to 954 | IN | 2 |  | M1 - Proposed | 5500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | Central | IL | 25316 | 28417 | Line New | 2029-12-31 | Colchester | Macomb |  | 69 | 69 | New Colchester-Macomb 336 ACSR 69 kV Line | IL |  | 4.7 | M1 - Proposed | 3055000 | PRAIRIE POWER, INC. | Not Shared
B | B | East | MI | 50064 | 50131 | Substation | 2028-06-01 | East Tawas | Karn | 1 | 138 |  | Replace station equipment at East Tawas | MI | 38.34 | 7.8 | M1 - Proposed | 590000 | METC | Not Shared
A | B | West | IA | 25448 | 28610 | Line New | 2026-12-01 | Browns Woods | Ashawa | 1 | 161 |  | Tap Ashawa-16th & Wabash 161 kV | IA |  |  | M1 - Proposed | 4750000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25308 | 28372 | Line New | 2028-12-31 | Leon Rodeo | Sailing | 1 | 69 | 69 | ITCM will construct new line taps for the new Leon Rodeo sub and retire any existing 69 kV line no longer needed. | IA |  |  | M1 - Proposed | 127500 | ITC MIDWEST | Not Shared
A | B | West | MN | 25498 | 28766 | Substation | 2027-09-01 | Beaver Creek | Harmony | 1 | 161 |  | New 4-breaker ring, 161 kV switching station at POI and 6.0 miles of 161 kV on New Right-of-way | MN |  | 6 | M1 - Proposed | 19574516 | DAIRYLAND POWER COOPERATIVE | Not Shared
A | B | East | MI | 25277 | 28480 | Substation | 2027-12-31 | METC Facilities |  |  | 345 | 138 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI |  |  | M1 - Proposed | 2500000 | METC | Not Shared
A | B | Central | IL | 25279 | 28491 | Line Upgrade | 2026-12-31 | Multiple |  |  | 345 | 138 | Replace Pole and Insulators | IL |  |  | M1 - Proposed | 20000000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 24533 | 27989 | Substation | 2026-05-13 | Greenwood |  |  | 345 |  | Install 345 kV BKR KT at Greenwood. Replace Annunciator panel with RTU panel. | MI |  |  | M1 - Proposed | 1364741 | ITC | Not Shared
A | B | Central | IN | 25545 | 28751 | Misc. | 2025-12-01 | Lowland Solar | J1390 POI |  | 230 |  | J1390 150MW net Lowland Solar Park, LLC - Oversite of Self-Build Switching Station by developer (3-CB ring); inserted in the 23004 Gallagher to Columbus ckt; includes relay upgrades on the remote ends, 23004 loop-through line work; and reroute of the 23005 around the new switching station | IN |  |  | M1 - Proposed | 6843406 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | Central | IN | 25350 | 28523 | Substation | 2028-05-31 | 08BEDFRD | 08COLMBU |  | 345 | 69 | 345 kV ring bus substation with 4 breakers and two 345 kV :69 kV transformers. A 69kV ring-bus station one the low-side. | IN |  |  | M1 - Proposed | 33000000 | HOOSIER ENERGY | Not Shared
A | B | West | MN | 25374 | 28561 | Line Upgrade | 2027-12-10 | Goodland | Warba | 1 | 69 |  | Rebuild 7.4 miles of the Goodland to Warba line. | MN | 7.4 |  | M1 - Proposed | 5876908 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IL | 24738 | 28070 | Line Upgrade | 2025-12-01 | Hull | Herleman |  | 138 |  | Rebuild the Hull-Herleman-1682 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL |  |  | M1 - Proposed | 24000000 | AMEREN ILLINOIS | Not Shared
A | B | West | MN | 25423 | 28574 | Line Upgrade | 2027-06-30 | Fox Lake | Fox Lake Tap | 1 | 69 |  | Rebuild 6 miles of the Fox Lake to Fox Lake tap. | MN | 6 |  | M1 - Proposed | 7214678 | GREAT RIVER ENERGY | Not Shared
B | B | West | WI | 25259 | 28444 | Transformer | 2028-09-30 | Grassland |  |  | 69 |  | Replace existing transformers with 50 MVA units | WI |  |  | M1 - Proposed | 8000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25021 | 28181 | Line New | 2025-10-16 | Thayer |  |  | 69 |  | Network Upgrades work consists of: • installation of three (3) new class H1direct-embed wood poles, • 336 kcmil ‘Merlin’ ACSR conductor to interconnect the 6958 line into the new 69kV tap substation’s • two (2) 69kV 1200 ampere disconnect switches. CUI//CEII/PRIV Original Sheet No. 87 Three new H1 structures will be placed in the line with 2 of them having 69kV disconnect switches. Transmission Owner will also install direct transfer trip relay equipment at Transmission Owner’s Thayer substation on 6958 breaker to communicate with the new station. | IN |  |  | M1 - Proposed | 1066894 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | B | Central | KY | 25081 | 28198 | Line Upgrade | 2025-12-01 | Webster County | Reid EHV | 1 | 161 |  | 18 miles of OPGW and related equipment. | KY |  |  | M1 - Proposed | 0 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | B | Central | IN | 25089 | 28230 | Substation | 2025-10-01 | New Harmony |  | T2 | 69 |  | Replacement of 69/12kV T2 transformer and breakers at New Harmony Substation | IN |  |  | M1 - Proposed | 5300000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | WI | 24980 | 28154 | Misc. | 2027-12-31 | Pioneer |  |  | 138 |  | Pioneer SS Breaker Relay Asset Renewal | WI |  |  | M1 - Proposed | 3600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 25151 | 28233 | Line Upgrade | 2025-12-31 | Y67/Z78 Junction | Jasper South | 67 | 69 |  | Replacement of poles along Y67 from Y67/Z78 Junction to Jasper South and several switches along the way. | IN |  |  | M1 - Proposed | 10000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | MN | 25199 | 28349 | Substation | 2025-02-01 | Fairmont 10th St |  |  | 69000 |  | Replacing 4 69kV circuit breakers and associated equipment. | MN |  |  | M1 - Proposed | 1800000 | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
A | B | East | MI | 25223 | 50263 | Substation | 2027-06-11 | Dorset |  |  | 120 |  | Install FOC jumpers | MI |  |  | M1 - Proposed | 25506 | ITC | Not Shared
A | B | South | TX | 24959 | 28144 | Line Upgrade | 2025-02-01 | Kolbs | Port Acres Bulk |  | 230 |  | Upgrade Kolbs to Port Acres Bulk 230 kV line | TX |  |  | M1 - Proposed | 17300000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | WI | 25323 | 28450 | Line New | 2029-09-30 | Junction Mill | South Hudson | 1 | 115 |  | New 115kV transmission line from the proposed Junction Mill substation in River Falls to a new South Hudson substation. | WI |  | 6 | M1 - Proposed | 12000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 25195 | 28314 | Transformer | 2028-06-01 | MCV |  |  | 345 | 138 | Install a new 345/138 kV transformer and terminated it at the newly created 345 & 138 kV positions. | MI |  |  | M1 - Proposed | 6500000 | METC | Not Shared
A | B | East | MI | 24462 | 27949 | Substation | 2025-11-17 | Grassmere |  |  | 345 |  | Install Grassmere switch CQA and line entrance structure at position CQ for generator interconnection. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
A | B | East | MI | 22018 | 26682 | Line Upgrade | 2028-06-01 | Leoni |  |  | 138 |  | Upgrade terminal equipment at Leoni. | MI |  |  | M1 - Proposed | 136000 | METC | Not Shared
A | B | West | WI | 50120 | 50191 | Substation | 2028-09-10 | Morgan |  |  | 138 |  | Existing Morgan Substation will add one (1) new 138kV breaker and two (2) disconnect switches to expand the ring bus configuration to allow the J1615 line to enter the Morgan Substation. Existing G8 bus VTs will be relocated at end of existing bus. One (1) new protective relay panel will be added to the existing control house for the new line and new breaker protection. The new breaker control/protection relaying will be installed in an existing breaker control panel to provide protection for the new breaker. The existing substation yard will be expanded by 175’ x 70’ to the Southwest to square out that corner. | WI |  |  | M1 - Proposed | 2909000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | West | WI | 25299 | 28514 | Substation | 2025-04-01 | Nimbus |  |  | 138 |  | A new 138/24.9 kV breaker-and-a-half substation named Nimbus and 4 short 138 kV transmission lines (less than 1.0 mile) from the existing Mount Pleasant Substation to the new Nimbus Substation. New bus positions at the Mount Pleasant Substation will need to be added to connect the new transmission lines. | WI |  |  | M2 - Appendix A Approved | 89000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25399 | 28635 | Line Upgrade | 2024-12-03 | Pratt Tap |  |  | 69 |  | Upgrade Pratt Tap (SS2765) switches to 2000 A. | MN |  |  | M1 - Proposed | 300000 | GREAT RIVER ENERGY | Not Shared
A | B | South | MS | 25417 | 28738 | Line Upgrade | 2025-12-01 | Rocky Creek | Lucedale |  | 69 |  | To ensure reliable service a complete rebuild of L34 (Lucedale – Rocky Creek 7.97 miles) is recommended. | MS |  |  | M1 - Proposed | 5000000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | East | MI | 50038 | 50081 | Misc. | 2026-08-19 | HSC | Orr Road | 1 | 138 |  | Re-route OHL to accommodate Orr Road expansion | MI |  |  | M1 - Proposed | 1471000 | METC | Not Shared
B | B | West | WI | 24982 | 28172 | Line Upgrade | 2028-12-31 | Range Line Dist | Range Line Switchyard | 61441 | 138 |  | Replace underground cable between Range Line Distribution SS and Range Line Switchyard. | WI |  |  | M1 - Proposed | 3000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | TX | 25432 | 28673 | Transformer | 2028-12-01 | Legend |  |  | 500 | 230 | Install 500-230 kV Auto at Legend | TX |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 21968 | 26597 | Substation | 2026-06-01 | Delaney |  |  | 138 |  | Remove METC equipment from Delaney substation. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | Central | IN | 25372 | 28536 | Substation | 2029-06-30 | Petersburg | Thompson | 1 | 345 | 138 | 2 bay 345/138 kV breaker-and-a-half substation with 2 40 MVA transformers. | IN |  |  | M1 - Proposed | 35348000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
B | B | West | MN | 25255 | 28386 | Substation | 2026-12-31 | Verndale |  |  | 115 | 35 | Rebuild 115/34.5 kV Verndale Substation with new transformers and circuit breakers. Remove line connected transformer. | MN |  |  | M1 - Proposed | 4000000 | MINNESOTA POWER INC. | Not Shared
A | B | East | MI | 25191 | 28294 | Line Upgrade | 2028-12-31 | Cadillac | Richland | 1 | 138 |  | Rebuild and upgrade 5 miles of 69 kV line to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | MI |  |  | M1 - Proposed | 6500000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | South | LA | 25465 | 28689 | Voltage Device | 2025-06-01 | Paincourtville |  |  | 115 |  | Split current capacitor bank into two smaller banks, by reducing the size of the existing bank and installing a second smaller bank. | LA |  |  | M1 - Proposed | 4400000 | ENTERGY SERVICES, LLC. | Not Shared
B | B | West | ND | 25474 | 28709 | Line Upgrade | 2028-06-01 | Tatanka North |  |  | 230 |  | Replace all breakers, disconnects, and wavetraps. | ND |  |  | M1 - Proposed | 2600000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | Central | IL | 25450 | 28631 | Line Upgrade | 2027-12-31 | Breiner | Spring Lake Jct. |  | 69 | 69 | Rebuild Breiner-Spring Lake Jct. 336 ACSR 69 kV Line | IL | 10.36 |  | M1 - Proposed | 5500000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | MN | 22487 | 27355 | Substation | 2025-11-30 | Erie 230 kV (620326) | Erie 115 kV (620226) | 1 | 230 | 115 | Adjust Erie 230/115 kV transformer tap. | MN |  |  | M1 - Proposed | 1000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | West | MN | 25446 | 28667 | Misc. | 2025-12-05 | Willmar System |  |  | 230 | 69 | Willmar is upgrading SCADA, relays, RTUs, and replacing 69 kV poles due to age. | MN |  |  | M1 - Proposed | 1600000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A | B | West | MN | 23851 | 27653 | Substation | 2026-11-05 | Stanton |  |  | 230 |  | Replace Stanton oil breakers 31RB1, 2, 3, 4 & 6. | MN |  |  | M1 - Proposed | 2179821 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IL | 25091 | 28239 | Transformer | 2025-12-01 | Norris City North |  |  | 345 | 138 | Replace the existing Transformer 2 at Norris City North with a new 345/138kV 700 MVA unit | IL |  |  | M1 - Proposed | 7000000 | AMEREN ILLINOIS | Not Shared
A | B | West | WI | 50036 | 50062 | Substation | 2023-07-31 | Big Hill Park |  |  | 138 |  | 605093 - J1304 Big Hill Park SS Network Upgrades | WI |  |  | M4 - Project in Service | 6124839 | AMERICAN TRANSMISSION COMPANY | Shared
B | B | West | MN | 25282 | 28599 | Voltage Device | 2027-09-30 | MNEC |  |  | 345 |  | Reactive Support Equipment for radial generation | MN |  |  | M1 - Proposed | 20000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 24574 | 28206 | Substation | 2027-01-01 | Carrigan |  |  | 120 |  | Expand station to extend bus 102 and begin row "J". Install breaker position GF and disconnect switches at positions GD and JH | MI |  |  | M1 - Proposed | 1969214 | ITC | Not Shared
A | B | Central | IN | 25146 | 28218 | Line Upgrade | 2024-12-01 | Fairlawn |  |  | 69 |  | Replace several 69kV switches due to aging infrastructure. | IN |  |  | M1 - Proposed | 1000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | MN | 50002 | 50014 | Substation | 2024-05-01 | T Corners |  |  | 69 |  | Replace overstressed breaker T Corners 4E16 that is at end of life with breaker of larger interrupting capacity. | MN |  |  | M1 - Proposed | 80000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | South | MS | 25229 | 28328 | Line New | 2026-01-01 | Lake Castle | North Park | 1 | 230 |  | Costas 230 kV will cut into the existing Lake Castle - North Park 230 kV transmission line. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | South | MS | 25215 | 28335 | Line Upgrade | 2027-06-01 | Andes | Soldiers | 2 | 230 |  | 2x230 kV short transmission lines will connect the Soldiers 230 kV substation to Andes 500/230 kV station. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | IN | 25442 | 28585 | Line Upgrade | 2026-12-31 | NW | PIGEON CREEK | 91-1 | 138 |  | Rebuilding ~3 miles of 138kV line from 795 to 954 | IN | 3 |  | M1 - Proposed | 11000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | IA | 25346 | 28503 | Substation | 2029-12-30 | Walcott 80 | Substation |  | 69 | 69 | Covert the 34 kV operated sub to 69 kV operation along with the Dixon-Fulton conversion. | IA |  |  | M1 - Proposed | 442821 | ITC MIDWEST | Not Shared
A | B | East | MI | 50121 | 50198 | Substation | 2028-06-01 | Quary |  |  | 138 |  | Terminate OPGW at Quary station | MI |  |  | M1 - Proposed | 280000 | METC | Not Shared
A | B | Central | IL | 25318 | 28418 | Transformer | 2029-12-31 | Winchester |  |  | 138 | 69 | Upgrade Winchester 138/69 kV Transformer with Y-Y and 140 MVA Rating | IL |  |  | M1 - Proposed | 3500000 | PRAIRIE POWER, INC. | Not Shared
A | B | East | MI | 24537 | 27998 | Line Upgrade | 2025-03-03 | Michigan Avenue | Newton |  | 138 |  | Extend the Newton - Michigan Ave 138kV line to loop in Lukesport station. | MI |  |  | M1 - Proposed | 2585000 | METC | Not Shared
A | B | West | MN | 25270 | 28434 | Line Upgrade | 2026-12-31 | Redwing | Lake City | 1 | 69 |  | Rebuild 18 miles 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | 18 |  | M1 - Proposed | 10000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25448 | 28611 | Line New | 2026-12-01 | Browns Woods | 16th & Wabash | 1 | 161 |  | Tap Ashawa-16th & Wabash 161 kV | IA |  |  | M1 - Proposed | 4750000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | South | MS | 25489 | 28752 | Line New | 2027-12-01 | North Lucedale GOAB | North Lucedale |  | 69 |  | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | MS |  |  | M1 - Proposed | 3675000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | Central | IL | 23151 | 26982 | Line Upgrade | 2025-12-01 | East Quincy | Hamilton | 4 | 138 |  | Rebuild the 30.5 mile East Quincy-Hamilton-4 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL |  |  | M1 - Proposed | 46000000 | AMEREN ILLINOIS | Not Shared
A | B | West | IA | 50030 | 50054 | Substation | 2025-08-01 | Johnson Creek |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 25223 | 50264 | Substation | 2027-06-11 | Spruce |  |  | 120 |  | Install FOC jumpers | MI |  |  | M1 - Proposed | 25506 | ITC | Not Shared
A | B | South | LA | 25283 | 28402 | Substation | 2025-12-15 | Dolet Hills |  |  | 345 |  | Upgrade terminal equipment for R1004 | LA |  |  | M1 - Proposed | 1956770 | CLECO POWER LLC | Not Shared
B | B | South | LA | 50092 | 50137 | Misc. | 2027-12-31 | Rodemacher |  |  | 230 |  | Upgrade the Protection system at Rodemacher | LA |  |  | M1 - Proposed | 1550000 | CLECO POWER LLC | Not Shared
A | B | Central | IN | 25386 | 28547 | Substation | 2025-12-22 | North |  |  | 138 |  | Replace 2 138 kV breakers. #3 and #4. | IN |  |  | M1 - Proposed | 1800000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | IA | 25308 | 28373 | Substation | 2028-12-31 | Leon | Substation |  | 69 | 69 | Retire the Leon substation after the Leon Rodeo sub is online. | IA |  |  | M1 - Proposed | 484263 | ITC MIDWEST | Not Shared
A | B | Central | IN | 24274 | 28785 | Line Upgrade | 2028-12-31 | Teppco | Rockville |  | 138 |  | Reconductor 138kV line from Teppco to Rockville | IN | 2 |  | M1 - Proposed | 700000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
B | B | Central | IL | 24988 | 28190 | Line Upgrade | 2027-12-01 | Greenville McCord | S. Centralia |  | 138 |  | Rebuild, re-conductor, and add OPGW to the Greenville McCord-S. Centralia-1419 138kV line. | IL |  |  | M1 - Proposed | 30000000 | AMEREN ILLINOIS | Not Shared
B | B | South | MS | 25502 | 28767 | Line Upgrade | 2026-12-01 | Lake | Decatur |  | 69 |  | A complete rebuild of Line 4B and line extension to the existing Decatur Substation (Lake – Decatur 16.8 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Lake and Decatur. | MS |  |  | M1 - Proposed | 9936900 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | MN | 25399 | 50360 | Line Upgrade | 2027-06-30 | Cleveland | Jamestown Tap | 1 | 69 |  | Rebuild Cleveland - Jamestown Tap 8.7 miles | MN | 8.7 |  | M1 - Proposed | 7819920 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 50151 | 50246 | Substation | 2027-09-01 | Sphinx |  |  | 138 |  | Build a new 138 kV four-row breaker-and-a-half configuration station Sphinx. Install twelve 138 kV, 3000 A breakers with at least 40 kA interrupting capability and install all associated equipment capable of at least 3000A SE. | MI |  |  | M1 - Proposed | 13900000 | METC | Not Shared
A | B | West | MN | 25260 | 28350 | Substation | 2025-02-01 | Loon Lake Substation |  |  | 69000 |  | Replacing 4 69kV circuit breakers and associated equipment. | MN |  |  | M1 - Proposed | 1800000 | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
B | B | East | MI | 20041 | 25741 | Line Upgrade | 2028-06-01 | Bard Road | Higgins | 1 | 138 |  | The proposed solution is to remove sag limits on the Bard to Higgins 138 kV line up to the conductor’s limit. | MI |  |  | M1 - Proposed | 1505000 | METC | Not Shared
A | B | East | MI | 24463 | 27950 | Substation | 2027-07-01 | Greenwood | Rapson |  | 345 |  | Construct a new 345kV ring bus station with three 40kA breakers for the J1557 interconnection | MI |  |  | M1 - Proposed | 12408239 | ITC | Not Shared
A | B | Central | IL | 24739 | 28071 | Line Upgrade | 2025-12-01 | Greenback | Lanesville |  | 138 |  | Rebuild the Greenback-Lanesville-1314 138 kV line from Str. 159-Lanesville Substation with conductors capable of carrying 2000 amps under Summer Emergency conditions at 2 OPGW's. | IL |  |  | M1 - Proposed | 2200000 | AMEREN ILLINOIS | Not Shared
A | B | West | WI | 25324 | 28462 | Substation | 2025-10-15 | Downing |  |  | 69 | 24 | Install new distribution substation in the Downing area. | WI |  |  | M1 - Proposed | 4000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25434 | 28674 | Substation | 2027-06-30 | Substation 92 |  |  | 345 |  | Network Upgrades for J1218/J1229 Generator | IA |  |  | M1 - Proposed | 4000000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | East | MI | 25249 | 28315 | Transformer | 2028-06-01 | Stephens |  |  | 345 | 120 | Install a new 345/120kV transformer 302 at Stephens station. | MI |  |  | M1 - Proposed | 5185000 | ITC | Not Shared
A | B | West | MN | 25357 | 28562 | Misc. | 2023-12-15 | Byron | North Rochester | 1 | 345 |  | Install modern leased Ethernet circuits and associated communication equipment for this protection system, point to point between substations. | MN | 14 |  | M1 - Proposed | 200000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | WI | 50112 | 50181 | Substation | 2030-03-10 | Hill Valley |  |  | 345 |  | The facility upgrades required to support J1781 consists of modifying Hill Valley Substation to add a fifth 345 kV terminal position and making it a breaker and a half configuration to accommodate new interconnection facilities. Relay protection and control will be added for the new bus, breakers and line position. The Transmission Owner will maintain ownership of all work at Hill Valley Substation up to the PCO near the POI for the Interconnection Customer’s generation collection facility transmission line. | WI |  |  | M1 - Proposed | 5829000 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | Central | KY | 25081 | 28199 | Misc. | 2025-12-01 | Hopkins |  |  | 161 |  | Upgrade relaying to accommodate the new Webster County switching station. | KY |  |  | M1 - Proposed | 0 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | B | East | MI | 24558 | 28024 | Misc. | 2025-12-01 | Coldwater |  |  | 138 |  | Install a SEL2506 at Coldwater for island mitigation. | MI |  |  | M1 - Proposed | 338050 | METC | Not Shared
A | B | West | WI | 50041 | 50072 | Substation | 2026-12-31 | West Junction |  |  | 138 |  | • Add a 138 kV bus with two-line breakers and a bus tie breaker and associated facilities at West Junction substation to provide for the required sectionalizing facilities, • Retirement of the West Junction Tap to Bluemound portion of 138 kV line 5066 and associated facilities in coordination with the Milwaukee Area 230 kV conversion to 345 kV Project, • Modification of the protection scheme and implement required networking protection. | WI |  |  | M1 - Proposed | 8700000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 25278 | 28481 | Misc. | 2024-12-31 | METC Facilities |  |  | 345 | 138 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI |  |  | M1 - Proposed | 2500000 | METC | Not Shared
A | B | Central | MO | 25349 | 28515 | Line Upgrade | 2025-12-01 | Labadie | Montgomery |  | 345 |  | Address aging infrastructure issues on the Labadie-Montgomery 345kV line | MO |  |  | M1 - Proposed | 10500000 | AMEREN MISSOURI | Not Shared
A | B | West | MN | 25399 | 28632 | Line Upgrade | 2025-09-26 | Cleveland |  |  | 69 |  | Upgrade Cleveland C515 switch to 1200 A. | MN |  |  | M1 - Proposed | 655705 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 25399 | 28636 | Line Upgrade | 2025-03-07 | Johnson Junction |  |  | 115 |  | Upgrade Johnson Junction (SS380) switches to 2000 A. | MN |  |  | M1 - Proposed | 479508 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 25469 | 28726 | Transformer | 2027-12-31 | Silver Lake |  |  | 230 | 42 | Replace the Silver Lake transformer. | MN |  |  | M1 - Proposed | 4646984 | GREAT RIVER ENERGY | Not Shared
A | B | South | LA | 50067 | 50128 | Substation | 2026-09-01 | Coughlin | Plaisance |  | 138 | 138 | Tap the existing Coughlin to Plaisance 138 kV line for the new Whiteville 138 kV substation. This will be the POI for J1686 solar generator | LA |  |  | M1 - Proposed | 18175765 | CLECO POWER LLC | Not Shared
B | B | West | MN | 25255 | 28387 | Line New | 2026-12-31 | Verndale | Dog Lake |  | 115 |  | Extend 24 Line (Verndale - Dog Lake) into new Verndale substation. | MN |  |  | M1 - Proposed | 500000 | MINNESOTA POWER INC. | Not Shared
A | B | Central | IN | 24555 | 28011 | Substation | 2029-12-01 | Honey Creek | Centerton | 21 | 138 | 12 | New substation cutting into existing "21" 138 kV transmission line between Centerton and Honey Creek | IN |  |  | M1 - Proposed | 6000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | IA | 25346 | 28502 | Line New | 2026-12-30 | Walcott 80 | Line Taps |  | 69 | 34 | IPL has notified ITC that they will be constructing a new Walcott 80 Substation which will replace their existing Walcott and Walcott North substations. The new substations will initially connect at 34.5 kV and then be converted to 69 kV as part of the Fulton – Dixon 69 kV conversion. IPL has requested ITC install two 69 kV busses with two line breakers and a bus tie breaker. New line taps for Walcott 80 substation to be constructed with T2-4/0 ACSR conductor. While operating at 34.5 kV, one new breaker looking toward Calamus 3350 should be operated as the new normal open point, with PTS 3372 becoming normally closed to allow the Walcott 80 load to be switched between the two 34.5 kV sources. Existing taps to Walcott and Walcott North to be retired under separate future EI Sketches prior to 69 kV conversion. | IA |  |  | M1 - Proposed | 347500 | ITC MIDWEST | Not Shared
A | B | West | IA | 25467 | 28690 | Substation | 2025-12-01 | Sub P IC |  |  | 161 |  | Add two 161 kV breakers at Substation P to separate the distribution transformers from the substation's line terminals | IA |  |  | M1 - Proposed | 900000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 24534 | 27990 | Substation | 2026-05-13 | Greenwood |  |  | 345 |  | Install line entrance structures and disconnect switch. Install position KQ at Greenwood to interconnect J1526 generation. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
A | B | East | MI | 50038 | 50076 | Substation | 2026-08-19 | Murphy |  |  | 345 |  | Install one (1) 345 kV breaker and associate equipment at Murphy 345 kV to accommodate the new Murphy – Orr Road 345 kV line. The new breaker is 3000 A, 63 kA breaker. Connect OPGW at Murphy station. | MI |  |  | M1 - Proposed | 2000000 | METC | Not Shared
A | B | Central | MO | 25092 | 28240 | Substation | 2025-12-01 | Zachary |  |  | 161 |  | Add six breakers at Zachary 161 kV station to complete a breaker-and-a-half arrangement | MO |  |  | M1 - Proposed | 3000000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
B | B | West | ND | 25474 | 28710 | Line Upgrade | 2028-06-01 | Merricourt |  |  | 230 |  | Re-tap CT bushings at the Merricourt substation | ND |  |  | M1 - Proposed | 20000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | West | WI | 25323 | 28451 | Line New | 2029-09-30 | South Hudson | Willow River | 1 | 115 |  | New 115kV transmission line from new South Hudson substation to Willow River substation. | WI |  | 4 | M1 - Proposed | 8000000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | WI | 24925 | 28173 | Line Upgrade | 2028-12-31 | Range Line Dist | Range Line Switchyard | 61452 | 138 |  | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | WI |  |  | M1 - Proposed | 3000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
B | B | West | MN | 25282 | 28600 | Substation | 2027-09-30 | Terminus |  |  | 345 |  | Radial collector substation for renewable generation. | MN |  |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 25191 | 28295 | Line Upgrade | 2028-12-31 | Richland | Leroy | 1 | 138 |  | -Rebuild and upgrade 15 miles of 69 kV line to 138 kV using Wolverine’s construction standards. Line to be built with double circuit steel structures. | MI |  |  | M1 - Proposed | 18000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | South | MS | 25229 | 28329 | Voltage Device | 2026-01-01 | Costas |  |  | 230 |  | A 108 MVAR capacitor bank will be added to the Costas 230 kV substation. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 18072 | 24855 | Line Upgrade | 2028-06-01 | Hubbard Lake | Spruce Road |  | 138 |  | Completely remediate the sag on the Hubbard Lake – Spruce Road section of the Alpena – Iosco 138kV line. | MI |  |  | M1 - Proposed | 700000 | METC | Not Shared
A | B | East | MI | 22015 | 26664 | Line Upgrade | 2028-06-01 | Blackstone | Leoni | 1 | 138 |  | Rebuild approximately 4.2 miles of the Blackstone – Leoni #1 and #2 138 kV lines using 954 ACSR on double-circuit structures constructed at 138kV. Install OPGW along the entire length from Blackstone to Leoni. | MI |  |  | M1 - Proposed | 9232000 | METC | Not Shared
A | B | West | WI | 50110 | 50176 | Substation | 2028-09-10 | Young St |  |  | 138 |  | J1751 138kV Interconnection Substation Interconnection Facilities | WI |  |  | M1 - Proposed | 496000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 24778 | 28084 | Substation | 2028-01-01 | Grant County |  |  | 69 |  | New load interconnection request in SW Wisconsin. Project scope includes construction of a new 69-kV transmission line to network Hillman – Miners (Y-130) 69-kV line with a new 69-kV substation near the customer site. | WI |  |  | M1 - Proposed | 50100000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 25443 | 28586 | Line Upgrade | 2026-12-31 | Culley | Tennyson | 84-1 | 138 |  | Replacing ~20 miles of poles for the 138kV line from Culley to Tennyson | IN | 20 |  | M1 - Proposed | 27500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | South | TX | 24960 | 28145 | Line New | 2027-07-31 | Legend | Sandling | 2 | 230 |  | Construct a new Legend to Sandling 230 kV Ckt 2 | TX |  |  | M1 - Proposed | 77320000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 25216 | 28336 | Line Upgrade | 2028-06-01 | Gaines | Caledonia Jct. | 1 | 138 |  | Remediate sag on the 795 ACSS up to 153 MVA (summer ratings) on the Gaines – Caledon J. section of the Thompson Road – Gaines 138 kV circuit. | MI |  |  | M1 - Proposed | 520000 | METC | Not Shared
A | B | South | LA | 25352 | 28537 | Substation | 2027-04-01 | Leeville |  |  | 115 |  | Supporting the interconnection of Gas Generator (J1833) at the Leeville 115 kV station. | LA |  |  | M1 - Proposed | 17825000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | ND | 25503 | 28739 | Line Upgrade | 2026-10-01 | Wishek |  |  | 230 |  | Wishek substation - terminal equipment to interconnect project (PCB, Disconnects, bus work) | ND |  |  | M1 - Proposed | 3600000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | West | MN | 50002 | 50009 | Substation | 2026-05-01 | Crossroads |  |  | 115 |  | Replace Overstressed Crossroads TR3 with new breaker with larger interrupting capacity. | MN |  |  | M1 - Proposed | 80000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 50068 | 50108 | Substation | 2025-10-17 | HE Taylorsville 69/12kV Sub | new distribution sub |  | 69 | 12 | HE Taylorsville 69/12kV Sub: construct new 22MVA sub at the same location as existing HE Taylorsville sub; to be served radially off the DEI 69146 ckt.; load at HE Taylorsville will be transferred from Edinburgh sub 69/12kV bank #2 = 3MW+/- | IN | 0 | 0 | M1 - Proposed | 900000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | IA | 25448 | 28612 | Misc. | 2026-12-01 | 63rd & Park | Monarch Tap | 1 | 69 |  | 63rd & Park Substation and associated 69 kV lines will be retired | IA |  |  | M1 - Proposed | 200000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 25223 | 28279 | Substation | 2027-06-11 | Lulu |  |  | 345 |  | Construct Lulu 345 kV switching station | MI |  |  | M1 - Proposed | 20342722 | ITC | Not Shared
A | A | West | ND | 4295 | 28492 | Line New | 2028-12-31 | East Oliver | Nelson Lake 345kV |  | 345 |  | New double-circuit capable 345kV line connecting HVDC to Nelson Lake | ND |  | 2.5 | M1 - Proposed | 10000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | ND | 24375 | 27845 | Line Upgrade | 2028-12-31 | Jamestown | Buffalo |  | 345 |  | Buffalo - Jamestown 345 KV Line | ND |  |  | M1 - Proposed | 2000000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
B | B | Central | MO | 50073 | 50113 | Voltage Device | 2026-12-01 | Miller |  |  | 161 |  | Add cap bank in area of Miller, Gasco, Belle or Meta | MO |  |  | M1 - Proposed | 600000 | AMEREN MISSOURI | Not Shared
A | B | South | MS | 25489 | 28753 | Line New | 2027-12-01 | North Lucedale GOAB |  |  | 69 |  | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | MS |  |  | M1 - Proposed | 125000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
B | B | West | WI | 25203 | 28255 | Line New | 2029-12-31 | Highland | Hill Valley |  | 138 |  | Create a new Highland – Hill Valley 138 kV line by converting 6.4 miles of Highland – Eden 69 kV line Y-207 and constructing a new 1.0 mile section to Hill Valley. | WI | 6.4 | 1 | M1 - Proposed | 5500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24537 | 27999 | Misc. | 2025-04-03 | Coldwater |  |  | 138 |  | Install 2506 for anti-islanding | MI |  |  | M1 - Proposed | 114406 | METC | Not Shared
B | B | South | MS | 25541 | 28768 | Line Upgrade | 2025-12-01 | Newton | Decatur |  | 69 |  | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 9.7 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | MS |  |  | M1 - Proposed | 5656100 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | MN | 25321 | 28419 | Substation | 2025-10-31 | Winnebago City |  |  | 69 |  | Winnebago City Substation | MN |  |  | M1 - Proposed | 4833754 | ITC MIDWEST | Not Shared
A | B | West | ND | 10001 | 21424 | Substation | 2026-12-31 | Voltaire 115 kV |  |  | 115 | 42 | Tap Xcel's 115 kV line between GRE McHenry and Magic City and build a new 115/41.6 kV substation in the Voltaire area. Install three 115 kV breakers and three 41.6 kV breakers. Install one 56 MVA 115/41.6 kV transformer. | ND |  |  | M1 - Proposed | 8100000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | South | LA | 25283 | 28403 | Line New | 2026-12-15 | Dolet Hills | Dolet Solar | 1 | 345 |  | Generation Tie line from Dolet Hills to Solar Site | LA |  | 7.7 | M1 - Proposed | 17730535 | CLECO POWER LLC | Not Shared
B | B | South | MS | 25490 | 28772 | Line Upgrade | 2027-12-01 | Missionary | Newton |  | 69 |  | A complete rebuild of Line 6 (Newton – Missionary 16.4 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Missionary. | MS |  |  | M1 - Proposed | 10004000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | WI | 50107 | 50165 | Substation | 2028-09-10 | Badger |  |  | 138 |  | 138kV Badger Substation Remote End | WI |  |  | M1 - Proposed | 458000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | MO | 22950 | 26914 | Substation | 2026-06-01 | Watson |  |  | 138 |  | Add line breakers to Pos. V & W Remove HSGS' and Add CS/PCB on the XFMRs 1,2,3 | MO |  |  | M1 - Proposed | 6200000 | AMEREN MISSOURI | Not Shared
A | B | Central | IN | 24274 | 28786 | Line Upgrade | 2029-12-31 | Lafayette Rd | Royalton |  | 138 |  | Reconductor existing line between Lafayette Rd and Royalton | IN | 4.2 |  | M1 - Proposed | 1600000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | East | MI | 15831 | 23884 | Substation | 2028-06-01 | Alma |  |  | 138 |  | Upgrade the 336 ACSR line entrance at Alma. | MI |  |  | M1 - Proposed | 694000 | METC | Not Shared
A | B | Central | IN | 25090 | 28231 | Substation | 2025-10-17 | Northwest |  |  | 138 |  | Replacement of several breakers at Northwest substation | IN |  |  | M1 - Proposed | 5000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | East | MI | 24463 | 27951 | Line Upgrade | 2027-07-01 | Greenwood | Rapson |  | 345 |  | Extend the Greenwood-Rapson #1 345kV line to loop in the J1557 interconnection 345kV station. | MI |  |  | M1 - Proposed | 1586250 | ITC | Not Shared
A | B | South | LA | 25435 | 28675 | Substation | 2028-12-01 | Tupper |  |  | 69 |  | Upgrade Tupper 69 kV Bus | LA |  |  | M1 - Proposed | 1200000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | Central | MO | 50086 | 50126 | Substation | 2026-03-01 | Montgomery |  |  | 161 |  | This project will facilitate the connection of a 250 MW datacenter load at Montgomery (161 kV) Substation with a new straight bus and terminal | MO |  |  | M2 - Appendix A Approved | 2500000 | AMEREN MISSOURI | Not Shared
B | B | East | MI | 25219 | 28351 | Line Upgrade | 2028-06-01 | Sunbird | Bloomfield | 1 | 120 |  | Upgrade approximately 0.47 miles of the Bloomfield – Sunbird 120 kV circuit and line drops from Sunbird to Colorado #2 Tap to 1431 ACSR. | MI |  |  | M1 - Proposed | 1800000 | ITC | Not Shared
A | B | South | LA | 50039 | 50070 | Substation | 2026-04-01 | Richard |  |  | 138 |  | Network Upgrades to tie J1561. | LA |  |  | M1 - Proposed | 6383000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | IL | 23426 | 27071 | Line New | 2029-12-31 | Rushville | Astoria | 1 | 69 | 69 | New Rushville-Astoria 336 ACSR 69 kV line | IL |  | 14.5 | M1 - Proposed | 9425000 | PRAIRIE POWER, INC. | Not Shared
A | B | East | MI | 25228 | 28316 | Substation | 2029-03-31 | DBGEN 41 |  |  | 120 |  | New station constructed as five rows of breaker and a half 120 kV station. | MI |  |  | M1 - Proposed | 62000000 | ITC | Not Shared
A | B | West | MN | 25399 | 28637 | Line Upgrade | 2025-03-07 | Benton County |  |  | 230 |  | Upgrade Benton County wave trap and jumpers. | MN |  |  | M1 - Proposed | 300000 | GREAT RIVER ENERGY | Not Shared
A | B | West | WI | 23951 | 27683 | Line Upgrade | 2027-06-30 | Various Lines |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 5400000 | AMERICAN TRANSMISSION COMPANY | Not Shared
B | B | East | MI | 18009 | 24783 | Line Upgrade | 2028-06-01 | Regal | Luce | 1 | 138 |  | Rebuild 0.75 mile of the Luce - Regal 138kV circuit using 954 ACSR conductor with double circuit steel structures. | MI | 0.75 |  | M1 - Proposed | 1834000 | METC | Not Shared
A | B | South | TX | 25468 | 28691 | Line New | 2027-06-01 | Jacinto | Southline |  | 138 |  | New ~6 mile 138 kV line | TX |  |  | M1 - Proposed | 40700000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | IL | 50045 | 50084 | Transformer | 2027-12-01 | Austin |  |  | 345 | 138 | Replace transformer 3 at Austin Substation which is AIC owned. | IL |  |  | M1 - Proposed | 6800000 | AMEREN ILLINOIS | Not Shared
B | B | West | MN | 25264 | 28388 | Substation | 2027-12-31 | Ridgeview |  |  | 115 |  | Add two 115kV circuit breakers to existing Ring Bus to allow for a new 115/34.5 kV Transformer addition. | MN |  |  | M1 - Proposed | 2000000 | MINNESOTA POWER INC. | Not Shared
B | B | West | ND | 25474 | 28711 | Transformer | 2028-06-01 | Ellendale |  |  | 230 | 115 | Replace the Ellendale 230/115 xfmr with at least 200 MVA | ND |  |  | M1 - Proposed | 5500000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | South | MS | 25215 | 28330 | Substation | 2027-06-01 | Soldiers |  |  | 230 |  | Soldiers 230 kV Substation will connect to the new Andes 500/230 kV station by 2 short transmission lines. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | WI | 25375 | 28563 | Line Upgrade | 2025-12-01 | Eau Galle | Durand | 1 | 69 |  | Line W3415 refurb and insulator replacement on 5.9 miles between Eau Galle - Durand. | WI | 5.9 |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | MN | 25282 | 28601 | Voltage Device | 2027-09-30 | Terminus |  |  | 345 |  | Reactive support at terminus substation to support radial renewable generation | MN |  |  | M1 - Proposed | 75000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 23706 | 27486 | Line Upgrade | 2027-03-31 | Cromwell | Portage Lake |  | 115 |  | Rebuild Cromwell to Portage Lake ("158 Line") 115 kV Transmission Line. | MN |  | 30 | M1 - Proposed | 25000000 | MINNESOTA POWER INC. | Not Shared
A | B | Central | IN | 25387 | 28548 | Substation | 2025-12-22 | Prospect |  |  | 138 |  | Replace 1 138 kV breaker. #2. | IN |  |  | M1 - Proposed | 900000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | Central | KY | 25081 | 28200 | Misc. | 2025-12-01 | Reid EHV |  |  | 161 |  | Upgrade relaying at Reid EHV to accommodate the new switching station Webster County. | KY |  |  | M1 - Proposed | 0 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | B | South | AR | 50090 | 50134 | Substation | 2026-09-13 | Wheatley |  |  | 500 |  | A new 500kV generator point of interconnection on the Keo - Heth 500kV line. | AR |  |  | M1 - Proposed | 32354000 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | West | MI | 50109 | 50170 | Substation | 2028-09-10 | Nordic |  |  | 138 |  | Existing Nordic Substation will add a new Generator Lead Line terminal with one (1) new 138kV line breaker (included in TOIF) and one (1) line VT. One (1) new relay panel will be added to the existing control house for protecting the new Generator Lead Line. | MI |  |  | M1 - Proposed | 1059000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 50110 | 50173 | Line Upgrade | 2028-09-10 | Badger West | Saratoga | X-43 | 138 |  | The X-43 138 kV Transmission Line Loop-In project will consist of two (2) horizontal monopole dead-end structures routing the line through the Transmission Owner’s new substation, segmenting X-43 between the Badger West and Saratoga substations. Line renaming will be required and determined in detailed design. | WI |  |  | M1 - Proposed | 849000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | MO | 25093 | 28241 | Line Upgrade | 2025-12-01 | Zachary |  |  | 161 |  | Add one 161 kV breaker and line terminal for Locust Creek (AECI) | MO |  |  | M1 - Proposed | 1500000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
B | B | East | MI | 25192 | 28296 | Line New | 2027-12-31 | Dover |  |  | 138 |  | Build approximately 0.5 miles of new transmission line to connect the New Dover Substation to METC’s nearby 138kV line. | MI |  | 0.5 | M1 - Proposed | 1000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
B | B | East | MI | 25400 | 28538 | Substation | 2027-12-31 | Superior |  |  | 120 |  | Multiple project alternatives (including operational) are currently being considered to increase this area’s black-start reliability. This project entry will be updated as soon as a scope and cost estimates are determined. ITC will send a formal request for MISO to move this project to “Target Appendix A” in the MTEP24 cycle as soon as the scope has been finalized. | MI |  |  | M1 - Proposed | 1500000 | ITC | Not Shared
A | B | Central | IN | 25404 | 28575 | Substation | 2026-12-31 | Winslow |  |  | 69 |  | Replacing 2 69kV circuit breakers | IN |  |  | M1 - Proposed | 1500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | East | MI | 25082 | 28207 | Substation | 2027-01-01 | Carrigan |  |  | 120 |  | Install line entrance structures and disconnect switch. Install position KQ at Greenwood to interconnect J1526 generation. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
B | B | West | SD | 24335 | 27826 | Line Upgrade | 2027-06-01 | Hwy. 12 (620215) |  |  | 115 |  | Replace OTP's 115 kV switch at the Hwy 12 substation. | SD |  |  | M1 - Proposed | 350000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | East | MI | 25230 | 28337 | Transformer | 2027-12-31 | Manning |  |  | 345 | 138 | Replace the Manning #2 345/138 kV transformer with at least 650 MVA (2718 Amps) summer emergency rated transformer. Also install a new high side 3000 Amps disconnect switch. | MI |  |  | M1 - Proposed | 7060000 | METC | Not Shared
A | B | Central | IN | 25347 | 28504 | Substation | 2025-10-01 | WVPA Lebanon Industrial 69/12kV Sub |  |  | 69 | 12 | WVPA Lebanon Industrial 69kV Sub - Construct a new 69/12kV substation to serve a new Eli Lilly facility, the substation will have a high side 69kV ring bus | IN |  | 1.9 | M1 - Proposed | 12215000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | East | MI | 25223 | 28280 | Substation | 2027-06-11 | Maple |  |  | 345 |  | Upgrade line position CI relaying | MI |  |  | M1 - Proposed | 300084 | ITC | Not Shared
B | B | South | MS | 25541 | 28769 | Line New | 2025-12-01 | Decatur |  |  | 69 |  | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 9.7 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | MS |  |  | M1 - Proposed | 125000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
B | B | West | WI | 25203 | 28256 | Substation | 2029-12-31 | Highland | Hill Valley |  | 138 |  | Create a new Highland – Hill Valley 138 kV line by converting 6.4 miles of Highland – Eden 69 kV line Y-207 and constructing a new 1.0 mile section to Hill Valley. | WI |  |  | M1 - Proposed | 4000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25448 | 28613 | Misc. | 2026-12-01 | 63rd & Park | West Des Moines | 1 | 69 |  | 63rd & Park Substation and associated 69 kV lines will be retired | IA |  |  | M1 - Proposed | 200000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | IL | 23373 | 28404 | Line New | 2027-12-31 | Table Grove | Ipava |  | 69 | 69 | New Table Grove-Ipava 336 ACSR 69 kV Line | IL |  | 12 | M1 - Proposed | 8200000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | MN | 25319 | 28420 | Misc. | 2024-04-01 | Sheas Lake | Wilmarth | 1 | 345 |  | Replace secondary pilot communication circuit from SLL - WLM 345 kV. Install a modern Ethernet circuit and associated communication equipment for this protection system | MN |  |  | M1 - Proposed | 300000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | ND | 25503 | 28740 | Line Upgrade | 2026-10-01 | Mandan | Napoleon |  | 230 |  | Mandan-Napoleon 230 kV line - terminal equipment (Re-tap CTs Mandan and jumpers at Napoleon) | ND |  |  | M1 - Proposed | 75000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | Central | IN | 25546 | 28754 | Misc. | 2026-06-01 | Galea Springs SPV | J1388 POI |  | 138 |  | J1388 - 150MW Galea Springs SPV - solar farm - construct new switching station (3-CB ring) in the radial Oakland City 13862 ckt. - includes Oakland City relay upgrades and rebuilding 6.75 miles of 138kV line from POI to Oakland City | IN | 6.75 |  | M1 - Proposed | 52928159 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | Central | IN | 25350 | 28526 | Line New | 2028-05-31 | Waynesville | Walesboro |  | 69 |  | New ~4.5 mile, 69kV line, from Waynesville Station to Walesboro | IN |  | 4.5 | M1 - Proposed | 11000000 | HOOSIER ENERGY | Not Shared
A | B | Central | IN | 50174 | 50304 | Substation | 2026-12-31 | Roxana | Stateline B |  | 138 |  | 200MW load looping into 13853 Roxana-StatelineB circuit.(NIPSCO-CE) | IN |  |  | M1 - Proposed | 12000000 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | B | West | MN | 50101 | 50150 | Substation | 2025-07-31 | Hodges Substation |  |  | 115 |  | Install a 3-way manual load break 115 kV, 2000 A switch on GRE’s Walden – Morris 115 kV line (near structure 89) and construct about 2 spans of 115 kV line with 477 ACSR conductor to the high side of Agralite’s new Hodges area distribution substation. Install metering/telecom and a new EEE for the distribution substation. | MN |  | 0.25 | M1 - Proposed | 750116 | GREAT RIVER ENERGY | Not Shared
B | B | South | MS | 25491 | 28773 | Line Upgrade | 2027-12-01 | Morton | Donald Rd GOAB |  | 69 |  | A complete rebuild of Line 62C (Morton – Donald Road GOAB 0.8 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Morton and the Donald Road GOAB. | MS |  |  | M1 - Proposed | 840000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | East | MI | 25327 | 28482 | Substation | 2026-12-31 | METC Facilities |  |  | 345 | 138 | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. | MI |  |  | M1 - Proposed | 53960000 | METC | Not Shared
B | B | West | WI | 25087 | 28220 | Line Upgrade | 2029-12-31 | East Madison |  |  | 69 |  | Rebuild AGAT-AGA 0.4 mile single circuit tapped line section as a 0.5 mile double circuit configuration in the East Madison Area. | WI | 0.4 |  | M1 - Proposed | 14000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 50031 | 50056 | Substation | 2024-08-01 | Maffitt Lake |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25412 | 28676 | Line Upgrade | 2025-12-01 | CBEC | Sub 706 | 1 | 69 |  | Rebuild section of CBEC-Sub 706 69 kV line | IA | 1.2 |  | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 25228 | 28317 | Line New | 2029-03-31 | DBGEN 41 |  |  | 120 |  | Reterminate all DB041 lines into the new locations at DBGEN 41 station. | MI |  |  | M1 - Proposed | 2200000 | ITC | Not Shared
A | B | Central | IN | 25350 | 28524 | Line New | 2028-05-31 | Waynesville | Ogilville |  | 69 |  | New ~4.5 mile, 69kV, line from Waynesville to Ogilville | IN |  |  | M1 - Proposed | 8000000 | HOOSIER ENERGY | Not Shared
A | B | West | MN | 25399 | 28638 | Line Upgrade | 2024-10-31 | Inman | Miltona | 1 | 115 |  | Replace structures in the Inman - Elmo - Parkers Prairie - Miltona line to increase rating. | MN |  |  | M1 - Proposed | 1190849 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IN | 25280 | 28352 | Substation | 2025-11-15 | Decatur Switch Station 138kV |  |  | 138 |  | Construct Transmission Owner’s Interconnection Facilities at Decatur Substation. | IN |  |  | M1 - Proposed | 3248872 | HOOSIER ENERGY | Not Shared
A | B | East | MI | 24537 | 28000 | Misc. | 2025-04-03 | Michigan Avenue |  |  | 138 |  | Install 2506 for anti-islanding | MI |  |  | M1 - Proposed | 114406 | METC | Not Shared
A | B | West | ND | 25475 | 28712 | Voltage Device | 2026-12-31 | Merricourt |  |  | 230 |  | Add 50 Mvar reactor to the Merricourt Substation | ND |  |  | M1 - Proposed | 5000000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | East | MI | 24494 | 27952 | Substation | 2027-07-01 | Cribbins |  |  | 345 |  | Install Cribbins position CQ line entrance structure and switch CQA for generator interconnection. | MI |  |  | M1 - Proposed | 0 | ITC | Not Shared
A | B | South | LA | 25470 | 28692 | Substation | 2027-06-01 | Sunrise |  |  | 230 |  | New 230 kV station on the Wells to Labbe 230 kV line. | LA |  |  | M1 - Proposed | 39600000 | ENTERGY SERVICES, LLC. | Not Shared
B | B | Central | MO | 50072 | 50112 | Voltage Device | 2026-12-01 | Copley area |  |  | 138 |  | Evaluate possible cap bank locations including Copley, Bland, Tegeler, Clover Bottom (AECI) | MO |  |  | M1 - Proposed | 600000 | AMEREN MISSOURI | Not Shared
B | B | West | MN | 25265 | 28389 | Substation | 2029-12-31 | Wrenshall |  |  | 115 |  | Rebuild 115/34.5 kV Wrenshall project. | MN |  |  | M1 - Proposed | 4000000 | MINNESOTA POWER INC. | Not Shared
B | B | West | WI | 50010 | 50023 | Line Upgrade | 2031-12-31 | Mukwonago | University | UNIG52 | 138 |  | Rebuild ~20 miles of existing 1920’s vintage lattice structure towers with new steel monopoles, new conductor, and fiber. Design for double circuit capability. | WI |  |  | M1 - Proposed | 55000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 24274 | 28012 | Line New | 2025-12-31 | Rockville | Maloney | 93 | 138 |  | New 8.45 mile 138 kV transmission line and ROW to serve customer load in Brownsburg. | IN |  | 7.8 | M1 - Proposed | 14600000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | WI | 50111 | 50178 | Substation | 2030-03-10 | Edmund |  |  | 345 |  | J1773 345 kV Interconnection Substation | WI |  |  | M1 - Proposed | 15994000 | AMERICAN TRANSMISSION COMPANY | Shared
A | B | West | MN | 25325 | 28463 | Line Upgrade | 2026-12-31 | Prairie Island | Red Rock | 2 | 345 |  | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0986. | MN | 31 |  | M1 - Proposed | 15000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25547 | 28787 | Voltage Device | 2027-12-30 | Blind Lake |  |  | 69 |  | Remove switch 58NSM4 and replace with a circuit breaker. Replace existing breakers B1 and B2. Add a second 6.12 MVAR capacitor bank or replace cap bank with 18 mVAR statcom. | MN |  |  | M1 - Proposed | 8777667 | GREAT RIVER ENERGY | Not Shared
A | B | South | MS | 25215 | 28331 | Substation | 2027-06-01 | Andes |  |  | 500 | 230 | New Andes 500/230 kV station will cut in on the Lakeover - McAdams 500 kV transmission line and feed the Soldiers 230 kV substation. | MS |  |  | M1 - Proposed | 158000000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | MN | 25453 | 28728 | Substation | 2026-11-30 | Medina |  |  | 115 |  | Replace and add breakers at Medina substation. | MN |  |  | M1 - Proposed | 1400052 | GREAT RIVER ENERGY | Not Shared
B | B | West | MN | 25398 | 28602 | Line New | 2027-06-01 | King | King Renewable |  | 230 |  | New ~40 mile transmission line from AS King substation to collector switching stations for replacement renewable generation. | MN |  | 40 | M1 - Proposed | 73000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 24939 | 28146 | Substation | 2025-08-01 | s. valparaiso |  |  | 138 |  | South Valparaiso substation 138kV yard will be expanded by one breaker to accommodate the Generating Facility lead line. Additionally, existing 13820 terminal pole 1008845 will be relocated | IN |  |  | M1 - Proposed | 5401744 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | B | Central | IN | 25389 | 28549 | Substation | 2025-12-22 | Northeast |  |  | 138 |  | Replace 2 138 kV breakers. #1 and #3. | IN |  |  | M1 - Proposed | 1800000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | WI | 25375 | 28564 | Line Upgrade | 2025-12-01 | Durand | Arkansas | 1 | 69 |  | Line W3415 refurb and insulator replacement on 5.5 miles between Durand - Arkansas. | WI | 5.5 |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 50121 | 50221 | Line New | 2028-06-01 | Cottage Grove | Relocated Lines |  | 138 |  | Construct ~1.5 mile from Cottage Grove to relocated lines utilizing standard 138 kV double- circuit structures, 954 ACSR with OPGW on a new ROW. | MI |  | 1.5 | M1 - Proposed | 5430000 | METC | Not Shared
A | B | West | WI | 50107 | 50164 | Substation | 2028-09-10 | Clintonville |  |  | 138 |  | Add one (1) new 138kV bus tie breaker and one (1) new CCVT, wave trap, and line tuner will be installed on the 86502 Line to Badger. Four (4) new relay panels will be added to the existing control house for protection of the new bus section and Generator Lead Line. | WI |  |  | M1 - Proposed | 1501000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25294 | 28452 | Transformer | 2025-10-15 | Tracy Switching Station |  |  | 69 | 14 | Upgrade existing transformer at Tracy Switching Station to 14 MVA. | MN |  |  | M1 - Proposed | 2200000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | SD | 50006 | 50017 | Line Upgrade | 2025-12-31 | Wilmot 41.6 kV | Summit 41.6 kV | 1 | 42 |  | Rebuild 6 miles of 41.6 kV line between Wilmot 41.6 kV and Summit 41.6 kV surrounding Marvin/Corona 41.6 kV. | SD | 6 |  | M1 - Proposed | 1500000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | East | MI | 20119 | 25823 | Line Upgrade | 2028-06-01 | Claremont | Cornell #2 | 1 | 138 |  | METC is to raise the sag limit on the 477 ACSR to 257F and 795 ACSR to 178F on the Bell Road – Cornell section of the Claremont - Cornell #2 138 kV Line | MI |  |  | M1 - Proposed | 1263000 | METC | Not Shared
A | B | West | MN | 24413 | 27840 | Line Upgrade | 2025-02-28 | Richer | Roseau | 1 | 230 |  | Roseau-Richer 230 kV | MN |  |  | M1 - Proposed | 630000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | Central | IN | 25353 | 28539 | Substation | 2024-12-05 | Southwest |  |  | 138 |  | Replace breaker #1. | IN |  |  | M1 - Proposed | 900000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | East | MI | 25223 | 28281 | Line New | 2027-06-11 | Monroe | Milan |  | 345 |  | Cut the Milan-Monroe-Morcco 345 kV line into the Lulu switchyard | MI |  | 0.6 | M1 - Proposed | 4768750 | ITC | Not Shared
B | B | East | MI | 25192 | 28297 | Substation | 2027-12-31 | Dover |  |  | 138 |  | Build 138kV bus | MI |  |  | M1 - Proposed | 300000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | East | MI | 22018 | 26666 | Line Upgrade | 2028-06-01 | Blackstone | Leoni | 3 | 138 |  | Rebuild approximately 4.2 miles of the Blackstone – Leoni #3 138 kV line using 954 ACSR on double circuit structures constructed at 138kV Standards, with future double circuit on the northeast side of the towers. Install OPGW along the entire length from Blackstone to Leoni. | MI |  |  | M1 - Proposed | 7972000 | METC | Not Shared
A | B | East | MI | 25198 | 50240 | Substation | 2028-06-01 | Port Calcite |  |  | 138 |  | Remove transmission equipment at Port Calcite. | MI |  |  | M1 - Proposed | 551000 | METC | Not Shared
A | B | South | AR | 50035 | 50061 | Substation | 2025-05-01 | Doylestown |  |  | 115 |  | Cut in of a new 115kV 3 breaker ring switching station on the Hardin West - Sheridan 115kV line section. Relay upgrades will be performed at the Hot Springs and Woodward remote ends. New fiber will be installed back to Hardin West. | AR |  |  | M1 - Proposed | 3797000 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | East | MI | 24535 | 27991 | Substation | 2025-05-30 | Bingham |  |  | 138 |  | Expand Bingham station. Extend Blue bus and move the capacitor. Install Row 4 and install breaker 8W8, 8B7, 4B7, and 4M9. Reterminate the Cornell - Bingham line at position BM4. | MI |  |  | M1 - Proposed | 5488031 | METC | Not Shared
A | B | West | WI | 25505 | 28770 | Substation | 2025-06-30 | Apple River |  |  | 161 |  | 161 kV substation modifications at Apple River to accomodate J1314 interconnection | WI |  |  | M1 - Proposed | 1263371 | DAIRYLAND POWER COOPERATIVE | Not Shared
A | B | West | IA | 25184 | 28257 | Substation | 2024-09-06 | Traer | Subustation |  | 161 | 161 | TOIF includes surge arrestors, switch, current transformers, and relay dedicated to J1365 radial line and generating facility. | IA |  |  | M3 - Under Construction | 462831 | ITC MIDWEST | Not Shared
A | B | Central | IN | 25443 | 28587 | Line Upgrade | 2027-12-31 | Tennyson | Dubois | 84-1 | 138 |  | Replace ~13 miles of poles on the 138kV line from Tennyson to Dubois | IN | 13 |  | M1 - Proposed | 20000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | WI | 50017 | 50031 | Line Upgrade | 2026-10-01 | West Middleton | Struture 36 | 6967/6963 | 69 |  | Rebuild 2 miles of double circuit 6967/6963 from structure 36 to West Middleton. Install new structures, conductor, shield wire. | WI | 2 |  | M1 - Proposed | 7200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25399 | 28614 | Line Upgrade | 2027-04-22 | Cleveland | End of Double Circuit |  | 69 |  | Rebuild the 1.6 miles of double circuit line from Cleveland substation to the end of the double circuit and interconnection with ITC & Xcel lines. | MN | 1.6 |  | M1 - Proposed | 3455298 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IL | 23374 | 28405 | Line New | 2027-12-31 | Babylon | Canton |  | 69 | 69 | New Babylon-Canton 336 ACSR 69 kV line | IL |  | 13.8 | M1 - Proposed | 8970000 | PRAIRIE POWER, INC. | Not Shared
A | B | Central | IN | 25504 | 28755 | Misc. | 2026-04-01 | Greentown 230 | J1481 POI |  | 230 |  | J1481 200MW net Emerald Green Solar LLC: Greentown 230 - Expand 230 kV sub by adding a new CB that will share the existing ring bus terminal of the 23022 line and add line terminal equipment | IN |  |  | M1 - Proposed | 8535044 | DUKE ENERGY INDIANA, LLC | Not Shared
B | B | Central | IL | 25328 | 28483 | Line Upgrade | 2026-06-01 | Charleston NE |  |  | 138 |  | Add line breakers and address aging infrastructure | IL |  |  | M1 - Proposed | 5800000 | AMEREN ILLINOIS | Not Shared
A | B | West | IA | 25412 | 28677 | Line Upgrade | 2026-12-01 | Percival | Hamburg | 1 | 69 |  | Rebuild Percival-Hamburg 69 kV line | IA | 7.5 |  | M1 - Proposed | 7500000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | West | IL | 50158 | 50268 | Substation | 2029-01-31 | Rosecrans |  |  | 345 |  | o Construct a new four position 345kV ring bus substation (ultimate breaker and a half) at ATC “Rosecrans” site. o Reconfigure existing 345kV line in WI (Line PLPL81 Arcadian to Pleasant Prairie) – tap into line PLPL81 west of Lakeview SS. Construct new double circuit transmission circuit to loop into “Rosecrans” site. o Reconfigure existing 345kV line in Illinois (Line 2224 from Zion SS to Libertyville) – tap into line near ZEC SS to loop into “Rosecrans” site. | IL |  |  | M1 - Proposed | 97000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25428 | 28654 | Substation | 2027-06-01 | New Shenandoah |  |  | 69 |  | Construct new substation with two 69 kV line terminals and a 69 kV capacitor bank | IA |  |  | M1 - Proposed | 10000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | WI | 25257 | 28436 | Line Upgrade | 2024-12-31 | Hegg Tap |  |  | 69 |  | Replace damaged 3-way switch with new 3-way switch on steel pole. | WI |  |  | M1 - Proposed | 700000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | ND | 50037 | 50067 | Substation | 2024-09-01 | Ellendale |  |  | 230 | 35 | Breakers, and line work. | ND |  |  | M3 - Under Construction | 16776939 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | Central | IN | 25147 | 28221 | Substation | 2028-12-31 | Mead Johnson |  |  | 69 |  | Replacement of 69/12kV transformer and several breakers | IN |  |  | M1 - Proposed | 3800000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
B | B | South | MS | 25492 | 28774 | Line Upgrade | 2028-12-01 | Polkville | Donald Rd GOAB |  | 69 |  | A complete rebuild of Line 62A (Polkville – Donald Road GOAB 10.6 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Polkville and the Donald Road GOAB. | MS |  |  | M1 - Proposed | 6519000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | WI | 24980 | 28155 | Misc. | 2027-12-31 | Stiles |  |  | 138 |  | Stiles SS Breaker Relay and Remote Ends Asset Renewal | WI |  |  | M1 - Proposed | 200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
B | B | East | MI | 25250 | 28318 | Substation | 2027-12-31 | DBGEN 42 |  |  | 120 |  | New station constructed as a three rows of breaker and a half 120 kV station. | MI |  |  | M1 - Proposed | 47520000 | ITC | Not Shared
A | B | East | MI | 25217 | 28338 | Voltage Device | 2028-06-01 | Blendon |  |  | 138 |  | Install (1) 33.33 MVAR capacitor bank with associated 138kV, 40 kA synchronous breakers and disconnect switch at the Blendon 138kV substation. The proposed capacitor will be connected to bus 40 and Transformer 1 will be moved to Bus 50. | MI |  |  | M1 - Proposed | 3400000 | METC | Not Shared
A | B | South | LA | 25455 | 28693 | Voltage Device | 2027-06-01 | Multiple |  |  | 230 |  | Install cap banks at Little Gypsy, Peters Road, and Munster | LA |  |  | M1 - Proposed | 21100000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | WI | 50102 | 50151 | Line Upgrade | 2025-12-31 | University | Whitewater | UNIG51 | 138 |  | • Reconductor 3.54 miles of UNIG51 (University-Whitewater 138-kV line), increasing UNIG51’s ratings. This increase allows continuous operation of University generation at full capability after the University – Mukwonago 138-kV line contingency, prepares the corridor for future needs, and enhances operational flexibility in the area. • Install OPGW (24-strand retrofit) in the roughly 6.3 miles of UNIG51, contingent upon no structure replacements needed. OPGW addition completes the communication circuit and create a self-healing optical ring between University and Whitewater substations, leveraging both pre-existing fiber and the future OPGW. • Replace the two bus-side disconnect switches at University SS on both Line UNIG51 and Line UNIG52 • Project to be done in parallel with MTEP ID 24782 J1304 J1305 J1460 MPFCA Network Upgrades, which optimizes ATC’s expenditures and local generation outages. | WI |  |  | M1 - Proposed | 4825000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24558 | 28025 | Misc. | 2026-02-02 | Moore Road |  |  | 138 |  | Install a SEL2506 at Moore Road for island mitigation | MI |  |  | M1 - Proposed | 384456 | METC | Not Shared
A | B | Central | IN | 25350 | 28527 | Line New | 2028-05-31 | Walesboro Jct | Woodside |  | 69 |  | New 1.2-mile, 69kV line | IN |  |  | M1 - Proposed | 2160000 | HOOSIER ENERGY | Not Shared
A | B | Central | IN | 25414 | 28713 | Line Upgrade | 2025-12-31 | Speed | Jeffersonville |  | 138 | 69 | Rebuild entire 13898 ckt from Speed to Jeffersonville with 954ACSS@200C; upgrade very short 13882 tie with LGE at Jeffersonville to 954ACSS@200C and have LGE add ATO switches at the 13882 3-way line junction; rebuild 6955 ckt where double circuited with 13898 ckt; upgrade line terminals and substation buses as needed | IN | 17.23 |  | M1 - Proposed | 38300000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | Central | IL | 23373 | 27072 | Line New | 2027-12-31 | Industry | Table Grove | 1 | 69 | 69 | New Industry-Table Grove 336 ACSR 69 kV Line | IL |  | 13.6 | M1 - Proposed | 7500000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | WI | 24922 | 50220 | Misc. | 2027-12-01 | Forest Junction |  |  | 345 | 69 | Scope of work combines work at Forest Junction with remote end work at Kaukauna Central, Lake Park, Melissa, and Tecumseh Rd. Forest Junction: Replacement of various line relay panels, various 138 kV breaker protection and control panels, various 345 kV breaker protection and control panels, and RTUs. Kaukauna Central: Replacement of one circuit breaker and one line relay panel for line 971K11, one bus protection panel, and GPS Clock. Lake Park: Replacement of 728K21 line protection panel, RTU, and GPS clock. Melissa: Replacement of 971K11 line protection panel. Tecumseh Rd: Replacement of 971K11 and X-106 line projection panels, RTU, two 138 kV and three 69 kV disconnect switches, and three 138 kV bus potential transformers. | WI |  |  | M1 - Proposed | 6480000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 50110 | 50175 | Substation | 2028-09-10 | Petenwell |  |  | 138 |  | Petenwell Substation remote end work | WI |  |  | M1 - Proposed | 250000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 50110 | 50172 | Substation | 2028-09-10 | Young St |  |  | 138 |  | J1751 138kV Interconnection Station | WI |  |  | M1 - Proposed | 7873000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25300 | 28353 | Transformer | 2028-05-01 | Nobles County |  | 11 | 345 | 115 | Install third 345/115 kV transformer at Nobles County | MN |  |  | M1 - Proposed | 12500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | ND | 25503 | 28741 | Line Upgrade | 2026-10-01 | Wishek | Merricourt |  | 230 |  | reconductor and pole replacement | ND |  |  | M1 - Proposed | 12800000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | South | LA | 50065 | 50106 | Substation | 2026-11-15 | Adams Creek | Angie |  | 230 |  | This construction of a new station on the Adams Creek - Angie 230 kV line to accommodate the interconnection of a solar facility (J1576) | LA |  |  | M1 - Proposed | 19725228 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 50151 | 50251 | Misc. | 2027-09-01 | East Paris |  |  | 138 |  | Install 2 wall mounted patch panels for termination of new fiber cable from the the East Paris – Plaster Creek, and the East Paris – Gaines Line. Install and terminate 2 new underground cables from the patch panels to splice closures on the East Paris – Plaster Creek and East Paris Gaines Lines. | MI |  |  | M1 - Proposed | 125000 | METC | Not Shared
A | B | West | MN | 50002 | 50012 | Substation | 2025-11-21 | Red Rock |  |  | 115 |  | Replace overstressed breakers Red Rock 5P96, Cap1 and Cap 3 that are at end of life with breakers of larger interrupting capacity. | MN |  |  | M1 - Proposed | 240000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | South | MS | 25215 | 28332 | Transformer | 2027-06-01 | Andes |  |  | 500 | 230 | 2x500/230 kV 720 MVA autotransformers will be installed at the new Andes 500/230 kV station. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | MN | 25380 | 28516 | Line New | 2023-11-01 | Audubon | Hubbard | 1 | 230 |  | Build two deadend structures to accommodate in-and-out Erie Junction interconnection (MTEP ID 15344). | MN |  |  | M1 - Proposed | 650000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | West | MN | 25398 | 28603 | Substation | 2027-06-01 | King |  |  | 345 |  | Substation upgrades including two 345/230kV transformers at King substation to accommodate 230kV line for radial renewable generation. | MN |  |  | M1 - Proposed | 38000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25295 | 28453 | Line Upgrade | 2023-09-30 | Raptor | Red Rock | 1 | 115 |  | Replace structures at 1 clearance limited span between Raptor - Red Rock. | MN |  |  | M1 - Proposed | 50000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 50038 | 50075 | Substation | 2026-08-19 | Orr Road |  |  | 138 |  | Expand Orr Rd 138 kV Station to the south to add a new row 4 and install 5 additional breakers at Orr Road to accommodate the CE transformers at available positions in row 8, row 14, row 16, and new positions in row 4. All new breakers are 3000 A, 63 kA breakers. No longer relocating Orr Road-Semiconductor #2 line to row 4, it will remain in row 6. | MI |  |  | M1 - Proposed | 6806000 | METC | Not Shared
A | B | West | MN | 25452 | 28729 | Substation | 2027-06-01 | Dickinson |  |  | 115 |  | Replace 3 breakers at Dickinson substation. | MN |  |  | M1 - Proposed | 1845219 | GREAT RIVER ENERGY | Not Shared
A | B | West | WI | 25190 | 28282 | Substation | 2026-06-01 | Badger |  |  | 138 |  | - Replace control building and contents - Replace 138 kV circuit breaker | WI |  |  | M1 - Proposed | 5900000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25388 | 28550 | Substation | 2025-10-01 | Cleveland |  |  | 69 |  | Replace breakers at Cleveland substation. | MN |  |  | M1 - Proposed | 1311954 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 25341 | 28464 | Line Upgrade | 2026-12-31 | Red Rock | Prairie Island | 1 | 345 |  | Replace wood K-frame and H-frame structures with new steel H-frame structures on 345 kV line 0987. | MN | 31 |  | M1 - Proposed | 15000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25406 | 28576 | Line Upgrade | 2028-12-31 | Santa Claus |  |  | 69 |  | Replacing several 69kV switches | IN |  |  | M1 - Proposed | 1500000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
B | B | West | MN | 25266 | 28390 | Substation | 2028-12-31 | Little Falls |  |  | 115 |  | Rebuild Little Falls 115/34.5 kV Substation. | MN |  |  | M1 - Proposed | 4000000 | MINNESOTA POWER INC. | Not Shared
A | B | East | MI | 50121 | 50196 | Substation | 2028-06-01 | East Tawas |  |  | 138 |  | Replace station equipment at East Tawas | MI |  |  | M1 - Proposed | 590000 | METC | Not Shared
A | B | West | WI | 25348 | 28505 | Line New | 2027-12-31 | Saratoga | 7 Mile Creek |  | 138 | 69 | • Construct a new Saratoga – 7 Mile Creek (X-New) 138-kV line, double-circuiting it with existing Saratoga – ACEC Grant (Y-301) 69-kV line. • At 7 Mile Creek SS, relocate existing 7 Mile Creek – Sand Lake (X-11) 138-kV line to connect the new line at existing X-11’s terminal. In addition, construct a new section of approx. 0.05 miles on X-11 for its interconnection to bus 4, eliminating the need for 138-kV crossings. | WI |  | 1.1 | M1 - Proposed | 5150000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24998 | 28147 | Substation | 2027-06-01 | Pontiac |  |  | 345 |  | Extend bus 303 and construct a fifth breaker and a half row for terminating Transformer 301 and Transformer 303 into breaker and a half positions. All breakers should be 3000 A, 63 kA breakers. Transformer 301 will be terminated at Pos AI. Transformer 303 will be terminated at Pos BQ. Rename AD switch to AA and rename AV switch to AZ. | MI |  |  | M1 - Proposed | 5900000 | ITC | Not Shared
A | B | Central | IN | 25560 | 28788 | Line New | 2025-09-30 | HE Wilbur | DEI Centerton |  | 69 |  | New 5.8 miles 69kV line, 795 ACSR | IN |  | 5.8 | M1 - Proposed | 12000000 | HOOSIER ENERGY | Not Shared
A | B | West | IA | 25247 | 28298 | Line Upgrade | 2028-12-31 | Abbott | Marshalltown | 1 | 161 | 161 | ITC will rebuild the Pheonix/SD and Rail portions of Abbott – Marshalltown 161kV circuit with T2-Grosbeak. | IA | 7.41 |  | M1 - Proposed | 10762500 | ITC MIDWEST | Not Shared
A | B | Central | IN | 25383 | 28540 | Substation | 2025-04-28 | South |  |  | 138 |  | Replace 3 breakers. #1, #2, and #3 | IN |  |  | M1 - Proposed | 2700000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | Central | IL | 22878 | 26917 | Substation | 2026-06-01 | Cat Mapleton |  |  | 138 |  | New ring bus across road with two lead lines back to Cat Mapleton. | IL |  |  | M1 - Proposed | 8700000 | AMEREN ILLINOIS | Not Shared
A | B | West | IA | 25204 | 28258 | Substation | 2024-07-26 | Traer | Substation |  | 161 | 161 | A new 161 kV, breaker, and ring-bus expansion at the station will be constructed for J1365. | IA |  |  | M4 - Project in Service | 1574200 | ITC MIDWEST | Not Shared
A | B | West | MN | 25285 | 28426 | Line Upgrade | 2025-12-15 | West St Cloud | Crossroads | 1 | 115 |  | Rebuild 4.1 miles 115 kV from West St. Cloud - Crossroads with new structures and new OPGW shield wire. | MN | 4.1 |  | M1 - Proposed | 3500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25449 | 28615 | Substation | 2027-12-31 | Norwoodville |  |  | 69 |  | Construct new 69 kV switching substation | IA |  |  | M1 - Proposed | 12900000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | IL | 23374 | 28406 | Line New | 2026-06-01 | Babylon | Ellisville/Smithfield |  | 69 | 69 | New Babylon-Ellisville/Smithfield double-circuit 336 ACSR 69 kV line | IL | 0.5 | 0.5 | M1 - Proposed | 625000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | MN | 16289 | 24284 | Substation | 2025-12-31 | Bemidji 115/12.5 kV |  |  | 115 | 13 | New Bemidji 115/12.5 kV Substation design with express feeders and source transfer, one transformer 37MVA/this is a multi-year project. | MN |  |  | M1 - Proposed | 8000000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | West | ND | 24375 | 27846 | Line Upgrade | 2028-12-31 | Buffalo | Bison |  | 345 |  | Bison - Buffalo 345 KV Line | ND |  |  | M1 - Proposed | 750000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | Central | IN | 25350 | 28525 | Line Upgrade | 2028-05-31 | Ogilville Jct | Ogilville |  | 69 |  | Rebuild 1.75-mile, 69kV line from Ogilville Jct to Ogilville sub | IN |  |  | M1 - Proposed | 4000000 | HOOSIER ENERGY | Not Shared
A | B | West | IA | 25449 | 28619 | Line New | 2027-12-31 | Norwoodville | E. 17th & Broadway | 1 | 69 |  | Norwoodville-E. 17th & Broadway 69kV line | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25428 | 28655 | Line New | 2027-06-01 | Shenandoah | New Shenandoah | 1 | 69 |  | Construct new Shenandoah-Shenandoah 69 kV line | IA |  | 2 | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 50151 | 50247 | Line Upgrade | 2027-09-01 | Gaines | Sphinx | 1 & 2 | 138 |  | Rebuild approx. 2.5 mile of Gaines – Plaster Creek 138 kV line to double circuit structures 1431 ACSS and create two new circuits Gaines – Sphinx #1 and #2 138 kV lines and install OPGW. Remove temporary feed equipment (from phase 1) as necessary. | MI |  | 2.5 | M1 - Proposed | 9430000 | METC | Not Shared
A | B | West | IA | 50106 | 50158 | Line New | 2026-03-31 | Beverly | Big Cedar | 2 | 345 | 345 | Add 2nd Beverly - Big Cedar 345 kV line on existing double circuit capable structures. | IA |  | 2 | M2 - Appendix A Approved | 2652500 | ITC MIDWEST | Not Shared
A | B | South | MS | 25489 | 28756 | Substation | 2027-12-01 | North Lucedale |  |  | 69 |  | In order to serve the member delivery points economically and reliably, L34 (Lucedale – Rocky Creek) will be tapped with a 69kV Goab and a new 2.6-mile radial line will be constructed from the Goab to the member delivery point. | MS |  |  | M1 - Proposed | 2599100 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | Central | IN | 24274 | 28013 | Substation | 2025-12-31 | Maloney |  |  | 138 |  | New breaker-and-a-half (3 bays, 6 positions) 138 kV substation to serve customer load | IN |  |  | M1 - Proposed | 13500000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | Central | IN | 25148 | 28222 | Substation | 2024-10-01 | AB BROWN | Gibson | X15 | 345 |  | New switching station for solar generation project J1308 | IN |  |  | M1 - Proposed | 20000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
B | B | East | MI | 50064 | 50163 | Misc. | 2028-06-01 | Quary | Halsey | 1 | 138 |  | Terminate OPGW at Quarry station | MI |  |  | M1 - Proposed | 280000 | METC | Not Shared
B | B | East | MI | 25250 | 28319 | Line New | 2027-12-31 | DBGEN 42 |  |  | 120 |  | Reterminate lines into the new locations at DBGEN 42 station. | MI |  |  | M1 - Proposed | 2150000 | ITC | Not Shared
A | B | East | MI | 25217 | 28339 | Line Upgrade | 2028-06-01 | Blendon |  |  | 138 |  | Relocate the existing Blendon- Northridge (formerly Four Mile) 138kV line termination from bus 20 to bus 10. Also, relocate the existing Blendon-Zeeland Riley 138kV line termination from bus 10 to bus 20. | MI |  |  | M1 - Proposed | 860000 | METC | Not Shared
A | B | West | MN | 25321 | 28422 | Line New | 2025-10-31 | Huntley | Winnebago City | 1 | 69 |  | Bring existing Huntley - Winnebago Local 69 kV line into new Winnebago City substation | MN |  |  | M1 - Proposed | 827500 | ITC MIDWEST | Not Shared
A | B | Central | IL | 22872 | 26900 | Substation | 2027-12-01 | Macomb NE |  |  | 138 |  | Add line breaker on the Macomb West line Relay: Replace relays: MCBW-MCNE-1, SEL-221-16 MCBW-MCNE-1, SEL-221F MCBW-MCNE-1, REL-302 | IL |  |  | M1 - Proposed | 1800000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 50121 | 50195 | Line Upgrade | 2028-06-01 | Cottage Grove | Karn | 1 | 138 |  | Relocate approximately ~ 7.5 miles from Cottage Grove to Karn onto the vacant side of the recently-rebuilt Shale – Twining utilizing existing double- circuit structures, using 954 ACSR conductor and install OPGW. De-energize old section after relocating to new location. | MI | 7.5 |  | M1 - Proposed | 6650000 | METC | Not Shared
A | B | East | MI | 14344 | 23317 | Line Upgrade | 2028-06-01 | Airport | Hillman Tap | 1 | 138 |  | Remediate the sag limit on ~17.0 miles of 266.8 ACSR conductor of the ~21.3 mile-long Airport - Hillman Tap 138 kV section of the Airport - Mio 138 kV line to at least the planned target summer emergency rating of 133 MVA/556 Amps. | MI |  |  | M1 - Proposed | 1061250 | METC | Not Shared
A | B | West | MN | 50002 | 50011 | Substation | 2024-05-01 | Fifth Street |  |  | 115 |  | Replace overstressed breaker Fifth Street 89T4H that is at end of life with breaker of larger interrupting capacity. | MN |  |  | M1 - Proposed | 80000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 25363 | 28494 | Substation | 2029-06-01 | Throughout ITC System |  |  | 345 | 120 | 2029 blanket for projects to address locations where single point of failure (SPOF) are identified that cause system issues. | MI |  |  | M1 - Proposed | 12100000 | ITC | Not Shared
A | B | Central | IN | 25336 | 28528 | Substation | 2025-07-24 | Greensburg Washington St. |  |  | 69 |  | Replace (3) 69kV oil CBs with SF6 gas circuit breakers (GCBs) – 6937, 6964, 69119; replace relays on (3) 69kV lines; replace (12) 69kV switches. | IN |  |  | M1 - Proposed | 2141580 | DUKE ENERGY INDIANA, LLC | Not Shared
B | B | West | MN | 25351 | 50351 | Substation | 2035-10-15 | 345 |  |  | 345 |  | Replace switches 30JSM1, 30JSM4, and 30JSM5 with two 345 kV breakers such that Sherco-Bunker Lake and Bunker Lake-Coon Creek are separate, breakered 345 kV line sections. | MN |  |  | M1 - Proposed | 10000000 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 20034 | 25732 | Line Upgrade | 2028-06-01 | Higgins | Mio Dam | 1 | 138 |  | The proposed solution is ITC is to remove the sag limit on the 266.8 ACSR on the Higgins – Mio Dam 138kV line up to the conductor’s limit. | MI |  |  | M1 - Proposed | 2800000 | METC | Not Shared
B | B | East | MI | 18040 | 50046 | Line Upgrade | 2028-06-01 | Cottage Grove | Saganing J. | 1 | 138 |  | Completely remove the sag limit on the the Cottage Grove to Seven Mile J. to Saganing J. 138 kV sections. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | MN | 25358 | 28588 | Substation | 2028-05-31 | Burnsville |  |  | 115 |  | Expand Burnsville substation 115 kV bus. | MN |  |  | M1 - Proposed | 4000000 | GREAT RIVER ENERGY | Not Shared
A | A | West | MN | 4295 | 8219 | Misc. | 2028-12-31 | St Louis County | VSC HVDC Converter |  | 250 |  | New, Relocated VSC HVDC Converter Station, Symmetric Monopole Configuration, +/-250kV | MN |  |  | M1 - Proposed | 352500000 | MINNESOTA POWER INC. | Not Shared
A | B | East | MI | 24537 | 28001 | Misc. | 2025-04-03 | Wagner |  |  | 138 |  | Install 2506 for anti-islanding | MI |  |  | M1 - Proposed | 107756 | METC | Not Shared
B | B | South | MS | 25493 | 28775 | Line New | 2025-12-31 | North Hattiesburg GOAB | West Hattiesburg GOAB |  | 69 |  | Construct approximately 5 miles of new transmission line from the West Hattiesburg Delivery point to a new 69kV GOAB located adjacent to the North Hattiesburg Substation. The addition of this line will provide loop transmission service between North Hattiesburg Substation and Rawls Springs Substation, provide an OPGW communication link between West Hattiesburg and North Hattiesburg and improve reliability for the areas served. | MS |  |  | M1 - Proposed | 4175000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | IA | 25412 | 28694 | Line Upgrade | 2027-12-01 | Various |  |  | 345 | 69 | Blanket project to rebuild 69 kV, 161 kV and 345 kV lines due to condition and to improve reliability and operational flexibility. | IA |  |  | M1 - Proposed | 32000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25295 | 28454 | Line Upgrade | 2023-09-30 | Wilmarth | Swan Lake | 1 | 115 |  | Replace structures at 3 clearance limited spans between Wilmarth - Swan Lake. | MN |  |  | M1 - Proposed | 200000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25300 | 28354 | Voltage Device | 2028-05-01 | Nobles County |  |  | 345 | 115 | Add 50 MVAR tertiary reactor to new 345/115 kV transformer | MN |  |  | M1 - Proposed | 750000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 25478 | 28730 | Misc. | 2025-12-31 | ITCT Facilities |  |  | 345 | 120 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI |  |  | M1 - Proposed | 2500000 | ITC | Not Shared
A | B | West | MN | 25376 | 28565 | Line Upgrade | 2024-12-01 | Redwood Falls |  |  | 115 |  | Line 0876 Switch 278 replacement at SMMPA Redwood Falls tap. | MN |  |  | M1 - Proposed | 350000 | NORTHERN STATES POWER COMPANY | Not Shared
A | A | West | MN | 4295 | 28484 | Substation | 2028-12-31 | St Louis County | New 345/230kV Substation |  | 345 | 230 | New 345/230kV Substation, 1x 345kV line entrance, 1000 MVA transformer, 2x 230kV line entrances (includes 345 kV line from HVDC station) | MN |  | 0.5 | M1 - Proposed | 45000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | WI | 50112 | 50182 | Substation | 2030-03-10 | Hill Valley |  |  | 345 |  | J1781 345kV Interconnection Substation Interconnection Facilities | WI |  |  | M1 - Proposed | 1390000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 50108 | 50169 | Substation | 2028-09-10 | Plover |  |  | 115 |  | J1573 115kV Interconnection Facilities | WI |  |  | M1 - Proposed | 898000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 25390 | 28551 | Substation | 2025-12-22 | Brookwood |  |  | 138 |  | Replace 2 138 kV breakers. #1 and #2 | IN |  |  | M1 - Proposed | 1800000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | ND | 25503 | 28742 | Line Upgrade | 2026-10-01 | Merricourt |  |  | 230 |  | Add another breaker and re-terminate one of the 230 kV lines | ND |  |  | M1 - Proposed | 1500000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | West | WI | 50147 | 50241 | Line Upgrade | 2027-05-01 | Frederic | Lewis |  | 69 |  | Upgrade structure design and wire size | WI | 2.5 |  | M1 - Proposed | 660000 | NORTHWESTERN WISCONSIN ELECTRIC CO. | Not Shared
A | B | Central | IL | 25193 | 28299 | Transformer | 2025-12-01 | Turkey Hill |  |  | 345 | 138 | Replace Turkey Hill XFMR 1 with a new 345/138kV 700 MVA transformer. | IL |  |  | M1 - Proposed | 6700000 | AMEREN ILLINOIS | Not Shared
A | B | West | IA | 25221 | 28259 | Substation | 2028-09-01 | Bryant | Substation |  | 345 | 345 | TOIF includes facilities and equipment at the Bryant 345 kV switching station dedicated to the 345 kV radial line and Generating Facility | IA |  |  | M1 - Proposed | 716244 | ITC MIDWEST | Not Shared
A | B | Central | IL | 23426 | 28407 | Line New | 2029-12-31 | Astoria | Ipava |  | 69 | 69 | New Astoria-Ipava 336 ACSR 69 kV line | IL |  | 10.4 | M1 - Proposed | 6760000 | PRAIRIE POWER, INC. | Not Shared
A | B | West | IA | 25449 | 28616 | Line New | 2027-12-31 | Norwoodville | E. 46th & Jefferson | 1 | 69 |  | Norwoodville-E. 46th & Jefferson 69 kV line | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | WI | 24983 | 28174 | Line Upgrade | 2026-10-31 | Hilltop | Council Creek | Y-74 | 69 |  | Rebuild and install OPGW on approximately 29 miles of 69 kV line Y-74 from Hilltop Substation to Council Creek Substation and rebuild ~0.5 miles of Camp Douglas Tap. | WI | 29 |  | M1 - Proposed | 56000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25449 | 28620 | Line New | 2027-12-31 | Norwoodville | John Deere West | 1 | 69 |  | Norwoodville-John Deer West 69 kV line | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25405 | 28577 | Substation | 2025-09-30 | Lakeville II | Lakeville II Tap | 1 | 115 |  | Build a new tap line to the new Lakeville II distribution substation. | MN |  | 0.02 | M1 - Proposed | 1200000 | GREAT RIVER ENERGY | Not Shared
A | B | South | LA | 50048 | 50086 | Line Upgrade | 2026-06-09 | Champagne | Colton |  | 138 |  | Upgrade of Champagne – East Opelousas – Colton 138kV line. | LA |  |  | M1 - Proposed | 9105556 | ENTERGY SERVICES, LLC. | Not Shared
A | B | South | AR | 50040 | 50071 | Substation | 2026-04-01 | Morrilton East |  |  | 161 |  | A new point of interconnection at the existing Morrilton East 161kV substation that includes an extension of the operating bus, new breaker, CCVT, and support structures and foundations. | AR |  |  | M1 - Proposed | 3175000 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | Central | IN | 25384 | 28541 | Substation | 2025-04-29 | East |  |  | 138 |  | Replace 5 138 kV breakers. #1, #2, #4, #5, and #7. | IN |  |  | M1 - Proposed | 4500000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | IA | 25428 | 28656 | Line New | 2027-06-01 | New Shenandoah | Clarinda | 1 | 69 |  | Construct new Shenandoah-Clarinda 69 kV line | IA |  | 6.5 | M1 - Proposed | 7000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 25208 | 28304 | Transformer | 2027-12-31 | Brownstown |  |  | 345 | 120 | Replace Brownstown 304 345/120kV Transformer. | MI |  |  | M1 - Proposed | 6572000 | ITC | Not Shared
B | B | West | MN | 25267 | 28391 | Line Upgrade | 2028-12-31 | Hibbing | Maturi |  | 115 |  | Rebuild 115kV 180 Line (Hibbing -Maturi) with 636 ACSR. | MN |  |  | M1 - Proposed | 9750000 | MINNESOTA POWER INC. | Not Shared
A | B | Central | IN | 25560 | 28789 | Line Upgrade | 2025-05-31 | MooresJct | WilburJct |  | 69 |  | Rebuild 2.3 miles of 69kV line from Wilbur Jct to Mooresville Jct | IN | 2.3 |  | M1 - Proposed | 2300000 | HOOSIER ENERGY | Not Shared
A | B | West | IA | 25212 | 28589 | Line New | 2026-12-31 | ITCM Asset Blanket for 2026 | Throughout system |  | 345 | 69 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA |  |  | M1 - Proposed | 52625000 | ITC MIDWEST | Not Shared
A | B | West | MN | 25321 | 28427 | Misc. | 2025-10-31 | Huntley |  |  | 69 |  | Relay upgrades at Huntley for new Winnebago City substation interconnection | MN |  |  | M1 - Proposed | 318432 | ITC MIDWEST | Not Shared
A | B | East | MI | 50060 | 50100 | Substation | 2028-06-01 | Macomb |  |  | 120 |  | Install a new 120 kV breaker at Macomb position "HC" to terminate the new Bismarck - Macomb 120 kV line. | MI |  |  | M1 - Proposed | 1360000 | ITC | Not Shared
A | B | East | MI | 25218 | 28340 | Substation | 2027-12-31 | Sterling |  |  | 230 | 120 | Replace the Sterling #201 230/120 kV transformer with a transformer of at least 728 MVA (3503 Amps) summer emergency rating. Install a breaker and associated equipment on the high side of the transformer. | MI |  |  | M1 - Proposed | 7950000 | ITC | Not Shared
A | B | West | WI | 25368 | 28517 | Line Upgrade | 2024-12-31 | Owen Area Substation | Lakehead Pump | 1 | 69 |  | W3418 line refurb on 2.8 miles from structures 716-762. | WI | 2.8 |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25321 | 28423 | Line New | 2025-10-31 | Huntley | Winnebago City | 2 | 69 |  | Bring existing Huntley - Thisius 69 kV line in and out of new Winnebago City substation | MN |  |  | M1 - Proposed | 931250 | ITC MIDWEST | Not Shared
A | B | East | MI | 24535 | 27992 | Substation | 2025-05-30 | Bingham |  |  | 138 |  | Reterminate the Bingham - Cornell 138kV line at position BM4 | MI |  |  | M1 - Proposed | 712500 | METC | Not Shared
A | B | East | MI | 24998 | 28148 | Line New | 2027-06-01 | Pontiac |  |  | 345 |  | Fitz-Pontiac 345kV line termination will be moved from position BQ to position AQ. | MI |  |  | M1 - Proposed | 144000 | ITC | Not Shared
A | B | West | MN | 25381 | 28529 | Line Upgrade | 2027-12-19 | Long Siding | Milaca | 1 | 69 |  | Rebuild Long Siding - Milaca | MN | 8.6 |  | M1 - Proposed | 4449792 | GREAT RIVER ENERGY | Not Shared
A | A | West | ND | 4295 | 8220 | Misc. | 2028-12-31 | East Oliver | VSC HVDC Converter |  | 250 |  | New, Relocated VSC HVDC Converter Station, Symmetric Monopole Configuration, +/-250kV | ND |  |  | M1 - Proposed | 352500000 | MINNESOTA POWER INC. | Not Shared
A | B | West | MN | 50002 | 50008 | Substation | 2024-05-01 | Bluff Creek |  |  | 115 |  | Replace Overstressed Bluff Creek TR2 with new breaker with larger interrupting capacity. | MN |  |  | M1 - Proposed | 80000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 50005 | 50016 | Line Upgrade | 2025-12-31 | Donaldson 41.6 kV | Drayton 41.6 kV | 1 | 42 |  | Reconductor 10.5 miles of 41.6 kV line between Donaldson 41.6 kV and Drayton 41.6 kV. | MN | 10.5 |  | M1 - Proposed | 800000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | South | MS | 25501 | 28757 | Line New | 2026-12-01 | County Line GOAB | County Line |  | 115 |  | In order to serve the member delivery point, tap the Olive Oil Loop line with a 115kV Goab and construct a new line to the new delivery point. | MS |  |  | M1 - Proposed | 1960000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | A | West | ND | 3856 | 7379 | Line Upgrade | 2027-12-31 | HVDC Line | ND Reconductor | 1 | 250 |  | Short segment of reconductor in ND to increase capacity | ND |  |  | M1 - Proposed | 6000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | WI | 25342 | 28465 | Substation | 2029-06-01 | Missouri Creek |  |  | 69 | 24 | Rebuild Eau Galle distribution substation as new Missouri Creek substation and convert existing Eau Galle distribution to 23.9kV. | WI |  |  | M1 - Proposed | 9000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | WI | 22798 | 26866 | Substation | 2027-06-30 | Various Subs |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 45000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
B | B | East | MI | 25249 | 28320 | Line Upgrade | 2028-06-01 | Bismarck | Stephens | 1 | 345 |  | Relocate and re-terminate Stephens 345/230 kV Transformer #304 from Position CQ to Position BI. | MI |  |  | M1 - Proposed | 1640000 | ITC | Not Shared
A | B | West | WI | 25348 | 28506 | Substation | 2027-12-31 | Saratoga | 7 Mile Creek |  | 138 | 69 | • At 7 Mile Creek SS, relocate existing 7 Mile Creek – Sand Lake (X-11) 138-kV line to connect the new line at existing X-11’s terminal. In addition, construct a new section of approx. 0.05 miles on X-11 for its interconnection to bus 4, eliminating the need for 138-kV crossings. Finally, install new 138 kV substation equipment (breaker and switch) at 7 Mile Creek to complete its 4-position ring bus. • At Saratoga SS, install one 138-kV line circuit breaker with manual line and bus-side disconnect switches for the new line. In addition, install a new 138-kV bus-tie breaker and replace Saratoga – Badger West (X-43) 138-kV line jumpers, and buses 1 and 2 jumpers, to allow higher ratings on existing facilities. Finally, reroute X-159 line preventing it from being above the new line’s terminal. • After Northern Adams County Area Network Improvement Project is placed in service in 2027, retire Saratoga 138/69-kV T33 transformer and re-terminate the new line with this vacated position. | WI |  |  | M1 - Proposed | 5150000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25160 | 28223 | Line Upgrade | 2026-06-01 | Weston | Morrison Ave | Z-52 | 115 |  | Reconfigure Weston - Sherman Street (O-41) line terminal to new position on West bus and relocate the Weston - Morrison Ave (Z-52) line terminal to the vacated position. Z-52 to be reconductored from Weston to Morrison Ave. Install upgraded communication equipment at remote ends. | WI |  |  | M1 - Proposed | 3800000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25437 | 28679 | Substation | 2027-12-31 | Substation 85 |  |  | 161 |  | Install 161 kV circuit breakers and bus work to convert Substation 85 to a ring bus configuration | IA |  |  | M1 - Proposed | 7000000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | West | SD | 24335 | 27827 | Line Upgrade | 2027-06-01 | Hwy. 12 (620215) | Ortonville (620216) | 1 | 115 |  | Rebuild GRE's 3.14 miles of the Hwy 12 - Ortonville 115 kV line with a larger conductor. | SD |  |  | M1 - Proposed | 2000000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | East | MI | 24998 | 28193 | Substation | 2027-06-01 | Pontiac |  |  | 345 |  | Remove breakers EM and ET Remove KK disconnect switch and move existing breaker KM to ET position. Extend bus 303 to connect E Row and remove bus 305 Replace disconnect switches EO, ER, and EV with new standard disconnect switches Upgrade relaying as necessary to accommodate new configuration | MI |  |  | M1 - Proposed | 2230000 | ITC | Not Shared
A | B | Central | IN | 24274 | 28014 | Line New | 2026-12-01 | Maloney | Reservoir | 92 | 138 |  | A 4 mile 138 kV transmission line to serve load in Boone County. | IN |  | 4 | M1 - Proposed | 7500000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | East | MI | 24559 | 28026 | Substation | 2025-12-31 | Cronk |  |  | 138 |  | Install line entrance structure and disconnect as TOIF. Install position WM14 at Cronk to interconnect J1658 generator. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
B | B | South | MS | 25493 | 28776 | Line New | 2025-12-31 | North Hattiesburg GOAB |  |  | 69 |  | Construct approximately 5 miles of new transmission line from the West Hattiesburg Delivery point to a new 69kV GOAB located adjacent to the North Hattiesburg Substation. | MS |  |  | M1 - Proposed | 125000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | MN | 50002 | 50013 | Substation | 2023-05-01 | Rich Valley |  |  | 115 |  | Replace overstressed breaker Rich Valley 5TR1 that is at end of life with breaker of larger interrupting capacity. | MN |  |  | M1 - Proposed | 80000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | WI | 50136 | 50216 | Substation | 2027-06-01 | Baraboo |  |  | 69 |  | The LDC is planning to relocate the Baraboo substation from its current location to a nearby site. To accommodate this ATC will install 2x new T-Line structures and replace one T-Line structure to reroute the Kirkwood-Dam Heights 69kV (Y-75) line. This will require roughly 0.04 miles of new conductor. Additionally, a new 3 way tap structure to the new substation will be required. A new ATC control house will be required to retain supervisory control of the tap switches. Lastly, ATC to retire 9x T-Line poles and the substation equipment at the current Baraboo location. | WI |  |  | M1 - Proposed | 3000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25251 | 50353 | Substation | 2024-07-31 | Wever | BGS | 1 | 161 |  | Relay upgrades at BGS on Wever terminal | IA |  |  | M1 - Proposed | 179144 | ITC MIDWEST | Not Shared
A | B | Central | IN | 25150 | 28232 | Line Upgrade | 2025-12-31 | Mackey | Oakland City | 52 | 69 |  | Replacement of poles along Y52-2 from Mackey to Oakland City | IN |  |  | M1 - Proposed | 8000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | IA | 25188 | 28269 | Substation | 2025-12-01 | Boone South | Substation |  | 69 | 69 | Build 69kV portion of future IPL Boone South substation | IA |  |  | M1 - Proposed | 3761163 | ITC MIDWEST | Not Shared
A | B | West | SD | 25301 | 28355 | Voltage Device | 2024-09-01 | Leola |  |  | 115 |  | Add 2-10 Mvar capacitors to the 115 kV bus at Leola. | SD |  |  | M1 - Proposed | 1000000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | West | WI | 25226 | 28300 | Substation | 2026-11-01 | Union Townline |  |  | 69 |  | • ATC will construct an approximately 0.08 mile 69 kV transmission line extension from the Bass Creek-Sheepskin 69 kV line (Y-158) to the Union Townline substation for a networked substation feed. • ATC will construct a 69 kV loop-through straight bus with line breakers, associated switches, and space reserved for a potential bus-tie breaker. • Evansville Water & Light (WPPI) to install a second 69/12.47 kV transformer with high side circuit switcher protection and necessary low side bus equipment. | WI |  |  | M1 - Proposed | 11600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 25500 | 28731 | Misc. | 2025-12-31 | METC Facilities |  |  | 345 | 138 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI |  |  | M1 - Proposed | 2500000 | METC | Not Shared
B | B | Central | MO | 50070 | 50110 | Voltage Device | 2026-12-01 | Camden |  |  | 138 |  | Camden UE138 kV 15 Mvar Cap Bank | MO |  |  | M1 - Proposed | 600000 | AMEREN MISSOURI | Not Shared
A | B | Central | IL | 25315 | 28408 | Line New | 2029-12-31 | Forest City | Breeds |  | 69 | 69 | New Forest City-Breeds 336 ACSR 69 kV Line | IL |  | 22.1 | M1 - Proposed | 14865000 | PRAIRIE POWER, INC. | Not Shared
A | B | Central | MO | 22886 | 26954 | Substation | 2026-12-01 | Berkeley |  |  | 138 |  | Remove HSGS' on XFMRs 1,2,3,4. Add high side interrupting devices. Add line BRKs to Pos. D & J. Would require add'l bus diff panels for Buses 3 & 4 Relay: If no new Control Enclosure, upgrade two of the tie breakers and the 138 kV buses. | MO |  |  | M1 - Proposed | 39200000 | AMEREN MISSOURI | Not Shared
A | B | West | WI | 50091 | 50136 | Line New | 2027-06-01 | Oak Creek | Oakview | 836 | 138 |  | Tap Oak Creek-Oakview 138 kV line to serve new interconnection request. | WI |  |  | M1 - Proposed | 2600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25424 | 28621 | Substation | 2027-06-01 | NE 6th Street |  |  | 161 |  | Construct new 161-13 kV substation | IA |  |  | M1 - Proposed | 4000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25449 | 28617 | Line New | 2027-12-31 | Norwoodville | E. 29th & Hubbell | 1 | 69 |  | Norwoodville-E. 29th & Hubbell 69 kV line | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | South | AR | 25481 | 28699 | Misc. | 2025-12-01 | Arklahoma 115kV |  |  | 115 |  | Independent and redundant communication for each relay. Dual station batteries with separate DC system feeding each relay or monitoring sufficient to FERC 754 guidelines. Independent CT and PT winding inputs for each relay. | AR |  |  | M1 - Proposed | 2525674 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 50031 | 50057 | Substation | 2025-06-01 | Maffitt Lake |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | IN | 50089 | 50135 | Voltage Device | 2024-05-01 | Aetna |  |  | 138 |  | New Synchronous Condenser connected at Aetna 138kV substation. +360/-180 MVAR capabilities. | IN |  |  | M2 - Appendix A Approved | 91000000 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | B | East | MI | 21968 | 26593 | Substation | 2027-06-01 | New Station |  |  | 138 |  | The new Delaney 138 kV station will be rebuilt as a compressed four breaker ring bus configuration. Install new control house. Install (3) 138 kV, 3000 A breakers with at least 40 kA interrupting. The summer emergency rating of all new equipment should be no less than 644 MVA/2693 amps. | MI |  |  | M1 - Proposed | 5686000 | METC | Not Shared
A | B | West | ND | 50152 | 50255 | Substation | 2025-09-01 | Ellendale |  |  | 230 |  | Adding breakers and switches at the Ellendale sub for the new 230 kV line. | ND |  |  | M1 - Proposed | 3000000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | East | MI | 25223 | 28284 | Line New | 2027-06-11 | Lemoyne | Majestic |  | 345 |  | Cut the Lemoyne-Majestic 345 kV line into the Lulu switchyard | MI |  |  | M1 - Proposed | 3551250 | ITC | Not Shared
A | B | West | MN | 25391 | 28552 | Line Upgrade | 2027-06-01 | Mud Lake | Riverton | 1 | 230 |  | Upgrade Mud Lake - Riverton 230 kV line. | MN | 5.6 |  | M1 - Proposed | 1146876 | GREAT RIVER ENERGY | Not Shared
A | B | West | IA | 25428 | 28657 | Misc. | 2027-12-31 | Clarinda | Shenandoah | 1 | 69 |  | Retire section of the Clarinda-Shenandoah 69 kV line (approximately 2.5 miles) | IA |  |  | M1 - Proposed | 100000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25258 | 28438 | Substation | 2026-06-15 | Prior |  |  | 115 | 14 | Install second 115/13.8 kV transformer and associated equipment. | MN |  |  | M1 - Proposed | 7280000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25560 | 28790 | Line Upgrade | 2026-12-31 | Wilbur | Nelson |  | 69 |  | Rebuild 6.9 miles of 69kV line | IN | 6.9 |  | M1 - Proposed | 7500000 | HOOSIER ENERGY | Not Shared
A | B | Central | IL | 22969 | 26933 | Substation | 2026-06-01 | Decatur East Main |  |  | 138 |  | Add line breaker to the L1522 line. | IL |  |  | M1 - Proposed | 2250000 | AMEREN ILLINOIS | Not Shared
B | B | East | MI | 50064 | 50190 | Line Upgrade | 2028-06-01 | East Tawas | Quary | 1 | 138 |  | Rebuild approximately ~5.78 miles from structure #504804 to Quarry (J1210) circuit to 954 ACSR conductor utilizing standard 138 kV double- circuit structures with OPGW. Leave the west side of the double-circuit structures vacant. | MI | 5.78 |  | M1 - Proposed | 8800000 | METC | Not Shared
A | B | West | IA | 25213 | 28590 | Line New | 2025-12-31 | Blanket for SCADA M.O. Switches for2025 | Throughout system |  | 69 | 69 | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be utilized to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | IA |  |  | M1 - Proposed | 3125000 | ITC MIDWEST | Not Shared
A | B | South | AR | 50034 | 50060 | Substation | 2025-04-30 | AECC Dry Creek |  |  | 161 |  | Osage Creek 161 kV Switching Station: The network upgrades for EAL will include wave trap removal, relay upgrades, relay and telecom settings modifications. Green Forest 161 kV Substation: The network upgrades for EAL will include wave trap removal on capacitor bank. Green Forest South 161 kV Substation: The network upgrades for EAL will include wave trap removal on Transformer #2 and digital microwave network expansion. Harrison West 161kV Substation: The network upgrades for EAL will include wave trap removal on capacitor bank. Harrison East 161 kV Substation: The network upgrades for EAL will include wave trap removal, relay upgrades, relay and telecom settings modifications. Telecom: The network upgrades for EAL will include a new 195’ tower with shelter and digital microwave network expansion at AECC Dry Creek substation. | AR |  |  | M1 - Proposed | 1869029 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | West | WI | 25377 | 28566 | Line New | 2024-12-01 | Rice Lake | Barron | 1 | 69 |  | Build 3 way switching structure on line W3421 between Rice Lake - Barron 69 kV to accommodate DPC North Wal interconnection. | WI |  |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 24478 | 27927 | Substation | 2026-04-01 | Kenowa |  |  | 345 |  | Install BKRs 35F7, and 35H9 and associated disconnect switches at Kenowa 345 kV. | MI |  |  | M1 - Proposed | 5567500 | METC | Not Shared
A | B | East | MI | 25196 | 28305 | Line Upgrade | 2025-05-01 | Beecher | Knowles |  | 138 |  | Remediate the Beecher-Dowling Junction sag limit to achieve a rating of at least 219 MVA SN and 249 MVA WN. | MI |  |  | M1 - Proposed | 258750 | METC | Not Shared
B | B | West | WI | 25001 | 28175 | Line Upgrade | 2027-07-01 | North Monroe | Verona | Y-42/Y-208 | 69 |  | Rebuild and install OPGW on approximately 17 miles from Verona to New Glarus (Y-208) and 10 miles from New Glarus to North Monroe (Y-42). Also includes rebuilding tap to Monticello 1.6 miles. | WI | 28.6 |  | M1 - Proposed | 49000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25222 | 28260 | Substation | 2028-09-01 | Bryant | Substation |  | 345 | 345 | A new Bryant 345 kV, 3 breaker, ring-bus switching station will be constructed for the interconnection of project J1432. | IA |  |  | M1 - Proposed | 8987360 | ITC MIDWEST | Not Shared
A | B | West | MN | 50061 | 50101 | Misc. | 2026-12-15 | Monticello | Alexandria | 1 | 345 |  | Replace damaged OPGW on lines 0973 MNN-QRY, 0954 QRY-RVV, 0954 ALS-RVV | MN |  |  | M1 - Proposed | 4280000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 24537 | 28002 | Misc. | 2025-04-03 | Newton |  |  | 138 |  | Install 2506 for anti-islanding | MI |  |  | M1 - Proposed | 164769 | METC | Not Shared
A | A | West | MN | 4295 | 28485 | Line New | 2028-12-31 | St Louis County | Arrowhead Ckts 1&2 |  | 230 |  | Two new 230 kV lines from St Louis County to existing Arrowhead 230 kV bus | MN |  | 1 | M1 - Proposed | 5000000 | MINNESOTA POWER INC. | Not Shared
B | B | West | MN | 25281 | 28392 | Line Upgrade | 2031-12-31 | Maturi | Virginia |  | 115 |  | Rebuild 115kV 180 Line (Maturi - Virginia) with 636 ACSR. | MN |  |  | M1 - Proposed | 11250000 | MINNESOTA POWER INC. | Not Shared
A | B | West | ND | 25503 | 28743 | Line Upgrade | 2026-10-01 | Ellendale |  |  | 115 |  | 115 kV terminal equipment for line to Aberdeen | ND |  |  | M1 - Proposed | 140000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | East | MI | 50098 | 50148 | Line New | 2025-11-01 | Hagensville Junction | TBD | 1 | 138 | 138 | Install 5.7 miles of 795ACSS from Wolverine's Hagensville Junction location to near METC's Hagensville Tap location. | MI |  | 7 | M1 - Proposed | 8550000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A | B | South | LA | 25457 | 28695 | Substation | 2027-06-01 | PCI |  |  | 69 |  | Replace 3 69 kV breakers | LA |  |  | M1 - Proposed | 2730000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | MN | 25295 | 28455 | Line Upgrade | 2023-09-30 | St Augusta | Wakefield | 1 | 115 |  | Replace structures at 1 clearance limited span between St Augusta - Wakefield. | MN |  |  | M1 - Proposed | 50000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | KY | 25120 | 28201 | Line Upgrade | 2025-12-01 | Reid EHV |  |  | 161 |  | Add terminal on the 161 kV bus for POI of J1466. | KY |  |  | M1 - Proposed | 0 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | B | South | LA | 50087 | 50127 | Substation | 2025-07-01 | Marthaville | Belmont | 1 | 230 | 230 | New Ft Jessup substation tapped into the future Marthaville to Belmont 230 kV line 6.8 miles from Marthaville. | LA |  |  | M1 - Proposed | 4070667 | CLECO POWER LLC | Not Shared
A | B | West | IA | 25188 | 28270 | Line New | 2025-12-01 | Boone South | Substation |  | 69 | 69 | Install line taps for the new Boone South substation. | IA |  |  | M1 - Proposed | 436250 | ITC MIDWEST | Not Shared
A | B | West | MN | 25322 | 28424 | Line Upgrade | 2025-12-15 | Granite City | Crossroads | 1 | 115 |  | Rebuild 3.7 miles 115 kV line from Granite City - Crossroads with new structures and new OPGW shield wire. | MN | 3.7 |  | M1 - Proposed | 4000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 50014 | 50027 | Substation | 2025-06-30 | West Grand |  |  | 161 |  | Install 161 kV line breakers and relaying | IA |  |  | M1 - Proposed | 3000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | WI | 25369 | 28518 | Line Upgrade | 2024-12-31 | Ellsworth |  |  | 69 |  | Replace 3-way switch at Ellsworth substation tap with two 1-way switches. | WI |  |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | South | MS | 50160 | 50288 | Transformer | 2027-12-15 | Andrus 230 | Andrus 115 | 1 | 230 | 115 | Install second 230/115 kV 392 MVA Autotransformer. | MS |  |  | M1 - Proposed | 19750000 | ENTERGY MISSISSIPPI, LLC. | Not Shared
A | B | South | MS | 25438 | 28680 | Line Upgrade | 2026-01-01 | Pickens | Canton |  | 230 |  | Rebuild/reconductor Pickens - Canton line to 779 MVA rating. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
B | B | South | MS | 25494 | 28777 | Line Upgrade | 2026-06-01 | Rawls Springs | North Hattiesburg |  | 69 |  | A complete rebuild of Line 94 (Rawls Springs – North Hattiesburg 69kV) is recommended. | MS |  |  | M1 - Proposed | 2362500 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | East | MI | 25194 | 28301 | Line Upgrade | 2026-01-15 | Cronk | Moore Road |  | 138 |  | Rebuild the Cronk-Moore Road 138 kV circuit utilizing conductor rated at least that of 1431 ACSR. | MI |  |  | M1 - Proposed | 10900000 | METC | Not Shared
A | B | Central | IN | 25331 | 28507 | Substation | 2025-12-31 | WVPA Blacketor 69/12kV Sub |  |  | 69 | 12 | WVPA Blacketor 69kV Sub - Construct a new 69/12kV substation to serve load fed from an existing meter point | IN |  | 1.3 | M1 - Proposed | 8753000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | Central | IN | 25407 | 28578 | Substation | 2026-12-31 | Angel Mounds |  |  | 138 |  | Replacing several 138kV circuit breakers and switches | IN |  |  | M1 - Proposed | 3000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | Central | MO | 50057 | 50096 | Transformer | 2026-01-01 | Vessel |  |  | 138 |  | At Vessel Bulk Sub install the second 84 MVA transformer. | MO |  |  | M1 - Proposed | 4000000 | AMEREN MISSOURI | Not Shared
A | B | Central | IN | 24274 | 28015 | Substation | 2026-12-31 | Reservoir |  |  | 138 |  | A 138 kV breaker-and-a-half substation (4 bays, 8 positions) dedicated to serve REMC and IOU customer load in Boone County | IN |  |  | M1 - Proposed | 16500000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | SD | 25301 | 28356 | Substation | 2024-09-01 | Leola |  |  | 42 |  | Add breaker and switches to the 41.6 kV portion of the substation. | SD |  |  | M1 - Proposed | 2600000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A | B | East | MI | 24477 | 27912 | Substation | 2027-09-29 | Peddler |  |  | 138 |  | Install position WM6 at the new station for J1292 generator to connect. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | MN | 25321 | 28428 | Substation | 2025-10-31 | Winnebago Local |  |  | 69 |  | Retire existing transmission portion Winnebago Local substation after new Winnebago City substation is completed | MN |  |  | M1 - Proposed | 407160 | ITC MIDWEST | Not Shared
B | B | West | WI | 25155 | 28246 | Line Upgrade | 2028-12-31 | Bluemound |  |  | 345 | 138 | Milwaukee Area 230 kV transmission lines facilities will be fully rebuilt with new monopole construction and general scope is as follows: • Rebuild of Oak Creek to Bluemound 230 kV line 873 forming new “Bluemound to Arcadian” 345 line and 2nd “Arcadian to Elm Road” 345 kV line, along with double circuit partner portions of 345 kV PLPL81 (Existing Arcadian to Pleasant Prairie) to a “bundled” conductor. Additionally, double circuit partners 345 kV line LERG71 (Arcadian to Elm Road) and 138 kV line 9952 (Arcadian to Moorland) and a portion of 138 kV line 872k61 (Moorland to Kansas) will retain their existing conductors, • Rebuild of Oak Creek to Bluemound 230 kV line 862 forming new “Bluemound to Elm Road” 345 line, Additionally, double circuit partner 138 kV line 5066 (new West Junction to St Martins) will be rebuilt • Removal of the retired West Junction Tap to Bluemound 138 kV line 5066 portion as the 862/873 multiple circuit section adjacent to Bluemound substation is rebuilt, • Rebuild Bluemound 230 kV straight bus as a 5 position 345 kV ring bus, with two 345/138 kV transformers, terminate new transmission lines to develop 345 kV circuits to Elm Road 345 kV and Arcadian 345 kV Substations, • Add a 345 kV rung to Arcadian SS to loop in rebuilt line 873 portions that will connect into Arcadian substation, • Reconfigure the Elm Road 345 and Oak Creek 138 kV buses to interconnect the new rebuilt Bluemound to Elm Road 345 line and 2nd Arcadian to Elm Road 345 kV line. Removal of Oak Creek 230 kV facilities, • New control house, relays, conduit, and cabling at Bluemound substation. • Replace/Install and terminate communication fiber on select facilities, • Coordinate with the suspension/future plan of WEC generation resources • Allow retirement of all 230 kV facilities. | WI |  |  | M1 - Proposed | 542000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | MO | 25362 | 28495 | Substation | 2026-12-31 | All |  |  | 345 | 138 | Miscellaneous breaker and relay replacements. | MO |  |  | M1 - Proposed | 5000000 | AMEREN MISSOURI | Not Shared
B | B | Central | MO | 50071 | 50111 | Voltage Device | 2026-12-01 | Moreau |  |  | 161 |  | Moreau 161 kV 15 Mvar Cap Bank | MO |  |  | M1 - Proposed | 600000 | AMEREN MISSOURI | Not Shared
A | B | West | WI | 50042 | 50073 | Misc. | 2025-12-31 | Various |  |  | 0 |  | The Substation Technology Package #2 (SSTP#2) program of work will set the stage for the future of the digital substation field worker by providing enhanced Business Capabilities over ATC’s substation fiber network infrastructure. The SSTP#2 – 2025 project scope will include the following technology enhancements: • Installation of Wireless Access Points (AP) at various ATC substations • Installation of Cyber Security fortifications for Rogue Device detection at various ATC substations • Convert select Telecom equipment to DC power at various ATC substations | WI |  |  | M1 - Proposed | 10500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | South | AR | 24694 | 28064 | Substation | 2026-12-31 | Coop Office | Colt |  | 69 |  | Sectionalizing breaker to be added on the Coop Office to Colt 69kV line | AR |  |  | M1 - Proposed | 2500000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | B | West | MN | 25399 | 28618 | Line Upgrade | 2026-10-21 | Pleasant Valley |  |  | 161 |  | Replace breakers and wave trap at Pleasant Valley on the Pleasant Valley - Byron 161 kV line. | MN |  |  | M1 - Proposed | 1400000 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 24515 | 27993 | Substation | 2025-05-30 | Bingham |  |  | 138 |  | Install required entrance structures and disconnect switch as TOIF. Install position WM6 at Bingham to interconnect J1553 generator. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | IA | 50029 | 50051 | Substation | 2025-08-01 | SE Soteria |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 24413 | 27841 | Line Upgrade | 2025-02-28 | Roseau | Moranville |  | 230 |  | Moranville-Roseau 230 kV | MN |  |  | M1 - Proposed | 60000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | West | IA | 25424 | 28622 | Line New | 2027-06-01 | NE 6th Street | NE Ankeny | 1 | 161 |  | Tap NE Ankeny - Big Creek 161 kV | IA |  |  | M1 - Proposed | 1250000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 21968 | 26594 | Line New | 2027-06-01 | Delaney | Thetford | 1 | 138 |  | Reterminate the existing Delaney-Thetford 138kV line into the new station configuration. | MI |  | 1.1 | M1 - Proposed | 1473000 | METC | Not Shared
A | B | Central | IL | 25315 | 28409 | Line New | 2029-12-31 | Breeds | Sky Rocket |  | 69 | 69 | New Breeds-Sky Rocket 336 ACSR 69 kV Line | IL |  | 6 | M1 - Proposed | 3900000 | PRAIRIE POWER, INC. | Not Shared
A | B | East | MI | 25223 | 28285 | Substation | 2027-06-11 | Milan |  |  | 345 |  | Upgrade position CM, CQ, and CT relaying | MI |  |  | M1 - Proposed | 607350 | ITC | Not Shared
A | B | East | MI | 25198 | 50239 | Line Upgrade | 2028-06-01 | Port Calcite | Riggsville |  | 138 |  | Redirect line from Rockport into the new station utilizing 954 ACSR Conductor. | MI |  | 1.5 | M1 - Proposed | 580000 | METC | Not Shared
A | B | West | IA | 25464 | 28658 | Misc. | 2025-12-01 | CBEC |  |  | 345 | 161 | Relay replacement at CBEC substation | IA |  |  | M1 - Proposed | 1200000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 24560 | 28027 | Substation | 2025-12-31 | Aphis |  |  | 138 |  | Construct J1614 POI station as a 138kV breaker and half station with three 40kA breakers in a ring bus configuration. | MI |  |  | M1 - Proposed | 6679318 | METC | Not Shared
A | B | South | LA | 25483 | 28700 | Line Upgrade | 2025-12-31 | Multiple |  |  | 230 | 69 | AM Renewal | LA |  |  | M1 - Proposed | 9600000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | East | MI | 25195 | 28321 | Line Upgrade | 2028-06-01 | MCV | Tittabawassee | 1 | 345 |  | Relocate a structure to accommodate 345 kV station expansion. | MI |  |  | M1 - Proposed | 1125000 | METC | Not Shared
A | B | Central | IN | 25408 | 28591 | Voltage Device | 2025-12-31 | Fort Branch |  |  | 69 |  | Install 69kV 15.6MVAR capacitor bank | IN |  |  | M1 - Proposed | 3000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | WI | 50107 | 50167 | Substation | 2028-09-10 | Clintonville |  |  | 138 |  | J1513 138kV Interconnection Substation Interconnection Facilities | WI |  |  | M1 - Proposed | 1063000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 25354 | 28542 | Substation | 2025-05-21 | Parker |  |  | 138 |  | Replace 3 138 kV breakers. #1, #2, and #3. | IN |  |  | M1 - Proposed | 2700000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | MN | 25373 | 28553 | Substation | 2025-10-17 | Salem Switching Station |  |  | 69 |  | Add breakers to Salem Switching Station | MN |  |  | M1 - Proposed | 1342821 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 50038 | 50079 | Misc. | 2026-08-19 | HSC | Tittabawassee | 1 | 138 |  | Re-route OHL to accommodate Orr Road expansion | MI |  |  | M1 - Proposed | 1683000 | METC | Not Shared
A | B | West | MN | 25381 | 28530 | Line Upgrade | 2027-12-19 | Long Siding | Princeton | 1 | 69 |  | Rebuild Long Siding to Princeton | MN | 1.6 |  | M1 - Proposed | 924029 | GREAT RIVER ENERGY | Not Shared
A | B | Central | IN | 25560 | 28791 | Line Upgrade | 2026-04-01 | Nelson | WilburJct |  | 69 |  | Rebuild 3.45 miles of 69kV line | IN | 3.45 |  | M1 - Proposed | 3400000 | HOOSIER ENERGY | Not Shared
A | B | East | MI | 24458 | 27928 | Substation | 2026-12-31 | Kenowa |  |  | 345 |  | Install Kenowa switch 177 and line entrance structure at position FH35 for generator interconnection. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | IA | 25222 | 28261 | Line New | 2028-09-01 | Rock | Salem | 1 | 345 | 345 | The Salem to Rock Creek 345 kV line will be opened and 2 dead-end structures will be installed to allow the line to be looped through the Bryant 345 kV switching station. | IA |  |  | M1 - Proposed | 1726000 | ITC MIDWEST | Not Shared
A | B | West | MN | 21767 | 26360 | Line Upgrade | 2027-03-31 | Riverton | GRE-Portage Lake |  | 115 |  | Rebuild GRE-Portage Lake - Aitkin Tap 115 kV Line | MN |  | 25 | M1 - Proposed | 12000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | WI | 25309 | 28379 | Misc. | 2024-12-31 | Various |  |  | 0 |  | The Substation Technology Package #2 (SSTP#2) program of work will set the stage for the future of the digital substation field worker by providing enhanced Business Capabilities over ATC’s substation fiber network infrastructure. The SSTP#2 – 2024 project scope will include the following technology enhancements: • The installation of Wireless Access Points and enhanced Cyber Security fortifications at ~75 ATC substations. • Wireless connectivity will provide field workers with secure access from the substation ATC’s corporate data centers. • Cyber Security fortifications will introduce substation communication equipment protections in the event of a rogue device breach by pro-actively monitoring data activity between the substation router and switch. | WI |  |  | M1 - Proposed | 3600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IN | 25458 | 28696 | Substation | 2028-12-31 | Gibson Gen Station |  |  | 345 |  | Gibson 345kV CBs: replace (18) 345kV-63kA interrupting rated CBs with 80kA; replace breaker disconnect switches and upgrade bus conductor as needed | IN |  |  | M1 - Proposed | 27000000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | IA | 25188 | 28271 | Line New | 2025-12-01 | Boone Southeast Tap | Boone Southeast |  | 69 | 69 | Retire tap and PTSs to existing Boone Southeast station | IA |  |  | M1 - Proposed | 166250 | ITC MIDWEST | Not Shared
A | B | Central | IN | 50095 | 50145 | Misc. | 2026-09-30 | Stout CT |  |  | 138 |  | Relay packages for CT 4 and its GSU | IN |  |  | M1 - Proposed | 150000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | MN | 25293 | 28439 | Line Upgrade | 2024-12-31 | Tracy Switching Station | Walnut Grove | 1 | 69 |  | Rebuild 1 mile 69 kV with new structures, new OPGW shield wire, and new conductor. | MN | 1 |  | M1 - Proposed | 750000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25321 | 28425 | Line New | 2025-10-31 | Winnebago City | Garden City |  | 69 |  | Bring existing Winnebago Local Ckt 746 into new Winnebago City substation | MN |  |  | M1 - Proposed | 597500 | ITC MIDWEST | Not Shared
A | B | East | MI | 24537 | 28003 | Misc. | 2025-03-03 | Butters |  |  | 138 |  | Install a 2506 for anti-islanding | MI |  |  | M1 - Proposed | 107756 | METC | Not Shared
B | B | Central | MO | 50069 | 50109 | Voltage Device | 2026-12-01 | Sweetwater |  |  | 138 |  | Sweetwater 20 Mvar Cap Bank | MO |  |  | M1 - Proposed | 600000 | AMEREN MISSOURI | Not Shared
A | B | South | LA | 13905 | 22988 | Substation | 2028-06-01 | Burnside |  |  | 230 |  | 1) Construct a 3 breaker 230 kV ring bus at Burnside, Minimum of 2000 Amp equipment. 2) Cut in and out the Conway to Panama 230 kV line. 3) Install 300 MVA 230-115 kV Autotransformer, similar to the current Sorrento 230-115 kV Autotransformer. 4) Install 115 kV low side breaker at Burnside | LA |  |  | M1 - Proposed | 34260000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | MN | 25378 | 28567 | Substation | 2026-10-15 | Gaylord |  |  | 69 |  | Rebuild Gaylord substation at a new location, converting 4.16kV feeders to 13.8kV. | MN |  |  | M1 - Proposed | 5100000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 25194 | 28302 | Substation | 2026-02-02 | Moore Road |  |  | 138 |  | Replace Moore Road conductor and equipment to achieve a rating at least that of 348 MVA SE. | MI |  |  | M1 - Proposed | 423126 | METC | Not Shared
A | B | West | IA | 25439 | 28681 | Line New | 2030-12-31 | Sub G | Sub Q | 1 | 69 |  | Install two 69 kV line taps terminating at Sub G 69 kV line breakers. | IA |  |  | M1 - Proposed | 300000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | WI | 22911 | 26868 | Substation | 2027-06-30 | Various Subs |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 19000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25370 | 28519 | Line Upgrade | 2024-12-31 | Blair | Alma Center | 1 | 69 |  | W3401 line refurb on 18.8 miles from Alma Center to Blair. | WI | 18.8 |  | M1 - Proposed | 1000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 25080 | 28194 | Substation | 2025-06-01 | Lagrange |  |  | 138 |  | Relocate one existing 138kV line, create new position on LaGrange ring bus for generating lead line, replace control enclosure | IN |  |  | M1 - Proposed | 5431638 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | B | West | MN | 25421 | 28570 | Line New | 2024-11-20 | Sand Lake | Sand Lake Tap | 1 | 69 |  | Relocate a portion of the Sand Lake to Sand Lake Tap line. | MN |  | 0.75 | M3 - Under Construction | 1630051 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 50121 | 50193 | Line Upgrade | 2028-06-01 | East Tawas | Quary | 1 | 138 |  | Relocate approximately ~5.78 miles from structure #504804 to structure Quarry onto the vacant side of the recently-rebuilt Twining – Whittemore utilizing existing double- circuit structures, using 954 ACSR conductor and install OPGW. De-energize old section after relocating to new location. | MI | 5.78 |  | M1 - Proposed | 4700000 | METC | Not Shared
A | B | South | LA | 25312 | 28393 | Substation | 2024-07-15 | Plaisance |  |  | 138 |  | Expand Plaisance for J1832 Generation Project | LA |  |  | M1 - Proposed | 6512000 | CLECO POWER LLC | Not Shared
A | B | South | MS | 25501 | 28759 | Line New | 2026-12-01 | County Line GOAB |  |  | 115 |  | In order to serve the member delivery point, tap the Olive Oil Loop line with a 115kV Goab and construct a new line to the new delivery point. | MS |  |  | M1 - Proposed | 200000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
B | B | South | MS | 25495 | 28778 | Line Upgrade | 2026-12-01 | West Hattiesburg SS | West Hattiesburg |  | 69 |  | A complete rebuild of Line 97 (West Hattiesburg SS - West Hattiesburg 69kV is recommended. | MS |  |  | M1 - Proposed | 1141875 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
B | B | East | MI | 50062 | 50103 | Substation | 2028-06-01 | Charge |  |  | 138 |  | Add a new row (10) and install three 138 kV breakers to terminate the new lines at Charge station. | MI |  |  | M1 - Proposed | 3100000 | METC | Not Shared
A | B | West | IA | 25424 | 28623 | Line New | 2027-06-01 | NE 6th Street | Big Creek | 1 | 161 |  | Tap NE Ankeny - Big Creek 161 kV | IA |  |  | M1 - Proposed | 1250000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | IA | 25181 | 28247 | Line New | 2026-10-01 | Calamus East | Substation |  | 161 | 161 | TOIF includes facilities including, 161 kV breaker, switches, dead-end, and equipment at Calamus East substation dedicated to the 161 kV radial line and Generating Facility | IA |  |  | M1 - Proposed | 803119 | ITC MIDWEST | Not Shared
A | B | East | MI | 25223 | 28286 | Substation | 2027-06-11 | Monroe |  |  | 345 |  | Upgrade Monroe position MI relaying | MI |  |  | M1 - Proposed | 270254 | ITC | Not Shared
A | B | Central | IL | 25315 | 28410 | Line New | 2029-12-31 | Sky Rocket | St. David |  | 69 | 69 | New Sky Rocket-St David 336 ACSR 69 kV Line | IL |  | 2.1 | M1 - Proposed | 1365000 | PRAIRIE POWER, INC. | Not Shared
B | B | West | WI | 25103 | 28225 | Voltage Device | 2030-12-31 | Madison Area |  |  | 138 |  | To reduce high voltages observed in the Madison area under light load scenarios. | WI |  |  | M1 - Proposed | 6500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | Central | IL | 22880 | 26919 | Substation | 2026-06-01 | Zion |  |  | 161 |  | Add high side interrupting Device on 161/69kV Transformer | IL |  |  | M1 - Proposed | 2000000 | AMEREN ILLINOIS | Not Shared
A | B | East | MI | 21968 | 26595 | Line New | 2027-06-01 | Delaney | Hemphill | 1 | 138 |  | Reterminate the existing Delaney-Helphill 138kV line into the new station configuration. | MI |  | 1.1 | M1 - Proposed | 1473000 | METC | Not Shared
A | B | Central | IN | 25332 | 28508 | Line Upgrade | 2028-12-31 | WVPA Pike 69kV Line Rebuild |  |  | 69 |  | WVPA Pike 69kV Line Rebuild - Rebuild 69kV line feeding Pike substation | IN | 7.9 |  | M1 - Proposed | 15000000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | East | MI | 25522 | 28744 | Substation | 2027-06-01 | Oakland |  |  | 138 |  | New station constructed as a four breaker ring bus configuration. All 138 kV breakers should be standard 3000 A, 40 kA breakers. Terminate 138 kV lines into new Oakland station | MI |  |  | M1 - Proposed | 6500000 | METC | Not Shared
A | B | Central | IN | 24274 | 28016 | Line New | 2027-12-01 | Reservoir | Royalton | 90 | 138 |  | A new 4.51 mile 138 kV transmission line between Reservoir and existing Royalton substation | IN |  | 4.51 | M1 - Proposed | 8400000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | WI | 50111 | 50180 | Substation | 2030-03-10 | Edmund |  |  | 345 |  | J1773 345 kV Interconnection Substation Interconnection Facilities | WI |  |  | M1 - Proposed | 1399000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 25429 | 28659 | Substation | 2027-12-01 | Liberty |  |  | 161 | 69 | Expand Liberty Substation to install a 161-69 kV, 125 MVA transformer, a new 161 kV terminal and new 69 kV bus. | IA |  |  | M1 - Proposed | 10000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | South | TX | 25484 | 28701 | Line Upgrade | 2025-12-31 | Mulitple |  |  | 500 | 69 | AM Renewal Project | TX |  |  | M1 - Proposed | 38300000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 50029 | 50052 | Substation | 2026-06-01 | SE Soteria |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | IL | 50044 | 50083 | Line Upgrade | 2026-12-01 | Hull | Marion |  | 138 |  | Rebuild the 7 mile Hull-Marion-1690 138 kV Transmission Line with T2 conductor rated at 2,000 amps Summer Emergency Conditions and 2 EA 72-Fiber OPGW shield wires. | IL |  |  | M1 - Proposed | 5500000 | AMEREN ILLINOIS | Not Shared
A | B | West | IA | 25222 | 28262 | Substation | 2028-09-01 | Rock Creek | Substation |  | 345 | 345 | Network upgrades required to install fiber at Rock Creek. | IA |  |  | M1 - Proposed | 121752 | ITC MIDWEST | Not Shared
A | B | East | MI | 25195 | 28322 | Line Upgrade | 2028-06-01 | MCV | Tittabawassee | 2 | 345 |  | Relocate a structure to accommodate 345 kV station expansion. | MI |  |  | M1 - Proposed | 1125000 | METC | Not Shared
A | B | South | MS | 25416 | 28733 | Substation | 2025-10-01 | Lucedale |  |  | 69 |  | In order to serve the member delivery points of North Lucedale and South Lucedale economically and reliably a new 69kV switching will be constructed at near Lucedale, MS. | MS |  |  | M1 - Proposed | 2860000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | West | MN | 25396 | 28592 | Line Upgrade | 2028-06-01 | Albertville | Black Lake Tap | 1 | 69 |  | Rebuild 12 miles of the Albertville to Black Lake tap line. | MN | 12 |  | M1 - Proposed | 17075410 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 24560 | 28028 | Line Upgrade | 2025-12-31 | Cobb | Meyer |  | 138 |  | Extend the Cobb - Meyer 138kV line to loop in the J1614 POI station. Install fiber path to station. | MI |  |  | M1 - Proposed | 4818125 | METC | Not Shared
A | B | Central | IL | 24921 | 28150 | Substation | 2026-06-01 | Steamboat |  |  | 138 |  | Prairie Power Incorporated (PPI) 138 kV delivery point substation to supply a new bulk distribution transformer at the PPI Ellisville tap on the Ameren Castro-Galesburg Monmouth Blvd-1427 138 kV line | IL |  |  | M1 - Proposed | 9700000 | AMEREN ILLINOIS | Not Shared
A | B | Central | IN | 25560 | 28792 | Line Upgrade | 2027-12-31 | MooresJct | EastMad |  | 69 |  | Rebuild 2.7 miles 69kV line | IN |  |  | M1 - Proposed | 4450000 | HOOSIER ENERGY | Not Shared
A | B | South | LA | 25480 | 28697 | Misc. | 2025-06-01 | Port Hudson |  |  | 230 | 138 | Redundant high speed relaying on 230-138 kV autos | LA |  |  | M1 - Proposed | 4400000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 25302 | 28357 | Substation | 2025-12-01 | Hills |  |  | 69 |  | Replace the Hills 69 kV breaker 514 with a breaker that has interrupting rating of 40kA. | IA |  |  | M1 - Proposed | 500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | Central | IN | 25393 | 28579 | Transformer | 2026-12-31 | Chrisney |  |  | 69 | 12 | Replacement of 69/12kV T1 transformer | IN |  |  | M1 - Proposed | 4000000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | West | ND | 24375 | 27847 | Line Upgrade | 2028-12-31 | Bison | Maple River |  | 345 |  | Maple River - Bison 345 KV | ND |  |  | M1 - Proposed | 400000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | West | IA | 50075 | 50115 | Line Upgrade | 2025-06-01 | Raun | Remsen | 1 | 345 |  | Replace line structures to increase line ratings on Raun-Remsen 345 kV line. | IA |  |  | M1 - Proposed | 700000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25381 | 28531 | Line New | 2027-12-19 | Long Siding |  |  | 69 |  | Replace Long Siding tap switch | MN |  |  | M1 - Proposed | 354937 | GREAT RIVER ENERGY | Not Shared
B | B | East | MI | 25249 | 50043 | Line Upgrade | 2028-06-01 | Stephens | Stephens |  | 230 | 230 | Relocate few spans of Northeast - Stephens 230kV line to accommodate substation work related to re-termination of Stephens TRF #304 345/230kV. | MI |  |  | M1 - Proposed | 960000 | ITC | Not Shared
A | B | West | MN | 25286 | 28429 | Line Upgrade | 2025-12-15 | Buffalo | Maple Lake | 1 | 69 |  | Rebuild 8.2 miles 69 kV from Buffalo - Maple Lake with new structures, new OPGW shield wire, and new conductor. | MN | 8.2 |  | M1 - Proposed | 6000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | MN | 25456 | 28718 | Substation | 2029-12-31 | Spring Creek |  |  | 161 | 69 | Replace Spring Creek transformer and upgrade substation. | MN |  |  | M1 - Proposed | 19992124 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 25295 | 28456 | Line Upgrade | 2023-09-30 | North Rochester | Prairie Island | 1 | 345 |  | Replace structures at 3 clearance limited span between North Rochester - Prairie Island. | MN |  |  | M1 - Proposed | 175000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25439 | 28682 | Line New | 2030-12-31 | Sub G | Sub K | 1 | 69 |  | Install two 69 kV line taps terminating at Sub G 69 kV line breakers. | IA |  |  | M1 - Proposed | 300000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | West | WI | 25002 | 28176 | Line Upgrade | 2028-08-01 | North Lake Geneva | Walworth | Y-41 | 69 |  | Rebuild of line Y-41 from North Lake Geneva SS to Walworth SS and installation of OPGW. | WI |  |  | M1 - Proposed | 14600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25141 | 28212 | Misc. | 2024-12-31 | Arrowhead 115kV |  |  | 115 |  | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Arrowhead 115kV buses. | MN |  |  | M1 - Proposed | 250000 | MINNESOTA POWER INC. | Not Shared
A | B | West | IA | 25206 | 28272 | Substation | 2026-12-31 | Lime Creek | Substation |  | 161 | 69 | Replacing both aging transformers with one new transformer of 150MVA will allow for the same loading on the system. The transformer will only be tied to the L2 bus on the 161kV side, but to both the J1 and the J2 bus on the 69kV side. This is a lower cost option than rebuilding the 161kV into a breaker and a half or adding back in two transformers. | IA |  |  | M1 - Proposed | 5690194 | ITC MIDWEST | Not Shared
A | B | East | MI | 25364 | 28496 | Substation | 2027-12-31 | ITCT Facilities |  |  | 345 | 120 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2027 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million a separate project will be submitted for approval. | MI |  |  | M1 - Proposed | 2500000 | ITC | Not Shared
B | B | West | WI | 25392 | 28554 | Line Upgrade | 2030-12-31 | Forest Junction | Arcadian | 971L51 and LCYP31 | 345 |  | Uprate Forest Junction – Cypress – Arcadian 345kV 971L51 and LCYP31 lines. | WI |  |  | M1 - Proposed | 11600000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 24538 | 28004 | Substation | 2025-04-01 | Lukesport |  |  | 138 |  | Install line entrance structure and disconnect as TOIF. Install position WM14 at Lukesport to interconnect J1635 generator. | MI |  |  | M1 - Proposed | 0 | METC | Not Shared
A | B | West | IA | 25211 | 28343 | Line New | 2026-12-31 | Blanket for Customer Interconnections under $1 million for 2026 |  |  | 345 | 69 | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA |  |  | M1 - Proposed | 3750000 | ITC MIDWEST | Not Shared
A | B | West | MN | 25379 | 28568 | Substation | 2026-12-31 | Wabasha |  |  | 69 |  | Rebuild Wabasha substation at a nearby location due to flooding concerns. | MN |  |  | M1 - Proposed | 3000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | West | IA | 25425 | 28624 | Substation | 2027-12-01 | Metro East |  |  | 161 |  | Install 161 kV line breakers and relaying | IA |  |  | M1 - Proposed | 3000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 24516 | 27994 | Substation | 2026-12-31 | Beecher | Pixley |  | 138 |  | Construct new breaker and a half 138kV station Rouget in a ring bus configuration with three, 138kV, 40kA minimum capability breakers and associated disconnects. | MI |  |  | M1 - Proposed | 7887399 | METC | Not Shared
A | B | West | IA | 25412 | 28760 | Line Upgrade | 2029-12-01 | Northgate | Sub Y IC | 1 | 161 |  | Rebuild Northgate-Sub Y 161 kV line | IA |  |  | M1 - Proposed | 4000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | East | MI | 50038 | 50077 | Transformer | 2026-08-19 | Orr Road |  |  | 345 | 138 | Expand Orr Road to the North, East, and South to install two (2) additional 138 kV breakers to accommodate the METC’s 345/138 kV transformer at Orr Road and HSC – Tittabawassee 1 138 kV, HSC – Murphy 138 kV, and HSC – Orr Road 138 kV lines re-routing, and CE’s Husky transformers. Install a new 345/138 kV transformer and terminate the low side at new created 138 kV “WM4” position. The new Orr Road transformer will be similar to existing Murphy 345/138 kV transformer #4 with at least 623 MVA (2608 Amps) summer emergency rated transformer. Also install a new 199 345 kV breaker on high side of Orr Road 345/138 kV transformer. Connect OPGW at Orr Road station. | MI |  |  | M1 - Proposed | 19746000 | METC | Not Shared
A | B | West | MN | 50002 | 50010 | Substation | 2026-05-01 | Eden Prairie |  |  | 115 |  | Replace overstressed breakers Eden Prairie TR1 and TR3 that are end of life with breakers of larger interrupting capacity. | MN |  |  | M1 - Proposed | 160000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | South | LA | 25313 | 28394 | Substation | 2025-09-01 | Daspit |  |  | 138 |  | Build a new Daspit substation tapped into the Hopkins to Morbihan 138 kV line. This project is needed for J1599 generator. | LA |  |  | M1 - Proposed | 16236000 | CLECO POWER LLC | Not Shared
A | B | Central | MO | 25284 | 28411 | Line Upgrade | 2028-12-31 | Salem Bulk | Seminary | T10 | 69 |  | Rebuild 29.54 miles of 69kV between Salem Bulk and Seminary | MO | 29.54 |  | M1 - Proposed | 60000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
B | B | West | WI | 25259 | 28445 | Line New | 2028-09-30 | Grassland | Loyal | 1 | 69 |  | Build a new 4.3 mile line from Grassland substation to Loyal tap and retire section which ties to DPC line | WI |  | 4.3 | M1 - Proposed | 2000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | East | MI | 24443 | 27934 | Line Upgrade | 2026-05-01 | Argenta | Tallmadge |  | 345 |  | Extend the Argenta-Tallmadge 345kV line to loop in J1663 POI station. | MI |  |  | M1 - Proposed | 1175000 | METC | Not Shared
A | B | East | MI | 50151 | 50250 | Misc. | 2027-09-01 | Plaster Creek |  |  | 138 |  | Install a rack mounted patch panel for termination of new fiber cable from the Plaster Creek – East Paris Line. Install and terminate new underground cable from the patch panel to splice closure on the Plaster Creek – East Paris Line. | MI |  |  | M1 - Proposed | 55000 | METC | Not Shared
A | B | West | IA | 25200 | 28248 | Substation | 2026-10-01 | Calamus East | Substation |  | 161 | 161 | A 161 kV straight bus expansion at the Calamus East station will be constructed for the interconnection of project J1190. | IA |  |  | M1 - Proposed | 155146 | ITC MIDWEST | Not Shared
A | B | South | AR | 50059 | 50097 | Substation | 2026-10-01 | Kinder |  |  | 161 |  | A new 161kV switching station will be constructed on the Moreland - St. Vincent 161kV line section to interconnect the J1558 200 MW solar project. Line relaying panels will be upgraded at ANO and Pleasant Hill 161kV stations. | AR |  |  | M1 - Proposed | 14012000 | ENTERGY ARKANSAS, LLC | Not Shared
A | B | Central | IN | 25355 | 28543 | Substation | 2025-05-21 | Northwest |  |  | 138 |  | Replace 4 138 kV breakers. #1, #4, #21, and #22. | IN |  |  | M1 - Proposed | 3600000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | IA | 25429 | 28660 | Line New | 2027-12-01 | Liberty | Terra | 1 | 69 |  | Construct new 69 kV line from Liberty Substation to new Terra Substation | IA |  | 0.6 | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
B | B | West | WI | 24919 | 28140 | Line Upgrade | 2027-06-01 | Mill Road | Granville |  | 345 | 138 | - Construct new 345/138 kV Mill Road SS - Rebuild Mill Road SS – Granville SS section as 345 kV double circuit - Butler SS 138 kV reconfiguration and install series reactor - Granville SS 345 kV upgrades - Construct new Mill Road SS – Tamarack SS – Bulter SS 138 kV line | WI |  |  | M1 - Proposed | 300000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | IA | 50106 | 50157 | Line New | 2026-03-31 | Big Cedar | Morgan Valley |  | 345 | 345 | Line taps from existing Beverly - Morgan Valley line to new Big Cedar Switching Station | IA |  | 0.5 | M2 - Appendix A Approved | 5736250 | ITC MIDWEST | Not Shared
A | B | South | MS | 25486 | 28702 | Substation | 2025-12-31 | Grand Gulf |  |  | 500 | 115 | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. | MS |  |  | M1 - Proposed | 47800000 | ENTERGY SERVICES, LLC. | Not Shared
B | B | East | MI | 18040 | 24820 | Line Upgrade | 2028-06-01 | Cottage Grove | Karn |  | 138 |  | Completely remove the sag limit on the Cottage Grove - Karn 138kV circuit. | MI |  |  | M1 - Proposed | 500000 | METC | Not Shared
B | B | West | MN | 25371 | 28520 | Misc. | 2025-06-01 | Lake Yankton |  |  | 115 |  | Retire Lake Yankton SVC. | MN |  |  | M1 - Proposed | 700000 | NORTHERN STATES POWER COMPANY | Not Shared
B | B | East | MI | 25400 | 50140 | Line Upgrade | 2027-12-31 | Collins | SUPERIOR |  | 120 |  | Move Collins – Superior 120kV line lattice structure #700 within the substation to make space for the new equipment. | MI |  |  | M1 - Proposed | 806250 | ITC | Not Shared
A | B | West | IA | 25222 | 28263 | Line Upgrade | 2028-09-01 | Bryant | Rock Creek | 1 | 345 | 345 | Install the dual OPGW on the Bryant to Rock Creek 345 kV line. | IA |  |  | M1 - Proposed | 1952000 | ITC MIDWEST | Not Shared
A | B | West | WI | 25162 | 28226 | Misc. | 2027-12-31 | Milwaukee Metro Area |  |  | 0 |  | Installation of 8+ miles of ATC Owned Underground (UG) Fiber to replace leased UG Fiber with Midwest Fiber Networks in Milwaukee Metro Area. | WI |  |  | M1 - Proposed | 6000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 25209 | 28307 | Line Upgrade | 2027-02-01 | Battle Creek | Oneida |  | 345 |  | Cut the Battle Creek-Oneida 345 kV circuit into Oxby station using a conductor rated at least that of 2-1431 ACSR. | MI |  |  | M1 - Proposed | 2263750 | METC | Not Shared
B | B | West | MN | 25398 | 28604 | Substation | 2027-06-01 | King Solar Collector |  |  | 230 |  | Two collector substations for radial solar generation | MN |  |  | M1 - Proposed | 35000000 | NORTHERN STATES POWER COMPANY | Not Shared
A | B | Central | IN | 50096 | 50147 | Misc. | 2026-09-30 | Stout CT |  |  | 138 |  | Relay packages for Stout CT bus section | IN |  |  | M1 - Proposed | 150000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | West | ND | 24394 | 27848 | Line Upgrade | 2024-12-31 | Maple River | Kragnes |  | 69 |  | Maple River - Kragnes 69 kV | ND |  |  | M1 - Proposed | 2000000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | East | MI | 25522 | 28745 | Voltage Device | 2027-06-01 | Oakland |  |  | 138 |  | Replace existing 50 MVAR with two (2) 25 MVAR cap banks on separate buses with new synchronous breakers. | MI |  |  | M1 - Proposed | 1500000 | METC | Not Shared
A | B | Central | IL | 25041 | 28202 | Substation | 2026-07-01 | Virden |  |  | 138 |  | This project will install a new 138 kV line position to serve as the Point of Interconnection for Virden Wind, LLC under GIA J1408, within the new 3-position ring bus named Virden. | IL |  |  | M1 - Proposed | 8000000 | AMEREN ILLINOIS | Not Shared
A | B | South | LA | 25482 | 28698 | Line Upgrade | 2025-12-31 | Multiple |  |  | 500 | 69 | AM Renewal | LA |  |  | M1 - Proposed | 87900000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | IN | 25521 | 28734 | Misc. | 2025-08-15 | Walton | J992 POI |  | 230 |  | J992 Walton 230kV - 200MW Appleseed Solar, LLC (NextERA) Gen Intercon - Expand Walton 230 kV ring bus and add line terminal; new 23042 line terminal to be inserted between 23023 (to Logansport S.) and 23020 (to Webster St) | IN |  |  | M1 - Proposed | 7327980 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | Central | IN | 25359 | 28580 | Line Upgrade | 2028-12-31 | Louis Allis |  |  | 69 |  | Replacing several switches and distribution breakers | IN |  |  | M1 - Proposed | 2300000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A | B | Central | IN | 25560 | 28793 | Line Upgrade | 2027-12-31 | Wilbur Jct | ToytJct |  | 69 |  | Rebuild 3 miles of 69kV line | IN | 3 |  | M1 - Proposed | 5000000 | HOOSIER ENERGY | Not Shared
A | B | East | MI | 25522 | 50141 | Misc. | 2027-06-01 | Halsey |  | 1 | 138 |  | Replace relay panel at Halsey | MI |  |  | M1 - Proposed | 294000 | METC | Not Shared
A | B | East | MI | 24560 | 28029 | Misc. | 2025-05-15 | Cobb |  |  | 138 |  | Upgrade position 688 relaying at Cobb 138kV station. | MI |  |  | M1 - Proposed | 94973 | METC | Not Shared
A | B | South | AR | 50099 | 50162 | Transformer | 2025-10-01 | Lewisville West |  |  | 115 |  | Add 2nd autotransformer at Lewisville West substation. New transformer to be rated for 115/69 kV, 100 MVA. | AR |  |  | M1 - Proposed | 4500000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | B | South | TX | 25436 | 28683 | Substation | 2026-06-01 | Bobville |  |  | 230 | 138 | Bobville 230-138 kV Station | TX |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | B | West | IA | 25241 | 28273 | Substation | 2026-12-31 | Newton 8th Street | Substation |  | 161 |  | Replace the existing relaying and SCADA at Leon by ITC installing a new ITC owned control building. IPL owns and maintains this building. Separating the buildings by owner lines up with the current substation standards. | IA |  |  | M1 - Proposed | 2655119 | ITC MIDWEST | Not Shared
A | B | Central | IN | 50095 | 50146 | Misc. | 2026-09-30 | Stout CT |  |  | 138 |  | Relay packages for CT 5 and its GSU | IN |  |  | M1 - Proposed | 150000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | B | Central | IN | 25303 | 28358 | Substation | 2025-10-01 | Petersburg/Ratts 161 kV |  |  | 161 |  | Construct Transmission Owner’s Interconnection Facilities at Petersburg Substation. | IN |  |  | M1 - Proposed | 3636500 | HOOSIER ENERGY | Not Shared
A | B | Central | IN | 25333 | 28509 | Substation | 2026-12-31 | Westfield 156th St 69/12kV Sub |  |  | 69 | 12 | Westfield 156th St 69/12kV Sub (new sub) - Loop 69142 line through Sub; transfer 69155 wire to 5 new poles | IN | 0.25 | 0.5 | M1 - Proposed | 3442000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | B | West | MN | 25142 | 28213 | Misc. | 2024-12-31 | Forbes |  |  | 115 |  | Add redundancy or monitoring to the single point of failures to mitigate P5 contingences associated with the Forbes 115kV buses. | MN |  |  | M1 - Proposed | 250000 | MINNESOTA POWER INC. | Not Shared
A | B | West | ND | 50007 | 50018 | Line Upgrade | 2025-11-01 | Rugby 41.6 kV | Bottineau 41.6 kV | 1 | 42 |  | Rebuild and relocate 2.5 miles of 41.6 kV line between Rugby 41.6 kV and Bottineau 41.6 kV near Omemee. | ND | 2.5 |  | M1 - Proposed | 800000 | OTTER TAIL POWER COMPANY | Not Shared
A | B | East | MI | 25365 | 28497 | Misc. | 2024-12-31 | ITCT Facilities |  |  | 345 | 120 | Relocation portions of transmission lines located in public right of way at the government entities mandate. | MI |  |  | M1 - Proposed | 2500000 | ITC | Not Shared
A | B | West | MN | 25374 | 28555 | Line Upgrade | 2025-11-17 | Arbo Switch | Gunn | 1 | 69 |  | Rebuild from 1.1 miles of the line from Arbo Switch to just south of Gunn substation. | MN | 1.1 |  | M1 - Proposed | 949547 | GREAT RIVER ENERGY | Not Shared
A | B | West | MN | 25396 | 28593 | Line Upgrade | 2027-06-01 | Albertville | Otsego | 1 | 69 |  | Rebuild 8 miles of the Albertville to the double circuit EMX line east of the Otsego substation. | MN | 8 |  | M1 - Proposed | 14820167 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 25198 | 50238 | Line Upgrade | 2028-06-01 | Port Calcite | Rockport |  | 138 |  | Redirect line from Rockport into the new station utilizing 954 ACSR Conductor. | MI |  | 1.5 | M1 - Proposed | 580000 | METC | Not Shared
A | B | East | MI | 25198 | 28344 | Substation | 2028-06-01 | Port Calcite |  |  | 138 |  | METC: Rebuild Port Calcite into a four (4) position ring bus configuration that can be converted to Breaker and a half in the future. Arrange the four breaker ring bus so that the positions alternate between transformers and lines. All new 138 kV breakers should be standard 3000 A 40 kA breakers. The new substation is located to the Northwest of existing station. All new equipment should have a minimum summer emergency rating of 364 MVA. CE: Install circuit switcher or high side breaker on CE Transformer 1 & 2. | MI |  |  | M1 - Proposed | 8100000 | METC | Not Shared
A | B | South | LA | 50139 | 50219 | Substation | 2028-06-30 | Moss |  |  | 69 |  | Transmission Owner Interconnection Facilities will consist of a new 69kV rated 4” aluminum IPS bus, 69kV gas circuit breaker, bus support structures, 69kV center break disconnect switches, and incoming transmission line single bay dead end. A revenue accuracy metering panel with power quality monitor will be installed. A line protection panel and breaker control panel will also be installed. | LA |  |  | M1 - Proposed | 993000 | LAFAYETTE UTILITIES SYSTEM | Not Shared
A | B | West | MN | 24413 | 27842 | Line Upgrade | 2025-02-28 | Moranville | Lund |  | 230 |  | Moranville - Lund 230 KV | MN |  |  | M1 - Proposed | 360000 | MINNKOTA POWER COOPERATIVE, INC | Not Shared
A | B | West | IA | 25460 | 28625 | Substation | 2027-06-01 | Southridge |  |  | 161 |  | Construct new 161-13 kV substation | IA |  |  | M1 - Proposed | 4000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | B | West | MN | 25422 | 28571 | Substation | 2026-06-30 | Airport Substation |  |  | 69 |  | Add 3 breakers to Airport substation. | MN |  |  | M1 - Proposed | 5692565 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 24556 | 28017 | Substation | 2026-12-31 | Oxby |  |  | 345 |  | Construct J1586 POI station as a breaker and half 345kV station with three 50kA breakers. | MI |  |  | M1 - Proposed | 12667183 | METC | Not Shared
A | B | West | MN | 25337 | 28532 | Line Upgrade | 2027-12-01 | Meadowbrook | Side Lake | 1 | 69 |  | Rebuild Meadowbrook to Side Lake | MN | 15 |  | M1 - Proposed | 12124891 | GREAT RIVER ENERGY | Not Shared
A | B | East | MI | 25223 | 50265 | Substation | 2027-06-11 | Lark |  |  | 120 |  | Install FOC jumpers | MI |  |  | M1 - Proposed | 25506 | ITC | Not Shared
A | B | South | MS | 25419 | 28761 | Line New | 2028-11-01 | Hermanville GOAB | Hermanville |  | 115 |  | In order to serve the member delivery point, tap Utica Loop line with a 115kV Goab and construct a new line to the delivery point. | MS |  |  | M1 - Proposed | 500000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | Central | IL | 22951 | 26921 | Substation | 2025-12-01 | Rantoul |  |  | 138 |  | Reconfigure 138kV into ring bus | IL |  |  | M1 - Proposed | 7100000 | AMEREN ILLINOIS | Not Shared