## MTEP24 Appendix A-3
MTEP24 Appendix A-3 Active Projects - Previously approved projects not yet in service (as of 11-1-2024)
Target MTEP Cycle | Planning Region | MTEP Project ID | Project Name | Project Description | State(s) | Submitting TO | Project Type | Other Type | Expected ISD | Max kV | Planning Status | Current Cost
MTEP10 | West | 2577 | Columbus (CE) 69 kV Substation | Columbus (previously Elmcrest) (CE) 69 kV Substation | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2025-08-29 | 69 | M2 - Appendix A Approved | 1000065
MTEP10 | West | 2579 | Foster Lake (WH) 69 kV Substation | Foster Lake (WH) 69 kV Substation | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-11-01 | 69 | M2 - Appendix A Approved | 533240
MTEP10 | West | 3048 | Jefferson Co-Perlee 69kV Rebuild | Rebuild the Jefferson Co-Perlee 69kV line section. | IA | ITC MIDWEST | Other | Age and Condition | 2027-07-21 | 69 | M2 - Appendix A Approved | 2700000
MTEP10 | West | 3053 | Keokuk Hydro-Carbide 69kV Dbl Ckt | Build a new 69kV circuit from Keokuk Hydro-Carbide. | IA | ITC MIDWEST | Other | Local Reliability | 2024-11-29 | 69 | M2 - Appendix A Approved | 20062760
MTEP10 | West | 3057 | West Branch 34kV Load Shift Projects | Construct 69kV taps for the Moscow & New Liberty dist. Subs | IA | ITC MIDWEST | Other | Local Reliability | 2027-12-28 | 69 | M2 - Appendix A Approved | 1206000
MTEP10 | West | 3092 | Webb Lake 69KV line | Rebuild 34.5KV line to Webb Lake at 69KV with horizontal post construction and #4/0 ACSR | WI | NORTHWESTERN WISCONSIN ELECTRIC CO. | Other | Age and Condition | 2026-06-01 | 69 | M2 - Appendix A Approved | 650000
MTEP11 | West | 3127 | Proposed MVP Portfolio 1: N LaCrosse-N Madison-Cardinal-Hickory Creek 345 kV | Construct N LaCrosse-N Madison-Cardinal 345 kV & Hickory Creek-Cardinal 345 kV line. | IA; WI | AMERICAN TRANSMISSION COMPANY | MVP |  | 2024-12-31 | 345 | M3 - Under Construction | 1033927001
MTEP11 | East | 3285 | Shoal 120kV Capacitor | 33.3 Mvar Capacitor at Shoal 120kV | MI | ITC | BRP |  | 2024-10-24 | 120 | M3 - Under Construction | 9499859
MTEP11 | East | 3335 | Burnip Transmission Station Upgrade | Upgrade to replace outdated equipment. Bus, breakers, relays, and other equipment as necessary. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2024-12-31 | 69 | M2 - Appendix A Approved | 800000
MTEP12 | West | 3644 | Knoxville to Lucas County 69 kV Rebuild | Rebuild 10.6 miles of old line to new T2-4/0 ASCR. | IA | ITC MIDWEST | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 3750000
MTEP12 | West | 3645 | Triboji 6750 (Oleans Tap) 69 kV Rebuild | Rebuild ~9.5 miles of old line to new T2-4/0 ASCR. | IA | ITC MIDWEST | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 3350000
MTEP12 | West | 3647 | Eastern Iowa Project Rebuilds | Rebuild the 34.5 kV line sections to 69 kV construction and operate at 34.5 kV until conversion. | IA | ITC MIDWEST | Other | Age and Condition | 2029-12-18 | 34 | M2 - Appendix A Approved | 43838066
MTEP14 | Central | 4415 | Veedersburg West 230-69kv Bk 2 addition | Veedersburg West: Add 75MVA 230/69 Bk 2 with LTC at Veedersburg West sub; add breaker to 69kV ring bus and tie in new bank; convert 230kV bus into 4-breaker ring | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-11-19 | 230 | M3 - Under Construction | 15262408
MTEP16 | West | 10022 | PCI-Mt.Vernon-Lisbon-76th AVE Conv | ITC will be converting the PCI to Mt. Vernon to Lisbon North to 76th Ave. substation from 34.5 kV operation to 69 kV operation. To accommodate the conversion, a 69 kV breaker and associated equipment will be installed at the PCI substation, two (2) 69 kV breakers and associated equipment will be installed at the Lisbon North substation, approximately 0.6 mile of new 69 kV transmission line will be constructed to complete the PCI to 76th Ave circuit and OPGW will need to be installed. | IA | ITC MIDWEST | Other | Age and Condition | 2026-12-30 | 69 | M2 - Appendix A Approved | 5793932
MTEP16 | West | 10076 | West St Cloud – Millwood Tap Rebuild | Rebuild 24 miles of line from West St. Cloud to Millwood Tap. This new line will be built using 477 ACSR conductor. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-05-15 | 69 | M2 - Appendix A Approved | 10400000
MTEP16 | South | 8821 | Northeast to Peck | 69kv line connecting Northeast station to Gillman/Peck stations. This is part 2 of a 2 part project. The first project was a new 230-69 autotransformer located at Pont Des Mouton station and a new 69kv line from Pont Des Mouton to a new Northeast station. Part 2 of this project will be a 69kv transmission line from the Northeast station to Gilman/Peck stations. | LA | LAFAYETTE UTILITIES SYSTEM | Other | Local Reliability | 2026-08-31 | 69 | M2 - Appendix A Approved | 3360000
MTEP16 | West | 9666 | Emerald Isle-Beverly 34 to 69 kV Conv | Convert 34.5 kV system between Beverly and Emeral Isle to 69 kV operation. | IA | ITC MIDWEST | Other | Age and Condition | 2028-02-28 | 69 | M2 - Appendix A Approved | 10705088
MTEP16 | West | 9668 | Cedar Rapids-North Liberty area-Hills Upgrades | Add a new Hills area 345/161kV source and upgrade the 161 and 69kV systems in the North Liberty area. This includes a new North Liberty 161/69kV substation also. | IA | ITC MIDWEST | BRP |  | 2028-12-31 | 345 | M2 - Appendix A Approved | 70463392
MTEP16 | Central | 9897 | River Ridge Gateway 138-12kV New Sub. | River Ridge Gateway 138-12kV Sub. to be inserted in the 13857 ckt. between Clark Maritime and HE Northport | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-06-02 | 138 | M2 - Appendix A Approved | 1236000
MTEP16 | West | 9907 | Summit to Dovray 69 kV Rebuild | Phase 1: Rebuild ~12.9 miles of old line to new T2-4/0 ACSR | MN | ITC MIDWEST | Other | Age and Condition | 2026-02-02 | 69 | M2 - Appendix A Approved | 12508752
MTEP16 | West | 9908 | Dovray to Fulda 69 kV Rebuild | Rebuild ~14.5 miles of old line to new T2-4/0 ACSR | MN | ITC MIDWEST | Other | Age and Condition | 2025-04-01 | 69 | M2 - Appendix A Approved | 9410124
MTEP16 | West | 9910 | Fulda to Heron Lake 69 kV Rebuild | Rebuild ~20.14 miles of old line to new T2-4/0 ACSR | MN | ITC MIDWEST | Other | Age and Condition | 2028-12-31 | 69 | M2 - Appendix A Approved | 14976652
MTEP16 | East | 9915 | Oden Relay Upgrade | Upgrade the relaying on the Oden-Emmet terminal | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2024-12-31 | 69 | M2 - Appendix A Approved | 2600000
MTEP16 | East | 9994 | Custer - Monroe 120 kV Line Rebuild | Rebuild the entire ~3.1 mile Custer – Monroe 120 kV line to increase its summer emergency rating. Relocate approximately 1.8 miles of 120 kV circuit at the direction of the city of Monroe. The city has asked ITC to move the structures off the River Raisin National Battlefield to accommodate work they are doing on the battlefield and the visitor center. Replace station equipment at the Custer and Monroe substations. | MI | ITC | BRP |  | 2025-12-31 | 120 | M3 - Under Construction | 37501000
MTEP17 | Central | 11848 | Perry Twp 69 kV Loop/Substation Modification | 69kV line Y32 Loop for Perry Twp Sub and Perry Twp Sub Modifications | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Local Reliability | 2025-09-01 | 69 | M2 - Appendix A Approved | 6750000
MTEP17 | Central | 11957 | Wabash River Station new industrial load | Wabash River Station new industrial load @ 50MW on the 230kV bus section #2 or #3 | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-04-24 | 230 | M2 - Appendix A Approved | 5954443
MTEP17 | West | 11964 | Oak Hill-Marion 34.5 to 69kV Conversion | Convert 34.5 kV system between Oak Hill and Marion to 69 kV operation | IA | ITC MIDWEST | Other | Age and Condition | 2024-11-28 | 69 | M2 - Appendix A Approved | 4721202
MTEP17 | West | 11965 | Marshalltown-Grand Jct. 34.5 to 69 kV Conversion | Convert 34.5 kV system in Marshalltown - Grand Junction area to 69 kV operation. | IA | ITC MIDWEST | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 21875845
MTEP17 | West | 11977 | Anita-Grand Jct Area 34.5 to 69 kV Conversions | Convert the 34.5 kV system between Anita and Grand Junction to 69 kV operation, with associated line conversions, breaker stations and transformers. | IA | ITC MIDWEST | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 21602220
MTEP17 | Central | 11999 | Attica 69 to Attica 230 69kV Rebuild | Attica 69 to Harrison Stl Jct to Attica 230 69kV Rebuild - Rebuild 6936 ckt - 4.1 miles with 477acsr and steel poles; also rebuild 1.27 miles of 69121 where it is double circuited | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2026-05-27 | 69 | M2 - Appendix A Approved | 5601000
MTEP17 | Central | 12005 | Bloomington Rogers St. Substation Upgrades | Bloomington Rogers St. Substation Upgrades: 5-phase project to replace and add distribution/sub-transmission transformers, expand sub site, establish a 138kV breaker-and-a-half bus configuration, and establish a 69kV ring bus. | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-01-31 | 138 | M3 - Under Construction | 34248160
MTEP17 | South | 12063 | Big Creek 115kV: Construct new substation | Construct a new 115kV substation called Big Creek (previously Sheridan East) with two 115kV breakers, a 40 MVA load transformer, and four feeder breakers. | AR | ENTERGY ARKANSAS, LLC | Other | Local Reliability | 2024-12-01 | 115 | M3 - Under Construction | 5446780
MTEP17 | South | 12136 | Cullichia 230 kV: New substation | Construct a new 230 kV substation to replace the existing Arabi substation. Station name is changed to Cullichia. | LA | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2027-05-12 | 230 | M3 - Under Construction | 22738800
MTEP17 | West | 12185 | Rebuild 138 KV Butte des Morts - Sunset Point | Rebuild 138 KV Butte des Morts- Neevin - Woodenshoe - Mears Corners - Sunset Point. Line 43021, Line 80952, Line A-79, Line MCRG21 | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2024-10-30 | 138 | M3 - Under Construction | 25593395
MTEP17 | East | 12216 | Cadillac to Hersey OPGW | Replace existing shield wire with OPGW on the Cadillac to Hersey line section. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2024-12-31 | 138 | M2 - Appendix A Approved | 2300000
MTEP17 | West | 12344 | Kalona-Iowa Junction 34.5 to 69kV Conversion | Convert the 34.5kV system between Kalona and Iowa Junction to 69kV operation, with associated line conversion & breaker stations. | IA | ITC MIDWEST | Other | Age and Condition | 2026-12-31 | 69 | M2 - Appendix A Approved | 24261884
MTEP17 | West | 12403 | Eastern Iowa Wyoming Area 69kV Conversions | Eastern Iowa Study Wyoming Area Conversion Projects: Upgrade the Wyoming Substation - add 69kV terminals. Wyoming to Monticello Industrial line conversion. Wyoming to Bennett conversion. Wyoming to Maquoketa conversion. Wyoming to Wyoming REC conversion. Wyoming to Dixon conversion. | IA | ITC MIDWEST | Other | Age and Condition | 2026-12-31 | 161 | M2 - Appendix A Approved | 25968201
MTEP17 | East | 12443 | Nitro Interconnection | Construct the new 120 kV Nitro station. Station will be two disconnected busses. Station will be fed by taping the Coventry - Baltic 120kV line and the Hager - Hines 120kV line | MI | ITC | Other | Local Reliability | 2025-07-30 | 120 | M3 - Under Construction | 5365000
MTEP17 | Central | 12845 | New Tice 69/12.47 kV distribution substation | 1) New Tice 69/12.47 kV substation 2) New Fancy Creek-Tice 69 kV line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2029-12-31 | 69 | M2 - Appendix A Approved | 8870000
MTEP17 | East | 13574 | 138kV Voltage Conversion Alternate | Convert the following lines already constructed 138kV design • Lake County to Plains Junction (constructed to 138kV) • Redwood to Hart (constructed to 138kV) • Plains Junction to Hersey (constructed to 138kV) • Redwood to Lemon Junction (constructed to 138kV) Construct and convert the following MTEP Target A projects in MTEP17 due to condition • White Cloud to Rogers (MTEP Project 9903, Target A MTEP17) • Lemon Junction to Silver Lake (MTEP Project 12224, Target A MTEP17) Construct/upgrade the following lines not currently in MTEP • Replace Conductor only on Rogers to Lemon Junction (10.29mi) • Rebuild Plains Junction to Hart (22.09mi) • Add conductor on Hersey to Lincoln, designed for double circuit, continue to supply 69kV service to Lincoln substation (3.29mi) • Rebuild Hersey to White Cloud (25.37 mi) • Rebuild Paris Junction to Paris (1.26 mi) • Rebuild Brohman Junction to Brohman (1.34 mi) • Rebuild White Cloud to Casnovia (22.85 mi) • Rebuild Newaygo to Brooks (3.22 mi) • Rebuild Casnovia to Sternberg (19.39 mi) • Rebuild Lake County to Pere Marquette (18.25 mi) Construct the following new stations to replace existing 69kV stations: • Plains Junction (138kV station) • White Cloud (138kV station) • Rogers (138kV single breaker station) • Lemon Junction (138kV single breaker station) • Casnovia (138/69kV station Upgrades to the following stations: • Hersey (add 138/69kV transformer, utilize existing bus work to the extent practical) • Lake County (relocate 69kV line to 138kV bus, available position on 138kV bus currently installed) | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2024-12-31 | 138 | M2 - Appendix A Approved | 72168926
MTEP17 | Central | 1900 | Avon Industrial Park 138-12kV new dist sub | Avon Industrial Park - Construct 138-12kV - 22.4 MVA sub in the All Points Industrial Park and 2.5 miles of 138kV line | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-11-24 | 138 | M2 - Appendix A Approved | 3571000
MTEP17 | South | 8203 | Fred SW (Ivanhoe) - Fred 138kV | Construct a new Fred switching station (Ivanhoe) on Dogwood-Warren 138 kV line, a new 138 kV Fred substation, and a new 138 kV line from the Fred switching station (Ivanhoe) to the new Fred substation. | TX | EAST TEXAS ELECTRIC COOPERATIVE, INC. | Other | Local Reliability | 2025-07-31 | 138 | M2 - Appendix A Approved | 24200000
MTEP17 | South | 9781 | Jennings to Lawtag 69 kV L-13/L-19 and L-14: Rebuild lines | Reconductor both Jennings to Lawtag 69 kV lines (L-13, L-14). | LA | ENTERGY SERVICES, LLC. | BRP |  | 2024-12-31 | 69 | M3 - Under Construction | 19400001
MTEP18 | West | 12137 | Hwy V - Structure 123 69 kV (Z-26), Rebuild | The new proposed scope is to rebuild 5.5 miles of Z-26 from structure 123 to Hwy V. The rebuilt line will be monopole structures with conductor OPGW using the standard enhanced 69 kV design. If required in the future, this portion of the line could be converted to 138 kV with minimal upgrades. We will need new easements for approximately half of the line rebuild, and these easements will allow us to convert to 138kV in the future. The existing line from Oak St to structure 123 will remain in place. This section is a mix of wood and steel structures with 4/0 ACSR conductor with a range of age and conditions that we would maintain and monitor the condition of for the next 10-15 years. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-07-06 | 69 | M2 - Appendix A Approved | 18200000
MTEP18 | East | 12199 | Upgrade Grand Traverse Station | Upgrade the Grand Traverse Station, including the protection and control system, switches, bus and circuit breakers. Note: The project cost will be split 50/50 between TCLP and Wolverine, the cost for this MTEP project is the total cost of the project. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2024-12-31 | 138 | M2 - Appendix A Approved | 2150000
MTEP18 | South | 12663 | Palestine 161kV: Construct new substation | Construct the Palestine 161/13.8kV substation near Highway 70 on the Brinkley East to Moses 161kV T-Line between structures #84 - #92. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2030-12-15 | 161 | M2 - Appendix A Approved | 5991167
MTEP18 | South | 12664 | Ranchette 161kV: Construct new substation | Construct a new substation on Highway 64 east of Conway, AR. Install one 40 MVA 161/13.8kV LTC and four feeder breaker bays. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2029-12-01 | 161 | M2 - Appendix A Approved | 7433784
MTEP18 | East | 13327 | METC Beecher Control Relocation Project | Relocate the existing Saginaw River control center and its contents to the Beecher station following the retirement of Saginaw River. The Saginaw River control center was installed in 2013 and is still in good condition with many more serviceable years. The equipment from the Saginaw River control center that will be reused at Beecher includes the AC/DC systems and the 138kV Bus relaying panels. The battery from the Saginaw River Control house will be scrapped and be replaced with a new battery. The Beecher 677 and 977 panels will be moved over to the relocated Saginaw River control house. A new comm cabinet with a Nokia SAR-8 and Cisco routers and switches will be installed. Re-termination the fiber on the Tangent/Raisin on the Leoni line and the fiber on the Morocco line into the relocated enclosure. The 677 and 977 bypass switches will be removed. The existing SSVTs at Saginaw River will be relocated to Beecher and used to supply power to the new control center. Consumers Energy will be required to make CT and relay input/output modifications to accommodate the new METC 138kV Bus relay scheme. Reusing the existing Saginaw River control center allows METC to improve the reliability, human performance, and safety concerns at Beecher while saving on costs associated with a new control center. Utilizing a recently installed control center ensures many future years of reliable service at a cost much lower than a new control center. | MI | METC | Other | Local Needs | 2026-12-31 | 138 | M2 - Appendix A Approved | 1020000
MTEP18 | East | 13576 | Airport to Hillman Rebuild | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 5500000
MTEP18 | East | 13577 | Rebuild Atlanta to Hillman | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 13500000
MTEP18 | East | 13578 | Rebuild Gun Lake Junction to Otsego | Rebuild and upgrade 69 kV line to 138 kV design, 336ACSR conductor and OPGW | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2024-12-31 | 69 | M2 - Appendix A Approved | 6400000
MTEP18 | East | 13579 | South Boardman Station Rebuild | The control house and controls will be upgraded to include Wolverine’s standard protection and control system. The existing 69 kV switches limit facility ratings to sub-standard capacity and will be replaced. The existing bus configuration will be upgraded to a ring bus and will be built to 138 kV design. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2027-12-31 | 69 | M2 - Appendix A Approved | 10000000
MTEP18 | East | 13581 | Oden Area Support Project | The Oden area experiences severe undervoltage issues under matenance + contingency conditions. This project will upgrade the conductor, significantly reducing the line impedance, to provide support to the area from the Atlanta and Airport stations. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2024-12-31 | 69 | M2 - Appendix A Approved | 80400000
MTEP18 | South | 13604 | Social Hill 115kV: Construct new distribution substation | Build a new distribution 115/13.8kV substation with a new 40 MVA 115/13.8kV transformer and provisions for a future second 40 MVA transformer. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2024-12-01 | 115 | M3 - Under Construction | 4960344
MTEP18 | South | 13621 | Norfork - Southland 161kV: Rebuild line | Rebuild the ~9 mile line segment and upgrade all station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2026-06-01 | 161 | M2 - Appendix A Approved | 12230000
MTEP18 | South | 13622 | Southland - Mt. Home 161kV: Rebuild line | Rebuild the ~1.4 mile line segment and upgrade all station equipment to achieve a 1300 Amp (363 MVA) flow through rating. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2027-06-01 | 161 | M2 - Appendix A Approved | 2260000
MTEP18 | West | 13647 | Detroit Lakes Industrial Substation Reconfiguration | Construct a new line-breaker substation adjacent to the existing Detroit Lakes Industrial Substation in order to relocate the existing distribution transformer at Detroit Lakes Industrial Substation, as well as add a second distribution transformer in the new line-breaker substation. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Local Reliability | 2027-11-01 | 115 | M2 - Appendix A Approved | 7900000
MTEP18 | East | 13687 | Equipment Upgrade Morrow 138kV – Station | The proposed solution is to upgrade the station equipment at Morrow position “500” to meet or exceed 338 MVA/1413 Amps (summer emergency). | MI | METC | BRP |  | 2026-03-31 | 138 | M2 - Appendix A Approved | 31000
MTEP18 | West | 13756 | Edgewater SS, 345 kV Asset Renewal and Bus Reconfiguration | Substation Equipment Asset Renewal - Replace four 345 kV model GW oil circuit breakers, breaker mechanism and bushing type cause units to have a history of chronic oil leakage. - Retire two 345 kV live tank line circuit breakers and six associated free standing CTs. Three of these CTs are a model with a history of failures. - Retire 345 kV outdoor SF6 GIS bus. Heaved foundations have caused past leaks and future shifting of foundations risks continued leakage. Bus reconfiguration is coordinated with the retirement of select Edgewater generation units. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2025-06-01 | 345 | M2 - Appendix A Approved | 14200000
MTEP18 | Central | 13765 | Metea to Lucerne 69kV Rebuild | Metea to Lucerne 6926 (Part 1) 69kV Rebuild w/ 477ACSR | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2025-10-13 | 69 | M2 - Appendix A Approved | 7078000
MTEP18 | West | 13792 | Keel Ridge SS, New DIC | UMERC will: • construct a new Keel Ridge Substation • install one 69/13.8 kV, 18 MVA transformer ATC will: • loop through line 6820 (Armory-Quinnesec Fall) • extend 0.6 mile double-circuited 69 kV T-Line • install two line switches (load-break), and one bus-tie switch | MI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2025-12-01 | 69 | M2 - Appendix A Approved | 8894678
MTEP18 | Central | 13820 | Galveston New 69-12kV Sub | Galveston New 69-12kV Sub: loop 69173 ckt thru with (3) 1200A switches and 954AAC bus; 22.4MVA NLTC xfmr | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-12-31 | 69 | M2 - Appendix A Approved | 1767000
MTEP18 | West | 13826 | Physical Security Current Cycle | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2018. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2025-12-01 | 345 | M3 - Under Construction | 67198396
MTEP18 | West | 13851 | Hawick Re-Route | Construct approximately 4 miles of new 69 kV line. Move and rebuild approximately 2.5 miles of existing 69 kV transmission line to accommodate the MNDOT Highway 23 project near Paynesville. Project schedule determined by MNDOT road move schedule. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2025-03-21 | 69 | M3 - Under Construction | 8763724
MTEP18 | West | 13869 | Stanley Substation | Rebuild Stanley 115 kV tap to a three position ring bus and replace 115/69 kV transformer | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Local Reliability | 2026-12-31 | 115 | M2 - Appendix A Approved | 4720000
MTEP18 | East | 13871 | Alpena - Rockport 138 kV Sag Remediation | Remediate the sag limit on the Alpena - Rockport 138 kV line to a minimum of 133 MVA. | MI | METC | BRP |  | 2025-02-28 | 138 | M2 - Appendix A Approved | 1950000
MTEP18 | South | 13882 | Rebuild L73 (Rocky Creek - Agricola) 69kV Line | Completely rebuild Line 73 (Rocky Creek - Agricola, 8.2 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Local Reliability | 2024-11-01 | 69 | M3 - Under Construction | 2460000
MTEP18 | South | 13885 | Rebuild L37C (Wiggins GOAB - Stillmore) 69kV Line | Completely rebuild Line 37C (Wiggins GOAB - Stillmore, 7.22 mi.) at 161kV construction with more reliable concrete structures. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2025-10-01 | 69 | M2 - Appendix A Approved | 3104600
MTEP18 | South | 13896 | Rebuild L33B (Rocky Creek - Sawmill Rd) 69kV Line | Completely rebuild Line 33B (Rocky Creek - Sawmill Road, 5.54 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2025-01-01 | 69 | M3 - Under Construction | 1662000
MTEP18 | South | 13897 | Rebuild L33D (Sawmill Rd - SE Greene) 69kV Line | Completely rebuild Line 33D (Sawmill Road - SE Greene, 1.39 mi.) at 161kV insulation with 795 ACSR and OPGW. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2025-03-01 | 69 | M2 - Appendix A Approved | 417000
MTEP18 | South | 13902 | Mossville to Lockmoor 69 kV: Rebuild/Reconductor line | Rebuild or re-conductor the approximately 2.10 mile long Mossville to Lockmoor 69 kV transmission circuit to a minimum of 1200 A, 143 MVA. Open line 253 between Mossville and Alfol 69 kV and designate it as normally open. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2025-12-30 | 69 | M3 - Under Construction | 8270000
MTEP18 | East | 13949 | Long Rapids Station | Build a new breaker and half scheme station in a less flood prone location and move all METC Alpena lines into the new station. Build three tie lines between the new station and Alpena’s station. Utilize existing line sections where possible. Remove all METC equipment at the existing Alpena station. | MI | METC | Other | Local Reliability | 2025-01-31 | 138 | M2 - Appendix A Approved | 22996285
MTEP18 | South | 13992 | Pine Tree 230kV Substation | Construct a 230 kV substation west of the Hernando 115 kV substation. Build new in & out 230 kV line tapping the Church Rd to Getwell 230 kV line. | MS | ENTERGY SERVICES, LLC. | Other | Load Growth | 2025-06-01 | 230 | M2 - Appendix A Approved | 56301691
MTEP18 | South | 13993 | Tap EAI Harrison East - Osage Creek: Construct Dry Creek 161 kV switching station | AECC will construct the new Dry Creek 161 kV switching station on the Entergy Harrison East to Osage Creek 161 kV transmission line. Entergy's interconnection requirements will likely require the switching station to be a 4 breaker ring bus. From the point of interconnection, Carroll Electric Cooperative Corporation (AECC's member), will construct two new 161 kV transmission lines. The first 161 kV transmission line will head north approximately 16 miles and tie into the existing Osage Creek 69 kV system via the new Long Creek 161/69 kV substation to be constructed by AECC. The second 161 kV transmission line will head south approximately 30 miles and tie into the existing Osage Creek 69 kV system via the new Smyrna 161/69 kV substation to be constructed by AECC. | AR; MO | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Local Reliability | 2024-12-15 | 161 | M2 - Appendix A Approved | 12620000
MTEP18 | East | 14000 | Rebuild Burnips to Portland | Rebuild and upgrade 69 kV line to 138 kV design, 795ACSS conductor and OPGW | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 50000000
MTEP18 | East | 14001 | Blendon Area Upgrade | This project will provide a third 138kV source into the Blendon station from the Bradley station. The existing 69kV lines between the Bradley and Blendon are constructed to 138kV design and will be converted as part of this project. Additional Projects Associated with the Conversion: Bradley Station - MTEP#4383 Bradley Line Mods (Wolverine) - MTEP#8222 Fairview Station - MTEP#9916 Burnips Station - MTEP#3335 Burnips to Portland Rebuild - MTEP#14000 Other Company Work Required: ZBPW: Fairview Transformer and Associated Equipment MTEP#14188 METC: Blendon 138kV upgrades MTEP#14060 and Bradley Connections MTEP#14067 | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2025-12-31 | 138 | M2 - Appendix A Approved | 14144525
MTEP18 | East | 14007 | Enrico Fermi-Shoal 120kV Rebuild | Rebuild 1.3 miles wood pole circuit from Enrico Fermi to Toll Road 120kV and 3.7 miles wood pole section of the Toll Road - Shoal 120kV circuit utilizing 120kV single circuit steel poles and 954 ACSR conductor. Also install OPGW on both circuits and replace line entrance at Enrico Fermi. | MI | ITC | Other | Age and Condition | 2024-12-31 | 120 | M3 - Under Construction | 9278500
MTEP18 | West | 14045 | Louise - Install 2nd Distribution Transformer | This project will install a 2nd 115/13.8 kV 50 MVA transformer, circuit switcher, 2 new feeders, and one 115 kV breaker at Louise substation. | SD | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2024-04-22 | 115 | M2 - Appendix A Approved | 7350000
MTEP18 | West | 14056 | Parkers Prairie 115/12.5 kV Tap | Parkers Prairie existing 41.6 kV load will be moved to a Parkers Prairie 115/12.5 kV Tap | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-08-31 | 115 | M2 - Appendix A Approved | 950000
MTEP18 | East | 14071 | Trenton Channel 120 kV – Upgrade HJ-IQ Station Equipment | Upgrade station equipment at positions “HJ" and “IQ” to at least 747 MVA (3594 Amp). | MI | ITC | BRP |  | 2024-12-31 | 120 | M2 - Appendix A Approved | 795000
MTEP18 | West | 14108 | Lehman Avenue Substation | New distribution substation cutting into the Hills-Sub E 161 kV line. Includes 161 kV line circuit breakers and a 33 MVA transformer. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2024-12-15 | 161 | M3 - Under Construction | 3500000
MTEP18 | West | 15126 | Edgewater SS, DIC, replace transformer and substation rebuild | Alliant will: - rebuild and relocate Edgewater Substation ATC will: - loop through the 138 kV line X-37 with line breakers | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2030-12-31 | 138 | M2 - Appendix A Approved | 5100000
MTEP18 | East | 3135 | Airport – Long Rapids 2 138 kV line | Rebuild the Airport – Long Rapids 138 kV line from Long Rapids to Str. #103G100 (~6.3 miles) by replacing the existing single-circuit structures with new double-circuit structures and reinstalling the existing conductor on one side for the Airport – Long Rapids 1 138 kV line and installing new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps) on the other side for the Airport – Long Rapids 2 138 kV line. Utilize the existing assets of the Airport – Mio 138 kV line from Str. #103A7743 to the Airport station’s new location in the construction of the new Airport – Long Rapids 2 138 kV line. Any new conductor used in jumpering from Str. #103G100 to Str. #103A7743 should meet or exceed the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). Acquire new ROW and construct new transmission assets for the Airport – Mio 138 kV line utilizing single-circuit structures heading north from Str. #103A7707 to the Airport station’s new location (~2.6 miles). Install new conductor which meets or exceeds the summer emergency rating of 477 ACSR conductor (260 MVA/1088 Amps). The conductor from Str. #103A7707 to Str. #103A7742 will now be de-energized. Construct Row 4 at the Long Rapids 138 kV switchyard and install the necessary 138 kV station equipment to terminate the Airport 2 138 kV line at Pos. BM4. The summer emergency rating of all new 138 kV equipment should be no less than the summer emergency rating of 477 ACSR conductor (260/1088 Amps). The details of how the new line is connected to Airport are preliminary and will need to be coordinated with Wolverine Power Supply Cooperative (WPSC) as they are the owner of the Airport station. | MI | METC | BRP |  | 2025-01-31 | 138 | M3 - Under Construction | 22423000
MTEP18 | West | 4726 | Hillman - Darlington 138kV (X-14/X-101), rebuild | Rebuild Hillman - Darlington (X-14/X-101) 138kV line -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild a portion of the 12.35 mile line (X-14) and 6.38 mile line (X-101) -1950's vintage original construction | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-31 | 138 | M2 - Appendix A Approved | 28500000
MTEP18 | West | 7763 | McKenna - Castle Rock, 69kV (Y-47), rebuild | Rebuild Y-47 from McKenna - Castle Rock 69 kV -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild a portion of the 8.52 mile line -1950's vintage original construction | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 13000000
MTEP18 | West | 7765 | Lincoln - McKenna 69kV (Y-145), rebuild | Rebuild Y-145 from Lincoln Pumping Station - McKenna 69 kV -Line inspection reports indicate line requires rebuild to continue reliable operation. -Wood poles and cross-arms show decay, deterioration and woodpecker activity. -Rebuild a portion of the 12.06 mile line -1950, 1960 and 1980 vintage original construction | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-06-15 | 69 | M3 - Under Construction | 9000000
MTEP19 | Central | 11971 | Reconfigure Jenkins (Formerly Grand Tower) 138 kV substation to BAAH | Establish a Breaker-and-a Half 138 kV bus arrangement | IL | AMEREN ILLINOIS | Other | Local Reliability | 2028-12-01 | 138 | M2 - Appendix A Approved | 22000000
MTEP19 | West | 15449 | Ottumwa Heights 161kV Substation Interconnection | As part of a long term plan to shift the load in Ottumwa off the 69kV and onto the 161kV system, IPL and ITC will be building a 161:26.2/13.1kV substation near Rutledge substation. IPL will purchase the land and own the joint use assets. ITCMW will construct a 4-position ring bus. All terminal equipment should be capable of 2000A minimum. ITC will build two independent taps from Ottumwa Generation – Woody #1 to the Ottumwa Heights substation. | IA | ITC MIDWEST | Other | Load Growth | 2025-12-31 | 161 | M2 - Appendix A Approved | 9774134
MTEP19 | West | 15456 | Brooklyn-Malcom 69kV line & Grinnell 69kV Terminal | ITC Midwest will construct a new ~9 mile 69kV line from Brooklyn to the Malcom Tap, install new 69kV switches at the Malcom substation, and rebuild 1 mile of line from the Malcom Tap to the Grinnell Substation to double circuit 69kV. ITC Midwest will add a 69kV terminal and breaker at the Grinnell substation. | IA | ITC MIDWEST | Other | Age and Condition | 2026-12-31 | 69 | M2 - Appendix A Approved | 10686722
MTEP19 | East | 15754 | Mio Dam - Plywood Tap 138 kV Sag Remediation | The proposed solution is to remediate the sag limit on the Mio Dam – Lewiston Tap 138 kV section of the Gaylord – Mio Dam 138 kV line to increase its summer emergency rating to a minimum of 147 MVA/615 Amps and remediate the sag limit on the Lewiston Tap – Plywood Tap 138 kV section of the Gaylord – Mio Dam 138 kV line to increase its summer emergency rating to a minimum of 147 MVA/615 Amps. | MI | METC | BRP |  | 2026-12-31 | 138 | M2 - Appendix A Approved | 875000
MTEP19 | Central | 15774 | New Pleasant View 138/69 kV Substation | 1) New (Ameren) Dempsey-(PPI) Pleasant View 138 kV line 2) New Pleasant View 138/69-34.5 kV Substation | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 138 | M2 - Appendix A Approved | 7100000
MTEP19 | West | 15780 | Lignite-Kincaid 60 kV | Build new Lignite-Kincaid 60 kV line | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Age and Condition | 2026-08-31 | 60 | M2 - Appendix A Approved | 6100000
MTEP19 | East | 15806 | Chopin-Arthur Jct. 138kV Sag Remediation | The proposed solution is to completely remediate sag on the Chopin – Arthur Jct. section to conductor limit of 908 Amps (217 MVA). | MI | METC | BRP |  | 2027-06-01 | 138 | M2 - Appendix A Approved | 3230000
MTEP19 | Central | 15815 | New Fancy Creek-Middletown 69 kV Line | New Fancy Creek-Middletown 69 kV line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 9141500
MTEP19 | Central | 15840 | Tetersburg 69/12kV Sub | Tetersburg 69/12kV Sub: install new sub in the 69191 ckt | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-04-14 | 69 | M2 - Appendix A Approved | 1040000
MTEP19 | East | 15879 | Monroe - Lulu 345 kV Station Equipment Upgrade | Upgrade the station equipment at Monroe 345 kV positions “MF” and “MM”. | MI | ITC | BRP |  | 2025-06-16 | 345 | M3 - Under Construction | 1259810
MTEP19 | West | 15921 | Lake 26-Tower Road 69KV Lake 26 Road | Rebuild the 69KV line with 477 ASCR and horizontal post construction. | WI | NORTHWESTERN WISCONSIN ELECTRIC CO. | Other | Local Reliability | 2028-12-01 | 69 | M2 - Appendix A Approved | 262500
MTEP19 | West | 4232 | NW Minnesota Projects | Support load growth with the following projects: - Winger 2nd 230/115 kV transformer and sub expansion. - 115 kV capacitors at Donaldson and Thief River Falls. - Automatic UVLS at Crookston, Donaldson, and Plummer 115 kV. - Replace Disconnects at Winger 115 kV to increase facility ratings. - Replace switches at Plummer and Oslo 115 kV to increase facility ratings. - 4 breaker ring at Oslo 115 kV. - 5 mile 115 kV line from Oslo - Lake Ardoch 115 kV | MN; ND | OTTER TAIL POWER COMPANY | BRP |  | 2025-02-28 | 230 | M3 - Under Construction | 17050811
MTEP19 | Central | 9851 | Reconductor Edwards-Kewanee 138 kV line (7423) | Reconductor Ameren portion to 1200 A summer emergency capability | IL | AMEREN ILLINOIS | Other | Age and Condition | 2024-12-01 | 138 | M2 - Appendix A Approved | 1400000
MTEP20 | Central | 18305 | Westwood 345kV / 138kV relays and breakers replacement | Westwood misc station equipment replacement including: upgrade relays on 13806, 13808, 138345-1, Bk2, 138 bus 1 and 2, 138 bus tie ; Replace OCB 13820, 13883 and relays | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-12-15 | 345 | M2 - Appendix A Approved | 7605000
MTEP20 | Central | 18307 | New Noblesville West 69/12 kV substation | Noblesville West (previously Westfield East): new sub - 69/12kv - 22.4 MVA xfmr bank, single phase regulators SCADA/IVVC, 2 breakers, and space for second bank. Normal feed from 6917 ckt, alternate from 69142. | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-05-05 | 69 | M2 - Appendix A Approved | 5376105
MTEP20 | Central | 18308 | New Hunts Creek 138/12 kV substation | Hunts Creek 138/12 kV substation: new sub to be located in the 13855 ckt between LGE Ghent 138 kV and DEI Fairview 138 kV | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-04-01 | 138 | M2 - Appendix A Approved | 3313000
MTEP20 | Central | 18331 | Whitesville to Advance 69kV Rebuild | 69154 rebuild from Whitesville to Advance with 477ACSR and light-duty steel poles | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-02-13 | 69 | M3 - Under Construction | 14410000
MTEP20 | West | 18364 | OTP Oslo 115 kV Switch Replacement | Replace 600 Amp Switch at OTP Oslo with 1200 Amp Switch. | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-05-31 | 115 | M2 - Appendix A Approved | 200000
MTEP20 | Central | 2864 | Reconductor Centerton to Martinsville 69kV - 69163 ckt. | Reconductor the 69kV-69163 ckt - 3.47 miles of 366ACSR 80C and 0.23 miles of 477ACSR 80C to 954ACSR 100C | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2027-06-01 | 69 | M2 - Appendix A Approved | 6477000
MTEP21 | West | 10590 | Academy - Columbus, 69kV (Y-21), rebuild & OPGW | The Academy - Columbus (Y-21) 69kV circuit is 3 miles long and uses 336 kcmil ACSR supported on lattice steel structures - Field inspection reports indicate the 1910 vintage structures require replacement to continue reliable operation - New conductor will be installed and will be similar or slightly larger than the existing circuit capability - Optical Ground Wire (OPGW) will be installed to provide protection and SCADA communications along this ROW Substation Work Scope: - Academy Substation - Replace line side jumper to meet planning long term rating needs and terminate fiber. - Columbus (ALTE) - Remove control house, oil circuit breakers, and switches; - Install motor operated disconnects, gas circuit breaker, control house, and RTU for SCADA control - Improve drive access to site with purchase and demolition of existing residence - Terminate fiber with line project. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-07-15 | 69 | M2 - Appendix A Approved | 3263000
MTEP21 | South | 13995 | Mannsdale 230kV Substation | Build new Mannsdale 230kV substation in operating and transfer configuration. Include appropriate high-side fault protection. Install two (2) – 40 MVA, 230 kV-13.8kV, LTC, transformers including high-side circuit switchers to operate at 12.47kV. Install two (2) – 2,000 amp, 13.8kV, main breakers. Install eight (8) 1200 amp, 12.47 kV, breaker bays and equip with six (6) breakers; three (3) breakers to be served by T-1, and three (3) to be served by T-2. Install control house and all necessary relaying equipment. | MS | ENTERGY SERVICES, LLC. | Other | Load Growth | 2025-06-01 | 230 | M2 - Appendix A Approved | 32312508
MTEP21 | West | 14964 | Small Capital Project and Asset Renewal Program 2022 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, re-insulations and uprates and Pole hardware replacements - Estimated Cost - $4,000,000 Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. - Estimated Cost - $40,000,000 Substation Battery Replacement Program - Estimated Cost - $3,000,000 Substation Physical Security Asset Renewal - Estimated Cost - $3,000,000 Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-12-01 | 345 | M3 - Under Construction | 52320773
MTEP21 | West | 14965 | Communication Reliability Program 2022 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2025-12-31 | 345 | M3 - Under Construction | 19252066
MTEP21 | West | 14967 | Physical Security Program 2022 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2022. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2024-12-31 | 345 | M3 - Under Construction | 11797871
MTEP21 | West | 14968 | Load Interconnection Program 2022 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2022. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-12-31 | 138 | M3 - Under Construction | 27586994
MTEP21 | South | 15848 | Jayess Loop Project | Rebuild L523 (Norfield SS to Little Creek) and L549 (Jayess SS to Jayess) with sufficient ACSR conductor. Tap L549 (Jayess SS to Jayess) with a 115kV GOAB, tap L523 with a 115kV GOAB and build a new 115kV transmission line from Jayess GOAB to Little Creek GOAB. Build a new 115kV breaker switching station at Jayess and build a new 115kV breaker switching station at Norfield. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Local Reliability | 2027-03-01 | 115 | M2 - Appendix A Approved | 19844000
MTEP21 | South | 15850 | Olive Oil Loop Project | Rebuild L546 (Pisgah GOAB to Magee Road SS) with sufficient ACSR conductor. Rebuild L547 (Arlington GOAB to Arlington) with sufficient ACSR conductor. Tap L547 with a 115kV GOAB, tap L576 (Magee Road SS to Olive Oil) with a 115kV GOAB and build a new 115kV transmission line from Arlington GOAB to Olive Oil GOAB. Build a new 115kV breaker switching station at Arlington. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Local Reliability | 2026-12-01 | 115 | M2 - Appendix A Approved | 12106000
MTEP21 | West | 16489 | Empire SS, Control House, Relays, and Circuit Breaker Asset Renewal | Asset renewal at the Empire SS would include: - Install new control building - Retirement and replacement of circuit breakers, protective relays, and disconnect switches | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2024-12-31 | 138 | M3 - Under Construction | 9900000
MTEP21 | West | 16490 | Granville SS, Control House and Relay Replacement and Asset Renewal | 345kV Project Scope • Replace 4 1970-vintage Westinghouse 3450-GW-25000 oil breakers • Replace 7 disconnect switches 138kV Project Scope • Replace 7 1969-vintage Westinghouse 1380-GM-15000 oil breakers • Replace 2 underground HPFF lines with overhead and retire pump house at Granville and East Granville Terminal General Project Scope • Reconfigure 345kV bus to 6-position ring (5 positions plus one future position) • Vacate existing control house, transfer ownership to We Energies, obtain new high-security control house • Replace all relays and SCADA with current standard • Address planning-identified need for redundant bus differential protection • Expand yard to accommodate ring bus | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-30 | 345 | M3 - Under Construction | 40577000
MTEP21 | West | 18048 | Lincoln - 43rd Street Terminal 138 kV (5053), Replace with double circuit duct bank and XLPE cable | • Rebuild existing 5053 HPFF line with new XLPE in double circuit duct bank in existing road ROW. o Install ~2.2 miles of XLPE in double circuit duct bank package and new manholes. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-07-01 | 138 | M2 - Appendix A Approved | 74300000
MTEP21 | West | 18066 | Badoura 115kV Substation Modernization | Relocate existing 115 kV lines into ring bus and remove/retire old substation yard. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2025-12-31 | 115 | M2 - Appendix A Approved | 1820000
MTEP21 | Central | 18605 | New Hardinsburg 161kV Substation (J753) for solar Interconnection | Hardinsburg 161kV Substation (J753) for 100 MW solar Interconnection | KY | BIG RIVERS ELECTRIC CORPORATION | GIP |  | 2025-10-01 | 161 | M2 - Appendix A Approved | 200000
MTEP21 | Central | 18606 | New Meade 161kV Substation (J762) for solar Interconnection | Meade County 161kV Substation modification for (J762) solar Interconnection | KY | BIG RIVERS ELECTRIC CORPORATION | GIP |  | 2024-10-01 | 161 | M2 - Appendix A Approved | 500000
MTEP21 | Central | 18889 | Rebuild Hickok-North LaSalle 138 kV line (1659) | Rebuild the Hickok-North LaSalle 138 kV line for 2000 amps. | IL | AMEREN ILLINOIS | BRP |  | 2026-06-01 | 138 | M2 - Appendix A Approved | 6500000
MTEP21 | Central | 19025 | New J815 Hickory Point Wind Generator Interconnection (Yvonne 138 kV switching Station) | Install new Yvonne 138 kV switching Station (J815 Hickory Point Wind Generator Interconnection) on the Austin-Taylorville S.-1545 line. | IL | AMEREN ILLINOIS | GIP |  | 2026-06-01 | 138 | M2 - Appendix A Approved | 6600000
MTEP21 | Central | 19026 | New J912 Christian County Solar Generator Interconnection (Pana 138 kV switching station) | New J912 Christian County Solar Generator Interconnection at Pana 138 kV switching station | IL | AMEREN ILLINOIS | GIP |  | 2026-06-01 | 138 | M2 - Appendix A Approved | 900000
MTEP21 | West | 19165 | Fieldon Retirement | This project bypasses and retires the Fieldon series capacitor and removes the substation, whose only function is for the series capacitor. This facility is no longer required and has a significant recurring maintenance cost. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-26 | 345 | M2 - Appendix A Approved | 1000000
MTEP21 | West | 19325 | Hensel-Bowesmont 69 kV Rebuild | Rebuild Hensel-Glasston-Lincoln 69 kV to 115 kV construction (still operated at 69 kV) with 477 ACR conductor. Lincoln-Bowesmont 69 kV to be reconductored with 477 ACSR. | ND | MINNKOTA POWER COOPERATIVE, INC | Other | Local Reliability |  | 69 | M2 - Appendix A Approved | 3
MTEP21 | East | 19546 | J875 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Parr Road - Whiting 138 kV circuit. | MI | METC | GIP |  | 2025-06-02 | 138 | M3 - Under Construction | 21786067
MTEP21 | West | 19587 | Petenwell – Council Creek, (X-40) 138kV, Partial Structure and OPGW Replacement | - Replace 30 miles of shield wire with 48 Strand OPGW Fiber cable between Petenwell and Council Creek substations - Replace ~67 wood monopoles structures | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2025-12-01 | 138 | M2 - Appendix A Approved | 9000000
MTEP21 | West | 19705 | Crivitz SS, Transformers and Relays Asset Renewal | • Replace T1, 138/69 kV power transformer with the on-site 138/69 kV system spare • Replace T3, 138/69 kV power transformer with the 138/69kV power transformer from Pioneer SS that will be taken out of service in 2023 due to elimination of the 69 kV system at that substation • Replace 69 kV Mark V circuit switcher with an existing on site circuit breaker and new disconnect switch • Replace a single line relay in an existing panel | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2024-10-31 | 138 | M3 - Under Construction | 4599154
MTEP21 | West | 19706 | North Appleton SS, Transformer and Reactor Asset Renewal | • Replace T7 138/345 kV power transformer (three single phase units) with the on-site system spare (standard three phase). • Retire two three-phase reactors, bus, structures and insulators and install a new standard 24.9 kV design connected to the tertiary of the newly installed 138/345 kV power transformer • Retire original design 34.5 kV vacuum breaker and associated disconnect switches • Install new station service on 24.9 kV bus salvaging three newer vintage reactors for use in a future project • Replace seven 138 kV disconnect switches | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2024-12-01 | 345 | M3 - Under Construction | 4197000
MTEP21 | West | 19729 | J732 Superior SS Network Upgrades and Interconnection Facilities | Interconnection of about 560 MW the facility composed of one (1) steam turbine unit and one (1) natural gas unit in a 1x1 combined cycle facility interconnecting at the new Superior Substation. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2026-11-17 | 345 | M2 - Appendix A Approved | 21245605
MTEP21 | Central | 19746 | Rebuild Joppa-Shawnee 161 kV line Ckt 2 | Rebuild the GridLiance Heartland portion of the Joppa - Shawnee 161 kV ckt 2 line | IL; KY | GRIDLIANCE HEARTLAND LLC | Other | Age and Condition | 2026-12-31 | 161 | M2 - Appendix A Approved | 11000000
MTEP21 | Central | 19805 | New UMC 69 kV Substation | Build a new UMC substation and add a new 69/13.8 kV transformer, build a 69 kV ring bus switch station, and connect two 69 kV lines to UMC ring bus. Ring bus will have four 69 kV breakers protecting two incoming 69 kV transmission lines, and will be connected to two parallel output 69 kV lines feeding two 69/13.8 kV transformers through their own 69 kV breakers. | MO | CITY OF COLUMBIA, MISSOURI (WATER AND LIGHT DEPT.) | Other | Local Reliability | 2025-09-01 | 69 | M2 - Appendix A Approved | 26000000
MTEP21 | West | 19806 | Bonnie Road SS, DIC, New Substation | • Extend approximately 0.38 miles of 69 kV double circuit transmission line on new right-of-way. • Construct new 69 kV substation with a bus-tie switch and provisions for a future bus-tie breaker. • Install 69 kV line breakers as sectionalizing devices. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-12-31 | 69 | M2 - Appendix A Approved | 3500000
MTEP21 | Central | 19847 | New Golden 138/69 kV Substation | New Golden 138/69 kV substation near La Prairie, IL | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 138 | M2 - Appendix A Approved | 7425000
MTEP21 | Central | 19848 | New Camden - Rushville 69 kV Line | New ~12-mile Camden to Rushville 69 kV line in AEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 7680000
MTEP21 | Central | 19849 | New Rushville - Sugar Grove 69 kV Line | New ~13-mile Rushville to Sugar Grove 69 kV line in AEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 8448000
MTEP21 | Central | 19850 | New Sugar Grove - Mt. Sterling 69 kV Line | New ~9-mile Sugar Grove to Mt. Sterling 69 kV line in AEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 5548800
MTEP21 | Central | 19851 | New Mt. Sterling - Kellerville 69 kV Line | New ~18-mile Mt. Sterling to Kellerville 69 kV line in AEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 13585000
MTEP21 | Central | 19852 | New Sikeston 161 kV Substation | Construct new Comstock (Sikeston) 161kV breaker-and-a-half substation to interconnect Ameren's Miner-Sikeston line and Sikeston Board of Municipal Utilities' New-Madrid-Sikeston 161kV line. The City of New Madrid will install a 161/69kV xfmr to serve new industrial customer. | MO | AMEREN MISSOURI | Other | Load Growth | 2025-06-01 | 161 | M2 - Appendix A Approved | 44240000
MTEP21 | West | 19913 | Howard Lake to Big Swan, Delano to Howard Lake, Cokato to Winstead Rebuild | Howard Lake to Big Swan - Rebuild 16.0 miles , Delano to Howard Lake – Rebuild 19.7 miles , Cokato to Winstead – Rebuild 14.3 miles to current 69kV standard for end of life asset renewal | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2024-05-31 | 69 | M3 - Under Construction | 17979041
MTEP21 | West | 19914 | High Bridge-Rogers Lake Bifurcation to Double Circuit | Convert the bifurcated 115 kV line from High Bridge to Rogers Lake to a double circuit 115 kV line to alleviate curtailment on the High Bridge Generating Plant. Construct new breaker positions at High Bridge and Rogers Lake to accommodate the second 115kV circuit | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2023-05-13 | 115 | M3 - Under Construction | 5770000
MTEP21 | West | 19915 | Replace Alma Substation | Replace the existing Alma sub which is at end of life and in a poor access location with new sub with 7MVA TR with two regulated feeders at new site. | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 3000000
MTEP21 | West | 19925 | Albia-Melrose 69kV Rebuild | The majority of the Albia to Melrose 69kV line is near end of life and in poor condition. The line between the Albia and Melrose substations (~17.25 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | ITC MIDWEST | Other | Age and Condition | 2028-12-31 | 69 | M2 - Appendix A Approved | 16293244
MTEP21 | West | 19926 | Osceola North-Woodburn Jct 69kV Rebuild | The majority of the Osceola North to Woodburn 69kV line is near end of life and in poor condition. The line between the Osceola North, Osceola Rec, and Woodburn Jct. substations (~9.57 miles) will be rebuilt to current 69kV standards. All new equipment should be rated at 600A or higher minimum summer normal rating. | IA | ITC MIDWEST | Other | Age and Condition | 2028-12-31 | 69 | M2 - Appendix A Approved | 8964000
MTEP21 | West | 19928 | Marion-Old Settlers 115kV Ckt#2 | To better serve the Northeast Cedar Rapids load pocket, ITC will energize the second circuit on the Marion – Old Settlers 115kV structures and terminate it into Marion & Old Settlers substations. | IA | ITC MIDWEST | Other | Local Reliability | 2026-12-31 | 115 | M2 - Appendix A Approved | 4232578
MTEP21 | Central | 19932 | New Disco to Lomax 69 kV Line | New ~15-mile Disco to Lomax 69 kV line in WIEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 9862500
MTEP21 | Central | 19933 | New Disco to Powellton 69 kV Line | New ~12-mile Disco to Powellton 69 kV line in WIEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 8000000
MTEP21 | Central | 19934 | Add Elvaston 69 kV Breakers | Add breakers on the Elvaston to Powellton line and the Elvaston to Sutter line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 350000
MTEP21 | Central | 19935 | New Sutter - Ursa 69 kV Line | New ~21-mile Sutter to Ursa 69 kV line between WIEC and AEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 13312000
MTEP21 | Central | 19937 | New Wolf Run 69 kV Breaker Substation | New Wolf Run 69 kV Breaker substation located near Bluffs, IL in IEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 2844450
MTEP21 | Central | 19939 | Rebuild Grand Island - Topeka 69 kV Line | Rebuild ~5-mile Grand Island to Topeka 69 kV line in MEC | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2025-04-01 | 69 | M2 - Appendix A Approved | 2764000
MTEP21 | Central | 19940 | Replace Grand Island 138/69 kV Transformer | Replace 56 MVA Delta-Wye 138/69 kV transformer with 84 MVA Wye-Wye 138/69 kV transformer | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 138 | M2 - Appendix A Approved | 1500000
MTEP21 | Central | 19949 | New ISHI Shelbyville 69 kV Loop | New ~7-mile ISHI Distribution to Johnston to Crest to Airport 69 kV line in SEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 7791500
MTEP21 | Central | 19951 | Rebuild Pisgah - Berlin 69 kV Line | Rebuild Pisgah to Berlin 69 kV line between IEC and MEC | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 7880000
MTEP21 | South | 19954 | Newton 138 kV Station | Convert existing radial substation to looped substation and install 138/69 kV transformer. | TX | EAST TEXAS ELECTRIC COOPERATIVE, INC. | Other | Local Reliability | 2026-03-31 | 138 | M2 - Appendix A Approved | 5300000
MTEP21 | South | 19957 | Lake Arthur 69 kV Switch Upgrade | Replace switch 732 at Lake Arthur with a motorized load break switch that has whips and bottles. Move the Normally Open point from switch 8873 to switch 732 so that Lake Arthur 69 kV station is fed out of Lawtag 69 kV station. | LA | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2024-12-31 | 69 | M2 - Appendix A Approved | 706000
MTEP21 | West | 19965 | Marquette County Reactive Power Project | Relocate one 138 kV line position (line 16343) to a different bus position at National substation. • Install one +/- 50 MVA, 138 kV STATCOM (Static Synchronous Compensator) at National substation. o Include one spare 138 kV transformer o Add a new 138 kV circuit breaker and protection package at National | MI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2025-02-01 | 138 | M3 - Under Construction | 30000000
MTEP21 | Central | 19969 | New Belleau 138 kV Capacitor Bank | Install 120 Mvar capacitor bank at Belleau 138 kV | MO | AMEREN MISSOURI | BRP |  | 2026-06-01 | 345 | M2 - Appendix A Approved | 3500000
MTEP21 | East | 19970 | Rebuild Alma - Vestaburg 138 kV 477 ACSR | Rebuild approximately 0.43 mile of the Alma - Vestaburg 138kV circuit using 954 ACSR on double circuit structures constructed at 138kV Standards with OPGW. Also replace terminal equipment at Alma. | MI | METC | BRP |  | 2026-12-31 | 138 | M2 - Appendix A Approved | 3434000
MTEP21 | South | 19987 | Nelson 230/138 kV Relay Improvement SPOF | Dual Battery installations or monitoring sufficient to FERC 754 guidelines at Nelson 230 kV and 138 kV stations. Install and verify high speed dual primary protection on the GSU for all power plants interconnected at Nelson 230 kV and 138 kV substations | LA | ENTERGY SERVICES, LLC. | BRP |  | 2026-01-01 | 230 | M2 - Appendix A Approved | 21500000
MTEP21 | West | 19993 | Triboji 69kV Cap Bank | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the Triboji J2 bus. All new substation equipment should have a minimum rating of 1200A. | IA | ITC MIDWEST | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 813960
MTEP21 | West | 19994 | Marcus East to Hospers 69 kV Line and Rebuild Marcus East Substation | Construct a new 69 kV line from Hospers-Marcus East, construct new 69 kV line terminal at Hospers Substation, rebuild Marcus East Substation to install 69 kV breakers and a 69 kV capacitor bank | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2024-12-01 | 69 | M3 - Under Construction | 24500000
MTEP21 | West | 19995 | West Union 69kV Cap Bank | ITC will install a 11.25MVAR Effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor on the West Union J2 bus. All substation equipment should have a minimum rating of 1200A. | IA | ITC MIDWEST | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 812280
MTEP21 | West | 19996 | Monona 69kV Sub Rebuild & Cap Bank Addition | ITC rebuild the Monona 69kV substation and install a 11.25MVAR effective cap bank, zero crossing/sync breaker and 0.5 mH pre-insertion reactor at a new Monona Substation adjacent to the existing site. All substation equipment should have a minimum rating of 1200A. This will allow for two 69kV buses and the cap bank installation at the new Monona site improving operational flexibility and addressing voltage concerns in the area. | IA | ITC MIDWEST | Other | Local Reliability | 2026-09-30 | 69 | M2 - Appendix A Approved | 6933731
MTEP21 | West | 19997 | Circuit Breaker Additions and Replacements 2022-2024 | Blanket project to add new 345 kV and 161 kV circuit breakers and replace existing 345 kV, 161 kV and 69 kV circuit breakers to increase reliability and operating flexibility. | IA; IL | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2030-12-31 | 345 | M2 - Appendix A Approved | 20450000
MTEP21 | West | 19998 | NW 2nd Street Substation | Construct a new 69 kV substation and associated 69 kV line work. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2026-07-31 | 69 | M2 - Appendix A Approved | 10000000
MTEP21 | West | 20000 | Bondurant Substation: Add 345-161 Xfmr | Add a 345-161 kV xfmr. | IA | MIDAMERICAN ENERGY CO. | BRP |  | 2025-06-01 | 345 | M2 - Appendix A Approved | 13900000
MTEP21 | Central | 20001 | Rebuild Joppa-Shawnee 161 kV Ckt 3 | Rebuild the GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 3 | IL; KY | GRIDLIANCE HEARTLAND LLC | Other | Age and Condition | 2026-12-31 | 161 | M2 - Appendix A Approved | 11700000
MTEP21 | West | 20002 | Waukee: Add 69 kV Capacitor Bank | Install 69 kV capacitor bank and 69 kV breakers | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-08-02 | 69 | M2 - Appendix A Approved | 6000000
MTEP21 | West | 20003 | Highway 6 161/13.2 kV Substation | Construct a new 161 kV substation and associated 161 kV line work. New substation will have 161 kV connections to Grimes & South Waukee substations from line taps on future 161 kV lines | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2026-07-31 | 161 | M2 - Appendix A Approved | 6000000
MTEP21 | Central | 20004 | Rebuild Joppa-Shawnee 161 kV Ckt 4 | Rebuild the GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 4 | IL; KY | GRIDLIANCE HEARTLAND LLC | Other | Age and Condition | 2026-12-31 | 161 | M2 - Appendix A Approved | 11700000
MTEP21 | Central | 20005 | Rebuild Joppa-Shawnee 161 kV Ckt 1 | Rebuild GridLiance Heartland portion of Joppa-Shawnee 161 kV Ckt 1. | IL; KY | GRIDLIANCE HEARTLAND LLC | Other | Age and Condition | 2026-12-31 | 161 | M2 - Appendix A Approved | 14700000
MTEP21 | West | 20007 | Clarion: Add 69 kV Breakers | Presently, Clarion Substation is tapped off the Hampton West--Eagle Grove 69 kV line. Reconfigure the 69 kV lines into Clarion Substation from a single tapped arrangement to an in and out breakered configuration, similar to Goldfield Substation. Build new 69 kV bus on MEC owned property adjacent to existing substation footprint. Install 69 kV circuit switcher between 69 kV bus and existing 69-13 kV transformer. Construct new 69 kV bus to accommodate a future 69 kV bus tie breaker, a future 69 kV circuit switcher, and a future second 69-13 kV transformer. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2028-12-31 | 69 | M2 - Appendix A Approved | 2000000
MTEP21 | West | 20011 | Sub 84: 69 kV Line Taps and Line Upgrades | 69 kV line tap work to support converting Sub 84 from a tapped substation to an in-and-out substation with 69 kV line circuit breakers. Install OPGW from Valley Drive to Sub 84 to Sub 55 for communications and replace structures and conductor on sections of line subject to galloping. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 14800000
MTEP21 | West | 20012 | Sub 17: Add 161-13.2 kV Transformer | Add 161 kV line circuit breaker at Sub 17 on the Sub 28 line terminal to support the addition of a new 161-13.2 kV transformer. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2030-12-31 | 161 | M2 - Appendix A Approved | 1000000
MTEP21 | East | 20018 | Rebuild Bullock - Shale 138 kV | Rebuild the Bullock to Structure 006A6682 (approximately 5 miles) utilizing 954 ACSR conductor with 230 kV double circuit structure standards with OPGW. Rebuild from Structure 006A6682 to the future Shale Substation (approximately 15 miles) utilizing 954 ACSR conductor with 138 kV double circuit structures standards with OPGW. Upgrade Terminal equipment at Bullock Substation 188 above overhead line conductor rating. | MI | METC | BRP |  | 2026-12-31 | 138 | M2 - Appendix A Approved | 37395385
MTEP21 | West | 20025 | Bethel-Tripoli 69kV Rebuild | The majority of the Bethel-Tripoli 69kV line is near end of life and in poor condition. The line between the Bethel substation and Fredericksburg Tap (~8 miles) will be rebuilt to current 69kV standards. All new equipment should be rated 600A or higher minimum summer normal rating. | IA | ITC MIDWEST | Other | Age and Condition | 2025-07-11 | 69 | M2 - Appendix A Approved | 7740000
MTEP21 | West | 20026 | Osage Jct-Rice 69kV Rebuild | The majority of the Osage JCT-Rice 69kV line is near end of life and in poor condition. The line between Osage JCT and Douglas Tap (~13.9 miles) and Riceville to Rice (~9.8 miles) will be rebuilt to current 69kV standards. All new line equipment should be rated 600A or higher. | IA | ITC MIDWEST | Other | Age and Condition | 2029-12-31 | 69 | M2 - Appendix A Approved | 22980000
MTEP21 | West | 20028 | Emery-6th Ave 69kV Rebuild | Beginning at where the double circuit ends (~0.35 miles outside Emery) - IPL’s 6th Ave substation will be rebuilt (~5.54 miles of line) to current 69kV standards. All new line should be rated 1200A or higher. | IA | ITC MIDWEST | Other | Age and Condition | 2025-06-30 | 69 | M2 - Appendix A Approved | 7200000
MTEP21 | West | 20029 | Southern Iowa New 161kV line and Breaker Stations | ITC will be building about 29 miles of 161kV line from CIPCO’s Winterset Jct. to Osceola’s new substation. This new line will be constructed using T2 636 ACSR and all new 161kV terminal equipment should be rated at 2000A or higher minimum summer normal rating. In addition, a new 161/69kV, 150 MVA transformer will be needed at the Osceola substation. ITC and CIPCO will install new breaker(s) at their respective substations. ITC will be building a new breaker station northeast of the Albia substation. This station will connect the 69kV line from Albia to Court and the 69kV line from Bridgeport to Centerville. Since the two lines have an intersection point (about 1.5 miles NE of the Albia sub), minimal line construction will be needed. ITC will be building a new breaker station at the “Lenox Tap” position. This station will replace the 3-way switch currently in use and connect our Lenox line and substation (IPL owned) to the new 69kV transmission system being built by CIPCO from the northwest (Corning/Brooks). All new 69kV equipment will need to be rated for 1200A minimum summer normal rating. ITC will be installing a 2-way switch outside IPL’s Lenox substation, building a new 69kV line (about 2.6 miles), and connecting it into CIPCO’s substation “Lenox Muni”. ITC will need to coordinate with CIPCO, NEMO, and IPL for necessary outages and construction | IA | ITC MIDWEST | Other | Local Reliability | 2028-01-05 | 161 | M2 - Appendix A Approved | 71210187
MTEP21 | West | 20037 | Carbide-Viele 161kV Rebuild | ITC Midwest has entered into an agreement with Northeast Missouri Electric Cooperative to rebuild approximately 12.3 miles of the ITC Carbide – Viele 161 kV line to double circuit to allow Northeast to connect a new 161 kV line from their Franklin Substation in Lee County, Iowa to their Winchester Substation in Clarke County, Missouri. Per the terms of the agreement, Northeast will be responsible for design and construction for this project. ITC will contribute a fixed amount of $6,120,00 for the project as a credit for planned maintenance ITC needs to perform on this line. The ITC portion of the rebuild will be constructed with T2-795 ACSR conductor and OPGW. ITC will own the double circuit poles, conductor, insulators, and 1 OPGW static wire. | IA | ITC MIDWEST | Other | Load Growth | 2025-12-02 | 161 | M2 - Appendix A Approved | 6200000
MTEP21 | West | 20038 | Sub 56 - Sub 85 161 kV Line Uprate | Replace substation terminal equipment at Sub 56 to uprate the Sub 56-Sub 85 161 kV line | IA | MIDAMERICAN ENERGY CO. | Other | Local Needs | 2024-12-31 | 161 | M2 - Appendix A Approved | 900000
MTEP21 | East | 20044 | ITCT Customer Interconnections - Year 2024 | Customer interconnection requests and retirements less than $1 million with in service date in year 2024. | MI | ITC | Other | Load Growth | 2024-12-31 | 120 | M2 - Appendix A Approved | 2000000
MTEP21 | East | 20047 | METC Customer Interconnections - Year 2024 | Customer interconnection requests and retirements less than $1 million with in service dates in the year 2024. | MI | METC | Other | Load Growth | 2024-12-31 | 138 | M2 - Appendix A Approved | 2000000
MTEP21 | East | 20049 | Rebuild and Sag Remediate Gallagher - Twining 138kV | The proposed solution is to Raise the sag limit on the 336 ACSR between Gallagher and Withey Lake Jct. and replace the 1/0 Copper on the Withey Lake Jct. - Twinning 138kV line with 477 ACSR utilizing standard 138 kV double circuit structures | MI | METC | BRP |  | 2025-06-01 | 138 | M2 - Appendix A Approved | 4679000
MTEP21 | East | 20054 | Warren 138 kV 377 Equipment Upgrades | Upgrade terminal station equipment, including a 138 kV breaker, at Warren position 377 to meet or exceed the rating of a 954 ACSR conductor. | MI | METC | BRP |  | 2026-05-01 | 138 | M3 - Under Construction | 1050000
MTEP21 | South | 20073 | Ponderosa 230 kV: Install Power Transformer | Install power transformer at the Ponderosa 230 kV substation. There are no power transformers currently installed at Ponderosa. | TX | ENTERGY SERVICES, LLC. | Other | Load Growth | 2024-11-30 | 230 | M3 - Under Construction | 1297855
MTEP21 | West | 20075 | Forbes 230 kV Modernization | Replace aging 230 kV cap bank and 230 kV circuit breakers at Forbes Substation, as well as a large 230/115 kV autotransformer. Project includes several other asset renewal components and substantial civil work at the site. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2027-12-31 | 230 | M2 - Appendix A Approved | 7350000
MTEP21 | West | 20081 | Stinson Asset Renewal Project | Replace aging capacitor bank, 115W breaker, switches, PT's, and relay panels. | WI | MINNESOTA POWER INC. | Other | Age and Condition | 2024-12-31 | 115 | M3 - Under Construction | 1530000
MTEP21 | East | 20107 | Atlanta-Karn-Thetford Split & Station Reconfiguration (ITCT) | Install a 120 kV, 3000 Amp, 40 kA section breaker and expand 138 kV into a ring bus configuration Add two 138 kV breakers to configure the 138 kV into a ring bus. Add 0.75 miles of 1431 ACSR to complete the Atlanta – Thetford circuit. New equipment should be rated for 3000 Amps or higher. | MI | ITC | Other | Local Reliability | 2026-12-01 | 138 | M3 - Under Construction | 5885000
MTEP21 | East | 20108 | Atlanta-Karn-Thetford Split & Station Reconfiguration (METC) | Split the three-ended Atlanta-Karn-Thetford 138 kV line into Altanta – Karn 138 kV and Atlanta – Thetford 138 kV. | MI | METC | Other | Local Reliability | 2026-12-01 | 138 | M3 - Under Construction | 931000
MTEP21 | East | 20132 | Pontiac 303 Transformer Replacement | Replace the Pontiac #303 345/120 kV transformer with at least 750 MVA summer emergency rated transformer. | MI | ITC | Other | Age and Condition | 2026-12-31 | 345 | M2 - Appendix A Approved | 4800000
MTEP21 | East | 20133 | Hines 201 Transformer Replacement | Replace the Hines #201 230/120kV transformer. The anticipated replacement is the ITCT-standard 230/120kV 560MVA transformer. | MI | ITC | Other | Age and Condition | 2025-12-31 | 230 | M2 - Appendix A Approved | 5870000
MTEP21 | West | 20135 | Panther - Big Swan Rebuild | - Rebuilding most of the line to 477 standard due to age and condition - Adding a breaker station at Adams Wind tap to sectionalize the line - Converting the City of Litchfield tap structure to a double circuit structure | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2029-09-16 | 69 | M2 - Appendix A Approved | 33900000
MTEP21 | West | 20136 | Pine Lake to Dunn Ethanol N4 Rebuild | This project is a mix of a rebuild of DPC’s existing 69 kV line in the area and construction on new right-of-way. The recommended plan in this area is to construct new transmission line with 477 ACSR conductor, a mix of replacement of existing line and new right-way from XEL’s Pine Lake transmission substation to the east towards the Dunn Ethanol distribution substation. The recommended plan will address the age and condition issues, constructing the line with new poles and 477 ACSR conductor. The plan will also address the longer tap lines to distribution substations with individual taps to all five distribution substations served from this line. Finally, building to the Dunn Ethanol distribution substation will provide backup service. | WI | DAIRYLAND POWER COOPERATIVE | Other | Age and Condition | 2026-12-17 | 69 | M2 - Appendix A Approved | 13051780
MTEP21 | East | 20144 | Argenta 2 Transformer Replacement | Replace the Argenta #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | METC | Other | Age and Condition | 2026-06-30 | 345 | M3 - Under Construction | 5400000
MTEP21 | East | 20145 | Tallmadge 2 Transformer Replacement | Replace the Tallmadge #2 345/138kV transformer. The anticipated replacement is the METC-standard 345/140kV 500MVA transformer. | MI | METC | Other | Age and Condition | 2027-12-31 | 345 | M2 - Appendix A Approved | 6100000
MTEP21 | West | 20148 | Appleton - Benson (AG-AB) 115 kV Line | Construct about 27 miles of 115 kV transmission line from Appleton to GRE’s AG-BK line and about 1.75-mile 115 kV transmission line from AG-BK line to Benson Muni substation with associated tap switch, distribution sub, and retirement projects. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2029-12-31 | 115 | M2 - Appendix A Approved | 54609279
MTEP21 | West | 20153 | 69 kV Line Rebuilds Blanket 2021 - 2024 | Blanket project to rebuild 69 kV lines due to condition and to improve reliability and operational flexibility. | IA; IL | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 34358650
MTEP21 | West | 20154 | 69 kV Substation Line Tap Blanket 2021-2024 | Blanket project to add new 69 kV line taps into new or existing substations to serve new distribution substations or to increase reliability. | IA; IL | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2030-12-31 | 69 | M2 - Appendix A Approved | 5200000
MTEP21 | West | 20155 | Relaying, Communication and Control Equipment Replacements 2021-2024 | Blanket project to replace existing relaying, communication equipment and control house equipment to increase reliability and operating flexibility. | IA; IL | MIDAMERICAN ENERGY CO. | Other | Local Needs | 2028-12-31 | 345 | M2 - Appendix A Approved | 38679000
MTEP21 | East | 20162 | Claremont 138 kV Station Rebuild | The proposed solution is to rebuild Claremont 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a five-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | METC | Other | Age and Condition | 2028-12-31 | 138 | M2 - Appendix A Approved | 24227000
MTEP21 | East | 20164 | Wealthy Street 138 kV Station Rebuild | The proposed solution is to rebuild Wealthy Street 138 kV station with a new control house at a new site just to the southwest of the existing site utilizing new equipment in a four-row, breaker-and-a-half scheme configuration. The new 138 kV station to be built will be called New Station. This new 138 kV station would reduce equipment failures, unplanned outages, and repair costs. In addition, it would enable routine maintenance to be performed again in a safe and efficient manner. | MI | METC | Other | Age and Condition | 2028-08-01 | 138 | M2 - Appendix A Approved | 24000000
MTEP21 | West | 20166 | Delano_Municipal_Utilities_Substation_A_Transformer_Upgrade | Facility Type: Transformer Project Description: Replace the Sub A 10 MVA 69/12.47kV transformer with a new 12/16/20 MVA 69/12.47kV transformer. System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformers. The Sub A transformer is 27 years old built in 1993, rewound once, and reaching the end of its life. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. Proposed Solution: Delano is planning to replace the Sub A transformer with a new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2021-04-05 | 69 | M2 - Appendix A Approved | 1750000
MTEP21 | East | 20167 | Cato – Corktown 120 kV | Build approximately 0.85 miles of 120kV 1600mm² underground cable from Cato to Corktown and expand the Cato and Corktown stations to accommodate a third line termination. | MI | ITC | Other | Local Reliability | 2027-12-31 | 120 | M2 - Appendix A Approved | 40000000
MTEP21 | West | 20168 | Delano_Municipal_Utilities_Substation_B_Transformer_Upgrade | Facility type: Transmission System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. Delano currently has two 10 MVA 69/12.47kV transformer. The Sub B transformer was original in 1970 and rewound in 1999. There has been another project submitted into MTEP 21 for the substation A transformer upgrade. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers in 2022 extra capacity is needed. With the Delano load forecast surpassing the combined 20 MVA rating of both transformers by 2022, extra capacity is needed. Proposed Solution: Delano is planning to replace substation B transformer with new 12/16/20 MVA 69/12.47kV transformer. This new transformer will meet the load growth forecasted for the city and provide reliability for its customers. Reconfiguration within the substation may also allow for more customers to be served in the event one of the two 69kV transformers is out of service. This solution also includes a new fire wall between the new transformers and additional distribution feeders for load transfer. | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2022-04-04 | 69 | M2 - Appendix A Approved | 2500000
MTEP21 | West | 20169 | Delano_Municipal_Utilities_New_69_kV_Industrial_Park_Substation | Facility Type: Substation Project Description: Build a new 69kV substation to serve expected residential and future industrial park load growth. System Need: Delano has recently updated it’s 10-year load forecast to add 6-8MW of new load starting as early as fall 2020 and escalating by middle of 2022. The downtown substation does not have room for expansion. A new substation next to the GRE Crow River 115/69kV substation will need the future load growth needs of Delano. Proposed Solution: Delano is planning to build a new 69kV substation to serve expected residential and future industrial park load growth on the NW side of the city. Please also refer to the attachment of a DGR study for the new substation request under "Attachments". | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2026-01-01 | 69 | M3 - Under Construction | 4100000
MTEP21 | West | 20173 | Quick-Sub 701 161 kV Line and Line Terminals | Construct a new Quick-Sub 701 161 kV line and line terminals.at Quick and Sub 701. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-06-01 | 161 | M2 - Appendix A Approved | 27250000
MTEP21 | West | 20177 | Missouri Valley East 69-13.2 kV Substation | Construct a new 69-13.2 kV distribution substation and associated 69 kV line work | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2028-06-01 | 69 | M2 - Appendix A Approved | 800000
MTEP21 | West | 20180 | ITCM Customer Interconnects with short lead time 2024 | These projects are being done at the request of an interconnection customer in order to facilitate new load, re-distribute existing load, improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA; IL; MN | ITC MIDWEST | Other | Load Growth | 2024-12-31 | 345 | M3 - Under Construction | 2400000
MTEP21 | Central | 20184 | New REOS 138 kV substation | Ring bus North of RS Wallace that ties together RS Wallace - Spring Bay and CAT2 - Hines 138 kV lines. | IL | AMEREN ILLINOIS | BRP |  | 2024-12-01 | 138 | M3 - Under Construction | 22400000
MTEP21 | Central | 20187 | Upgrade Chesterville 138 kV Substation | Add 2 line breakers | IL | AMEREN ILLINOIS | Other | Local Reliability | 2026-06-01 | 138 | M2 - Appendix A Approved | 3100000
MTEP21 | West | 20189 | Washburn: 161 kV Bus A Improvement | Washburn Bus A: Same upgrades needed on Bus A as are being completed on Bus B under T91PK. The 161 kV circuit switcher on 161-69 kV transformer does not interrupt faults | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-12-31 | 161 | M2 - Appendix A Approved | 3000000
MTEP21 | Central | 20190 | Rebuild Monroe City Jct - Petersburg Jct 69 kV line | 6960 Pt 3 Rbld Monroe City Jct_Petersburg Jct w/ 477acsr - 6.25 miles. Reconductor 2.4 miles of circuit 13825 (structures #844-1162 to #844-1190/#844-3100) and 1.2 miles of circuit 13838 where they are double-circuited with 6960. Replace Monroe City Jct #1 and #2 switches and rename to 69-1 and 69-2. Rebuild the line at the Petersburg Jct (poles #821-1322 through 821-1327). | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2025-10-31 | 138 | M2 - Appendix A Approved | 14060000
MTEP21 | Central | 20191 | Upgrade Marion N 138 kV Substation | Add line breakers, disconnect switches and circuit switcher | IL | AMEREN ILLINOIS | Other | Local Reliability | 2024-12-01 | 138 | M3 - Under Construction | 9300000
MTEP21 | West | 20192 | Rock Valley: Replace 69 kV Breakers & Relays | Replace two 69 kV oil circuit breakers and electromechanical line and bus relaying at Rock Valley Substation | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2025-07-15 | 69 | M2 - Appendix A Approved | 1100000
MTEP21 | Central | 20193 | Replace Breakers Program - MTEP21 | Breaker Upgrades Requested by Maintenance. Ameren Transmission has an initiative to replace about 35 Hitachi breakers (HVB) on the system. There were eight (8) inadvertent transmission interruptions in the period of 2014-2021 due to HVB breakers, which is a high percentage for such a small population. In addition, modern breakers have spring trip (stored energy) and air close (compressor) mechanisms while HVB breakers have air trip and spring close mechanisms. Having an air trip mechanism makes HVB breakers dependent on a hydraulic system to trip, which is prone to problems. Also having a stored energy for close operation means that workers have to be alert to controlling this energy when working on HVB breakers to avoid any accident. | IL; MO | AMEREN ILLINOIS | Other | Age and Condition | 2024-12-01 | 345 | M2 - Appendix A Approved | 20300000
MTEP21 | Central | 20194 | Replace Relays Program - MTEP21 | Electromechanical Relay Upgrades Requested by System Protection | IL; MO | AMEREN ILLINOIS | Other | Age and Condition | 2024-12-01 | 345 | M2 - Appendix A Approved | 7550000
MTEP21 | Central | 20195 | Replace Pole and Insulator Program - MTEP21 | Pole and Insulator replacements requested by Maintenance. 432 structures in Missouri. 320 structures in Illinois. | IL; MO | AMEREN ILLINOIS | Other | Age and Condition | 2024-12-01 | 345 | M2 - Appendix A Approved | 78600000
MTEP21 | Central | 20196 | New Rosston 69/12 kV substation | new sub to be fed from the 69182 ckt and will replace existing Whitestown 69/12kV sub in the 6983 ckt. | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-04-28 | 69 | M2 - Appendix A Approved | 1337000
MTEP21 | Central | 20206 | Rebuild Huntington 138 kV to Meridian Rd Jct 69 kV | 6923 Part 2 rebuild with 954acsr; replace switches at Erie Stone jct | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-05-12 | 69 | M2 - Appendix A Approved | 3540000
MTEP21 | Central | 20225 | Rebuild McKay Rd Jct. to H.E. Lewis Creek Jct. 69 kV line | Rebuild transmission line 6975 from McKay Rd Junction (pole #807-3096) to H.E. Lewis Creek Junction (pole #807-3168) using light duty steel poles, 477 ACSR conductor and OPGW. - 5.9 miles ; Replace two switches at McKay Rd Junction 2000A | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 7244000
MTEP21 | Central | 20227 | Reconfigure Middlefork 69 kV substation | Replace misc. 69kV OCBs and relays; replace 6910-01 line switch with 2000A; establish 69kV ring bus | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2024-12-05 | 69 | M3 - Under Construction | 12000000
MTEP21 | Central | 20228 | Reconfigure Prescott 345 kV substation | Replace misc. 69kV OCBs and relays; establish 345kV ring bus | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-06-04 | 345 | M3 - Under Construction | 9733000
MTEP21 | West | 20229 | J732 Stone Lake XFMR Upgrade | Transformer upgrade for J732 in Aug 17 ATC DPP cycle | WI | NORTHERN STATES POWER COMPANY | GIP |  | 2026-07-31 | 345 | M2 - Appendix A Approved | 5800000
MTEP21 | Central | 20245 | J805 Gwynneville Solar | J805 Gwynneville Solar | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-07-08 | 345 | M3 - Under Construction | 10835593
MTEP21 | Central | 20246 | J829 Fairbanks Solar | J829 Fairbanks Solar | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-05-31 | 345 | M3 - Under Construction | 16477181
MTEP21 | Central | 20247 | Rebuild Lafayette S. to Shadeland 138 kV line | Rebuild 138100 ckt with 954ACSR@120C - 3.2 miles | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2024-10-18 | 138 | M3 - Under Construction | 8180000
MTEP21 | South | 20265 | Glendale Capacitor Bank | Install 9.6 MVAR capacitor bank at Glendale. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Local Reliability | 2025-01-03 | 69 | M2 - Appendix A Approved | 1000000
MTEP21 | Central | 20607 | New Illinois Winds Pittsfield 69 kV Generator Interconnection | New Illinois Wind Panther Creek 44.5 MW Wind Farm connecting to the PPI Pittsfield 69 kV bus. | IL | PRAIRIE POWER, INC. | GIP |  | 2024-12-31 | 69 | M2 - Appendix A Approved | 6676401
MTEP21 | South | 20628 | J1158 Generator Interconnection at Vacherie 230 kV | Facilities required for the interconnection of J1158 at the existing Vacherie 230 kV substation. | LA | ENTERGY SERVICES, LLC. | GIP |  | 2025-09-01 | 230 | M2 - Appendix A Approved | 40000
MTEP21 | East | 20845 | Apache-Seneca 120kV Relocation | Relocate 9 structures of the Apache-Seneca 120kV circuit along Rochester Road in the city of Troy | MI | ITC | Other | Local Needs | 2024-12-31 | 120 | M2 - Appendix A Approved | 2040000
MTEP21 | East | 20885 | Cimmaron Interconnection | Install tap pole and 2 switches on White Cloud to Hesperia line section to allow Consumers to interconnect service for new Cimmaron substation. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Load Growth | 2025-12-31 | 69 | M2 - Appendix A Approved | 600000
MTEP21 | West | 20925 | Lancaster Transformer Replacement & Substation Rebuild | ATC will retire the Lancaster 138/69 kV transformer, 69 kV bus, and associated equipment and expand the 138 kV bus (box structure) and add bus-tie switches and space provisions for a future bus-tie breaker. In addition: - install 2 circuit breakers on line X-1 - replace the control house and relay equipment | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2026-02-28 | 138 | M3 - Under Construction | 6200000
MTEP21 | East | 21105 | Apollo Interconnection | Construct a new in-and-out station consisting of a single tie breaker and three straight buses with room for future tie breaker. Install one 120 kV tie breaker, two 120 kV line breakers, buswork, and associated disconnects. Connect two customer owned transformers to the new station. | MI | ITC | Other | Load Growth | 2025-12-31 | 120 | M2 - Appendix A Approved | 17147252
MTEP21 | East | 21170 | Lenox-Stephens- Henry Ford MH - Shrine | Henry Ford Macomb Hospital is a DTE interconnection request. ITCT will construct Shrine as a straight bus station with two line breakers and a section breaker. ITCT will extend the Lenox-Stephens 120kV line by adding about 1 mile of 954 DCT to loop in the new station. Fiber will be run from Bismarck 120kV station requiring fiber patches at Bismarck, Jewell, and Sigma 120kV station. Interconnection will require relaying upgrades at Lenox and Stephens. | MI | ITC | Other | Load Growth | 2024-12-31 | 345 | M3 - Under Construction | 17684839
MTEP21 | East | 21205 | Clinton Area Alternative | Wolverine proposes to utilize Wolverine’s existing Clinton station and double circuit line as an alternative to METC’s MTEP Project #20158. In order to address other future drivers, Wolverine also proposes to convert its Bradley to Clinton line from 69kV to 138kV that is additional to METC’s protection needs. See Exhibit 1 for one-line diagram of configuration (Warning – CEII information) The scope of work includes: • Reconfiguring Wolverine’s Clinton Station to create an in-and-out path for METC’s Delhi – Island Road 138kV line and accommodate the converted Bradley– Clinton 138kV line • Replacing 4/0 conductor on one circuit of Clinton’s double circuit line with 795ACSS • Replacing the Vermontville high side to accommodate 138kV operation • Replacing the Hastings high side to accommodate 138kV operation • Replacing the Otsego high side to accommodate 138kV operation • Rebuilding Wolverine’s Eaton Rapids 69 kV line to 138 kV design and relocating from Clinton Station to METC’s Delhi-Island Road line. • Replacing the Eaton Rapids high side to accommodate 138kV operation | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Local Reliability | 2026-12-31 | 138 | M2 - Appendix A Approved | 17000000
MTEP21 | East | 21206 | Coventry to Hager 120 kV Projects | Rebuild approximately 1 mile from Duvall tap to Hager utilizing 954 ACSR conductor on standard double circuit steel pole 120 kV structures. Disconnect the 954 ACSR conductor running north from the Baltic Tap and connect it to the 1431 ACSR conductor on the north side of the structures heading toward Coventry 120 kV. Remediate sag from Coventry to the Nitro cut-in to a target rating of 269 MVA SE. Install 3000 A 40 kA 120kV section breaker at Duvall 120 kV and all associated standard 3000 A 40 kA line breakers at Coventry and Hager 120 kV stations | MI | ITC | BRP |  | 2025-12-31 | 120 | M2 - Appendix A Approved | 13500000
MTEP21 | South | 21207 | Slidell Airport Line Move | Slidell airport expansion requires moving our North Slidell to Tailsheek 230 kV line and North Slidell to Cane Bayou 230 kV line. | LA | CLECO POWER LLC | Other | Local Needs | 2026-06-01 | 230 | M2 - Appendix A Approved | 9800000
MTEP21 | East | 21208 | Clinton Station Cut-in | Cut into the Island Rd – Delhi 138 kV line at the Clinton Junction with a new double tap structure and install pole top switches at the Packard and Eaton Rapids taps. Wolverine to utilize existing 795 ACSS conductor on the east side of the structures for the Clinton Rd – Delhi 138 kV circuit and reconductor the line on the west side of the structures utilizing 795 ACSS conductor to complete the Island Rd - Clinton 138 kV circuit | MI | METC | Other | Local Reliability | 2026-12-31 | 138 | M2 - Appendix A Approved | 3300000
MTEP21 | West | 21265 | Sub A Riverside 69 kV Upgrades | Replace 69 kV breakers and protective relaying. Also replace 161-69 kV Transformer Bank 8T1 and 8T2 with a new 161-69 kV, 125 MVA transformer. | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2026-12-31 | 161 | M3 - Under Construction | 10000000
MTEP21 | East | 21305 | North Belding - Control House Replacement | Install new Control House at North Belding 138kV station. Migrate relaying and vacate old control houses. Install SSVTs and Battery system. | MI | METC | Other | Local Reliability | 2025-05-15 | 138 | M2 - Appendix A Approved | 2976071
MTEP21 | Central | 21387 | Hancock County Capacitor Bank Addition | Add a 35 MVar capacitor bank on the 69 kV bus at the existing Hancock County substation. | KY | BIG RIVERS ELECTRIC CORPORATION | BRP |  | 2024-10-01 | 69 | M2 - Appendix A Approved | 500000
MTEP21 | West | 23368 | LRTP-01: Jamestown – Ellendale | Install single circuit 345kV transmission line (constructed with double circuit capable 345kV structures) from the existing Jamestown Substation, to the existing Ellendale Substation. | ND | Midcontinent Independent System Operator | MVP |  | 2028-12-31 | 345 | M2 - Appendix A Approved | 438700000
MTEP21 | West | 23369 | LRTP-02: Big Stone South – Alexandria – Big Oaks (Cassie’s Crossing) | Install single circuit 345kV transmission line from existing Big Stone South Substation, to the existing Alexandria Substation (constructed with double circuit capable 345kV structures), to the new Big Oaks Substation (Cassie’s Crossing). | MN; SD | Midcontinent Independent System Operator | MVP |  | 2030-06-01 | 345 | M2 - Appendix A Approved | 573500000
MTEP21 | West | 23370 | LRTP-03: Iron Range – Benton County – Big Oaks (Cassie’s Crossing) | Install double circuit 345kV transmission line from the existing Iron Range Substation, to the existing Benton Country Substation, to the new Big Oaks Substation (Cassie’s Crossing). | MN | Midcontinent Independent System Operator | MVP |  | 2030-06-01 | 500 | M2 - Appendix A Approved | 969900000
MTEP21 | West | 23371 | LRTP-04: Wilmarth – North Rochester – Tremval | Install single circuit 345kV transmission line from the existing Wilmarth Substation, to the existing North Rochester Substation, to the existing Tremval Substation. | MN; WI | Midcontinent Independent System Operator | MVP |  | 2028-06-01 | 345 | M2 - Appendix A Approved | 689140000
MTEP21 | West | 23372 | LRTP-05: Tremval – Eau Claire – Jump River | Install single circuit 345kV transmission line from the existing Tremval Substation, to the existing Eau Claire Substation, to the new Jump River Substation. | WI | Midcontinent Independent System Operator | MVP |  | 2028-06-01 | 345 | M2 - Appendix A Approved | 504500000
MTEP21 | West | 23408 | LRTP-06: Tremval – Rocky Run – Columbia | Install single circuit 345kV transmission line from the existing Tremval Substation, to the existing Rocky Run Substation, to the existing Columbia Substation. | WI | AMERICAN TRANSMISSION COMPANY | MVP |  | 2029-06-01 | 345 | M2 - Appendix A Approved | 1049700000
MTEP21 | West | 23409 | LRTP-07: Webster – Franklin – Marshalltown – Morgan Valley | Install single circuit 345kV transmission line from the existing Webster Substation, to the existing Franklin Substation, to the existing Marshalltown Substation (constructed with double circuit capable 345kV structures), to the existing Morgan Valley Substation. | IA | Midcontinent Independent System Operator | MVP |  | 2028-12-31 | 345 | M2 - Appendix A Approved | 755000000
MTEP21 | West | 23410 | LRTP-08: Beverly – Sub 92 | Install single circuit 345kV transmission line from the existing Beverly Substation to the existing Sub 92 Substation. | IA | Midcontinent Independent System Operator | MVP |  | 2028-12-31 | 345 | M2 - Appendix A Approved | 231000000
MTEP21 | West | 23411 | LRTP-09: Orient – Denny - Fairport | Install single circuit 345kV transmission line from the existing Orient Substation to a new Denny Substation, to the existing Fairport Substation. | IA; MO | Midcontinent Independent System Operator | MVP |  | 2030-06-01 | 345 | M2 - Appendix A Approved | 389900000
MTEP21 | Central | 23412 | LRTP-10: Denny – Zachary – Thomas Hill – Maywood | Install single circuit 345kV transmission line from the new Denny Substation to the existing Zachary Substation, to the existing Thomas Hill Substation, to the existing Maywood Substation. | MO | Midcontinent Independent System Operator | MVP |  | 2030-06-01 | 345 | M2 - Appendix A Approved | 768700000
MTEP21 | Central | 23413 | LRTP-11: Maywood – Meredosia | Install single circuit 345kV transmission line from the existing Maywood Substation to the existing Meredosia Substation. | IL; MO | Midcontinent Independent System Operator | MVP |  | 2028-06-01 | 345 | M2 - Appendix A Approved | 300800000
MTEP21 | West | 23414 | LRTP-12: Madison – Ottumwa – Coddington | Install single circuit 345kV transmission line from the existing Madison Substation, to the existing Ottumwa Substation, to the existing Skunk River Substation. | IA | Midcontinent Independent System Operator | MVP |  | 2029-06-01 | 345 | M2 - Appendix A Approved | 673000000
MTEP21 | Central | 23415 | LRTP-13: Coddington – Ipava | Install single circuit 345kV transmission line from the existing Coddington Substation to the existing Ipava Substation. | IA; IL | Midcontinent Independent System Operator | MVP |  | 2029-12-31 | 345 | M2 - Appendix A Approved | 594400000
MTEP21 | Central | 23416 | LRTP-14: Ipava – Maple Ridge – Tazewell – Brokaw – Paxton East | Install single circuit 345kV transmission line from the existing Ipava Substation, to the existing Maple Ridge Substation, to the existing Tazewell Substation, to the existing Brokaw Substation, to the existing Paxton East Substation. | IL | AMEREN ILLINOIS | MVP |  | 2028-06-01 | 345 | M2 - Appendix A Approved | 571700000
MTEP21 | Central | 23417 | LRTP-15: Sidney – Paxton East – Gilman South – Morrison Ditch | Install single circuit 345kV transmission line from the existing Sidney Substation, to the existing Paxton East Substation, to the existing Gilman South Substation, to the existing Morrison Ditch Substation. | IL; IN | Midcontinent Independent System Operator | MVP |  | 2029-06-01 | 345 | M2 - Appendix A Approved | 515579323
MTEP21 | Central | 23418 | LRTP-16: Morrison Ditch – Reynolds – Burr Oak – Leesburg – Hiple | Install single circuit 345kV transmission line from the existing Morrison Ditch Substation, to the existing Reynolds Substation, to the existing Burr Oak Substation, to the existing Leesburg Substation, to the existing Hiple Substation. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | MVP |  | 2029-06-01 | 345 | M2 - Appendix A Approved | 675420677
MTEP21 | East | 23419 | LRTP-17: Hiple – Duck Lake | Install double circuit 345kV transmission line from the existing Hiple to the new Duck Lake Substation. | IN; MI | Midcontinent Independent System Operator | MVP |  | 2030-06-01 | 345 | M2 - Appendix A Approved | 696200000
MTEP21 | East | 23420 | LRTP-18: Oneida – Nelson Rd. | Install double circuit 345kV transmission line from the existing Oneida Substation, to the existing Nelson Road Substation. | MI | Midcontinent Independent System Operator | MVP |  | 2029-12-29 | 345 | M2 - Appendix A Approved | 403400000
MTEP21 | Central | 3439 | New Ensor 161/69 kV Substation | Construct new 161/69 kV substation with 56 MVA transfomer. Include a 30 MVAR 69 kV capacitor | KY | BIG RIVERS ELECTRIC CORPORATION | BRP |  | 2024-12-31 | 161 | M2 - Appendix A Approved | 5800000
MTEP21 | West | 4247 | Sub 18 - Sub 85 161 KV reconductor | Reconductor the 161 kV line from Sub 85 to Sub 18 and uprate substation terminal equipment | IA; IL | MIDAMERICAN ENERGY CO. | Other | Local Needs | 2024-12-31 | 161 | M2 - Appendix A Approved | 4160000
MTEP22 | South | 15649 | Texas 138 kV: New Distribution Station | Cut the Texas substation in and out of the Lewis Creek to Goree 138 kV line. | TX | ENTERGY SERVICES, LLC. | Other | Load Growth | 2026-10-01 | 138 | M2 - Appendix A Approved | 19865081
MTEP22 | East | 15652 | Rebuild Atlanta to Gaylord 138kV | Rebuild 22 miles to Wolverine's 138 kV standard | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2026-12-31 | 138 | M2 - Appendix A Approved | 16500000
MTEP22 | East | 15875 | Kentucky - Luzon 120 kV Sag Remediation | Completely remove the sag limit on the Kentucky – Luzon 120 kV line. | MI | ITC | BRP |  | 2026-06-01 | 120 | M2 - Appendix A Approved | 500000
MTEP22 | East | 15910 | Marquette - Bingham 138 kV Rebuild | Rebuild 18.76 miles of the Marquette – Bingham circuit using 954 ACSR conductor with double-circuit steel structures. | MI | METC | Other | Local Reliability | 2026-12-31 | 138 | M2 - Appendix A Approved | 27600000
MTEP22 | West | 16766 | Small Capital Project and Asset Renewal Program 2023 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-01 | 345 | M3 - Under Construction | 34925540
MTEP22 | West | 16767 | Communications Reliability Program 2023 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2025-12-31 | 0 | M3 - Under Construction | 19593713
MTEP22 | West | 16769 | Physical Security Program 2023 | Physical Security projects typically have shorter project life cycles. The Physical Security Program is guided by the NERC Standard CIP-014 and is designed to harden substation infrastructure. Specific project locations and scopes of work are not made public. Initial capital spend for this program expected in 2023. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2028-12-31 | 345 | M3 - Under Construction | 1859619
MTEP22 | West | 16770 | Load Interconnection Program 2023 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2023. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2026-06-30 | 345 | M3 - Under Construction | 18045914
MTEP22 | West | 17868 | Duluth Loop 115 kV Project | Construct new 115 kV lines: Hilltop - Haines Road 115 kV and Haines Road - Ridgeview 115 kV Combine existing Arrowhead - Haines Road 115 kV and Haines Road - Swan Lake 115 kV lines to create Arrowhead - Swan Lake 115 kV Line Expand Ridgeview Substation to a ring bus which will allow 2 additional transmission line connections Add 115 kV line entrance at Hilltop and add a breaker at Haines Road | MN | MINNESOTA POWER INC. | BRP |  | 2026-12-31 | 115 | M2 - Appendix A Approved | 46900000
MTEP22 | East | 17999 | Re-conductor Corktown - Waterman 120 kV UG | The proposed solution is to re-conductor approximately 3.7 miles of the Corktown – Waterman 120 kV underground cable utilizing 5000 Kcmil underground cable. | MI | ITC | BRP |  | 2029-12-29 | 120 | M2 - Appendix A Approved | 7000000
MTEP22 | West | 18046 | Darlington – Rock Branch, (Y-109), 69kV, Rebuild & OPGW | T-Line Scope o Rebuild approximatley 14 miles of the Y-109 line from Darlington - Rock Branch o Install new conductor IT/Communications o Install fiber and terminate at substations Substation Scope o Fiber terminations at remote ends. o Asset Renewal of substation equipment: -Rock Branch: Replace disconnect switches, jumpers, strain bus and (1) breaker. -Darlington: Replace jumpers and strain bus section. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-06-15 | 69 | M2 - Appendix A Approved | 16700000
MTEP22 | West | 18047 | South Beaver Dam - Hubbard, (Y-134), 69kV Rebuild & OPGW | T-Line Scope to replace: • South Beaver Dam SS to Str 230: (~13.2 miles) • Str 230 to Hubbard: (~3.3miles) • Install new conductor and install new OPGW fiber Substation Scope • South Beaver Dam: replace jumpers and 600A switches, fiber terminations • Horicon: replace existing 336 jumpers, fiber terminations. • Hubbard: Fiber terminations, no other work planned. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-06-01 | 69 | M2 - Appendix A Approved | 20100000
MTEP22 | West | 18049 | Portage St - 3 Mile 69 kV (6901/ESE_6902), Re-insulate & Underground Fiber | 9 mile SW STA – Portage (6901/6902), 69kV, Re-insulate | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-01 | 69 | M3 - Under Construction | 8180000
MTEP22 | West | 18058 | Square Butte - Arrowhead HVDC Line Hardening | Structure replacements to improve HVDC line resiliency and restorability at critical locations, including transportation and infrastructure crossings. | MN; ND | MINNESOTA POWER INC. | Other | Local Reliability | 2027-12-31 | 250 | M2 - Appendix A Approved | 14000000
MTEP22 | Central | 18063 | New Skunk River 345 kV substation (fka Mt. Pleasant) | Maywood-Sub T Ring Bus Addition and Customer-Funded 69 kV Municipal Loop. At the request of Mt. Pleasant Municipal Utilities (MPMU), Ameren Missouri to construct three breaker, 345 kV substation west of Mt. Pleasant, Iowa, along Ameren Missouri's Maywood-Sub T Transmission Line. Ameren Transmission Company of Illinois (ATXI) to install 345/69 kV step-down transformer and construct 69 kV networked loop to interconnect MPMU's distribution substations. Now Skunk River 345 kV Substation | IA | AMEREN MISSOURI | Other | Load Growth | 2027-12-01 | 345 | M2 - Appendix A Approved | 2600000
MTEP22 | South | 18262 | Tarkington to New Long John 138 kV: Rebuild Line | Rebuild Tarkington to New Long John (L870). | TX | ENTERGY SERVICES, LLC. | BRP |  | 2024-12-31 | 138 | M2 - Appendix A Approved | 16130000
MTEP22 | West | 19525 | Saratoga SS - Control House and Breaker Asset Renewal | • Replace control building and contents • Replace 69kV oil breakers • Replace 2 CCVT’s • Install normally-open GOAB line switch outside the fence to enable the connection of radial lines Y-301 and Y-302 • Retire inoperable 922-A and 923-A breaker bypass switches which will no longer be required with the installation of the new GOAB • Reconductor 138kV Bus 2 to match the higher capacity X-43 line rating • Install Dual batteries to meet future TPL-002-2 standards | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-01 | 138 | M2 - Appendix A Approved | 8200000
MTEP22 | Central | 19945 | New Topeka-Bishop 69 kV Line | New Topeka--Bishop 69 kV line (~8-mile) w/ 556 MCM in MEC | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 5120000
MTEP22 | Central | 19950 | New St. David-Wee-Ma-Tuk-Canton 69 kV line | New St. David-Wee-Ma-Tuk-Canton 69 kV line (10.4-mile) in Spoon River Electric Cooperative | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 5596000
MTEP22 | Central | 19952 | Rebuild Walkerville-Eldred 69 kV line | Rebuild Rebuild Walkerville-Eldred 69 kV line (7.3-mile) in Illinois Electric Cooperative | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 3942000
MTEP22 | West | 19962 | Nelson Dewey - Bloomington 69 kV (Y-184), Rebuild and OPGW | The project scope is to rebuild and install OPGW on 69kV line Y-184 from Nelson Dewey SS to Bloomington SS, approximately 15 miles. Need drivers include asset renewal, increased ratings, and improved communications. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 23600000
MTEP22 | West | 19966 | Munising Area Reactive Power Project | Install one +/- 10 MVA, 69-kV STATCOM (Static Synchronous Compensator) at Munising substation | MI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2026-01-30 | 138 | M3 - Under Construction | 14400000
MTEP22 | South | 20063 | Choctaw - TVA French Camp 500 kV: Decommission Line | Decommission and demolish the existing Choctaw-TVA French Camp 500kV line that was recently acquired by Entergy in November of 2019 (~0.75mi). | MS | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2025-12-15 | 500 | M2 - Appendix A Approved | 1100000
MTEP22 | South | 20064 | Choctaw - Wolf Creek 500 kV: Build New Line | Utilize ~0.1mi of existing Choctaw-French Camp 500kV line to tie into Wolf Creek (Choctaw – French Camp 500 kV decommissioned with a separate project). Convert Wolf Creek 500kV switching yard to 4 breaker ring bus to accommodate 2nd line. | MS | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2025-12-15 | 500 | M2 - Appendix A Approved | 8600000
MTEP22 | West | 20074 | Two Islands 115 kV Project | Construction of new 115 kV switching station near the existing Tac Harbor Substation. Route North Shore-Tac Harbor and Mesaba Junction-Tac Harbor Ckt #1 & Ckt #2 into the new switching station. One capacitor bank will be added to the switching station and it will connect to a new GRE 115/69 kV Two Islands Substation | MN | MINNESOTA POWER INC. | Other | Local Reliability | 2024-12-31 | 115 | M2 - Appendix A Approved | 14100000
MTEP22 | West | 20077 | Hilltop 230 kV Reliability Project | Upgrade Hilltop 1TR to 373 MVA base 230/115 kV transformer. Add 230 kV breaker to high side of transformer. Disconnect Hilltop Tap from 3-Terminal 230 kV line and extend this tap 0.7 Miles to a new line entrance at Arrowhead 230 kV. | MN | MINNESOTA POWER INC. | BRP | Local Reliability | 2024-12-31 | 230 | M2 - Appendix A Approved | 13100000
MTEP22 | South | 20163 | Many Area Transmission Expansion | Tap the existing Fisher to Mansfield Compressor 230 kV line 8.3 miles from Fisher. From the Tap point build two new new 2.8 mile 230 kV lines to a new substation (Belmont) tapped into the Pelican to Loring and Loring to Many 138 kV lines. At Belmont substation add a 230/138 kV 300 MVA Auto. | LA | CLECO POWER LLC | BRP |  | 2025-06-25 | 230 | M2 - Appendix A Approved | 35689000
MTEP22 | East | 20182 | Northeast 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Northeast 120 kV bus. | MI | ITC | Other | Local Reliability | 2025-01-17 | 120 | M2 - Appendix A Approved | 3000000
MTEP22 | East | 20183 | Stephens 345kV 55 MVAR Reactor | Install a 345 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Stephens 345kV bus. | MI | ITC | Other | Local Reliability | 2025-02-14 | 230 | M2 - Appendix A Approved | 4340373
MTEP22 | East | 20185 | Warren 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Warren 120kV bus. | MI | ITC | Other | Local Reliability | 2026-12-31 | 120 | M2 - Appendix A Approved | 1800000
MTEP22 | East | 20186 | Mack 120kV 55 MVAR Reactor | Install a 120 kV, 55 MVAR shunt reactor along with a 3000 A synchronizing breaker and disconnect switches at Mack 120kV bus. | MI | ITC | Other | Local Reliability | 2025-03-21 | 120 | M2 - Appendix A Approved | 3231000
MTEP22 | West | 20385 | OTP Buffalo to Alice 115 kV Rebuild | Rebuild 7 miles of 115 kV line due to poor performance. | ND | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2026-12-31 | 115 | M2 - Appendix A Approved | 2000000
MTEP22 | West | 20505 | Blue Earth-South Bend Area Upgrades | Rebuild approx. 30 miles of 161 kV line and upgrade South Bend TR6 to a 336 MVA transformer. | MN | NORTHERN STATES POWER COMPANY | BRP |  | 2025-10-31 | 161 | M2 - Appendix A Approved | 26376000
MTEP22 | West | 20805 | Rock County Reliability Project | To address the limited connections, ATC is proposing to develop 345-138 kV connections at Kittyhawk. The specific scope is likely to be: •add two 500-MVA, 345-138 kV transformers at the Kitty Hawk substation •add a 138 kV line between the Kitty Hawk and Town Line Road substations •loop into Kittyhawk existing Paddock-Town Line and Town Line-Bass Creek 138 kV lines •uprate Rock River-Marine 138 kV line •increase ground grid fault capability at several nearby substations. | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2024-12-31 | 345 | M3 - Under Construction | 54000000
MTEP22 | West | 20946 | Poplar2 115/60 kV | Build a Poplar Oil Field 115/60 kV sub and a 115 kV line from the Poplar Trans sub to the Poplar Oil Field sub to tie into the 60 kV system near MDU's Poplar Oil Field load. | MT | MONTANA-DAKOTA UTILITIES CO. | Other | Load Growth | 2025-12-31 | 115 | M2 - Appendix A Approved | 8525000
MTEP22 | East | 21145 | J996 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Beecher - Morocco 138 kV circuit. | MI | METC | GIP |  | 2025-12-19 | 138 | M2 - Appendix A Approved | 6618732
MTEP22 | East | 21146 | J1172 Generator Interconnection | Build a new 138 kV, 3 breaker ring switching station cut in from the METC Dort - Garfield 138 kV circuit. | MI | METC | GIP |  | 2024-12-31 | 138 | M2 - Appendix A Approved | 8470670
MTEP22 | East | 21166 | Maple - J1062 Generator Interconnection | Build a new 345kV 3 breaker substation cut-in from the Lemoyne - Majestic 345kV circuit, and removal of terminal equipment at Majestic 345kV substation. | MI | ITC | GIP |  | 2027-06-01 | 345 | M2 - Appendix A Approved | 16434520
MTEP22 | Central | 21167 | New Menges Ditch 138/69 kV Substation | New 138/69kV Substation source from AEP's E. Elkhart substation. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2025-12-31 | 138 | M2 - Appendix A Approved | 42368620
MTEP22 | Central | 21168 | New Hiple to Northport 138kV Line | New Hiple to Northport 138kV line | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2024-12-31 | 138 | M2 - Appendix A Approved | 27527004
MTEP22 | Central | 2125 | Upgrade Centerton 138/69kV Bk 1 | Upgrade/replace existing 75MVA 138/69kV bank with 150MVA bank | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-10-02 | 138 | M2 - Appendix A Approved | 7969251
MTEP22 | Central | 21306 | New Whitetail 138 kV Substation | Ameren would construct a new 138 kV substation ring bus configuration on the existing Ameren Monument-Macomb West-1646 138 kV line near structure 97. PPI would construct a 138 kV line to connect their Golden 138/69 kV step down station. This is in support of PPI Interconnection. | IL | AMEREN ILLINOIS | Other | Load Growth | 2025-12-01 | 138 | M2 - Appendix A Approved | 8000000
MTEP22 | Central | 21326 | New Duff 138 kV Substation | 3-position initial, 4 ultimate ringbus on the Ipava-Meredosia E-1568 138 kV line for PPI Indian Creek 138/69kV substation. This is in support of a PPI Interconnection. | IL | AMEREN ILLINOIS | Other | Load Growth | 2026-06-01 | 138 | M2 - Appendix A Approved | 8000000
MTEP22 | West | 21345 | National - Presque Isle SW YD 138 kV (446), Re-insulate & OPGW | PR08836: Reinsulate ~50% of structures on the line with like for like porcelain bells. Replacement of structures (~15% based on ground inspection) for woodpecker damage. Install OPGW. PR09237: This fiber addition is also being done in a similar location and is being combined with this project to terminate UG fiber from structure 156 into the North Lake SS. PR09232: Rerate of line 446. This portion of the project was formerly in the Line Clearance Mitigation program and has been now combined with this project to create efficiencies for work being done on the same line. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-04-15 | 138 | M2 - Appendix A Approved | 18000000
MTEP22 | West | 21347 | Huiskamp - Ruskin 69 kV (6937), Partial Rebuild | Replace 23 legacy steel lattice towers with 23 new structures. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-03-31 | 69 | M3 - Under Construction | 7900000
MTEP22 | West | 21348 | Tower Dr - Pulliam 69 kV (P-16/R-70), Partial Rebuild | Rebuild and reroute ~1 mile of double circuit 69 kV transmission line from structure 12 to Pulliam on lines P-16/R-70. This would get structures out of the high-water area where they are susceptible to ice damage and would replace the aging river crossing conductor. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-04-01 | 69 | M2 - Appendix A Approved | 17200000
MTEP22 | Central | 21385 | Rebuild Austin-Taylorville South 138 kV line (1545) | Rebuild Austin-Taylorville South 138 kV line (1545) | IL | AMEREN ILLINOIS | Other | Age and Condition | 2024-12-01 | 138 | M2 - Appendix A Approved | 8900000
MTEP22 | Central | 21406 | Rebuild Sparta Tap 138 kV radial line | Rebuild Sparta Tap on the Tibbs-Sparta-1723 138 kV line due to issues found during inspections. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2029-12-01 | 138 | M2 - Appendix A Approved | 4300000
MTEP22 | East | 21445 | Donaldson Creek - White Lake 138 kV Rebuild (J1071) | Rebuild approximately 18.43 miles of the 336 ACSR conductor utilizing 954 ACSR on standard 138 kV double circuit structures with OPGW. Upgrade 336 ACSR Line Drop and 336 ACSR Bus at White Lake Position 188, as well as the 336 ACSR line drop at Donaldson Creek position BM11 to meet or exceed the summer emergency rating of the new conductor. | MI | METC | GIP |  | 2026-05-01 | 138 | M2 - Appendix A Approved | 33529131
MTEP22 | East | 21485 | Lawndale - Murphy 138kV Sag Remediation | The proposed solution is to remove sag limits on the Lawndale to Murphy 138 kV line to conductor limit. | MI | METC | BRP |  | 2027-12-31 | 138 | M2 - Appendix A Approved | 931000
MTEP22 | East | 21505 | Houghton Lake Interconnection | Create a three-breaker ring bus switching station. Install three 138kV breakers, buswork, and associated disconnects. Loop in the METC Bard Rd - Higgins 138kV circuit to the new switching station. Connect CE Houghton Lake Substation to new switching station. | MI | METC | Other | Load Growth | 2025-05-15 | 138 | M3 - Under Construction | 8472092
MTEP22 | South | 21565 | Ward Breaker Additions | Install five (5) breakers, one of which will be a transfer breaker, at AECC's Ward 115kV Switching Station. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Local Reliability | 2024-12-16 | 115 | M2 - Appendix A Approved | 3000000
MTEP22 | West | 21605 | Hibbing Transmission Exits | Rebuild two 115 kV lines coming into Hibbing Substation on double circuit structures and realign entrances to coordinate with Hibbing Substation Modernization Project (MTEP #18064) | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2027-12-31 | 115 | M2 - Appendix A Approved | 2000000
MTEP22 | West | 21608 | 105 & 106 Line Upgrade | Rebuild and upgrade the two short parallel Blackberry - Iron Range 230 kV Lines | MN | MINNESOTA POWER INC. | BRP | Local Reliability | 2024-12-31 | 230 | M2 - Appendix A Approved | 5931200
MTEP22 | West | 21627 | North Lake SS, Power Transformer Asset Renewal | Replace TG2, a 1971 vintage 138/69 kV 47 MVA power transformer with a new 138/69 kV 60 MVA replacement. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-31 | 138 | M2 - Appendix A Approved | 4221065
MTEP22 | West | 21628 | Rockdale and Christiana SS - Control House and Relay Asset Renewal | • Replace Rockdale 138kV control building and contents, reusing three bus differential panels installed in 2011 as appropriate. • Replace X-65 and X-66 line relay panels at Christiana SS and coordinate with Rockdale work. • Install Dual batteries to meet future TPL-002-2 standards in the Rockdale 138kV building. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-01 | 345 | M2 - Appendix A Approved | 5800000
MTEP22 | West | 21629 | Oak Creek, Racine SS and Remote Ends, Control Buildings and Relaying Asset Renewal | • Replace control building and contents at Racine and Oak Creek 138kV. • Replace 9 138kV oil breakers at Racine, Dewey and Lincoln • Replace 21 138kV Model ACBL, ATA-2A and MK-40 at Dewey and Racine • Install approximately 35 relay panels • Provide room for WEC distribution equipment at Racine, demo existing building | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-05-31 | 345 | M3 - Under Construction | 31352034
MTEP22 | Central | 21645 | New Prairie Solar (J1139) Interconnection at Sidney 138kV | One 138 kV terminal in the Sidney Substation. The terminal will consist of all necessary terminal equipment to connect the J1139 leadline to the Sidney Substation 138 kV bus. | IL | AMEREN ILLINOIS | GIP |  | 2024-12-01 | 138 | M2 - Appendix A Approved | 500000
MTEP22 | East | 21665 | Day Interconnection | New ROW and line for interconnection | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Load Growth | 2025-06-01 | 138 | M2 - Appendix A Approved | 3500000
MTEP22 | West | 21686 | Mesaba Junction 137 Line Extension | Add breaker and transmission line entrance to Mesaba Junction Switching Station. Extend existing Embarrass - Babbitt 115 kV Line to switching station and establish a normal open between the Babbitt Tap and the Argo Tap | MN | MINNESOTA POWER INC. | BRP |  | 2026-03-31 | 115 | M2 - Appendix A Approved | 9000000
MTEP22 | East | 21726 | Warren 120kV Pos JJ Station Equipment Upgrade | Replace station equipment at Warren to meet or exceed 528 MVA (2540 Amps) | MI | ITC | BRP |  | 2026-12-31 | 120 | M2 - Appendix A Approved | 160000
MTEP22 | East | 21745 | Cato - Waterman 120 kV Re-conductor | The Cato – Waterman 120 kV underground cable is projected to overload for P11 and P6 contingencies during peak load. The limiting elements on this circuit are the cable conductor. | MI | ITC | BRP |  | 2029-12-31 | 120 | M2 - Appendix A Approved | 15000000
MTEP22 | Central | 21746 | New Bluff Hall-E. Hannibal 69 kV line | New Bluff Hall-E. Hannibal 69 kV line (~9-mile) 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 4184000
MTEP22 | Central | 21749 | New Bluff Hall 69 kV Substation | New Bluff Hall (Was Trailblazer) 69 kV breaker substation near Marblehead, IL. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2025-12-31 | 69 | M2 - Appendix A Approved | 2935000
MTEP22 | Central | 21750 | New Rock Creek 69 kV Substation | New Rock Creek 69 kV breaker station near Ursa substation in Adams Electric Cooperative. Breaker station will have terminals looking towards Elvaston, Golden, and Payson. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 2935000
MTEP22 | Central | 21751 | New Paragon 138/69 kV Substation | New Paragon 138/69 kV substation near Pana, IL in Shelby Electric Cooperative. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 138 | M2 - Appendix A Approved | 8995000
MTEP22 | Central | 21752 | New Paragon-Pana Tap 69 kV line | New Paragon-Pana Tap 69 kV line (~2.5-mile) in Shelby Electric Cooperative (Previously Panther) | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 4575500
MTEP22 | Central | 21753 | New Pana Tap-Lakewood 69 kV line | New Pana Tap-Lakewood 69 kV line (~12-mile) in Shelby Electric Cooperative | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 7680000
MTEP22 | Central | 21754 | New ISHI-Herrick 69 kV line | New ISHI-Herrick 69 kV line (~9.7-mile) in Shelby Electric Cooperative. This is part of the line from Panther to ISHI. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 6973000
MTEP22 | Central | 21755 | Rebuild Hadley Breaker-Barry 69 kV line | Rebuild portion of Hadley Breaker-E. Hannibal Tap 69 kV line | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 350000
MTEP22 | Central | 21756 | Rebuild Hadley Breaker-Hadley 69 kV line | Rebuild Hadley Breaker-Hadley 69 kV line | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 880000
MTEP22 | Central | 21757 | Rebuild Barry-Liberty 69 kV line | Rebuild portion of Barry-Liberty 69 kV line (6.35-mile) between Illinois Electric Cooperative and Adams Electric Cooperative. | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 3375000
MTEP22 | Central | 21758 | Rebuild Kampsville-Kampsville River Crossing 69 kV line | Rebuild Kampsville-Kampsville River Crossing 69 kV line (0.7-mile) in Illinois Electric Cooperative | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 650000
MTEP22 | Central | 21760 | New Rushville 69 kV Substation | New 69 kV Rushville breaker substation in Adams Electric Cooperative. Terminals will look to Golden and Liberty. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 2950000
MTEP22 | West | 21766 | 126 Line Asset Renewal | Replace transmission line structural components on Little Fork - I.Falls 115 kV Line, replace Little Fork 126L breaker, and replace relay panels on both ends of 126 Line | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2024-12-31 | 115 | M3 - Under Construction | 750000
MTEP22 | East | 21785 | Grawn Station Protection System Update | Replace obsolete electromechanical relays that require replacement by modern digital relays. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2024-12-31 | 69 | M2 - Appendix A Approved | 2000000
MTEP22 | East | 21787 | Westwood 138kV Interconnection | The Westwood Transmission station was fully rebuilt in 2009 and can accommodate the addition of a new 138kV/69kV power transformer. This project includes adding the power transformer, bus equipment, and protection systems, to accommodate the addition of a 138kV line terminal. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2027-12-31 | 138 | M2 - Appendix A Approved | 20500000
MTEP22 | Central | 21788 | Rebuild Andrew-Barclay 69 kV line | Rebuild Andrew-Barclay 69 kV line (~7.5-mile) in Menard Electric Cooperative. Replace 4/0 ACSR line built in 1964 with 556.5 MCM ACSR conductor. | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 3755000
MTEP22 | Central | 21789 | Rebuild Lanesville-Barclay 69 kV Line | Rebuild ~11.5-mile Lanesville to Barclay 69 kV line in Menard Electric Cooperative. Replace 4/0 ACSR line built in 1964 with 556.5 MCM ACSR conductor. | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2029-12-31 | 69 | M2 - Appendix A Approved | 6045000
MTEP22 | Central | 21791 | Rebuild E. Lanesville-Lanesville 69 kV line | Rebuild E. Lanesville-Lanesville 69 kV line (~0.9-mile) in Menard Electric Cooperative. Replace 336.4 MCM ACSR line built in 1981 with 556.5 MCM ACSR conductor. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2024-12-31 | 69 | M2 - Appendix A Approved | 450000
MTEP22 | Central | 21792 | Rebuild Fancy Creek-Andrew 69 kV line | Rebuild Fancy Creek-Andrew 69 kV line (~4.5-mile) in Menard Electric Cooperative. Replace 336.4 MCM ACSR line built in 1969 with 556.5 MCM ACSR conductor. | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2029-12-31 | 69 | M2 - Appendix A Approved | 2450000
MTEP22 | Central | 21793 | New Forest City-Bishop 69 kV line | New Forest City-Bishop 69 kV line (~2-mile) in Menard Electric Cooperative. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-31 | 69 | M2 - Appendix A Approved | 790600
MTEP22 | Central | 21794 | New Forest City 138/69 kV Substation | New 138/69 kV substation near Forest City, IL in Menard Electric Cooperative. This substation will connect to the Ameren Havana to Cincinnati 138 kV line at Winnebago on the high side and to the Menard Electric Cooperative Forest City to Bishop 69 kV line on the low side with an 84 MVA transformer, | IL | PRAIRIE POWER, INC. | BRP |  | 2026-12-31 | 138 | M2 - Appendix A Approved | 7725000
MTEP22 | Central | 21795 | New Middletown 69 kV Substation | New 69 kV breaker substation near Middletown, IL in Menard Electric Cooperative. Substation will have terminals looking to Fancy Creek, Grand Island, Forest City, and Middletown Distribution substation. | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2028-12-31 | 69 | M2 - Appendix A Approved | 3200000
MTEP22 | South | 21811 | Richard 500-138 kV AT1 Relay Improvement SPOF | Ensure the Richard 500-138 kV autotransformer #1 and 500 kV lines have redundant high-speed protection with independent CT and PT windings. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2028-11-01 | 500 | M2 - Appendix A Approved | 10270000
MTEP22 | West | 21824 | Riverton – Wing River Storm Structures | Install storm structures in the Riverton – Wing River 230 kV line. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2024-11-26 | 230 | M3 - Under Construction | 879672
MTEP22 | West | 21828 | Agency Street New Control Enclosure & Relay Replacements | The relays at Agency Street are approaching their 20 year end of life. ITC will install a new control enclosure with all new relays to provide ITC a separate control enclosure from IPL and minimize required outages and outage times for the relay replacements. All necessary outages should be coordinated with IPL. Also coordinate with IPL on location of new control building as this is an IPL owned site. | IA | ITC MIDWEST | Other | Age and Condition | 2026-03-31 | 69 | M2 - Appendix A Approved | 2090891
MTEP22 | West | 21833 | Mallard Facility Rebuild | Joint NSP - Central Power facility rebuild. NSP substation grading and fencing, 3 new box structures, control and wiring modifications to accommodate Central Power equipment moves | ND | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-31 | 115 | M3 - Under Construction | 5800000
MTEP22 | South | 21835 | Kaiser 230-115 kV Autotransformer | Install 300 MVA, 230/115kV Autotransformer to tie Kaiser 230 kV to Conquest 115 kV. Kaiser and Conquest stations are adjacent to each other. Remove Behrman to Pt Nickel 115 kV line from the model. This facility includes an under the Mississippi River section that has failed. The Kaiser Auto alleviates some of the potential radial concerns during outages with this line removed. | LA | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2025-03-01 | 230 | M2 - Appendix A Approved | 26320002
MTEP22 | Central | 21836 | Replace Sunnyside 345 kV and 138 kV Breakers | Replacement of three (3) 345 kV breaker #21, #22 & #23 and two (2) 138 kV breakers #1, & #3 | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-09-26 | 345 | M3 - Under Construction | 5100000
MTEP22 | Central | 21838 | Replace Southwest 138 kV Breakers | Replacement of five (5) 138 kV breakers #4, #5, #3, #26, #27 | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2024-11-27 | 138 | M2 - Appendix A Approved | 4500000
MTEP22 | Central | 21839 | Replace West 138 kV Breakers | Replacement of three (3) 138 kV breakers #1, #4, #7 | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Age and Condition | 2025-06-01 | 138 | M3 - Under Construction | 2959740
MTEP22 | West | 21842 | Jasper County Control Enclosure and Relay Replacements | A new Control Enclosure is required at the Jasper County Substation due to age and condition. ITC will install a new Control Enclosure with all new relays. | IA | ITC MIDWEST | Other | Age and Condition | 2025-08-15 | 161 | M2 - Appendix A Approved | 2486897
MTEP22 | South | 21843 | Neches River Crossing Structure Mitigation | Mitigation includes: Replace coffers, de-water and excavate soils Perform structure foundation inspection(s), fortify/repair where possible Restore soils around structure foundations, fill coffers to grade | TX | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2025-08-26 | 138 | M2 - Appendix A Approved | 28000000
MTEP22 | West | 21845 | NSPM Metro Steel Pole Replacement | Address painted poles concerns between Riverside Sub and Main Street Sub. Approximately 4-mile of triple circuit structure(35-structures) to be either replaced, painted or a combination of replace/paint | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-15 | 115 | M2 - Appendix A Approved | 21000000
MTEP22 | West | 21846 | Hyland Lake TR1 and TR2 Upgrade | Upgrade TR1 and TR2 to 115/13.8 kV 70 MVA transformers at Hyland Lake Substation. Install high-side line breaker. Install new feeder bay. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2024-10-15 | 115 | M2 - Appendix A Approved | 6407000
MTEP22 | West | 21853 | North Fork Sub Expansion | Retire the Flambeau breaker station and will add MOD’s to the switches at North Fork substation | WI | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2024-12-01 | 35 | M2 - Appendix A Approved | 1500000
MTEP22 | Central | 21867 | Rebuild Marktown 138 kV Substation | Rebuild Marktown 138kV Substation | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2024-12-31 | 138 | M2 - Appendix A Approved | 30190251
MTEP22 | West | 21868 | Canistota Junction Cap Bank Retirement | This cap bank is no longer needed to support the area and will be retired to prevent unnecessary maintenance costs on the system. | MN | NORTHERN STATES POWER COMPANY | Other | Local Needs | 2022-12-20 | 69 | M3 - Under Construction | 200000
MTEP22 | West | 21869 | BRI CHB 34.5kV Cap Bank Retirement | Retire 34.5kV cap banks at Buffalo Ridge/Chanarambe feeders BRI311, BRI312, and CHB341. | MN | NORTHERN STATES POWER COMPANY | Other | Local Needs | 2024-07-15 | 35 | M2 - Appendix A Approved | 1500000
MTEP22 | West | 21871 | Sub E East Moline 69 kV Upgrades | Replace aged equipment at Sub E East Moline. Project includes installing a new control building, replacing 69 kV oil circuit breakers, and replacing 69 kV cap-and-pin switches and insulators. | IL | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2028-12-31 | 69 | M2 - Appendix A Approved | 10000000
MTEP22 | West | 21872 | Sub E East Moline-Sub 37 69 kV OPGW Installation | Install OPGW on the Sub E East Moline-Sub 37 69 kV Line | IL | MIDAMERICAN ENERGY CO. | Other | Local Needs | 2028-12-31 | 69 | M2 - Appendix A Approved | 1500000
MTEP22 | West | 21873 | Sub 39-Sub 28 161 kV OPGW Installation | Install OPGW on the 161 kV line from Sub 39-Sub 28 | IL | MIDAMERICAN ENERGY CO. | Other | Local Needs | 2028-12-31 | 161 | M2 - Appendix A Approved | 270000
MTEP22 | Central | 21875 | Rebuild Lagrange 69 kV line-Circuit 6980 | Rebuild 6 miles of circuit 6980 | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2026-12-31 | 69 | M2 - Appendix A Approved | 6000000
MTEP22 | Central | 21881 | Upgrade Transmission Substation - 2024 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2024-12-31 | 345 | M2 - Appendix A Approved | 32711473
MTEP22 | Central | 21882 | Upgrade transmission lines - 2024 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2024-12-31 | 345 | M2 - Appendix A Approved | 31312504
MTEP22 | Central | 21883 | Upgrade Transmission Substation - 2025 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, and protection and communication equipment. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2025-12-31 | 345 | M2 - Appendix A Approved | 26977092
MTEP22 | Central | 21884 | Upgrade transmission lines - 2025 program | Rebuilds/upgrades 69 kV and up line based on age and condition, including structures, conductor, switches and communication upgrades (fiber) | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2025-12-31 | 345 | M2 - Appendix A Approved | 30216017
MTEP22 | Central | 21885 | Upgrade Transmission Substation - 2026 Program | Upgrades/replacements 69 kV and up Substation based on age and condition, including but not limited to switches, breakers, transformers, protection and communication equipment. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2026-12-31 | 345 | M2 - Appendix A Approved | 54852316
MTEP22 | Central | 21886 | Upgrade transmission lines - 2026 program | Rebuilds/upgrades 69 kV and up lines based on age and condition, including structures, conductor, switches and communication upgrades (fiber). | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Age and Condition | 2026-12-31 | 345 | M2 - Appendix A Approved | 68286845
MTEP22 | West | 21889 | Hettinger 115/69/41.6 | Rebuild Hettinger Substation 115/69/41.6 due to age and condition | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Age and Condition | 2028-12-31 | 115 | M2 - Appendix A Approved | 6500000
MTEP22 | East | 21890 | Gallagher - Ogemaw 138 kV Sag Remediation | Remediate sag on the 336 ACSR conductor on the Gallagher to Ogemaw 138 kV circuit up to at least 60 MVA summer emergency rating. | MI | METC | BRP |  | 2026-06-01 | 138 | M2 - Appendix A Approved | 660000
MTEP22 | West | 21891 | Line 0726 Rebuild | NSM 0726-69kV Line Major line rebuild from Pipestone to Tracy Switching Station. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2024-12-21 | 69 | M2 - Appendix A Approved | 17150000
MTEP22 | West | 21894 | Retire Tioga 1 | Retire Tioga 1, expand Tioga 2 to move the 60 kV lines from Tioga 1 to Tioga 2 along with a 115/60 kV transformer, move 115 kV lines position in station and add another 115 kV breaker. | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Age and Condition | 2024-12-31 | 115 | M2 - Appendix A Approved | 7050000
MTEP22 | West | 21896 | NE 94th Avenue 161-13.2 kV Substation | Construct NE 94th Ave 161-13.2 kV substation and taps | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2024-11-01 | 161 | M3 - Under Construction | 6700000
MTEP22 | West | 21897 | Berwick 161-13.2 kV Substation | Construct Berwick 161-13.2 kV substation and taps | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2028-06-01 | 161 | M2 - Appendix A Approved | 6700000
MTEP22 | West | 21898 | Increase Bus Withstand Capabiities | At Raun 161 kV, Neal North 161 kV, CBEC 161 kV, Sycamore 161 kV and Sycamore 69 kV, replace insulators, install new bus supports and/or replace bus to increase bus withstand capabilities | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2028-12-04 | 161 | M2 - Appendix A Approved | 8000000
MTEP22 | West | 21899 | Port Washington – Saukville 138 kV (X-132/X-133) partial rebuild | Full rebuild of 3.5 miles of X-132/X-133 and reconductor only for the remaining 1.4 miles due to newer steel poles -Use ATC standard T2 Dove ACSR 556 conductor -Replace legacy lattice towers, install new OPGW and static line | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2025-05-15 | 138 | M3 - Under Construction | 9194000
MTEP22 | West | 21901 | Raun Substation: 345 kV Switch Replacements | Replace 10 switches due to condition | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2024-12-01 | 345 | M3 - Under Construction | 1800000
MTEP22 | West | 21902 | Anthon Substation | Construct a new 69-12.47 kV distribution substation and associated 69 kV line work. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2028-12-01 | 69 | M2 - Appendix A Approved | 1500000
MTEP22 | West | 21904 | Sioux Center Substation | Construct a new 69-12.47 kV distribution substation and associated 69 kV line work. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2024-10-15 | 69 | M3 - Under Construction | 600000
MTEP22 | West | 21908 | Carroll County-Auburn-Sherwood 69 kV Line Rebuild & Terminal Upgrades | Rebuild 69 kV lines from Carroll County to Auburn and Auburn to Sherwood and replace line structures. | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2026-12-01 | 69 | M2 - Appendix A Approved | 15000000
MTEP22 | West | 21909 | Sac City Switching Station & Rebuild of Sac County-Odebolt-Schaller 69 kV Line | Construct new Sac City switching station to interconnect two MidAmerican 69 kV lines and one Corn Belt 69 kV line | IA | MIDAMERICAN ENERGY CO. | BRP |  | 2027-09-01 | 69 | M2 - Appendix A Approved | 41200000
MTEP22 | West | 21912 | Substation J 161 kV Capacitor Bank Replacement | Replace 161 kV capacitor due to condition and operational failures. | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2024-12-31 | 161 | M2 - Appendix A Approved | 1700000
MTEP22 | West | 21913 | Northgate Substation: Ring bus expansion and 161 kV tie line to ITCM’s Rose Hollow Substation | Expand Northgate Substation to a ring bus configuration and build 161 kV tie line from Northgate Substation to ITCM owned Rose Hollow Substation | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-06-01 | 161 | M2 - Appendix A Approved | 3500000
MTEP22 | West | 21914 | Butler 161-69 kV Transformer | Install 161-69 kV, 125 MVA Transformer at Butler Substation to accommodate a networked 69 kV system between MidAmerican’s Butler, New Hartford and Shell Rock Substations and Corn Belt’s Donald Feldman Switching Station. MTEP21. The project also include upgrading 34.5 kV lines from Butler to New Hartford and New Hartford to Shell Rock to 69 kV lines. | IA | MIDAMERICAN ENERGY CO. | BRP |  | 2025-12-31 | 161 | M3 - Under Construction | 29200000
MTEP22 | West | 21915 | Fitzgerald SS – Transformer and Breaker Asset Renewal | • Replace T1, a 1972 vintage 345/138 kV, 336 MVA power transformer with a new 345/138 kV 500 MVA standard three phase transformer • Replace three 138 kV oil circuit breakers with SF6 gas, eliminating all oil breakers at this station. • Replace one 138 kV 1600 A disconnect switch and associated jumpers • Remove bus arresters off bus 4 and install line arresters | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-31 | 345 | M2 - Appendix A Approved | 9488415
MTEP22 | West | 21916 | Browntown - South Monroe 69 kV (Y-155), Rebuild | Rebuild approximately 8.3 miles on Y-155 from Browntown substation to South Monroe substation and install OPGW. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 14600000
MTEP22 | West | 21917 | West Marinette SS – Transformer and Breaker Asset Renewal | West Marinette SS – Transformer and Breaker Asset Renewal | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2025-12-01 | 138 | M2 - Appendix A Approved | 8962353
MTEP22 | West | 21918 | Pine River - Mich Limestone Loading Dock 69 kV (ESE_6906), Rebuild | • T-Line rebuild of approximately 25.5 miles with steel poles and reconductor • Construction: o Utilize two winter cycles for constructability | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 31100000
MTEP22 | West | 21923 | Everett GIS Asset Renewal | -Rebuild the GIS substation in the same location and re-use existing HPFF (High-Pressure-FluidFilled) terminations | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2026-04-30 | 138 | M2 - Appendix A Approved | 22645727
MTEP22 | West | 21925 | Plymouth Reliability Project | New 138-kV/12.47-kV interconnection substation to be named the Plymouth 5 Substation. New double-circuit 138-kV transmission line approximately 8.0 miles in length from the Saukville-Elkhart Lake 138-kV line (8241) to loop in and out of the new Plymouth 5 Substation. Plymouth Utilities will install two distribution transformers with this project. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2026-03-01 | 138 | M2 - Appendix A Approved | 41100000
MTEP22 | West | 21926 | Harbor – Russell Terminal 138 kV (893K11), Rebuild | Norwich - Harbor 138kV, (893K11), underground line replacement | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2029-11-01 | 138 | M2 - Appendix A Approved | 61200000
MTEP22 | West | 21929 | Forks Switching Station & Forks-Rost 161kV Circuit | As part of a joint study to serve load expansion in Worthington, MN, ITC will construct a 161kV circuit between new Forks switching station and GRE Rost substations. | MN | ITC MIDWEST | BRP |  | 2026-12-31 | 161 | M2 - Appendix A Approved | 13456200
MTEP22 | West | 21930 | Millstream 69kV Switching Station | ITC has been working with Amana Society on way to improve reliability to their substation, and ITC will be building a new 69 kV switching station called “Millstream” adjacent to the existing Amana Society substation to improve area transmission system reliability. | IA | ITC MIDWEST | Other | Local Reliability | 2026-03-31 | 69 | M2 - Appendix A Approved | 7748400
MTEP22 | West | 21933 | Fox Lake Relay, Breaker, & SCADA Replacements | ITC will replace all of its relays and SCADA equipment as well as remove the existing carrier equipment/wave trap at the Fox Lake substation. Circuit Breaker 736 will also be replaced at Fox Lake substation. | IA; MN | ITC MIDWEST | Other | Age and Condition | 2025-12-31 | 161 | M2 - Appendix A Approved | 2651016
MTEP22 | West | 21935 | Hayward Transformer Replacement | ITC will replace the two 161/69kV transformers at Hayward Substation with a single 150 MVA 161/69kV unit. To make room for the new 161kV bus tie breaker. ITC will move the Glenworth – Hayward 161kV terminal to the opposite side of the Hayward – Murphy Creek 161kV terminal. | MN | ITC MIDWEST | Other | Age and Condition | 2025-12-31 | 161 | M2 - Appendix A Approved | 6744271
MTEP22 | West | 21936 | Centerville Cooper Creek 69kV Interconnection | IPL will be building a new 69/25x12.5 kV substation named “Centerville Cooper Creek” adjacent to the existing Centerville North substation on the location of the old combustion turbines. This new substation will replace the existing IPL/ITC Centerville North Substation and accommodate future area load growth as well as IPL’s future conversion to 25 kV distribution. IPL will be installing two 12/20 MVA transformers at the new Centerville Cooper Creek substation. For the ITC owned portion of Centerville North, ITC will build a new 69 kV substation with two single boxes, two line breakers, and a bus tie breaker. Once the new Centerville Cooper Creek substation is in-service, the existing Centerville North substation will be retired. | IA | ITC MIDWEST | Other | Load Growth | 2026-06-30 | 69 | M2 - Appendix A Approved | 3708274
MTEP22 | West | 21937 | Chariton North 69kV Substation Interconnection | IPL will be building a new 69/26.2 kV Substation named Chariton North. IPL will be installing one 69/26.2 kV 20/33 MVA or 30/50 MVA transformer initially but is planning the substation to accommodate a second 69/26.2 kV 20/33 MVA or 30/50 MVA transformer when all the load is added. All the ITC 69 kV substation equipment will be capable of 1200A or greater. The 69 kV lines to the new substation will be T2-4/0 or larger and will be the standard 69 kV construction. | IA | ITC MIDWEST | Other | Load Growth | 2027-07-02 | 69 | M2 - Appendix A Approved | 6836817
MTEP22 | West | 21938 | Worthington Sub 2 Breaker | A breaker will be added to Worthington Public Utilities(WPU) Sub #2. The breaker will protect for a fault between Sub #2 and Elk. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Local Reliability | 2025-02-01 | 69 | M3 - Under Construction | 375000
MTEP22 | West | 21939 | Cedar Rapids Hunter Field Substation Expansion | IPL has notified ITC that it will be adding a 3rd 161x69/24.9 kV transformer at the Hunter Field Substation. ITC will need to add an additional breaker and bus to connect the new IPL transformer at Hunter Field. All new ITC equipment to be designed to 161 kV specs to allow future conversion of the substation to 161 kV operation. Substation will initially be operated at 69 kV. | IA | ITC MIDWEST | Other | Local Reliability | 2027-12-31 | 69 | M2 - Appendix A Approved | 1284996
MTEP22 | West | 21940 | Turkey River to Guttenburg 69kV Rebuiild | The 9.04 mile Turkey River – Guttenberg 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Turkey River and Monona. | IA | ITC MIDWEST | Other | Age and Condition | 2029-12-31 | 69 | M2 - Appendix A Approved | 10376400
MTEP22 | West | 21941 | Guttenburg to Garnavillo 69kV Rebuild | The 11.23 mile Guttenberg - Garnavillo 69 kV line along with the 0.18 mile tap to Garnavillo are at the end of their useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Guttenberg and Monona. | IA | ITC MIDWEST | Other | Age and Condition | 2028-12-31 | 69 | M2 - Appendix A Approved | 14391600
MTEP22 | West | 21942 | Garnavillo to Elkader 69kV Rebuild | The 7.63 mile Garnavillo - Elkader 69 kV line is at the end of its useful life and needs to be rebuilt. New line should be rebuilt with T2-4/0 ACSR conductor and OPGW for future communications path between Garnavillo and Elkader. | IA | ITC MIDWEST | Other | Age and Condition | 2029-12-31 | 69 | M2 - Appendix A Approved | 10012800
MTEP22 | West | 21943 | Rose Hollow Add 161kV Terminal for North Gate line | MidAmerican has notified ITC that they will be building a new 161 kV line from their exiting North Gate substation to the ITC Rose Hollow substation. Per the terms of the agreement with MidAmerican, ITC will need to install a new 161 kV terminal at Rose Hollow for the new line to North Gate. | IA | ITC MIDWEST | Other | Local Reliability | 2026-07-01 | 161 | M2 - Appendix A Approved | 984000
MTEP22 | East | 21945 | Parr Road-Whiting 138kV Rebuild | Rebuild approximately 12 miles from Parr Rd - Tangent (J875 Generator Interconnection) and approximately 28.6 miles from Raisin Tap - Whiting on 138kV future double circuit steel poles with 1431 ACSR conductor with OPGW (coordinating with J875 Generator Interconnection project). | MI | METC | Other | Local Reliability | 2028-12-01 | 138 | M2 - Appendix A Approved | 60338593
MTEP22 | West | 21946 | Pelican-Triboji 69kV Rebuild | Two sections of the Pelican-Triboji 69kV line are near end of life and in poor condition. The line between Pelican and structure 162 (~1.04 miles) and the line between Triboji and structure 72 (~4.45 miles) will be rebuilt to current 69kV standards. All new line should be rated 600A or higher. All necessary outages should be coordinated with IPL and CBPC. | IA | ITC MIDWEST | Other | Age and Condition | 2029-12-31 | 69 | M2 - Appendix A Approved | 6462000
MTEP22 | East | 21947 | Roedel Road 138 kV PTS Replacements | The proposed solution is to replace 3185 and 3198 pole top switches with 2 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Roedel Road Tap. | MI | METC | Other | Local Reliability | 2024-10-28 | 138 | M2 - Appendix A Approved | 1200000
MTEP22 | Central | 21948 | Upgrade New Bourbon bus tie breaker (B40) | Replace B40 bus tie breaker. | MO | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Age and Condition | 2025-12-31 | 69 | M2 - Appendix A Approved | 381780
MTEP22 | Central | 21949 | Rebuild T2B 34.5 kV line | Rebuild 34 kV line that feeds the Mosher B,C,&F plants and the Geneva switching station. This includes most of the switches in the line section. | MO | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Age and Condition | 2025-03-31 | 35 | M2 - Appendix A Approved | 4558281
MTEP22 | Central | 21950 | New Timmons 69/12 kV substation | Build the new Timmons 69/12 kV 14.4 MVA sub. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2025-04-08 | 69 | M3 - Under Construction | 5301167
MTEP22 | East | 21952 | Dutton 138 kV PTS Replacements | Replace 3004, 3017 and 3493 pole top switches with 3 new 138kV, 1-way, full-load-break 2,000 A GOAB switch near the Dutton Tap. | MI | METC | Other | Local Reliability | 2024-12-31 | 138 | M2 - Appendix A Approved | 1700000
MTEP22 | Central | 21955 | Upgrade Fair Oaks 2nd bank 138/69/12 kV transformer | Add second 138/69/12kV 22.4MVA transformer to Fair Oaks substation to handle new load in area | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2026-12-31 | 69 | M2 - Appendix A Approved | 4176754
MTEP22 | Central | 21957 | Upgrade Oregon 69 kV Sub | Replace existing 7 MVA substation transformer at the KVREMC owned Oregon Substation to a 14 MVA. Add a backup transmission line for Oregon Substation and tap the nearby 69105 (0.25mi). New ATO scheme to be installed on KVL property on transmission line poles and to be owned by WVPA. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2024-10-31 | 69 | M3 - Under Construction | 1338591
MTEP22 | Central | 21965 | Upgrade Otter sub eqmnt | Otter substation in Steuben has an inoperable switch and transrupter that need replaced. Replacing switch with a load break manual switch and replacing the transrupter with a S&C Circuit Switcher. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Age and Condition | 2025-06-01 | 69 | M2 - Appendix A Approved | 872640
MTEP22 | Central | 21970 | Reconductor Kinmundy-Tanner 138 kV | Reconductor 27.4 miles Kinmundy-Tanner 138 kV line | IL | AMEREN ILLINOIS | Other | Local Reliability | 2027-06-01 | 138 | M2 - Appendix A Approved | 19800000
MTEP22 | Central | 21971 | Upgrade Callaway 345 kV Substation | Add breakers on the high side of safeguard transformer A and B at Callaway 345 kV substation | MO | AMEREN MISSOURI | BRP |  | 2026-12-01 | 345 | M2 - Appendix A Approved | 5700000
MTEP22 | West | 21973 | Blue Earth Light and Water- Rice Street Transformer Replacement | Blue Earth Light and Water has a Rice Street sub which carries a 10/14 MVA 69/12.47 kV Transformer. The transformer is showing signs of age as it is 28 years old and needs to be replaced because of potential load growth. | MN | Central Minnesota Municipal Power Agency | Other | Age and Condition | 2026-12-31 | 69 | M2 - Appendix A Approved | 3500000
MTEP22 | West | 21974 | Blue Earth Light and Water- West Sub Transformer Replacement | Blue Earth Light and Water West Sub Transformer replacement. | MN | Central Minnesota Municipal Power Agency | Other | Age and Condition | 2027-12-31 | 69 | M2 - Appendix A Approved | 3500000
MTEP22 | West | 21976 | Jasper to Laurel 161kV Line Rebuild | ITC will rebuild approximately 10 miles of the Jasper to Laurel 161kV line. The 161kV line conductor will be capable of 1600A or greater. | IA | ITC MIDWEST | Other | Age and Condition | 2028-12-30 | 161 | M2 - Appendix A Approved | 18781720
MTEP22 | West | 21980 | ITC Midwest Asset Replacement Program 2024 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA; IL; MN | ITC MIDWEST | Other | Age and Condition | 2024-12-31 | 345 | M3 - Under Construction | 37080000
MTEP22 | West | 21982 | Southern Dubuque 161/69kV Source & Bunker Hill 69kV Loop | ITC Midwest will construct a new Edval161/69kV substation on the south side of Dubuque. Then a new right of way 69 kV line ~2.65 miles to the existing Bunker Hill substation in the center of Dubuque. The new line will provide the 2nd 69kV line to the radial Bunker Hill 69kV sub. Alliant Energy will expand the Bunker Hill site to allow for a 2nd distribution transformer and ITC to have two 69 kV line breakers and a 69 kV bus tie breaker. The new ITC 161/69kV sub will be capable of two 150 MVA 161/69kV transformers (one initially). The 161kV will be constructed with the standard 161 kV ring convertible to breaker and 1/2 with just the single transformer and the two 161kV line taps initially. The 69kV will need to allow for a potential 2nd 150 MVA transformer and 69kV bus tie breaker, but will initially be just a single 69kV line to feed the Bunker Hill loop. | IA | ITC MIDWEST | Other | Load Growth | 2025-12-31 | 161 | M2 - Appendix A Approved | 19306266
MTEP22 | East | 21990 | Cut Iosco – Karn into Twining 138 kV | Cut the Iosco – Karn 138 kV circuit into the Twining 138 kV substation. This will require expand the Twining 138 kV substation and constructing approximately 0.15 miles of new right of way to bring the line into the substation. | MI | METC | Other | Local Reliability | 2026-06-01 | 138 | M2 - Appendix A Approved | 4100000
MTEP22 | East | 21993 | METC Pole Top Switch Additions/Replacement Program 2024 | Install or replace an existing pole top switch with a new 138 kV, 1-way full-load-break pole top switch at tap points. | MI | METC | Other | Local Reliability | 2024-12-31 | 138 | M2 - Appendix A Approved | 2400000
MTEP22 | East | 21995 | 2025 METC Customer Interconnections | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval | MI | METC | Other | Load Growth | 2025-12-31 | 138 | M2 - Appendix A Approved | 2000000
MTEP22 | West | 21996 | J1084 Generator Interconnection TOIF | TOIF includes facilities and equipment at the 345 kV substation dedicated to the 345 kV radial line and Generating Facility | IA | ITC MIDWEST | GIP |  | 2026-02-27 | 345 | M2 - Appendix A Approved | 661704
MTEP22 | West | 21997 | J1084 Generator Interconnection Network Upgrades | Rock Creek 345 kV ring bus will be expanded with a 345 kV breaker and other necessary equipment to interconnect the new terminal for project J1084. | IA | ITC MIDWEST | GIP |  | 2026-02-27 | 345 | M2 - Appendix A Approved | 1294462
MTEP22 | West | 21998 | J1164 Generator Interconnection TOIF | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | MN | ITC MIDWEST | GIP |  | 2026-08-14 | 161 | M2 - Appendix A Approved | 475538
MTEP22 | West | 21999 | J1164 Generator Interconnection Network Upgrades | Magnolia 161 kV substation currently has no circuit breakers protecting the Magnolia to Elk 161 kV line and the Magnolia to Rock County 161 kV line. The Facilities Study for J1164 identified Network Upgrades and TOIF necessary for the interconnection of project J1164 to ITCM’s Magnolia 161 kV substation. Project J1164’s impact to the transmission system is currently being evaluated as part of the DPP 2018 April West Area Study, which has not been finalized pending results of an Affected System Study. | MN | ITC MIDWEST | GIP |  | 2026-08-14 | 161 | M2 - Appendix A Approved | 8833588
MTEP22 | East | 22000 | 2024 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | METC | Other | Age and Condition | 2024-12-31 | 138 | M2 - Appendix A Approved | 39400000
MTEP22 | East | 22001 | Westwood 138 kV Interconnection | Install a 138 kV breaker and associated equipment at Plum station to accommodate Wolverine’s interconnection request. | MI | METC | Other | Load Growth | 2024-12-31 | 138 | M3 - Under Construction | 3700000
MTEP22 | East | 22016 | 2025 ITCT Customer Interconnections | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $1 Million that have an in service date within the year 2025 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $1 Million a separate project will be submitted for approval. | MI | ITC | Other | Load Growth | 2025-12-31 | 120 | M2 - Appendix A Approved | 2000000
MTEP22 | East | 22017 | 2024 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | ITC | Other | Age and Condition | 2024-12-31 | 345 | M2 - Appendix A Approved | 37140000
MTEP22 | East | 22020 | Leoni – Parr Rd 138kV Rebuild | Rebuild approximately 19 miles from Leoni to Parr Rd utilizing 1431 ACSR on standard 138 kV double circuit steel poles with OPGW. | MI | METC | Other | Age and Condition | 2026-12-01 | 138 | M2 - Appendix A Approved | 32630000
MTEP22 | East | 22021 | Chopin – Dupont – White Lake 138kV Rebuild | Rebuild approximately 21 miles of the Chopin – Dupont – White Lake 138 kV Circuit from around structure 003F410 to Dupont utilizing 954 ACSR conductor on standard 138 kV double circuit structures with OPGW and relocate Cobb - White Lake and Dupont White Lake lines to the other side of the new 138 kV standard structures utilizing 954 ACSR conductor. | MI | METC | Other | Age and Condition | 2026-06-01 | 138 | M2 - Appendix A Approved | 38942000
MTEP22 | West | 22025 | Parkwood 115 kV Ring Bus | Rebuild the 115 kV bus at Parkwood substation as a ring bus. | MN | GREAT RIVER ENERGY | BRP |  | 2024-12-31 | 115 | M3 - Under Construction | 7631997
MTEP22 | West | 22026 | Deer River - Jessie Lake - Wirt Tap 69 kV Line Rebuild | Rebuild the Deer River - Jessie Lake - Wirt Tap 69 kV line. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2026-07-31 | 69 | M2 - Appendix A Approved | 24781298
MTEP22 | West | 22028 | Denham - Harry Maser 69 kV Line Rebuild | Rebuild the Denham - Harry Maser 69 kV line. | MN | GREAT RIVER ENERGY | BRP |  | 2025-05-02 | 69 | M2 - Appendix A Approved | 10805394
MTEP22 | West | 22030 | Rost 161/69 kV Substation and Lorain - Rost 69 kV Line | Construct the Rost 161/69 kV substation interconnection in the Heron Lake – Round Lake 69 kV transmission line. Construct approximately 9 miles of 69 kV transmission line from the Lorain substation to the Rost substation. Previously named Worthington Area Projects. | MN | GREAT RIVER ENERGY | BRP |  | 2026-10-30 | 161 | M2 - Appendix A Approved | 21107282
MTEP22 | West | 22049 | J1101 Kewaunee SS Network Upgrades and Interconnection Facilities | Installation of a 20MW battery storage project at the J886 Generating Facility. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2026-06-01 | 138 | M2 - Appendix A Approved | 155000
MTEP22 | West | 22105 | J1042 North Lake Geneva SS Network Upgrades and Interconnection Facilities | Interconnection Customer shall install a 180MW solar farm interconnecting at North Lake Geneva SS in Walworth County. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2025-12-31 | 138 | M3 - Under Construction | 1407357
MTEP22 | South | 22125 | R1003 Generator Interconnection at Sabine 230/138 kV Station (OCAPS) | This project is to perform the required upgrades to accommodate the interconnection at the existing Sabine 230/138 kV station identified in the GIA for R1003(OCAPS) | TX | ENTERGY SERVICES, LLC. | GIP |  | 2025-05-31 | 230 | M2 - Appendix A Approved | 14762000
MTEP22 | Central | 22206 | Replace Dresser 138kV Breaker | Replace (5) over-dutied Dresser CBs: (13869-9, 13869-10, 138B3-1, 138B3-2, 138138) with higher interruption capacity (63 KIAC rating) | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2026-03-20 | 138 | M2 - Appendix A Approved | 5000000
MTEP22 | Central | 22208 | Rebuild Bedford to Mitchell Lehigh 138kV - 13822 Line | Bedford to Mitchell Lehigh 138kV - Rebuild 13822 line section with 954ACSR@120C; upgrade 1200A Wave trap at Bedford to 2000A; upgrade 954AL bus at Bedford to 1590AL | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2027-06-01 | 138 | M2 - Appendix A Approved | 19804000
MTEP22 | Central | 22209 | Upgrade Columbus 13830 Line Terminal | Columbus 13830 line terminal: upgrade 300CU bus to 954AL to increase facility rating to 178MVA (line conductor rating) ; P6 - 13828 + 13829 ckts; Relay loadability ok as-is | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2027-06-05 | 138 | M2 - Appendix A Approved | 1232000
MTEP22 | Central | 22211 | Rebuild and Reconfigure Huntington 138kV Sub | Huntington 138kV Sub rebuild and reconfigure: establish 4-position 138kV ring bus; replace (2)138/69/12 xfmrs with (2)50MVA 138/69 xfmrs and (1)22.4MVA 138/12 xfmr; establish 4-position 69kV ring bus | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-07-31 | 138 | M2 - Appendix A Approved | 27078000
MTEP22 | Central | 22226 | New Bolton 345kV-230kV Substation | build new Bolton 345kV-230kV Substation with (2) parallel 345/230kV 450MVA xfmrs | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2027-06-01 | 345 | M2 - Appendix A Approved | 86800000
MTEP22 | Central | 22228 | Upgrades HMPL Transmission Due to I-69 DOT Project | Rerouting of HMPL 69kV transmission lines (HMPL Sub 6 to HMPL Sub 1, HMPL Sub 6 to (BREC) HMPL6 Tap, HMPL Sub 6 to HMPL Sub 3, and HMPL Sub 3 to (BREC) Wolf Hills Tap) due to I-69 KY DOT project. | KY | CITY OF HENDERSON, KY, UTILITY COMMISSION, DBA HENDERSON MUNICIPAL POWER AND LIGHT (BA) | Other | Local Reliability | 2024-11-01 | 69 | M3 - Under Construction | 3800000
MTEP22 | Central | 22230 | Upgrade Gibson 34509 Line Terminal | Gibson 345 Switchyard 34509 Line Terminal Upgrades: M210313 - (for Ameren Albion ring bus project) WT / Relays replacement; M210371 - replace (2)345kV CBs, free-standing CTs, and disconnect switches | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2025-12-12 | 345 | M3 - Under Construction | 2950051
MTEP22 | Central | 22245 | Improve 23008 Tipton W-Cammack Rd Line | Noblesville to Tipton West 23008 ckt: reinsulate and implement anti-gallop line conductor modifications | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-11-30 | 230 | M2 - Appendix A Approved | 4716099
MTEP22 | South | 22345 | East Winstonville Delivery Point | Tap the Energy owned Delta SES - Shelby 115kV line with switching station and build a 115kV line to the new member East Winstonville delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2025-11-01 | 115 | M2 - Appendix A Approved | 1862800
MTEP22 | Central | 22365 | New Adna 345 kV Ring Bus for J1107 Lutesville Solar | The Adna switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Kelso-Lutesville 345 kV transmission line will be cut. | MO | AMEREN MISSOURI | GIP |  | 2026-06-01 | 345 | M2 - Appendix A Approved | 12100000
MTEP22 | Central | 22385 | New Dion 345 kV Ring Bus for J1115 Greenswitch Wind | The Dion switching station will be a ring bus arrangement with three-line terminal positions and provisions for one additional future terminal position. The existing Latham-Oreana 345 kV transmission line will be cut. | IL | AMEREN ILLINOIS | GIP |  | 2026-06-01 | 345 | M2 - Appendix A Approved | 9500000
MTEP22 | Central | 22406 | Add J994 Guthrie Solar at Guthrie 161 kV | Add 161 kV terminal in the Guthrie substation for J994 project. | MO | AMEREN MISSOURI | GIP |  | 2028-06-01 | 161 | M2 - Appendix A Approved | 1658000
MTEP22 | Central | 22407 | Add J974 Fulton Wind at MapleRidge 345 kV | Add position to the existing Mapleridge 345 kV switching station for J974 interconnection facilities. | IL | AMEREN ILLINOIS | GIP |  | 2025-06-01 | 345 | M2 - Appendix A Approved | 2242000
MTEP22 | Central | 22408 | Add J987 Warren Solar at Montgomery 161 kV | Add 161 kV terminal in the Montgomery substation for the J987 | MO | AMEREN MISSOURI | GIP |  | 2028-06-01 | 345 | M2 - Appendix A Approved | 2060000
MTEP22 | Central | 22465 | New Bullion 161 kV Ring Bus for J1087 Kelso Solar | Construct a new 161 kV switching station in Scott County, Missouri to provide a Point of Interconnection for the Generating Facility. The new 161 kV Bullion switching station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Kelso – Miner 161 kV transmission line. | MO | AMEREN MISSOURI | GIP |  | 2024-12-01 | 161 | M2 - Appendix A Approved | 9189000
MTEP22 | West | 22528 | Matter 69 kV Substation | Install a manual load break 3-way load break 69kV/1200A switch on a steel pole and foundation on GRE’s DX (Crow River to Victor) line. Install adjacent grading structures if needed. Build HS DE to 115kV. | MN | GREAT RIVER ENERGY | Other | Load Growth | 2025-12-03 | 69 | M2 - Appendix A Approved | 403343
MTEP22 | Central | 22529 | New Vanduser 161 kV Ring Bus for J1034 Ringer Solar | Construct a new 161 kV switching station in Stoddard County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Vanduser 161 kV J1034 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Morley – Stoddard 161 kV transmission line | MO | AMEREN MISSOURI | GIP |  | 2025-06-01 | 161 | M2 - Appendix A Approved | 6730000
MTEP22 | West | 22531 | Bell Center-Lancaster N6 Rebuild | This project is a rebuild of DPC's existing 69 kV line (N6) connecting the Bell Center and Lancaster transmission substations. The recommended plan is to rebuild 40.51 miles of new 69 kV transmission line on existing right-of-way with 477 ACSR conductor. The recommended plan will address the age and condition issues, constructing the line with new poles and new 477 ACSR conductor. | WI | DAIRYLAND POWER COOPERATIVE | Other | Age and Condition | 2028-12-01 | 69 | M2 - Appendix A Approved | 23877825
MTEP22 | Central | 22546 | New Rootbeer 345 kV Ring Bus for J976 Split Rail Solar | Construct a new 345 kV switching station in Warren County, Missouri to provide a Point of Interconnection for the Generating Facility. The new Rootbeer 345 kV J976 Interconnection Switching Station will have a four-terminal ring-bus design with three terminal positions installed. Split the existing Belleau – Montgomery 345 kV transmission line. | MO | AMEREN MISSOURI | GIP |  | 2025-12-01 | 345 | M2 - Appendix A Approved | 10801000
MTEP22 | East | 22586 | Buskirk - New CE Interconnection | METC to construct a new 138 kV substation (Tulip) with three 138 kV breakers in a ring bus configuration, expandable to 3-row breaker-and-half. Cut the Buck Creek–Hazelwood (formerly Beals Road–Hazelwood) 138 kV line into the new 138 kV station. Construct 138 kV tie between METC and CE’s substations using 954 ACSR conductor on single-circuit structure. Also, remove switch 3107 and replace switch 3120 at Titus Lake tap. | MI | METC | Other | Age and Condition | 2025-10-30 | 138 | M3 - Under Construction | 11430000
MTEP22 | West | 22606 | OTP Jamestown, ND Load Addition | OTP has a new customer requesting to be served in Jamestown, ND. The customer facility will have a demand of 100 MWs. OTP will serve the new customer from the 41.6 kV tertiaries of both the existing Jamestown 345/115/41.6 kV transformers. The load will be split 50/50 between each of the transformers. OTP will install a new 115/41.6 kV 24 MVA transformer at the Jamestown 345 kV substation. The 115 kV bus will be expanded to allow for the new 115/41.6 kV transformer. The existing 41.6 kV load will be moved to be served off the new 115/41.6 kV 24 MVA transformer. | ND | OTTER TAIL POWER COMPANY | Other | Load Growth | 2024-11-01 | 115 | M2 - Appendix A Approved | 2268000
MTEP22 | East | 22627 | Day - New WPSC Interconnection | Tap the Deja Jct. – Derby Jct. section of Eureka – Vestaburg 138kV line, approximately 2.5 miles West of Deja Tap. Transmission tap will be ~ 4 miles long. Install tap pole at the tap location, install two new 138 kV, 1-way, full-load-break 2000 A. | MI | METC | Other | Load Growth | 2024-12-31 | 138 | M2 - Appendix A Approved | 1132000
MTEP22 | Central | 22646 | New Decatur-Napoleon 161KV Station | New 161 kV transmission station between Decatur and Napoleon | IN | HOOSIER ENERGY | Other | Load Growth | 2030-06-01 | 161 | M2 - Appendix A Approved | 31409072
MTEP22 | West | 22747 | Interstate Containment Structures Installation Blanket | Based on recent experience from storms and its effects on transportation, installation of containment structures on either side of heavily traveled interstate and similar highway crossings is planned. The structures will reduce the likelihood of failure. If a severe storm occurs, the containment structures will reduce cascading and enable faster cleanup of the highway because the conductor can be cut free as it will not be under high tension. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-12-31 | 345 | M2 - Appendix A Approved | 13000000
MTEP22 | Central | 22808 | New Rush Island Area Statcoms | Add 250 MVAR Statcom at Bugle, Arnold, Mason and Highway N substations. | MO | AMEREN MISSOURI | Other | Local Reliability | 2025-06-01 | 161 | M3 - Under Construction | 175000000
MTEP22 | West | 22986 | Vinburn Substation 69 kV Capacitor Addition | Install a 69 kV capacitor bank configuration and associated automatic control features at Vinburn SS. | WI | AMERICAN TRANSMISSION COMPANY | BRP | Local Reliability | 2024-12-31 | 69 | M3 - Under Construction | 3620000
MTEP22 | West | 22988 | Gaston Road SS, DIC, Additional Transformer | New DIC, additional transformer | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2024-12-31 | 69 | M3 - Under Construction | 3600000
MTEP22 | West | 22989 | Columbus SS, DIC, Transformer Replacement | Columbus SS, new DIC, transformer replacement | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2028-09-11 | 69 | M2 - Appendix A Approved | 15690577
MTEP22 | West | 23007 | Duck Creek SS, DIC, New Substation | Distribution Interconnection, new substation | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2024-12-31 | 69 | M3 - Under Construction | 4200000
MTEP22 | West | 23008 | WisDOT I-94 Stadium Group of Projects | WisDOT Road Move: ATC’s 138kV lines and the Park Hill substation have been identified as impacted by the roadway construction in all WisDOT alternatives and will require relocation between the end of Calvary Cemetery and the 28th Street Substation to maintain the transmission network and distribution interconnections. Final transmission line routing and substation site selection to be determined through project investigations and coordination. Asset Renewal Rebuild of Structures 4145-4149: Install structures, OPGW/static, and new conductors. Communications: Install fiber communications between 96th Street Substation to structure 4145 and from the new substation location for the WisDOT road move to Valley Substation. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-31 | 138 | M2 - Appendix A Approved | 63700000
MTEP22 | South | 23147 | J1219/J1257 115 kV station(Hickory) | Construct a 115 kV substation between the existing Amite and Chicken Farm 115 kV stations | LA | ENTERGY SERVICES, LLC. | GIP |  | 2026-06-01 | 115 | M2 - Appendix A Approved | 14390000
MTEP22 | South | 23154 | Keo 500kV: Expansion for J1258 & J1415 | The KEO 500kV substation will be expanded to interconnect the J1258/J1415 gen-tie 500kV line. The Network Upgrades include a new 500 kV gas circuit breaker, two new 500 kV disconnect switches, relay panels, revising the station RTU configuration, wiring additions to the DFR, and telecommunication additions. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2028-06-01 | 500 | M2 - Appendix A Approved | 8888000
MTEP22 | Central | 23266 | New HE_AboutBit 115 MVA Load | Extend a new 69kV transmission line from an available bay position at Merom transmission station (Bus # 248774) to the new customer. The 69kV line will split at about 0.3 miles from Merom station, extending to two separate substations. Total estimated load is 115 MVA (20 MVA on substation 1 and 95 MVA on substation 2). | IN | HOOSIER ENERGY | Other | Load Growth | 2025-01-01 | 69 | M2 - Appendix A Approved | 1200000
MTEP22 | South | 23267 | Fountain Hill 115kV: J1281 Cut In Switching Station | Entergy will provide oversight for the construction of the transmission owners interconnection facilities and stand alone network upgrades associated with the interconnection of J1281 on the Crossett - Monticello East 115kV line. The Crossett North 115kV substation will have new line protection installed. The Monticello East 115kV substation will have new line protection installed alond with new CCVT's and a new breaker. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2027-05-31 | 115 | M2 - Appendix A Approved | 3796000
MTEP22 | South | 23308 | J1246 Bayou Labutte 500 kV Interconnection | The Bayou Labutte 500kV substation will be expanded to interconnect the J1246 gen-tie 500kV line. The Network Upgrades include relocation of the Willow Glen 500 kV line position, new 500 kV gas circuit breaker, two new 500 kV disconnect switches, along with other additional station equipment and upgrades at Bayou Labutte. Also Included in the network upgrades for J1246 are the replacement of two 230 kV breakers at the Point Pleasant 230 kV station to 63 kA IPO breakers along with relay upgrades for the associated equipment. | LA | ENTERGY SERVICES, LLC. | GIP |  | 2025-02-14 | 500 | M3 - Under Construction | 14344000
MTEP22 | South | 23326 | Tindall 230kV: J1215 New Switching Station Cut-In | A new 230kV three breaker ring bus substation will be cut-in to the Woodward - Stuttgart Ricuskey 230kV transmission line. Remote end upgrades will be performed at Stuttgart Ricuskey and Woodward substations. Approximately 2.6 miles of OPGW fiber will be installed between Stuttgart Ricuskey and the new J1215 stations. 230kV Circuit breakers B8414 and B8406 will be replaced at Stuttgart Ricuskey. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-11-01 | 230 | M2 - Appendix A Approved | 14695000
MTEP22 | South | 23330 | Rilla 115 kV: Expand Station (J1239) | The Rilla 115 kV station will be expanded to interconnect J1239. | LA | ENTERGY SERVICES, LLC. | GIP |  | 2025-06-26 | 115 | M3 - Under Construction | 7233000
MTEP22 | West | 23346 | Hutchinson Substation | This project will add a second 115/69 kV transformer to the existing City of Hutchinson MN, Hutchinson Substation. The project will also rebuild the Hutchinson 115 kV into a four position ring bus. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Load Growth | 2026-12-31 | 115 | M2 - Appendix A Approved | 14700000
MTEP22 | South | 23386 | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades | MPFCA J1281, J1294, J1458 Adams Creek 230 kV and Bogalusa 500-230 kV Upgrades. Replace breakers S4402/S4405 and switches at Adams Creek 230 kV with 4000 Amp equipment. Upgrade bus at Bogalusa 500-230 kV and install slipover current transformers on 230 kV bushings of existing 500-230 kV autotransformers. These upgrades will increase the rating of the circuit between the Adams Creek 230 kV station and the Bogalusa 500-230 kV station to 1281 MVA. | LA | ENTERGY SERVICES, LLC. | GIP |  | 2024-12-01 | 230 | M2 - Appendix A Approved | 3990001
MTEP22 | South | 23387 | Gerald Andrus - Tinnin 230 kV Cut-in and Line Upgrade (J1458) | Generator Interconnection new Panther Burn 230 kV station on the Gerald Andrus - Tinnin 230 kV line and Network Upgrade rebuild of the Greenville - SE Greenville 115 kV line. | MS | ENTERGY SERVICES, LLC. | GIP |  | 2026-03-31 | 230 | M2 - Appendix A Approved | 10425000
MTEP22 | West | 23452 | Brookings - Lyon, Hampton - Helena 2nd 345kV Circuits | Install second 345 kV circuit between the Brookings County and Lyon County substations. Install second 345 kV circuit between the Hampton Corner and Helena substations. Perform substation upgrades associated with installation of line. | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-09-01 | 345 | M2 - Appendix A Approved | 75300000
MTEP22 | West | 23480 | Substation 18: Replace Failed 161/69 kV Transformer 1 | Replace transformer that was failed in May 2022. Purchase replacement spare transformer for the unit being replaced at Sub. 18 | IL | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2025-12-31 | 161 | M2 - Appendix A Approved | 4050000
MTEP22 | West | 23516 | Enterprise Way South Substation | Construct new 161-13.2 kV distribution substation bisecting the existing Sub 56-Enterprise Way 161 kV line. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2026-01-31 | 161 | M2 - Appendix A Approved | 4660000
MTEP22 | South | 23518 | Tunica - Lula 115 kV Cut-in (J1440) | Generator Interconnection J1440 new Dundee 115 kV station cutting in on the Tunica - Lula 115 kV transmission line. Conditional on Ray Braswell - Franklin 500 kV MPFCA | MS | ENTERGY SERVICES, LLC. | GIP |  | 2026-11-01 | 115 | M2 - Appendix A Approved | 13560000
MTEP22 | West | 23520 | Johnstown SS, DIC, New Substation | DIC, New Substation | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2025-12-31 | 69 | M2 - Appendix A Approved | 6063398
MTEP22 | West | 23531 | Cottonwood - Summit Underground Fiber | This project will establish a fiber link between the Cottonwood to Summit substations, which will enhance communications resiliency by interconnecting into ATC’s larger substation fiber network infrastructure at Summit. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2024-12-31 | 138 | M3 - Under Construction | 2600000
MTEP23 | Central | 22946 | New Alta - Pioneer 138 kV Line | Construct a new 138 kV line from Alta to Pioneer. Rebuild Alta 138 kV substation as a 4-position initial, 6-position ultimate 138 kV ring bus. Rebuild Pioneer 138 kV substation as 5-position initial, 6-position ultimate 138 kV ring bus. TP5161 was created to rebuild Pioneer as a ring bus to address aging infrastructure. The aging infrastructure will be addressed by this project. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | M2 - Appendix A Approved | 46000000
MTEP23 | Central | 23406 | Upgrade Bedford 345 kV - 138 kV Bus 9 | Bedford 345 KV - Upgrade 138KV Bus 9 - from (1)954acsr@120C (overhead line rating) to (2)954ACSR@120C | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2027-03-23 | 138 | M2 - Appendix A Approved | 295115
MTEP23 | Central | 23568 | Replace Southwest 138 kV #16 Breaker | Replacement of one (1) 138 kV breaker at Southwest #16 | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2025-08-19 | 138 | M2 - Appendix A Approved | 380948
MTEP23 | Central | 23569 | New [BREC] McCracken-[GLH] Joppa 161 kV Tie Line | This relatively small and confined project will consist of one additional terminal at an existing Big Rivers’ substation (Big Rivers owned), 2 miles of 161 kV transmission line (Big Rivers owned), and a three bay switching station (GLH owned). Without this proposed project transmission voltages are very near a contingent TPL violation with normal forecasted load levels. Loads associated with extreme weather or a small load increase in this region will cause a contingent TPL violation. In addition to the TPL violation relief and providing needed capacity in the western part of Big Rivers system, the proposed project will alleviate the need to purchase transmission service from TVA. During contingent conditions, the majority of Jackson Purchase Energy (distribution cooperative served by Big Rivers) is dependent on one 161 kV interconnection with TVA. Therefore, Big Rivers must purchase transmission service as available from TVA during various planned and unplanned outage scenarios. The proposed project will provide a second MISO source to this load and alleviate the reliance on TVA transmission service and eliminate the need to purchase such service. This project will coincide with project ID 23827 submitted by GridLiance Heartland. | KY | BIG RIVERS ELECTRIC CORPORATION | Other | Local Reliability | 2026-12-31 | 161 | M2 - Appendix A Approved | 5300000
MTEP23 | East | 23704 | Abbe Jct - Mio 138kV Sag Remediation | Remediate sag on the 266.8 ACSR up to conductor’s limit on the Abbe Jct. – Mio Dam section of the Airport – Mio Dam 138 kV circuit. | MI | METC | BRP |  | 2026-12-31 | 138 | M2 - Appendix A Approved | 1700000
MTEP23 | Central | 23825 | Reconfigure Rockville 138 kV substation | Conversion of Rockville 138 kV to a ring bus configuration | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2026-12-01 | 138 | M2 - Appendix A Approved | 8500000
MTEP23 | Central | 23833 | New Edinburgh Industrial Park 69/12kV sub | DEI to construct high-side and loop 69kV lines into a new IMPA-owned Edinburgh Industrial Park substation; one 69/12kV 20MVA transformer; SCADA controlled MOLB 69kV line switches; two 69kV buses with a manually operated 69kV bus tie switch; 69kV connections from the 6950 and 69146 ckts. | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-10-13 | 69 | M2 - Appendix A Approved | 4570000
MTEP23 | East | 23847 | Bingham - Looking Glass 138 kV Rebuild | Rebuild approximately 19.3 miles of the Bingham – Looking Glass 138 kV circuit to 1431 ACSR conductor utilizing 138 kV double- circuit structures with OPGW. Leave the East side of the double-circuit structures vacant. Connect OPGW at Bingham 138 kV position WM6. | MI | METC | Other | Age and Condition | 2028-05-31 | 138 | M2 - Appendix A Approved | 35395000
MTEP23 | Central | 23861 | Upgrades Columbus 345 kV Sub Breaker | Columbus 345 Sub Breaker Upgrades: Replace (3) 138kV CBs on Xfmr Banks 1, 2, and 3 with higher fault interrupting capacity; MTEP24 - added 13831 line breaker; 2024: (Non-TPL compliance) 138TR and 69230-4 added | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2027-02-22 | 138 | M2 - Appendix A Approved | 3600000
MTEP23 | Central | 23862 | Upgrade Bedford 345 kV Sub - 138-138 Bus Tie | Bedford 345 KV Sub 138-138 bus tie path - Upgrade 138kV bus (increase to 2-1590AL), CTs (reconnect at 2000A:5A ratio), and (2) switches (replace with 3000A) | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2032-04-01 | 138 | M2 - Appendix A Approved | 667000
MTEP23 | Central | 23863 | Upgrade Cayuga to Nucor 34501 Line Terminal 345 kV | Cayuga to Nucor 34501 Line Terminal Bus Upgrades: Upgrade 2500AL bus to 2-1590AL at both line terminals | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2026-05-29 | 345 | M2 - Appendix A Approved | 320000
MTEP23 | Central | 23864 | New Bloomington Area 138kV Source | Construct new 345/138kV substation on the west side of Bloomington with (1) 138kV line to Bloomington Rogers St. | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2029-06-01 | 345 | M2 - Appendix A Approved | 53400000
MTEP23 | Central | 23867 | Rebuilding WVPA Anderson Grain 69/12kV Sub | Relocate transmission and add in&out with SCADA switches for new Anderson Grain substation. Install 69kV ckt switcher and relaying for high side protection. | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2025-03-14 | 69 | M3 - Under Construction | 1750000
MTEP23 | East | 23884 | 2025 ITCTransmission Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | ITC | Other | Age and Condition | 2025-12-31 | 345 | M2 - Appendix A Approved | 60370000
MTEP23 | Central | 23886 | New J1234 - J1235 IN Solar 1 | J1234 - J1235 IN Solar 1 - 150MW net solar farm (100 MW for J1234 and 50 MW for J1235) | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-05-16 | 138 | M2 - Appendix A Approved | 17232683
MTEP23 | Central | 23887 | J1378 Crossroads Solar | J1378 Crossroads Solar - 200MW: 230kV connection at existing Veedersburg West sub | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-11-20 | 230 | M2 - Appendix A Approved | 5992934
MTEP23 | Central | 23892 | Reconfigure Shelbyville Northeast 138kV Ring bus | Shelbyville Northeast: build 138kV ring bus; replace CIR 6946, 6976, 69183, 13803, 13865 relays, replace OCBs 6946, 6976, 69183, 69138-1, 13803, replace Bank 1 ground switch with circuit switcher, and station battery. | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-06-30 | 138 | M2 - Appendix A Approved | 10800000
MTEP23 | Central | 23923 | New WVPA Vandalia 69/12 kV Substation | Vandalia (Fillmore) Substation - Incorporate SCADA operated 69 kV flow-through switches into 6996 line between Greensboro and Amo. | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2025-04-22 | 69 | M3 - Under Construction | 7209000
MTEP23 | Central | 23925 | New Slugger 138kV Load | Project Slugger - large new customer load - early phases to be served from 138kV system followed by 345/138kV transformation as load projections increase; 8/7/24: scope increased to add remote transfer tripping scheme to Open Speed 345/138 Bk3 flo 345 line from Speed to Kenzig Rd and 345 line from Slugger to Trimble Co. | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2029-12-31 | 345 | M2 - Appendix A Approved | 123500000
MTEP23 | East | 23948 | 2025 METC Asset Replacement Program | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI | METC | Other | Age and Condition | 2025-12-31 | 345 | M2 - Appendix A Approved | 49570000
MTEP23 | Central | 23953 | Rebuild WVPA Greencastle 69/12kV Substation | Rebuild the existing 69-12.47 kV Greencastle Substation with 69 kV flow-through in another location due to size of site. Replace bank with 14.4 MVA. | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2025-12-30 | 69 | M2 - Appendix A Approved | 4828000
MTEP23 | Central | 23962 | Rebuild 6958 Line 69 kV for FAA | 6958 Line Rbld as required by FAA - Rebuild 39 Structures and replace conductor from HE Whitehall to structure 815-1069-01. Replace individual poles 815-1060 and 815-1061. Install monitored FAA warning lights on 37 of the poles. Install 36 marker balls on the static wire. | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-06-01 | 69 | M2 - Appendix A Approved | 3385000
MTEP23 | Central | 23963 | Rebuild 6932 Potato Crk to Thorntown 69 kV | 6932 Rebuild Potato Crk to Manson Jct to Clarks Hill to Thorntown with 954ACSR conductor | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2024-12-31 | 69 | M3 - Under Construction | 41811862
MTEP23 | Central | 23967 | J1295 Gibson Solar | J1295 Gibson Solar farm 280MW +/- w/ 345kV POI between Gibson and Francisco in ckt. 34516 (3-breaker ring); Includes required relay work at Gibson | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-05-31 | 345 | M2 - Appendix A Approved | 17700001
MTEP23 | Central | 23968 | New Greensfork East 69/12kV Sub | Greensfork East new 69/12kV - 22.4MVA Sub: looped-through feed from 69100 ckt. | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2028-08-08 | 69 | M2 - Appendix A Approved | 1440000
MTEP23 | Central | 23969 | New Williamsport 69/12kV Sub | Williamsport new 69/12kV - 22.4MVA sub: looped-through feed from the 6936 ckt. | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-10-02 | 69 | M2 - Appendix A Approved | 3152000
MTEP23 | Central | 23970 | Rebuild 69100 Greensfork to HE Jacksonburg Jct 69kV | Rebuild 69100 from Greensfork #1 switch (pole #862-3176) to Jacksonburg Jct switch (pole #862-3074) using light duty steel poles, 477ACSR and OPGW | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-10-30 | 69 | M2 - Appendix A Approved | 10800000
MTEP23 | Central | 23981 | New Saint Paul Northwest 10.5MVA 69/12kV Sub | Saint Paul Northwest (new) - Install 10.5MVA, 69-12kV non-LTC transformer; build/re-route the existing 6937 line to loop through the new substation with ATO/TLS switches | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-10-01 | 69 | M2 - Appendix A Approved | 1377000
MTEP23 | South | 24416 | Rosepine Substation | Build a new 230 kV substation Rosepine tapped into the existing Leesville to Cooper 138 kV line 11.5 miles from Leesville. Build a new 230 kV line 3.4 miles from Rosepine to Deridder. This substation and line will be energized at 138 kV. | LA | CLECO POWER LLC | BRP |  | 2027-07-15 | 138 | M2 - Appendix A Approved | 35585000
MTEP23 | East | 24593 | GM Orion Plant Expansion | At Sunbird, expand the existing substation to include 3-120 kV line breakers, 1-120 kV section breaker, and create bus 103. Construct a 2nd Pontiac-Sunbird 120 kV line and install 2-120 kV pole top switches on the Colorado taps on the Pontiac-Sunbird #1 and Sunbird-Bloomfield 120 kV lines. At Pontiac, bypass the existing series reactor and install a line breaker on the new Pontiac-Sunbird #2 line position. Install OPGW between Pontiac and Sunbird. | MI | ITC | Other | Load Growth | 2025-03-31 | 120 | M2 - Appendix A Approved | 25796000
MTEP23 | South | 25242 | Amite South Reliability Project Phase 1 - alternative | • Construct 500/230 kV Commodore station near the existing Derrick 230 kV Station o Cut in Derrick to Iberville and Richardson to Wise 230 kV lines. Upgrade 3.6 mile Iberville to Commodore 230 kV. o Cut in the Webre to Bayou Labutte 500 kV line o Install one 500-230 kV Autotransformer o Commodore 230 kV station will be a breaker and half station o Commodore 500 kV station will be a 4 breaker ring • Construct a new ~60 mile 230 kV line between Commodore and Waterford. • Construct a new ~85 mile 500 kV line between Commodore and Churchill. • Expand Waterford 500 kV into a three-breaker ring. Add additional bay at Waterford 230 kV to accommodate the new 230 kV line. • Construct a new 500 kV four-breaker ring at Churchill, to accommodate two 500 kV lines and two Autotransformers. Install two 500-230 kV Autotransformers. • Convert existing Waterford to Churchill 230 kV to 500 kV operation. | LA | ENTERGY SERVICES, LLC. | Other | Local Reliability | 2029-04-01 | 500 | M2 - Appendix A Approved | 1700000003
MTEP23 | Central | 3382 | Vincennes Vigo St. 138kV Dist Sub | Build new radial 138kV line and add breaker at Vincennes 138kV sub to convert Vigo St. sub from 34kV to 138kV | IN | DUKE ENERGY INDIANA, LLC | Other | Local Needs | 2026-07-14 | 138 | M2 - Appendix A Approved | 10932000
MTEP24 | South | 50013 | Grand Prairie 115kV: New substation | Construct a new 115 kV substation with two 115/4.16 kV 33.3 MVA transformers to serve the planned motors at the pumping station. Cut into the Devalls Bluff – Brinkley East 115kV line and build ~.20 circuit mile (.40 total circuit mile) of “in and out” 115kV line. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2025-04-01 | 115 | M3 - Under Construction | 15626062
MTEP24 | West | 50037 | Ellendale load 2 addition | MDU has an additional load request at Ellendale, ND for a total demand of 225 MW. MDU will serve the customer from its Ellendale 345 substation from the 230 kV. A 230 kV line will run to a new sub where a 230/34.5 transformer will be added along with the 34.5 kV breakers. | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Load Growth | 2025-04-01 | 230 | M3 - Under Construction | 16776939
MTEP24 | East | 50038 | Project Phoenix-Husky Substation | Install line tap on the Murphy-Orr Rd 1 138 kV line for the temp load. Expand Orr Rd station and constructs a new Murphy to Orr Rd 345 kV line and 345/138 kV transformer at Orr Road to support CE’s transformers and METC’s new transformer at Orr Rd. | MI | METC | Other | Local Needs | 2026-06-05 | 345 | M3 - Under Construction | 50252000
MTEP24 | Central | 50086 | Load addition at Montgomery 161 kV Substation | This project will facilitate the connection of a 250 MW datacenter load at Montgomery (161 kV) Substation with a new straight bus and terminal | MO | AMEREN MISSOURI | Other | Load Growth | 2026-03-01 | 161 | M2 - Appendix A Approved | 2500000
MTEP24 | West | 50106 | Big Cedar Interconnection | ITC Midwest will construct the new Big Cedar 345 kV Switching Station which will connect to the existing ITC Midwest Beverly - Morgan Valley 345 kV line and add a 2nd Beverly – Big Cedar 345 kV line on existing structures. The new switching station will be constructed in a breaker and ½ configuration and provide service/connections to multiple customer owned transformers/substations. | IA | ITC MIDWEST | Other | Load Growth | 2026-03-31 | 345 | M2 - Appendix A Approved | 63743317