## MTEP25 Appendix A
MTEP25 Appendix A - New Local Reliability Projects recommended for approval
Planning Region | MTEP Project ID | Project Name | Project Description | State(s) | Submitting TO | Project Type | Other Type | Expected ISD | Max kV | Current Cost
West | 50622 | Substation High Voltage Protection (HVP) Equipment Removal | The objective of ATC’s Substation (HVP) Equipment Removal project is to enhance safety within and outside the control house by decommissioning the remaining High Voltage Protection (HVP) telecommunications equipment from (~269) ATC substations. The legacy HVP (copper cable) equipment is no longer in use due to the migration to fiber optic technology upgrades within ATC’s substation environment. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2027-11-30 | 0 | 3000000
West | 50624 | Substation 74: Relocate 161 kV Capacitor Bank from Substation A | Relocate the existing 161 kV, 50.4 MVAR capacitor bank from Substation A to Substation 74. | IA | MIDAMERICAN ENERGY CO. | BRP |  | 2026-06-01 | 161 | 1600000
Central | 50628 | Upgrade LEAP Transmission Network Phase 2 | Additional load has committed to the LEAP District, an innovation district west of Lebanon, IN in Boone County. The total demand in the district is estimated to be 1200MW. This represents a 600MW increase to a prior approved submission. To meet the additional load requirements, WVPA will connect into the Qualitech-Whitestown 345kV line and construct a new 345kV ring bus and approx. 12 miles of 345kV line to the west side of Lebanon where WVPA will construct a 345/138kV substation. Approx. 15 miles of 345kV line will be built to network this 345/138kV station to a planned 345/138kV station on the north side of the LEAP district. WVPA will also connect into the Nucor-Whitestown 345kV line and construct a new 345kV ring and approx. 6 miles of new 345kV line to the new step down substation. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2029-06-30 | 345 | 345000000
West | 50514 | J1502 Emerson Rd SS Network Upgrades and Interconnection Facilities | J1502 is a 225 MW solar facility in Juneau County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-06-30 | 345 | 19847000
West | 50515 | J1779 Rockdale SS Interconnection Facilities | J1779 is a 200 MW solar facility in Dane County, WI. Per the GIA, there are no network upgrades associated with project, only TOIFs. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-10-31 | 345 | 25000
West | 50516 | S1017 Tennyson SS Network Upgrades | S1017 is a 100 MW Surplus project in Grant County, WI. The S1017 project consists of the installation of 100MW of battery storage at the J947 collector station. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2025-04-30 | 138 | 225000
West | 50517 | S1018 7 Mile Creek SS Network Upgrades | S1018 is a 75 MW Surplus project in Wood County, WI. The S1018 project consists of the installation of 75 MW battery storage at the J986 collector station. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2026-08-03 | 138 | 1475000
West | 50518 | J1773 J1781 MPFCA Network Upgrades | Each individual Interconnection Customer is responsible for a proportionate percentage share of the Common Use Upgrades (CUU) estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. J1773 is seeking interconnection service for 300 MW and J1781 is seeking interconnection service for 300 MW. Network upgrades will consist of Hill Valley – Eden 138kV (X-127) reconductor project and Eden – Highland 138 kV (X-147) rebuild project. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-10-10 | 138 | 7623089
West | 50519 | Reactor Relocation from North Madison SS to J1502 POI SS | Relocate the 80 Mvar reactor from North Madison SS to J1502 POI SS to regulate voltage when J1502 is unavailable. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2028-06-30 | 345 | 5165000
West | 50520 | OTP Donaldson - Donaldson South J1575 Network Upgrades | Network upgrades to accommodate interconnection customer J1575 to the Donaldson to Warsaw 115 kV transmission line. | MN | OTTER TAIL POWER COMPANY | GIP |  | 2028-12-31 | 115 | 776292
West | 50521 | OTP Donaldson South J1575 Interconnection | Interconnection customer J1575 will be interconnecting 70 MWs onto the Donaldson to Warsaw 115 kV transmission line. | MN; ND | OTTER TAIL POWER COMPANY | GIP |  | 2028-08-03 | 115 | 8060297
South | 50528 | Benoit 230 kV Station | Entergy is proposing to construct a new 230 kV station named Benoit to serve a new customer cut into the existing Mud Lake to Big Lake 230 kV line south of Lake Charles, LA. The Benoit 230 kV station will be a 5 bay breaker and a half substation, including two 64.8 MVAR capacitor banks. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2027-07-01 | 230 | 51800001
West | 50529 | Appleton Area Reliability Project | 1) Construct new 138kV line between City Limits – Northside 2) Rebuild a 138kV line section of 50632 (From STR132131 - City Limits), 3) Rebuild a 138kV line section of 43025 (From STR132131 - Northside), 4) Rebuild two 138kV line sections of 971K11 (Melissa - Meadows Tap and Meadows Tap - Kaukauna Central Tap). | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2029-05-01 | 138 | 35700000
West | 50530 | J1750 Grace Lake SS Network Upgrades and Interconnection Facilities | J1750 is a 153 MW solar facility in Marquette County, MI. | MI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2029-03-13 | 138 | 12110000
Central | 50531 | New AECI Load Addition at Ameren Fredericktown 138 kV | Description of the load: At full capacity, it is expected that the customer will consume up to 75 MW. Overview of Ameren Fredericktown: In the Fall of 2025, Ameren will expand its 138kV ring bus at Ameren-Fredericktown. This substation is located about 3 miles from the customer load. | MO | AMEREN MISSOURI | Other | Load Growth | 2027-12-01 | 161 | 1200000
West | 50532 | Stiles - Sherwood 138 kV (L-142), Partial Rebuild | Replace select ~50 wood poles across the line that were originally treated with Chromated Copper Arsenate (CCA). The initial assumption is to transfer existing wires. CCA treatment visually makes the poles look ‘green’ in the field and is a known bad performer on our footprint and in the industry. These poles are more brittle, decayed, dry out faster and susceptible to mechanical failure. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-05-01 | 138 | 7000000
West | 50533 | S1016 Lone Rock SS Network Upgrades | S1016 is a 25 MW Surplus project Richland County, WI. The S1016 project consists of battery storage at the J864 collector station. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2026-09-05 | 69 | 800000
West | 50534 | J1824 Academy SS Network Upgrades and Interconnection Facilities | J1824 is a 67 MW solar facility located in Columbia County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-12-31 | 138 | 10244000
West | 50535 | J1732 Wolfram Rd SS Network Upgrades and Interconnection Facilities | J1732 is a 98.4 MW solar facility in Columbia County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-12-31 | 138 | 9894000
Central | 50538 | J1386 IC Facilities | Construct Transmission Owner’s Interconnection Facilities at Transmission Owner’s Green Acres Substation consisting of one monopole, H frame pull off structure, metering equipment, conductor, and fiber optics. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2028-05-31 | 138 | 8123620
South | 50539 | Cargas 500 kV and Smalling 500-230 kV stations | Entergy is proposing to construct two new 500/230 kV stations to serve a new customer cut into the existing Perryville (Cargas) to Baxter Wilson 500 kV line in Holly Ridge, LA. Cargas 500 kV station will be cut into the Perryville to Sterlington 500 kV lines 1 and 2 and Perryville to Baxter Wilson 500 kV line. Smalling 500/230 kV station will be cut into the Cargas to Baxter Wilson 500 kV line. Two additional 27 mile 500 kV lines from Smalling to Cargas. The Smalling 230 kV station will be a breaker and a half substation, including four 1,500 MVA 500/230 kV autotransformers and eight 230 kV lines going to six 230 kV stations which will feed the new load. Upgrade Sterlington 500 kV Line trap on the El Dorado line, due to the loss of Grand Gulf Generation overloading the Sterlington to El Dorado 500 kV line. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2026-12-01 | 500 | 1210000001
South | 50540 | Sarepta to Mount Olive 500 kV Project | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer | LA | ENTERGY SERVICES, LLC. | BRP |  | 2028-12-01 | 500 | 470100002
South | 50541 | El Dorado 500/345kV Autotransformer Upgrade | EAL is proposing to upgrade the El Dorado 500/345kV Autotransformer including associated station equipment. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2028-12-01 | 500 | 35725000
West | 50511 | J1746 Columbia SS Network Upgrades and Interconnection Facilities | J1746 is a 150 MW solar facility in Columbia County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2029-06-11 | 138 | 1845000
West | 50512 | J1778 Paris SS Network Upgrades | J1778 is a 100 MW solar facility in Kenosha County, WI. Per the J1778 GIA, there are no TOIFs associated with this project. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-11-09 | 138 | 811000
West | 50124 | Portage SS Relay and Breaker Asset Renewal | Asset Renewal of the Portage SS control house, all assets within the control house, and 5 oil circuit breakers. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 138 | 7100000
West | 50125 | Rock River SS and Remote Ends Asset Renewal | Asset Renewal of several relay panels, disconnect switches, and two battery banks at Rock River SS. Project also includes asset renewals of several relay panels, RTU panel, disconnect switches, and battery bank at Town Line Road SS. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 138 | 5614000
West | 50126 | Coyne Street SS Relay, Breaker and House Asset Renewal | At Coyne Street SS, asset renewal of four 115 kV oil circuit breakers, six 115 kV disconnect switches, and 1 control house with all panels and components. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 115 | 7950000
West | 50127 | Finger Road SS Relays and Remote Ends Asset Renewal | Asset Renewal of the Finger Road SS control house and all assets within the control house. Project also includes the remote end asset renewal of 3 relay panels and the RTU panel at Danz Avenue. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 69 | 5801000
West | 50128 | Eden SS Relay and House Asset Renewal | Asset Renewal of the Eden SS control house and all assets within the control house. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 138 | 5081000
West | 50134 | Huiskamp - Division Street Tap 69 kV (Y-132), Rebuild | Rebuild and install OPGW on approximately 2.7 miles of Y-132 from Huiskamp SS to Division Street Tap switch structure, in addition rebuild 0.2 miles of the Division Street Tap to Division Street SS and install OPGW from Waunakee to Huiskamp SS. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-11-30 | 69 | 8500000
West | 50542 | S1025 Sheepskin SS Network Upgrades | S1025 is a 25 MW Surplus project in Rock County, WI. The S1025 project consists of battery storage at the J1188 collector station. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-06-15 | 69 | 225000
West | 50543 | Racine County, DIC, Cosmos Substation | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, 138 kV capacitor banks, and 4 – 345 kV line terminals, and 1 – 138 kV line terminals with a series reactor. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2028-04-01 | 345 | 195000000
West | 50544 | MPFCA Rockdale SS Network Upgrade | Each individual Interconnection Customer is responsible for a proportionate percentage share of the CUU estimated cost based on its proportionate impact on the constrained facilities causing the need for the CUU. Constrained facilities are those CUU facilities that are being upgraded in Section 1.2. J1502 is seeking interconnection service for 225 MW, J1629 is seeking interconnection service for 200 MW, J1706 is seeking interconnection service for 100 MW, J1732 is seeking interconnection service for 98.4 MW, J1746 is seeking interconnection service for 150 MW, J1773 is seeking interconnection service for 300 MW, J1779 is seeking interconnection service for200 MW, J1781 is seeking interconnection service for 300 MW, J1824 is seeking interconnection service for 67 MW. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2027-10-10 | 138 | 1120000
West | 50545 | J1752 Shady Dr SS Network Upgrades and Interconnection Facilities | J1752 is a 148.1 MW solar facility in Portage County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2028-05-15 | 138 | 16455000
South | 50546 | Bluepoint 230 kV New Substation and line Cut-ins | Entergy is proposing to construct a new 230 kV four breaker ring bus station named Bluepoint to serve a new customer cut into the new Commodore to Waterford 230 kV line (~10.4 miles in and out) near Donaldsonville, LA. The Bluepoint 230 kV station will also include (2) 150MVA transformers, (4) 3000A breakers. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2027-08-01 | 230 | 59600000
West | 50547 | East Beloit SS, DIC, Sub Rebuild | In support of a distribution substation relocation/rebuild, ATC will extend COR-BEG 138kV (X-41) line approximately 0.15 mile (double circuit transmission) to the new East Beloit substation and install 2 sets of bus-tie disconnect switches. ATC will retire COR-ESB 69kV (Y-140) line (Approx. 0.5 miles) and the existing East Beloit SS location and install 2 line circuit breakers and 2 line disconnects at Dickinson SS. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2028-12-30 | 138 | 7200000
West | 50548 | Juneau Industrial SS, DIC, Transformer Addition | In support of a distribution transformer addition, ATC will rebuild Juneau Industrial and will install 1 bus-side load break disconnect switch, 1 bus side air break 2 bus-tie disconnect switches. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-01 | 69 | 4800000
West | 50549 | Waupun Business Park SS, DIC, Transformer Addition | To support a new distribution substation and associated station retirements, ATC will loop through the existing WAN-WANT 69kV (Y-306) line for new Waupun Business Park SS. ATC will install 2 line disconnect switches and 2 bus-tie disconnect switches. ATC to retire portion of WAN-WANT 69kV (Y-306) line to Waupun Westside (WAW), Waupun Southside (WSS) and Comtech (COMH). | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2028-12-31 | 69 | 3200000
West | 50550 | North Monroe Breaker and SCADA Asset Renewal | Replace 138kV Capacitor cans and update bank specifications and equipment as appropriate. ATC Planning to confirm the required MVAR capacity and switching device required. Replace relay panels and Station Manager RTU. Install to current ATC standards including Dual bus differential relays on the 69kV and 138kV busses. Replace 69kV Siemens model SP breaker in Position 719-S. Replace three Turner Electric disconnects and one ITE model HPL disconnect. Replace S&C circuit switcher in Position 207-S. Replace station power transformer connected to 69kV bus. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 138 | 3105000
Central | 50551 | New Stillwell to Elderberry 345kV Line | The project is to construct a 345kV line from AEP’s Elderberry Substation to NIPSCO’s Stillwell substation. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2028-12-31 | 345 | 75000000
Central | 50577 | Henderson County Capacitor Bank | Henderson County Capacitor Bank Addition | KY | BIG RIVERS ELECTRIC CORPORATION | Other | Local Reliability | 2027-12-01 | 69 | 1500000
South | 50581 | Fort Mountain 161kV: Build New Substation | Build 1 mile of in and out cut-in transmission line to a new 161 kV substation called Fort Mountain on the Berryville - Green Forest 161kV line section in Berryville, AR. Entergy will construct and operate the high-side through bus of the station only. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2026-03-31 | 161 | 5727876
South | 50586 | 2026 ETI Asset Renewal Program | This project is for the ETI Asset Renewal Program that will be executed in 2026 | TX | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2026-12-31 | 500 | 34400000
West | 50587 | Darnen Substation | Tap the Great River Energy (GRE) owned 'AG-MB' 115 kV line between Morris and Walden to serve a new distribution substation with an 'in-and-out' configuration. | MN | GREAT RIVER ENERGY | Other | Load Growth | 2026-09-15 | 115 | 2362888
West | 50588 | Forest Junction – Branch River 345 kV (W-15), Line Uprate | Uprate W-15 Forest Junction – Branch River 345 kV line per ATC T-Line design standards to achieve minimum 1918 Amps (1146 MVA) normal and 2490 Amps (1488 MVA) emergency ratings for all seasons. | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2029-01-01 | 345 | 7754000
East | 50590 | Upgrade Sunset 120 kV Switch | Upgrade the 1200A switch "HI" at Sunset 120 kV station. | MI | ITC | BRP |  | 2030-06-01 | 120 | 168000
East | 50591 | Install Phoenix 120 kV Capacitor | Install a 50 Mvar capacitor with 40 kA synchronous breaker and associate switch at Phoenix 120 kV bus 103. | MI | ITC | BRP |  | 2030-06-01 | 120 | 1500000
South | 50594 | Helena Harbor Load Addition | A member cooperative has a new customer that will be adding a 250MW load. A new 230kV station (Helena Harbor) will be constructed and served on a new, approximately 6-mile radial off Entergy's existing Ritchie 230kV station. Entergy will add a new 230kV position at their Ritchie station to accommodate this new 230kV radial. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Other | Load Growth | 2028-12-01 | 230 | 18200000
East | 50597 | DTE New Hudson Interconnection | DTE interconnection for 120kV service in Lion Township. Cut in New Hudson (formerly Walbridge) 120kV station on the Cody – Proud 120kV line about 0.15 mile from Tamarack 120kV Tap. ITC will construct New Hudson as a new 4-breaker ring bus configuration, 120 kV station and allow enough space for future breaker and a half station configuration once DTE’s future positions are needed. Also cut in Cody – Proud 120 kV line about 0.15 mile from Tamarack 120 kV Tap into New Hudson 120 kV station. We want to reserve 4 additional rows for future connections. Install two 120/13.2 kV transformers with circuit switchers for high side protection. DTE want to build a substation with at least five connection points to 120 kV. DTE will want three connection points for a general-purpose substation and at least two extra positions if industrial substation(s) are needed. | MI | ITC | Other | Load Growth | 2028-03-31 | 120 | 12163500
West | 50598 | Progress SS, DIC, Substation Rebuild | ATC will install a 138 kV loop through substation on the Aviation - Ellinwood 138 kV (X-50) line with line switches to support a distribution substation rebuild. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-30 | 138 | 2500000
Central | 50599 | New Merom 345 kV Substation Load Addition | Extend a new 345kV line from Merom Transmission Station, approximately 1-mile, to a new data center. The data center has a total estimated load of 620 MW at 95% PF (653 MVA, 204 MVAR). | IN | HOOSIER ENERGY | Other | Load Growth | 2026-07-01 | 345 | 12790684
South | 50600 | Oak Bend 230 kV station | The Oak Bend 230 kV breaker and a half substation will be fed out of a new Baxter Wilson 230 kV substation. The existing Baxter Wilson 500 kV substation will expanded to include a new Baxter Wilson 230 kV substation fed from 2-500/230 kV Auto Transformers. Two bays to connect to (2) 3-mile 230 kV lines to the Oak Bend 230 kV substation. Customer load will be fed out of (3) 150 MVA 230/34.5 kV transformers. | MS | ENTERGY MISSISSIPPI, LLC. | Other | Load Growth | 2029-12-01 | 500 | 150000002
South | 50601 | Andes 230 kV Expansion | Expansion of the 230 kV Andes substation to include 3 additional bays, 9 breakers to allow for customer load addition and reactive resource installation. | MS | ENTERGY MISSISSIPPI, LLC. | Other | Load Growth | 2028-04-01 | 230 | 40000000
South | 50602 | Green Acres 500/230 kV New Substation | Construct a new 500/230 kV Green Acres Substation to serve a new customer. Green Acres 500 kV substation will be 4 bay breaker and a half substation. 500 kV will be cut in on Lakeover – Ray Braswell 500 kV and Lakeover - McAdams 500 kV lines. The Green Acres 230 kV station will be a 6 breaker ring expandable breaker and half scheme, including two 1200 MVA 500/230 kV autotransformers and 6 breakers with 5 nodes. 3-1 mile 230 lines supplying the new 230 kV County Line substation to support customer load. Construct County Line 230 kV substation breaker and a half station with 8 bays to support customer load and reactive resources | MS | ENTERGY MISSISSIPPI, LLC. | Other | Load Growth | 2029-12-01 | 500 | 312000002
West | 50603 | OTP Big Stone South Load Addition | OTP has a new customer requesting to be served near Big Stone, SD. OTP will serve the new customer by building a new 230/34.5 kV distribution substation connecting to the Big Stone South to Crowned Ridge 230 kV line right near the Big Stone South substation. | SD | OTTER TAIL POWER COMPANY | Other | Load Growth | 2025-09-19 | 230 | 0
South | 50608 | Riparian 115 kV Station | Entergy is proposing to construct a new 115 kV station named Riparian to serve a new customer cut into the existing Alliance to Happy Jack 115 kV line in Point Celeste, LA. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2026-12-30 | 115 | 38200000
West | 50612 | Terrace Ave Riser SS 69kV Pumping Plant Upgrade | Modernize the technology for the HPFF (high-pressure fluid-filled) pressurizing system, install physical security, install expanded metal fence, and make modifications to existing building to address corrosion issues at Terrace Ave Riser SS. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-01 | 69 | 3200000
West | 50613 | Central SS, DIC, New Substation | Construct a new substation with one new 69/12.47 kV, 3.75/5.25 MVA transformer with high-side switch. Install 3-way MOD with supervisory control near Y-71 structure 99. Route approx. 0.5 miles of new 69kV line to new SS location. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2026-04-01 | 69 | 3200000
Central | 50614 | New Marble Hill 345 kV Station and Load | Construct a new 345kV ring-bus station on the 08TRIMBL (249532) – 7GHENT (324105) transmission line, approximately 4 line-miles from LGEE’s Trimble County Generator Station. New customer will construct substation adjacent to ring-bus station. The station will serve a new data center with a total estimated load of 310 MW at 95% PF (344 MVA, 150 MVAR). | IN | HOOSIER ENERGY | Other | Load Growth | 2027-10-01 | 345 | 20500000
Central | 50615 | New Central 138 kV Substation Load Addition | Add a 138 kV position at Central substation for a new load. | MO | AMEREN MISSOURI | Other | Load Growth | 2028-06-01 | 138 | 1000000
Central | 50616 | New Rootbeer 345 kV Substation Load Addition | To serve the load proposed, Ameren will add a position at Rootbeer substation. | MO | AMEREN MISSOURI | Other | Load Growth | 2026-12-01 | 345 | 2000000
Central | 50617 | New 345 kV Lumberjack substation for Load Connection | Construct a new 345 kV substation called Lumberjack 8 position ultimate BAAH bus arrangement for the connection of Load Addition at New Florence, MO | MO | AMEREN MISSOURI | Other | Load Growth | 2027-12-01 | 345 | 38500000
Central | 50104 | Upgrade PJM project b3775.8 St. John to Crete 345 kV | Upgrade the existing terminal substation conductor at St. John on the existing St. John to Crete 345kV line. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2026-06-01 | 345 | 1150000
Central | 50105 | Reconfigure PJM project b3775.9. Green Acres 345kV substation | Project will reconfigure the existing St. John and Green Acres 345kV connections creating a Green Acres to University Park 345kV line and St. John to Olive 345kV line | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2026-06-01 | 345 | 2150000
Central | 22881 | Upgrade Belleau 138 kV substation | Expand Belleau by adding 2 positions for O'Fallon so they don't tap the lines. (i.e. (2)new 138kV Line positions for 138kV Feeds to O'Fallon) | MO | AMEREN MISSOURI | Other | Local Reliability | 2027-06-01 | 138 | 3000000
Central | 22908 | Rebuild Joppa - Marion South 161kV line | Rebuild the Joppa-Marion South-1 161 kV line on direct-embed steel H-Frame structures with conductor capable of carry 2000 amps at Summer Emergency conditions. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2030-12-01 | 161 | 46500000
Central | 22788 | Rebuild Prest-Tibbs 138 kV line (1558) | Repair issues found during inspections on the Prest-Tibbs 138 kV Line (1558) | IL | AMEREN ILLINOIS | Other | Local Reliability | 2025-12-01 | 138 | 23000000
Central | 22874 | Upgrade Ashley 161 kV substation | Install high side interrupting devices on XFMRs 1, 2, & 3 Install line breakers on Cahokia and Hall Street | MO | AMEREN MISSOURI | Other | Age and Condition | 2027-12-01 | 138 | 4100000
Central | 25269 | Replace West Frankfort East 345/138 kV transformer 1 | At West Frankfort East substation replace the existing 560 MVA 345/138 kV Transformer 1 with a new 345/138 kV 700 MVA transformer. Replace 138 kV breaker 1520 and 345 kV circuit switcher C3550. Also replace limiting bus conductor on the 138 kV Transformer 1 branch. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-01 | 345 | 10600000
West | 24925 | Range Line Dist (WE) - Range Line Switchyard 138 kV (61452), Replace Underground Cable | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-06-01 | 138 | 6000000
West | 24982 | Range Line Dist (WE) - Range Line Switchyard 138 kV (61441), Replace Underground Cable | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-06-01 | 138 | 4000000
West | 25161 | Sun Prairie Area Reliability Project | The Sun Prairie Area Reliability Project provides additional sources in the Sun Prairie Area to prevent thermal overloads due to multiple contingencies. Sun Prairie Area Reliability Project scope is as it follows: • Loop through Sun Prairie – Kegonsa (Y-81) 69-kV line in Reiner Road SS, constructing a 2-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Reiner Road SS. Finally, install new equipment due to asset renewal needs. • Loop through DeForest – Sun Prairie (Y-137) 69-kV line in Yahara River SS, constructing a 1.1-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Yahara River SS. Finally, install new equipment due to asset renewal needs. • Jumper replacements in Sun Prairie SS and additional modifications due to asset renewal needs. | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2029-06-30 | 138 | 61450000
West | 25185 | Small Capital Project and Asset Renewal Program 2026 | Asset replacements and upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Transmission Line Projects typically (but not limited to): - Structure, Cross-arm, Insulator, Surge-arrester, and Pole hardware replacements. Substation Projects typically (but not limited to): - Relays, Circuit breakers, Switches, Instrument Transformers (CTs & PTs etc.), Batteries, RTUs, and IT/OT/Communications hardware replacements. Project drivers may be Asset Renewal or small system limit upgrades. These projects have limited scope and cost. Initial capital spend for this program expected in 2026. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2031-03-31 | 345 | 45000000
South | 25541 | Line 5 Rebuild | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 69kV) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2026-04-01 | 69 | 6100000
Central | 22907 | Upgrade Tuscola West 138 kV substation | Install ring bus at Tuscola West 138 kV Substation after addressing aging infrastructure | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-01 | 138 | 5800000
Central | 25328 | Upgrade Charleston NE 138kV line | Add line breakers and address aging infrastructure items on Charleston NE 138 kV Line | IL | AMEREN ILLINOIS | Other | Age and Condition | 2027-06-01 | 138 | 4019794
West | 25187 | Load Interconnection Program 2026 | Load Interconnection Project life cycles are customer need driven and typically have shorter project life cycles. These Load Interconnections typically require limited infrastructure modifications and additions. These projects have limited scope and cost. Initial capital spend for this program expected in 2026. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-12-31 | 345 | 19000000
West | 24924 | Straits SS Power Transformer Asset Renewal | Power Transformer Asset Renewal at Straits SS. | MI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-12-01 | 138 | 11200000
Central | 25018 | New Moonshine Solar Bootleg 138 kV switching station (J1382) | The J1382 150MW Solar Interconnection Switching Station will split the existing Hutsonville-Neoga South-1 138 kV. | IL | AMEREN ILLINOIS | GIP |  | 2025-12-01 | 138 | 8000000
Central | 25040 | Replace Tyson 345/138 kV transformer 3 | Replace Tyson XFMR 3 with a new 345/138kV 700 MVA unit. | MO | AMEREN MISSOURI | Other | Age and Condition | 2030-12-01 | 345 | 8500000
West | 50149 | Arrowhead 230kV SPF Upgrade | Add redundancy or monitoring to the single point of failures to mitigate P5 contingencies associated with the Arrowhead 230kV buses. | MN | MINNESOTA POWER INC. | BRP |  | 2028-12-31 | 230 | 3000000
West | 50153 | Owatonna 161kV Cap Bank Addition | Addition of a 47MVAr cap bank to the existing West Owatonna Substation. | MN | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | BRP |  | 2027-01-01 | 161 | 3500000
Central | 50154 | Grain Belt Express AECI Facilities Construction Agreement (GI-083) | The network upgrades outlined in the affected system study for AECI GI-083 are being performed to accommodate the interconnection with GrainBelt Express HVDC interconnection (GBX) at McCredie substation. This is required per Ameren's contractual obligation with GBX and in compliance with FERC Order 888, Promoting Wholesale Competition Through Open Access Non-discriminatory Transmission Services by Public Utilities. | MO | AMEREN MISSOURI | GIP |  | 2027-12-01 | 345 | 70460000
West | 50157 | Big Cedar Load Expansion | Interstate Power and Light Company (IPL) has requested to interconnect two new loads to the transmission system the Cedar Rapids, Iowa area. ITC Midwest is proposing to serve the new load from the Big Cedar Switching Station which requires expansion to serve the two new loads. In addition to expanding the Big Cedar Switching Station, ITC Midwest will be installing reactive compensation at the Big Cedar Switching Station to support this load addition. ITC Midwest will also add a 2nd Big Cedar – Morgan Valley 345 kV line on the existing structures of the Big Cedar – Morgan Valley 345 kV line and construct a new Beverly – Hills 345 kV line to support the load addition. The LRTP Tranche 1 Marshalltown (Twinkle) - Morgan Valley 345 kV line is required to support the first phase of the load addition, and the LRTP Tranche 1 Beverly – Sub 92 345 kV line is required to support the second phase of the load addition. | IA | ITC MIDWEST | Other | Load Growth | 2028-09-30 | 345 | 380549625
West | 50161 | Empire Mine – Huron 138 kV (X-119), OPGW Addition | ~10.4 Miles of OPGW Installation - This project will align with the 446 T-Line Reinsulate Project between the National and Presque Isle substations as well as the ~7.5 Miles of OPGW Installation on X-118 (MTEP24) will provide an alternate fiber path establishing two diverse OPGW fiber routes providing high-speed fiber communications connecting into ATC larger OPGW Network Infrastructure. | MI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2027-12-31 | 138 | 13000000
West | 50162 | Substation Technology Package #2 – 2026 | High level scope is to install Wi-Fi AP’s & Rogue Detection at various substations and remove Inverter equipment at various substations to complete the Wireless connectivity and Cyber Security fortifications. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2026-12-31 | 0 | 11700000
Central | 50163 | New J1358 IC Facilities Interconnection 138 kV | Interconnection Facilities to Connect J1358 to NIPSCO's Luchtman Rd to Shoreline 138kV line | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2028-05-31 | 138 | 23396985
West | 50165 | Racine County, DIC, Stratus Substation | A new 138/24.9 kV breaker-and-a-half substation named Stratus, 138 kV capacitor banks, and construct short transmission lines to cut into the Mount Pleasant-Nimbus 138 kV lines (X-171, X-172) and loop in and out of the Stratus Substation. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2026-07-31 | 138 | 68500000
West | 50166 | Racine County, DIC, Mount Pleasant Substation Expansion | Install a new 500 MVA, 345/138 kV transformer, +/- 350 Mvar STATCOM, 138 kV capacitor banks, and associated 345 kV and 138 kV substation facilities. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-01-01 | 345 | 117000000
West | 50167 | Racine County, DIC, Jupiter Substation | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, +/- 350 Mvar STATCOM, 138 kV capacitor banks, 4 – 345 kV line terminal. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-01-01 | 345 | 295000000
West | 50168 | Racine County Western Feed Transmission Line Project | Construct two new 345 kV double circuit lines from the existing Arcadian – Pleasant Prairie (PLPL81)/Arcadian – Paris (W-30) 345 kV double circuit line to loop in and out of the Jupiter and Mount Pleasant. Construct a new Jupiter – Mount Pleasant 345 kV line. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-01-01 | 345 | 124000000
Central | 50731 | IPL Adoption of Seasonal Ratings - BRP | Indianapolis Power & Light is changing its Facility Rating Methodology to adopt seasonal ratings. This project covers all Facilities changes classified as BRPs. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Local Reliability | 2029-12-31 | 345 | 0
Central | 23530 | New Spencer Creek generation interconnection MPFCA (J956/J1026) | Expand 345kV bus at Spencer Creek Substation to connect J956 and J1026 | MO | AMEREN MISSOURI | GIP |  | 2024-05-03 | 345 | 4600000
South | 25436 | Bobville Area Menu Phases 1 through 7 | Phase 1 is relay improvement at Grimes 345 and 138 kV stations needed by 2025 Summer. Phase 2 adds the first 25.1 MVAR capacitor bank at Dobbin 138 kV substation needed by 2026 Summer. Phase 3 adds the second 25.1 MVAR capacitor bank at Dobbin needed by 2029 Summer. Phase 4 rebuilds the existing Fish Creek - Deer Lake 138 kV line needed by 2031 Summer. Phase 5 rebuilds the existing Dobbin - Tubular 138 kV line needed by 2031 Summer. Phase 6 rebuilds the existing Deer Lake - Spring Branch 138 kV line needed by 2034 Summer. Phase 7 rebuilds the existing Dobbin - Spring Branch line needed by 2034 Winter. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2034-12-31 | 345 | 138000000
West | 25186 | Communications Reliability Program 2026 | Communications network system upgrades typically require limited infrastructure modifications and additions with shorter project life cycles. Substation Communications Reliability Upgrade projects are typically (but not limited to): - OPGW additions, replacements, relocations, or removals. - Project drivers typically are communications support for SCADA, Relay protection, Security systems, Small communications network upgrades, and Telecom industry market transitions. These projects have limited scope and cost. Initial capital spend for this program expected in 2026. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2028-06-30 | 345 | 2100000
West | 24919 | Mill Road – Granville Project | - Construct new 345/138 kV Mill Road SS, with one 500 MVA 345/138 kV transformer, - Loop in Granville – Arcadian 345 kV line and Cypress – Arcadian 345 kV line to new Mill Road 345 SS, Rebuild Mill Road SS – Granville SS section as 345 kV double circuit, - Loop in Germantown – Bark River 138 kV line and west portion of the Tamarack – Sussex 138 kV line into new Mill Road 138 kV SS, install series reactor in line to Sussex. - Construct new Mill Road SS – Tamarack SS – Butler SS 138 kV line, - Butler SS 138 kV reconfiguration, and install series reactor between Butler bus 1 and bus 2, - Granville SS 345 kV ring bus expansion, Replace 345/138 kV transformer T3. | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2027-10-01 | 345 | 423705000
West | 25264 | Ridgeview Transformer Addition | Add 115/34.5 kV transformer to existing Ridgeview Substation. This project includes adding one breaker to the existing Ring Bus for the transformer addition. | MN | MINNESOTA POWER INC. | Other | Local Needs | 2027-12-31 | 115 | 2000000
West | 25314 | Pittsville Area Reliability Project | • ATC will construct ~9.6 miles of single circuit 138 kV transmission line to interconnect the proposed distribution substation. • ATC will construct a 138 kV loop-through straight bus with three line breakers to accommodate tapping X-42 and terminating the new line. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2028-12-31 | 138 | 35900000
Central | 9740 | Reconductor Grand Tower-Campbell Hill 138 kV line | Reconductor Grand Tower-Campbell Hill 138 kV Line to 2000 A summer emergency capability | IL | AMEREN ILLINOIS | Other | Age and Condition | 2029-12-01 | 138 | 34900000
East | 20020 | Rebuild Gaylord - Mio Dam 138kV line | Rebuild the Gaylord – Mio Dam 138kV line with 954 ACSR overhead conductor capable of double circuit 230kV. OPGW will be installed on the rebuild. Terminal equipment at Gaylord and Mio Dam substations will need to be upgraded. | MI | METC | Other | Age and Condition | 2029-12-31 | 138 | 87254000
Central | 50696 | New Huster-McClay 138 kV line tap for Hayford load | Temporary line tap on Huster-McClay 138 kV for new customer load | MO | AMEREN MISSOURI | Other | Load Growth | 2027-06-01 | 138 | 500000
Central | 50698 | New Scotland 345/69kV Substation | Construct a new 345kV ring-bus with 345/69kV transformation on the 16PETE (254529) – 16W_BLOOMGTN (254526) transmission line, approximately 35 line-miles from IPL’s Petersburg station and 19 line-miles from DEI’s planned 16W_Bloomington station. Extend a 69kV line from the new station to serve a new 20 MW customer. Bring the Hoosier Scotland-Bloomfield 69kV transmission line into the new 69kV station. Open 69kV branch 248537- 248538. | IN | HOOSIER ENERGY | Other | Load Growth | 2029-12-01 | 345 | 38000000
West | 50702 | Elm Road HVB Breaker and Relay Asset Renewal | Replacement of (5) 345kV HVB SF6 breakers and jumpers with new SF6 gas breakers at Elm Road. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2029-12-01 | 345 | 8400000
West | 50711 | Brookings County - Lyon County 345kV Davit Arm Replacement | Age and Condition replacement of Davit Arms on Brookings County - Lyon County, Lyon County - Helena, Hampton - Helena 345kV lines. Project is categorized as MVP because it replaces assets associated with previously approved MTEP11 MVP #1203 - Candidate MVP Portfolio 1 - Brookings, SD - SE Twin Cities 345 kV. | MN; SD | NORTHERN STATES POWER COMPANY | MVP |  | 2030-09-30 | 345 | 91900000
Central | 50077 | New Aster 138 kV interconnection (J1777) | The Great Plains Solar (J1777) Generating Facility will interconnect with the Transmission System via a 138 kV leadline running from the Interconnection Customer's collector substation to the Transmission Owner's Aster Substation in Perry County, IL. IF POS | IL | AMEREN ILLINOIS | GIP |  | 2026-06-01 | 138 | 800000
Central | 50084 | New Ramsey East 138 kV Connection (J1714) | Install a new 138 kV line position to serve as the Point of Interconnection for Saluki Solar, LLC within the Ramsey East Substation. IF POS | IL | AMEREN ILLINOIS | GIP |  | 2026-12-01 | 138 | 800000
Central | 50100 | Rebuild Baumgartner 138 kV Substation | This project will replace aging infrastructure at Baumgartner 138 kV substation | MO | AMEREN MISSOURI | Other | Age and Condition | 2028-06-01 | 138 | 6300000
Central | 50185 | Replace Marion South 161/138 kV transformer | Replace XFMR 1 at Marion South with a new 161/138kV 300 MVA unit | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-01 | 161 | 3600000
Central | 50186 | Grain Belt Express HVDC Network Upgrades (H104-H105) | This transmission project includes all the network upgrades that are required to support generation interconnection projects H104 and H105. | MO | AMEREN MISSOURI | GIP |  | 2030-12-01 | 345 | 171000000
Central | 50189 | Rebuild Latham-Docket-1409 138 kV line (C1903 MPFCA) | Rebuild 5 miles of the existing 138 kV Latham-Docket-1409 with OPGW and 1600 A conductor. | IL | AMEREN ILLINOIS | GIP |  | 2027-12-01 | 138 | 4000000
Central | 50190 | New Peru-Princeton 138 kV line | Rebuild the existing Princeton substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 23-mile 138 kV Transmission line from Ameren's Princeton substation to the new substation near the City of Peru. | IL | AMEREN ILLINOIS | Other | Load Growth | 2029-06-01 | 138 | 90000000
South | 50191 | Beebe North 115kV SS - Nelson 115kV SS | AECC will construct a new Beebe North 115kV switching station (now called McRae) on EAI's Beebe to AECC's Ward 115kV transmission line. This new switching station will tap the Beebe to Ward line approximately 0.2 miles south of EAI's Beebe station. AECC will also construct a new, approximately 7-mile long, 115kV transmission line from the new McRae 115kV SS to a new Sylvania 115kV substation. Additionally, AECC will construct another new, approximately 7-mile long, 115kV transmission line from the new Sylvania station to a new Nelson 115kV switching station. The new Nelson 115 kV SS will tie into the Member Coop's existing 115kV system. | AR | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | BRP |  | 2028-09-01 | 115 | 37000000
West | 50192 | J1529 POI New 69 kV Interconnection Substation and 69 kV Line Taps | J1529 POI New 69 kV Interconnection Substation and 69 kV Line Taps | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2027-09-01 | 69 | 13800000
West | 50193 | J1530 POI New 69 kV Interconnection Substation and 69 kV Line Taps | Construct new 69 kV POI substation and 69 kV line taps for J1530 solar farm. | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2026-09-30 | 69 | 13800000
West | 50194 | J1532 POI New 69 kV Interconnection Substation and 69 kV Line Taps | Construct new 69 kV POI substation and 69 kV line taps for J1532 solar farm. | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2027-09-01 | 69 | 13900000
West | 50195 | Carroll County-Carroll South 69 kV Line Rebuild for DPP 2020 | Rebuild and reconductor the line to increase line rating. | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2027-12-01 | 69 | 7500000
South | 50196 | Admiral 138 kV New Substation and Transmission Line | The Admiral 138 kV station will be designed as a 138kV six breaker ring bus. The substation will include six (6) breakers, one (1) Cap Bank, two (2) 67MVA power transformers, and two (2) main/feeder breakers. Construction and installation of a new line from Moril substation to Admiral will also be part of the permanent scope of work, along with the installation of a new 138kV breaker at Moril. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2025-09-01 | 138 | 54400001
Central | 50198 | New Wieland Metals 138 kV Load Addition | Construct a new 138 kV substation, four position ultimate in a ring bus arrangement, 3000 Amps minimum continuous capability. The substation will be located approximately 1 mile east from the existing Wood River 138 kV substation. Split the existing Granite City 23rd Street-Wood River-1452 138 kV line and route into the new substation. Provide two positions at the new ring bus for the connection of Wieland Metals (Falls) | IL | AMEREN ILLINOIS | Other | Load Growth | 2026-12-01 | 138 | 10700000
South | 50199 | Rhodair 230 kV New Substation and Transmission Lines | Entergy is proposing to construct new 230 kV transmission lines sourced from the existing Garden 230 kV station to serve new load at the new Rhodair 230 kV station near Port Arthur, TX. The Garden to Rhodair 230 kV circuits 1 and 2 are a combined ~4.5 miles long. | TX | ENTERGY SERVICES, LLC. | Other | Load Growth | 2025-08-26 | 230 | 85000000
West | 50200 | PLPL81 and W-30 345 kV Line, Uprate | Uprate low rated segments of the Arcadian to Pleasant Prairie 345 kV line (PLPL81) and the Arcadian to Paris 345 kV line (W-30). The line ratings of both segments PLPL81 and W-30 will become insufficient in the near future as the transmission system will need to accommodate new loads and generation sources. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2027-01-31 | 345 | 9500000
Central | 50201 | Rebuild Slugger to LGE Trimble 34530 Ckt. 345kV Line | 34530 Rebuild - Slugger to LGE Trimble to (2)954ACSS@200C (DEI-owned portion only) | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2031-06-01 | 345 | 42964000
East | 50203 | Rebuild and Relocate Alma 138 kV substation | Rebuild the 138 kV Alma station to three rows of breaker and a half station capable of three additional rows of BAH expansion. Install eight (8) 138 kV, 3000 A breakers with at least 40 kA interrupting capability. Install new control house and 25 MVAR capacitor. Reterminate all lines into the new station. Decommission and remove all equipment at the Alma 138 kV site. | MI | METC | Other | Local Needs | 2029-12-31 | 138 | 15190000
West | 50204 | Clinton Rail and Air Park 161 kV Interconnection | IPL has requested a new substation interconnection in the Clinton area for a new load in the Clinton Rail and Air Park. To facilitate the request ITC Midwest will be building a new 161 kV 2 row 4 position breaker and ½ substation with 2 line positions and 2 transformer positions. The new substation will be expandable to 4 rows. All new 161 kV equipment will be capable of 2000A or greater. The new substation will be a PD substation and the common facilities and substation naming will be owned by IPL. | IA | ITC MIDWEST | Other | Load Growth | 2026-06-01 | 161 | 8760389
West | 50205 | Belmond Diesel to Hancock 69 kV Line Reroute | Erosion around the existing Belmond Diesel to Handcock line is proving troublesome. Rebuild is not an option due to the close proximity of the river and the railroad. The Belmond Diesel to Handcock line is to be Re-routed to a different river crossing location. The potential re-route would call for 0.44 miles of double circuit with Corn Belt Power Co-op, 1.8 miles along US Highway 69, and 0.54 miles along 168th St. All new line is to use T2-4/0 ACSR conductor. | IA | ITC MIDWEST | Other | Age and Condition | 2028-12-31 | 69 | 4097500
West | 50206 | Rock Creek T2 Replacement | The existing Rock Creek T2 transformer is at the end of its useful life and in need of replacement. T2 will be replaced with a new 150 MVA 161/69 kV transformer with LTC, and the existing motor operated switch will be removed and replaced with a new high side breaker and disconnect. | IA | ITC MIDWEST | Other | Age and Condition | 2027-12-31 | 69 | 4044728
West | 50207 | Spirit Lake Anchor 69 kV Interconnection | IPL is to build a new 69/25 kV substation to be named Sprit Lake Anchor. ITCMW is to build the 69 kV portion of the substation. This substation will be located nearby the existing Spirit Lake South substation and is intended to take the load from the Spirit Lake South, Orleans, and Spirit Lake West substations. The new substation will support two IPL owned 69/25 kV 33/50 MVA transformers and one ITC owned capacitor bank rated at 13.2 Mvar(rated)/11.225 Mvar(effective). | IA | ITC MIDWEST | Other | Load Growth | 2028-12-31 | 69 | 5398911
Central | 50208 | New LEAP Transmission Network | A large customer has committed to the LEAP District, an innovation district west of Lebanon, IN in Boone County. This data center customer will be ramping to 600 MW of total demand. To meet the load requirements, WVPA will connect into the Whitestown-Hortonville 345kV line and construct a new 345/138kV substation, approximately 10 miles of double circuit 345kV, two 138kV stations and approximately 25 miles of 138kV transmission. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2026-12-31 | 345 | 222200000
South | 50209 | South China 138 kV New Substation | South China 138 kV station will be interconnected on the Cheek - Petry Woods 138 kV line. | TX | ENTERGY SERVICES, LLC. | Other | Load Growth | 2025-05-12 | 138 | 5800000
West | 50210 | Keokuk West Relay Replacement and 69 kV Tie Breaker Addition | IPL has notified ITC that due to aging equipment and to support their future conversion in the area, they will be doing a complete rebuild of the Keokuk West substation. As part of this, ITC will build a new, separate control enclosure and replace all of its existing relays and install a new bus tie breaker. | IA | ITC MIDWEST | Other | Age and Condition | 2027-12-31 | 69 | 2958416
West | 50211 | Hayward - County Line - Ellendale 69 kV Rebuild | Rebuild the 13.34 miles between Hayward and County Line and 5.71 miles between County Line and Ellendale. The line will be rebuilt with T2-477 ACSR conductor and OPGW for communications path between Ellendale – County Line – Hayward. | IA | ITC MIDWEST | BRP |  | 2028-12-30 | 69 | 16015755
East | 50212 | Avery - New DTE Interconnection | DTE interconnection for 120 kV service in Detroit City. Cut the Frisbie – Waterman 120 kV line about 2 miles from Frisbie 120 kV to loop in the new ITCT’s Avery Substation. ITC will build a new Avery 120 kV station as a five (5) breaker ring bus configuration. DTE will install capacitor banks connected to 13.2 kV side, two 120/13.2 kV transformers with breakers for high side protection. | MI | ITC | Other | Load Growth | 2027-09-30 | 120 | 16713000
West | 50213 | Rock Creek 345 kV Substation Expansion and Rock Creek - Quad Cities #2 345 kV line | ITC will be expanding the Rock Creek 345 kV substation to accommodate two additional 345 kV lines. ITC will be installing the 2nd Quad Cities to Rock Creek 345 kV circuit and increasing the rating on the existing circuit. The substation will be expanded to a Breaker and a Half configuration. All new substation equipment will be capable of 3000 Amps or greater. | IA; IL | ITC MIDWEST | Other | Local Reliability | 2028-12-31 | 345 | 44412329
Central | 50216 | Upgrade Petersburg 138 kV Breakers - 3 Breakers | Upgrade existing 138 kV Petersburg breakers 6, 7, & 9 from 40 kA to 63 kA. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2031-12-01 | 138 | 739000
Central | 50217 | Upgrade Stout South Breakers - 12 Breakers 138 kV | Upgrade Stout South 138 kV breakers 1A, 2A, 2C, 3A, 3B, 3C, 4A, 4C, 5A, 5B, 5C, and 5D from 63 kA to 80 kA. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2031-12-01 | 138 | 3050000
West | 50218 | Riverton STATCOM | Placing a +/- 300 MVAR STATOM at the Riverton 230 kV Substation | MN | MINNESOTA POWER INC. | BRP |  | 2028-03-31 | 230 | 70000000
Central | 50220 | Rebuild McCredie-Overton 345 kV Line (MPFCA) | Rebuild 35.5 miles of the 345 kV McCredie-Overton transmission line, including a river crossing | MO | AMEREN MISSOURI | GIP |  | 2031-06-01 | 345 | 63115000
Central | 50221 | Rebuild Overton-McBaine Tap 161 kV Line (MPFCA) | Rebuild the existing Loy Martin – Overton 161 kV transmission line from the McBaine Tap to Overton. | MO | AMEREN MISSOURI | GIP |  | 2030-12-01 | 161 | 9552000
Central | 50222 | Rebuild Overton-Sedalia East 161 kV Line (MPFCA) | Rebuild 10 miles of existing Overton – Sedalia East 161 kV | MO | AMEREN MISSOURI | GIP |  | 2030-12-01 | 161 | 9710000
West | 50223 | Whitewater – Sugar Creek 138 kV (WHIG53), Flow Control Device | The Whitewater – Sugar Creek (WHIG53) 138 kV, flow control device is needed to control power flow on WHIG52 and 6541 supporting load additions in south-east Wisconsin. The project will install three single-phase 20-ohm series reactors at the Sugar Creek terminal of WHIG53. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-01-01 | 138 | 3358000
West | 50225 | North Lake Geneva – Elkhorn 138 kV (X-55), Rebuild | Rebuild X-55 North Lake Geneva - Elkhorn 138 kV line per ATC T-Line design standards to achieve minimum 1342 Amps (321 MVA) normal and 1822 Amps (436 MVA) emergency ratings for all seasons. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2026-08-15 | 138 | 23900000
Central | 50226 | New Vulcan 138/34 kV Substation | Build a new 138-34.5 kV bulk substation on property adjacent to the MSD Lemay Pump. (fka Germania) | MO | AMEREN MISSOURI | Other | Load Growth | 2030-12-01 | 138 | 12000000
Central | 50227 | Upgrade California 161 kV Terminal | Add a line breaker on the AECI terminal and a new terminal for Apache Flats. New terminal contains a breaker and two switches and houses the line to Apache Flats. BARN-CALF-1 will be rebuilt into a double circuit from California to structure 197A which eliminates the tap to Apache Flats. | MO | AMEREN MISSOURI | Other | Local Reliability | 2028-06-01 | 161 | 22600000
East | 50229 | New Oneida - Tallman 138 kV circuit | Build new Oneida – Tallman 138 kV circuit utilizing 1431 ACSR and double circuit structures capable of OPGW. Use 9.5 miles METC existing easement and obtaining new 0.5 miles ROW to connect this corridor to Tallman. Install two one-way 3000A PTS at Tallman. Install new 138 kV breaker capable of 40 kA interrupting and complete an existing row at Oneida 138 kV station. Install new 138 kV three breaker ring bus station at Looking Glass. | MI | METC | Other | Local Needs | 2029-12-31 | 138 | 29630000
Central | 50230 | New Harco South-Carrier Mills 161 kV line | Rebuild the Harco South substation to install a new transformer and a new line to the South. Install a 161/138kV transformer at Harco South. Build a 161kV line from Ameren's Harco South substation to SIPC's Carrier Mills substation. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2029-12-31 | 161 | 30000000
Central | 50140 | Upgrade Fargo 138 kV Line Position for Lucky | New 138kV breaker required on Fargo 138kV Bus breaker and a half scheme, and new circuit switcher on the high side of the substation. AIC to construct a new 138kV/13.2kV distribution substation near the Fargo bulk supply substation | MO | AMEREN ILLINOIS | Other | Local Needs | 2029-12-01 | 345 | 2000000
West | 50145 | Beloit Area DIC, New Substation | - WPL will construct a new substation with two new 138/12.47 kV, 20/33 MVA transformers. - WPL will install a high side circuit breaker for transformer protection and low side bus. - ATC will install two 138kV feeds from the line section between BOC Gas Tap and Tripp Road (X-111) to the new Beloit LNG substation to support the new loop through configuration. - ATC will remove a section of the conductor from X-111. - ATC will install a new loop through configuration at the New Beloit LNG substation with space provision for a future bus tie breaker. - ATC will construct a 138 kV loop through bus at the new Beloit LNG substation and install two 138 kV line circuit breakers with associated line and bus side disconnect switches. - ATC will install two bus-tie disconnect switches and allow space provision for a future bus-tie breaker. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-06-30 | 138 | 9000000
West | 50146 | BOC Gasses Tap – Town Line Road 138 kV (X-111), Rebuild | Rebuild BOC Gasses Tap – Town Line Rd (X-111) 138-kV line to achieve target rating. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2027-01-01 | 138 | 2427000
Central | 50170 | New J1355 IC Facilities Interconnection 138 kV | Interconnection Facilites to connect J1355 to NIPSCO's Stillwell 138kV substation | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2028-06-01 | 138 | 4235626
Central | 50171 | Schahfer 345kV substation Redundancy | RM Schahfer station’s relay protection requires full redundancy. Both the northwest and northeast 345kV buses at RM Schahfer currently have only one system of protection. To meet the requirements triggered by this interconnection, both buses will require additional bus protection relays. The protection and control schemes require new relaying that will include two bus differential relay panels and the addition of battery monitoring. Major Items  Two (2) bus differential relay panels  Battery monitoring system | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | GIP |  | 2026-07-30 | 345 | 512947
West | 50172 | Arpin SS Power Transformer Asset Renewal | Arpin SS T21 Power Transformer Asset Renewal | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 345 | 9800000
West | 50173 | Ellinwood SS Power Transformer Asset Renewal | Ellinwood SS T1 Power Transformer Asset Renewal | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 138 | 9900000
Central | 50175 | Upgrade Taylorville South 138 kV Substation | This project will reconfigure Taylorville South 138 kV substation in a 4 position ring bus configuration. Replace circuit breakers 1511, 1512 and 1514. Replace associated switches 1511B, 1511L, 1512B, 1512L, 1514B, and 1514L. Install one new 138 kV circuit breaker and two associated breaker disconnect switches. Remove shield wire over substation and install lightning masts and finials. | IL | AMEREN ILLINOIS | Other | Local Reliability | 2026-12-01 | 138 | 5200000
South | 50176 | Audubon 230 kV Load Addition and Line upgrades | Entergy is proposing to construct new 230 kV facilities at the planned Audubon 230 kV station to serve new load near Geismar, LA. There will be two ~2.8 mile new 230 kV lines from Audubon to the customer station. Also part of this addition are small partial upgrade of the Willow Glen to Point Pleasant 230 kV line and station equipment upgrades on the Willow Glen to Wise 230 kv line. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2026-01-01 | 230 | 5900000
West | 50231 | J1359 Generator Interconnection - TOIF - PCI 69kV Terminal & Line | The 69 kV straight bus at PCI will be extended to accommodate an additional position for the J1359 project. The Interconnection Customer, Alliant Energy, has proposed connection of a 95 MW combustion turbine generating facility to the PCI 69 kV bus. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. An approximately 0.75 mile 69 kV line from PCI to the generating facility will need to be constructed using a standard 1200A tier conductor (T2-477 ACSR or equivalent). | IA | ITC MIDWEST | GIP |  | 2026-02-27 | 69 | 1845014
West | 50232 | J1359 Generator Interconnection - Network Upgrades - PCI 69kV Bus | The 69 kV straight bus at PCI will be extended to accommodate an additional position for the J1359 project. The Interconnection Customer, Alliant Energy, has proposed connection of a 95 MW combustion turbine generating facility to the PCI 69 kV bus. ITCM will TO-Fund the Network Upgrades and recover and earn on costs under a Facilities Service Agreement. | IA | ITC MIDWEST | GIP |  | 2026-03-01 | 69 | 401708
West | 50233 | Birnamwood Area Reliability Project | Build a greenfield 69 kV switching station near the location of the Birnamwood tap. The station will be a 6-position straight bus with three breakered line terminals, one for the line segment to Deer Trail, one for the segment to Whitcomb, and one for the radial line to Birnamwood. One position for an 8 MVAR cap bank, provisions for a bus tie breaker and two future positions. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2028-12-31 | 69 | 17500000
West | 50234 | MN River Breaker Install (position 5M518) | Install breaker on MN River Substation ring bus (position 5M518) | MN | MINNESOTA MUNICIPAL POWER AGENCY | Other | Local Reliability | 2027-02-15 | 115 | 625800
West | 50235 | J1444 Generator Interconnection - TOIF - DAEC 345kV Terminal | To interconnect projects J1444 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the DAEC 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the DAEC Substation for project J1444, a 200 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | ITC MIDWEST | GIP |  | 2025-09-01 | 345 | 760648
West | 50236 | J1444 Generator Interconnection - Network Upgrade | System Concern To interconnect projects J1444 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the DAEC 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the DAEC Substation for project J1444, a 200 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | ITC MIDWEST | GIP |  | 2025-09-01 | 345 | 3777724
West | 50237 | Butternut Area Projects | Rebuild BE-BUT line. SS145 to the Butternut Substation. Line length is approx. 4.5 miles | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2029-12-21 | 69 | 4947000
West | 50238 | MPFCA J1503 & J1504 - TOIF - Huntley 345 kV Terminal | The MISO interconnection projects J1503 & J1504 has proposed the connection of two 150 MW solar powered generating facilities to the Huntley 345 kV bus. This section is for the TOIF portion only including: 345 kV dead end structure, 345 kV switch, PTs, relay panel for the gen-tie line, and lightning arrestors dedicated to the interconnection customer’s 345 kV gen-tie line. The IC, MISO, and ITCM executed GIAs for J1503 & J1504, but all construction will be done under the MPFCA J1503 J1504 for the expansion of the Huntley 345 kV sub to accommodate a new 345 kV line terminal. The cost of the project will be split 50/50 between J1503 & J1504, but both projects are owned by the same customer. | MN | ITC MIDWEST | GIP |  | 2027-10-31 | 345 | 1083794
West | 50239 | MPFCA J1503 & J1504 - Network Upgrades - Huntley 345 kV Bus | To interconnect projects J1503 and J1504 to the ITC Midwest (“ITCM”) system at the Interconnection Customers’ requested point of interconnection, the Huntley 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV shared gen-tie terminal. The Interconnection Customers, MISO, and ITCM entered into a Multi-Party Facilities Construction Agreement (“MPFCA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the Huntley Substation for projects J1503 and J1504, each a 150 MW solar generating facility (300 MW total), under a Multi-Party Facilities Construction Agreement (“MPFCA”) as a condition of the project’s Interconnection Service. | MN | ITC MIDWEST | GIP |  | 2027-10-31 | 345 | 5489562
West | 50240 | J1520 Generator Interconnection - TOIF | To interconnect project J1520 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the Bluebill 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the Bluebill Switch Station for project J1520, a 135 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | ITC MIDWEST | GIP |  | 2027-10-31 | 345 | 1101322
Central | 50241 | Replace Boonville T1 69 kV | Replace transformer #1 with new 20MVA. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2027-12-31 | 69 | 2360000
West | 50242 | New Sweden Area Projects | Rebuild BE-NST line from SS2831 to New Sweden Substation. Line length is approx. 7.4 miles. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2030-02-28 | 69 | 6996498
West | 50243 | Merton Area Projects | Rebuild SW-OM line. SS2755 to Merton Substation. Line length is approx. 6.5 miles. Planning has requested line be rebuilt to 161kV. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2030-09-30 | 69 | 9273000
West | 50244 | J1520 Generator Interconnection - Network Upgrades | To interconnect project J1520 to the ITC Midwest (“ITCM”) system at the Interconnection Customer’s requested point of interconnection, the Bluebill 345 kV bus will need to be converted to a breaker and ½ to allow for the new 345 kV terminal. The Interconnection Customer, MISO, and ITCM entered into Generator Interconnection Agreement (“GIA”). Network Upgrades and Transmission Owner Interconnection Facilities (“TOIF”) are expected to be constructed at the Bluebill Substation for project J1520, a 135 MW solar generating facility, under a Generator Interconnection Agreement (“GIA”) as a condition of the project’s Interconnection Service. | IA | ITC MIDWEST | GIP |  | 2027-10-31 | 345 | 4048730
Central | 50245 | Replace Culley 138kV CCVT Boxes | Replace existing line, breaker, and bus relaying panels. Replace existing CCVT junction boxes with new stainless-steel boxes. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2027-12-31 | 138 | 1600000
East | 50246 | Replace Caniff #303AB PST Transformer | Replace the Caniff #303(AB) PST Transformer with at least 736 MVA (3543 Amps) summer emergency rated transformer. Phase-shift angle of +/-15°. Install a breaker and associated equipment on the high side of the transformer. | MI | ITC | Other | Age and Condition | 2028-12-31 | 345 | 30000000
Central | 50247 | Rebuild Elliott Transformer and Substation 69 kV | Replace existing ‘Transformer #1’ & ‘Transformer #2’ with new 100MVA transformers. Add new transformer protective relaying. Replace existing 138kV circuit breakers ‘1000’ & ‘3000’ and 69kV circuit breakers ‘100’, ‘200’, ‘300’ & ‘600’. Replace breaker foundations, breaker/line switches, and protective relaying. Replace two (2) existing 69kV capacitor banks. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Local Reliability | 2027-12-31 | 138 | 15700000
Central | 50248 | Replace Newburgh Circuit Switcher 69 kV | Remove existing 69kV high-side fuses and associated switch ‘199’ and replace with new 69kV circuit switcher. Install an auto-sectionalizing and RTU panels. Replace existing 7200V voltage regulators. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2027-12-31 | 69 | 1550000
Central | 50249 | Rebuild Dubois T2 138/69 kV Transformer | Replace existing 100MVA, 138/69kV ‘Transformer #1’. Replace existing 69kV breakers ‘100’, ‘200’, ‘300’, ‘400’ and ‘500’. Replace existing 138kV and 69kV CCVTs. Install new transformer, 138kV and 69kV breaker and line relaying panels. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Local Reliability | 2027-12-31 | 138 | 7870000
East | 50251 | Rebuild Batavia - Dorrance #1 & #2 138 kV lines | Rebuild sections of the Batavia – Byers and Batavia – Kinderhook jct. circuits between Structure 124D100 to Batavia (~4.1mi) with 954 ACSR conductor and OPGW | MI | METC | Other | Age and Condition | 2029-12-31 | 138 | 10555000
East | 50253 | Oliver - New DTE Interconnection | DTE interconnection request for transmission service tapped Cosmo – W-BA-C_TP section of the Bad Axe - Wyatt 120 kV line, approximately 12 miles West of W-BA-C_TP tap. DTE will install a single distribution transformer and associated high-side protection. | MI | ITC | Other | Local Reliability | 2027-12-01 | 120 | 5605500
West | 50254 | Remsen Township 345 kV Substation Expansion for J1590 | Add one new 345 kV line terminal at Remsen Township substation for J1590 wind farm generator tie line. | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2027-09-15 | 345 | 4000000
West | 50255 | Huiskamp - Ruskin 69 kV (6937), OPGW Addition | Install ~1.75 miles of ATC standard (DNO-10455) 48 strand OPGW fiber optic cable from structure #232 on T-Line (6937) into the Ruskin substation to complete the connection from Huiskamp. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2026-12-31 | 69 | 4000000
Central | 50256 | New Tibbe 138/34.5 kV Substation | Tibbe 138/34.5 kV Substation - Utilize 9.6 miles of existing 34.5 kV line in the Saddle Creek-73 feeder, at 138 kV. In addition, construct 6.1 miles of new 138 kV line to establish the Gray Summit-Prairie Dell and Franklin-Prairie Dell 138 kV lines. Establish a new 138 kV ring bus at the Tibbe 138-34.5 kV Substation. (fka Prairie Dell) | MO | AMEREN MISSOURI | Other | Load Growth | 2029-12-01 | 138 | 33000000
Central | 50257 | Reconfigure Steeleville 138 kV Substation to Ring Bus | Reconfigure Steeleville 138 kV as a five-position switching station, in a ring bus arrangement, with one additional position for future expansion with continuous capability of 3000 A. Install a new 40 Mvar 138 kV capacitor bank in one of the initial ring bus positions. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2026-12-01 | 138 | 6001746
Central | 50259 | Rebuild Fletcher-Pilot Knob-2 161 kV line | The project consists of replacing 8 wood H-frame with steel H-frame structures to increase system reliability. Replace structure 84 down guy due to age and condition. | MO | AMEREN MISSOURI | Other | Local Reliability | 2025-04-01 | 161 | 1400000
West | 50260 | Hettinger-Elgin rebuild to 115 kV | Rebuilding a 69 kV line to 115 kV from Hettinger, ND to Elgin, ND approximately 46.2 miles. Adding a new 115 kV bay at Hettinger and building a new substation at Elgin 115/69/41.6 kV. | ND | MONTANA-DAKOTA UTILITIES CO. | Other | Age and Condition | 2029-12-31 | 230 | 32100000
West | 50261 | Blue Earth - North Transmission Substation Add 84/140 MVA transformer | North Transmission Substation Add 2nd 161/69 Transformer 45-60-75 MVA. | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2026-12-31 | 161 | 11200000
West | 50262 | Chaffee Creek SS Breaker Asset Renewal | Asset renewal replacement of oil circuit breakers at Chaffee Creek SS. In addition, replace the aging capacitor bank and internal components of the control house. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2028-12-01 | 69 | 5155000
West | 50263 | Rush City Area Projects | Rebuild CP line. CPX Line to the CPT Line. Line length is approx. 11 miles. Rebuild RLT Line. Line length is approx. 0.1 miles Rebuild CPT Line. SS2984 to SS2555. Line length is approx. 1.5 miles | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2029-08-31 | 69 | 11751000
West | 50264 | Soderville Area Projects | Rebuild SP line. Soderville Substation to #152. Line length is approx. 10 miles | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2031-03-31 | 69 | 21269000
West | 50265 | Victor Area Projects | Rebuild DS line. DSX Line to SS377. Line length is approx. 9.25 miles | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2029-12-12 | 69 | 8093000
West | 50266 | Green Lake Area Projects | Rebuild SH line. SS306 to Green Lake Sub to Hawick Sub. Line length is approx. 13.7 miles | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2030-04-30 | 69 | 12790000
West | 50267 | Johnsville Double End | GRE to convert the existing Johnsville substation to an in-and-out substation. GRE will need to build a short 69 kV transmission line tap and add/alter metering/telecom for the 2nd transformer. 2000-amp motor operated FLB switches should be used. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2029-12-31 | 69 | 2362908
West | 50268 | Blue Earth Rice Street Transformer Replacement | Rice Street Transformer Upgrade to 12/20 MVA | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2026-05-31 | 69 | 2400000
West | 50269 | Blue Earth Northeast Add 2nd Transformer 20-37.3 MVA | Northeast Add 2nd Transformer 20-37.3 MVA | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2026-05-31 | 69 | 4800000
West | 50270 | J1808 Generation Interconnection Network Upgrades. | J1808 is a 148 MW net solar facility interconnecting at DPC's Barron 161 kV substation. This interconnection will require POI facilities as well as a Barron 161 kV ring bus expansion and disconnect switch. | WI | DAIRYLAND POWER COOPERATIVE | GIP |  | 2027-07-02 | 161 | 1438367
West | 50271 | Rock Dell-Pleasant Valley N469 Rebuild | Rebuild 2.0 miles of 69 kV transmission between Rock Dell and Pleasant Valley on DPC's N469 line & retire legacy switches. | MN | DAIRYLAND POWER COOPERATIVE | Other | Age and Condition | 2028-03-01 | 69 | 1227000
West | 50272 | Genoa Dist Tap-Ringe Tap N470 Rebuild | Rebuild 7.88 miles of 69 kV transmission between Genoa Dist. and Ringe on DPC's N470 line & retire legacy switch. | MN | DAIRYLAND POWER COOPERATIVE | Other | Age and Condition | 2026-06-02 | 69 | 2959357
West | 50273 | Heartland Lakes Area Projects | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. | MN | GREAT RIVER ENERGY | Other | Local Needs | 2029-10-01 | 115 | 8485501
West | 50274 | Iona Area Projects | The Iona 115 kV Conversion Project involves building a 0.5-mile 115 kV tap line to interconnect the existing Todd-Wadena Electric Cooperative (TWEC) Iona substation to the 47 Line via a 3-way, 2000-amp, full load break 115 kV switch. Utilize 477 ACSR conductor. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2027-12-31 | 115 | 2315747
West | 50275 | Blue Earth West Sub Transformer Upgrade | Add 2nd 10-14 MVA | MN | Central Minnesota Municipal Power Agency | Other | Load Growth | 2029-05-31 | 69 | 2900000
Central | 50279 | Replace Staunton 230/138kV Xfmr Bk1 and 2 | Staunton sub: (alternative project submittal to replace MTEP #22227) upgrade 230/138kV Banks 1 and 2 to 250MVA nameplate | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2028-05-26 | 230 | 18800000
Central | 50280 | New Neuron - Lafayette 27MW load | Project Neuron (fka Mars) - Lafayette new load 27MWs - 13806 line very near Tipmont Co Farm | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2029-12-31 | 138 | 24970000
Central | 50282 | New Radbourn 345 kV and Leghorn 345 kV Shunt Reactors | Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Radbourn 345 kV substation. Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Leghorn 345 kV substation. | IL | AMEREN ILLINOIS | Other | Load Growth | 2026-12-01 | 345 | 4800000
West | 50284 | Cormorant to Pelican Rapids Rebuild Projects | Rebuild all sections of the LR-PC line. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2030-11-29 | 115 | 15121921
Central | 50285 | New HE Shadow Lake 138/12kV Sub | New HE Shadow Lake 138/12kV distribution substation for Clark Co REMC to be inserted in the 13898 Speed – Jeffersonville 138kV line between River Ridge Central and Stoney Point Jct.; looped through with ATO; loop in/out with 954ACSS/TW20x7@200C conductor | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-06-01 | 138 | 2974000
Central | 50286 | Lebanon Industrial 2nd 69kV Source | Build approximately 13 miles of new 69kV transmission between new Rosston Substation and Eli Lilly facility | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2027-10-01 | 69 | 30311869
Central | 50287 | Gessie 69kV Rebuild | Rebuild the entire 3.5 miles of 69kV line due to age and condition. It will be rebuilt in two stages to minimize outages to the substation. This project will also support Warren's needed distribution underbuild. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Age and Condition | 2026-07-06 | 69 | 7194654
Central | 50288 | Replace Marblehead North 161/138 kV transformer | Replace Existing XFMR at Marblehead North with the onsite spare 161/138kV 300 MVA unit. | IL | AMEREN ILLINOIS | Other | Age and Condition | 2027-12-01 | 161 | 1500000
Central | 50289 | New Wabash Industrial 69/12kV Sub | Wabash Industrial 69/12kV new sub to serve new 20+MW customer in the 69132 ckt - near Chippewa; includes 14.4MVAR capacitor | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2026-10-16 | 69 | 2968000
Central | 50292 | Fishback Creek 69/12kV Substation | New substation near Whitestown Parkway to alliveiate heavy loading on existing Royalton substation | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2028-12-31 | 69 | 6000000
Central | 50293 | 6923 69kV Ring Bus | The 6923 line from Huntington North Junction to North Manchester is an 18.8 mile long line. In order to improve reliability, a 3-breaker ring bus substation will be added at the midpoint of this line at the tap point for Heartland’s Bippus Substation. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2029-12-31 | 69 | 6800000
Central | 50294 | Romine 69kV Switching Station | Currently the 6936 lines goes from Attica 230kV substation to Cayuga (43.6 miles), and a new 3-breaker ring bus would be added at the Flexel junction point to segment the line and improve reliability. This point has been agreed upon with Duke. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2028-12-31 | 69 | 6800000
Central | 50295 | 69154 69kV Ring Bus | A 4-position ring bus will be installed at the Cherry Grove substation along Duke’s 69154 transmission line. The line has a lot of mileage exposure and has multiple member delivery points served off it so the project will break up the line and improve the reliability of those delivery points. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2030-12-31 | 69 | 6800000
Central | 50296 | Dover 69/12kV Substation | Build new substation next to existing Dover substation to serve construction power for the LEAP district and other expected growth in the area. The sub will be built with a single transformer with provisions for a 2nd and the line will be looped through the station. Construction power requests have been between 6-12MW of load. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2027-12-31 | 69 | 5500000
Central | 50297 | Milnon 69/12kV Substation | Construct new 69/12kV substation between the NIPSCO Monon and Milroy delivery points and retire member meter points | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2027-11-24 | 69 | 6649226
Central | 50298 | Four Corners 69/12kV Substation | Build a new 69kV substation to serve load near Hanna, IN | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2027-12-01 | 69 | 14052130
Central | 50299 | New Wakefield 138 kV switching station | Construct a three (3) position 138 kV substation in a ring bus configuration, with one (1) additional position available for future expansion, all with a 3000 A minimum continuous capability. Route the existing South Bloomington-Tabor-1445 138 kV line in and out of the new Wakefield substation. | IL | AMEREN ILLINOIS | Other | Load Growth | 2027-12-01 | 138 | 10700000
Central | 50300 | Hayworth 69/12kV Substation | Build a new 69kV substation to retire the Morocco meter point and provide reliability to existing Berthaville & Colfax South substation | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2027-12-01 | 69 | 10249426
Central | 50301 | Maple Leaf 69kV Line | WVPA will build approximately 6 miles of new 69kV transmission line to provide a second transmission source to the existing Maple Leaf substation in Milford, IN. NIPSCO’s 69kV transmission line 6941 will be tapped just East of their Royal Outdoor substation in Milford, IN. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2027-12-31 | 69 | 15000000
Central | 50302 | Lacrosse 69/12kV Substation | Install new 14 MVA substation in LaCrosse, IN, near Dome substation to support the Lena Park and Kouts substations during switching orders and outages. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2029-12-31 | 69 | 12500000
Central | 50303 | Jacob Mack 2nd Bank & Source | A 22.4MVA transformer will be installed at Jacob Mack sub to serve member load and relieve the existing older bank. In addition to the bank work, the substation 69kV side will be built out for a looped transmission feed. Jacob Mack is currently radially fed with a normal feed from NIPSCO’s 6939 line out of Green Acres and a normally open point from circuit 6934, both lines will be looped into the station and the normally open point moved inside the fence. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Local Reliability | 2027-12-31 | 69 | 8594249
West | 50304 | Slayton Area Projects | Nobles is planning on relocating Slayton/Nobles substation out of town. Currently, Nobles is planning an energization date of fall of 2025. This will require GRE to tap into the new substation, retap in Xcel’s line from the new Slayton substation and retire the tap line (etc) from the old Slayton substation. | MN | GREAT RIVER ENERGY | Other | Local Needs | 2025-12-31 | 69 | 873200
West | 50305 | Blue Earth Substation Rebuild Projects | BENCO plans to rebuild their 69kV Blue Earth distribution substation on an adjacent property to replace the aged substation as well as increase transformer size to 7.5 MVA bottom 10.5 MVA top end rating . GRE will need to relocate line and install a new building, meter, and telecom equipment. GRE planning has requested the high side be an in-and-out. | MN | GREAT RIVER ENERGY | Other | Local Needs | 2027-10-29 | 69 | 1443735
Central | 50306 | Rebuild Southwest-Stout CT_132-02_138 kV Line | Rebuild existing 138 kV 132-02 Southwest-Stout CT line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2029-12-31 | 138 | 9300000
Central | 50307 | Rebuild Southwest-Northwest 132-04 138 kV Line | Rebuild existing 138 kV 132-04 Southwest-Northwest line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2029-12-31 | 138 | 15200000
Central | 50311 | Rebuild Stout North-Sanitation Belmont-Southwest_132-01_&_132-74_138 kV Lines | Rebuild existing 138 kV 132-01 Stout North-Sanitation Belmont line to new Summer rating of 2000A (478 MVA). New conductor and towers. Conversion of Stout North terminal from line breaker configuration to double breaker due to P23 and P42 planning events. Rebuild existing 138 kV 132-74 Sanitation Belmont-Southwest line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2033-12-01 | 138 | 14990000
Central | 50312 | Rebuild Southwest-Lilly South 132-10 138 kV Line | Rebuild existing 138 kV 132-10 Southwest-Lilly South line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2033-12-01 | 138 | 7070000
Central | 50313 | Rebuild Lilly South-Center 132-61 138 kV Line | Rebuild existing 138 kV 132-61 Lilly South-Center line to new Summer rating of 2000A (478 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2033-12-01 | 138 | 2900000
Central | 50314 | Rebuild Georgetown-North 132-86 138 kV Line | Rebuild existing 138 kV 132-86 Georgetown-North line to new Summer rating of 1600A (382 MVA). New conductor and towers, with review of necessary terminal equipment to be replaced. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2029-12-31 | 138 | 12760000
Central | 50315 | New Ralston 138 kV Substation Eagle Valley Reinforcement | New 138 kV Ralston substation looped in on 132-23 Eagle Valley-Sanitation Southport line. Add new 138 kV line terminal at Camby substation to re-energize nearby 138 kV idle line and connect into Ralston substation. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Local Reliability | 2031-03-01 | 138 | 24000000
Central | 50316 | Rebuild Z84 Duff to Petersburgh 138 kV | Complete rebuild of Z84 from Duff to IPL Petersburgh plant. Total rebuild distance is 19.9 miles and involves replacing wood h-frame structures with galvanized steel monopole structures. The existing 765 Drake ACSR conductor to be replaced with new 2-bundled 954 Rail conductor. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2028-12-31 | 138 | 38040000
East | 50317 | New Hagensville Junction Interconnection (METC) | Wolverine has requested to further integrate their Northeast Transmission System with METC’s around the Hagensville Tap location. To accommodate this request, METC proposes adding an additional row (row 6) on the parcel where future generators J1914 and J2875 will be located to terminate Wolverine’s 138kV lines. METC will install 5 new 138kV, 40kA breakers and associated switches. | MI | METC | Other | Load Growth | 2028-12-31 | 138 | 5010000
West | 50318 | Adams County-Creston 161 kV Line Uprate for DPP 2020 | Replace line structures to increase line rating. | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2027-09-01 | 161 | 700000
West | 50319 | West Des Moines 69 kV Breaker Replacement | Replace 69 kV breaker DAE601 at West Des Moines Substation. Rebuild and reconfigure West Des Moines 69 kV lines to 37th & Rock Island and 73rd & Buffalo substations. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-12-01 | 69 | 2550000
West | 50320 | E. 17th & Washington 69 kV bus expansion and line breaker installations | Expand E. 17th & Washington Substation steel to accommodate two 69 kV line breakers | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2028-06-01 | 69 | 0
West | 50321 | E. 17th & Broadway 69 kV breaker installations | Install three 69 kV line breakers at E. 17th & Broadway Substation | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2028-10-01 | 69 | 0
West | 50324 | 88th Street Substation bus expansion and 161-13 kV transformer installation | Expand 88th St Substation steel to ring bus and add a third 161-13 kV transformer | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-12-31 | 161 | 9000000
West | 50325 | NE Ankeny - Ames 161 kV relay replacements | Replace 161 kV line relaying for ITC substation cut-in | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-03-01 | 161 | 400000
Central | 50326 | Rebuild Z95 Northwest to AB Brown 138kV | Rebuild aging portions of the Z95 Northwest to AB Brown 138kV transmission line. The first section is approximately 1.57 miles long and the second section is approximately 3.47 miles long. Both sections have 795 Drake conductor, which will be replaced with 954 Rail conductor. Aging wood poles will be replaced with tubular steel structures. | IN | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Other | Age and Condition | 2027-12-31 | 138 | 8700000
West | 50327 | Raun: Tekamah 161 kV Line Relay Replacement SPP DISIS-2017 | Replace relaying at Raun Substation on Tekamah 161 kV line terminal | IA | MIDAMERICAN ENERGY CO. | GIP |  | 2028-09-01 | 161 | 750000
West | 50328 | Neal North: Replace 161-69 kV Transformer Relaying & 69 kV Breaker Replacement | Replace 161 kV transformer relaying and 69 kV breaker at Neal North Substation | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2029-12-01 | 161 | 1500000
West | 50329 | Substation 91 Expansion | Expand Substation 91 by converting the 345 kV yard to a ring bus configuration and by installing a second 345-161 kV transformer. | IA | MIDAMERICAN ENERGY CO. | BRP |  | 2028-12-31 | 345 | 66000000
West | 50330 | Plymouth-Merrill 69 kV Line Uprate | Replace structures on the Plymouth-Merrill 69 kV line to increase line's rating. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2026-06-01 | 69 | 325000
West | 50331 | Substation 39 Replace 345-161 kV Transformer 9T1 | At Substation 39, replace the existing 345-161 kV, 500 MVA Transformer 9T1 with a new 560 MVA transformer. | IL | MIDAMERICAN ENERGY CO. | BRP |  | 2029-06-01 | 345 | 10500000
West | 50332 | Division-Eastside 69 kV Line Rebuild & Terminal Upgrades | Rebuild and reconductor the line to increase line rating. | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2027-06-01 | 69 | 2200000
West | 50333 | Franklin: Replace Nuthatch Line Relaying | Replace primary and secondary line and breaker failure relaying on Franklin 161 kV Breaker 9920 to ITC Midwest’s Nuthatch Substation | IA | MIDAMERICAN ENERGY CO. | Other | Local Reliability | 2025-06-19 | 161 | 300000
West | 50334 | Eagle Grove-Goldfield 69 kV Interconnection and Clarion-Latimer 69 kV Line Rebuild | Install two line switches on a steel pole and rebuild the Clarion-Latimer 69 kV line sections. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2028-06-01 | 69 | 12000000
West | 50335 | Johnson Creek Add 161 kV Breakers | Install two 161 kV breakers and associated equipment at Johnson Creek Substation. | IA | MIDAMERICAN ENERGY CO. | Other | Load Growth | 2027-08-01 | 161 | 2000000
West | 50336 | Substation Equipment Replacement Blanket | Replace substation equipment because of condition and/or to improve reliability | IA | MIDAMERICAN ENERGY CO. | Other | Age and Condition | 2028-12-31 | 345 | 21000000
East | 50337 | Rebuild Tower - Black Lake 69 kV line to 138 kV capability | Rebuild and upgrade 4.5 miles of 69 kV line to 138 kV standard with steel poles, 336 ACSR conductor, and OPGW. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2029-12-31 | 69 | 4500000
East | 50338 | Rebuild Lincoln Junction - Lincoln 69 kV line to 138 kV capability | Rebuild and upgrade 5 miles of 69 kV line to 138 kV standard with steel poles, 336 ACSR conductor, and OPGW. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2029-12-31 | 69 | 5000000
East | 50339 | Rebuild Bass Lake - Wolf Lake 69 kV line to 138 kV capability | Rebuild and upgrade 11 miles of 69 kV line to 138 kV standard with steel poles, 336ACSR conductor, and OPGW. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2029-12-31 | 69 | 11000000
Central | 50341 | Replace 34507 Gibson-Petersburg 345 kV Line | 34507 Gibson-Petersburg Line Improvements - replace 16 aluminum Kaiser A, B, or C towers with 3 pole dead end structures at 2.5 mile intervals | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2027-05-21 | 345 | 15207000
Central | 50342 | Rebuild Greencastle Industrial Jct. to WVPA Vandalia 69kV Line | 6996 Greencastle Industrial Jct. to WVPA Vandalia Rebuild - 0.74 miles with 477ACSR/VR2@120C; Greencastle Industrial Jct. upgrade to ATO / SCADA control | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2026-06-01 | 69 | 1984000
Central | 50343 | Terre Haure Water St. 138kV Ring Bus | Terre Haure Water St. 138kV sub - construct 3-breaker 138kV ring bus | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2028-12-11 | 138 | 16520000
Central | 50345 | New WVPA Richland 69kV ring bus | WVPA Richland 69kV ring bus: install 3 - CB ring at existing sub; rebuild 0.9 mile WVPA Richland to Rochester Tap 6968 with 954ACSR | IN | DUKE ENERGY INDIANA, LLC | Other | Local Reliability | 2030-10-18 | 69 | 11736000
Central | 50347 | Replace Frankfort 230/69 Bk1 | Frankfort 230/69 Bk1: Replace 84MVA 230/69kV Transformer with new 150MVA transformer; replace 23069-1 ckt. switcher; replace substation RTU | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2026-07-31 | 230 | 6329000
Central | 50349 | Crane Naval Base load expansion | Crane South Substation: expand 138kV bus into (4) CB Ring; Install 100MVA 138/69kV Transformer Bank 2; Add (2) 69kV breakers to the existing ring; construct new 69kV line to Crane Naval Base NW; reconductor 69193 line from Crane South to Crane Naval Base | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2027-12-07 | 138 | 28966000
South | 50350 | Babel to Webre 500 kV New Line | Construct a new ~145-mile 500 kV line from Babel to Webre 500 kV line. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2030-06-01 | 500 | 1066000000
Central | 50351 | Rebuild Arcadia N to Arcadia 69kV Line | Arcadia N to Arcadia 69kV Rebuild - 2.5 miles of 69kV line 69180 from Arcadia north sub to Arcadia sub | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2027-11-23 | 69 | 5500000
South | 50352 | Amelia to Poly 69 kV Upgrades | Upgrade station equipment and line sections on Amelia - Poly 69 kV through path. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2029-12-31 | 69 | 3700000
South | 50353 | 2026 ENOL Asset Renewal Program | This project is for the ENOL Asset Renewal Program that will be executed in 2026 | LA | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2026-12-31 | 230 | 3200000
South | 50354 | Mid County to Stonegate 138 kV Rebuild | Rebuild Mid County-Stonegate 138 kV line | TX | ENTERGY SERVICES, LLC. | BRP |  | 2027-12-17 | 138 | 6540000
South | 50355 | 2026 ELL Asset Renewal Program | This project is for the ENLL Asset Renewal Program that will be executed in 2026 | LA | ENTERGY SERVICES, LLC. | Other | Age and Condition | 2026-12-31 | 500 | 83300000
South | 50356 | Port Acres Bulk to Legend 230 kV Rebuild | Cut Port Acres Bulk to Sandling 230 kV line in and out of Legend. Rebuild both Port Acres Bulk to Legend 230 kV lines. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2028-06-01 | 230 | 21900001
South | 50357 | Harelson-Jones Creek Tap 69kV Upgrades | Upgrade Harelson – Jones Creek Tap 69 kV line (~2.5 miles) and line bay riser | LA | ENTERGY SERVICES, LLC. | BRP |  | 2027-06-01 | 69 | 14700000
South | 50358 | Dupont Beamont to Nitro 69 kV Station Upgrades | Upgrade station equipment at Dupont Beaumont 69 kV substation. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2029-12-01 | 69 | 250000
South | 50359 | Bryan to Runny 138 kV New Line and Substation | Build a new 138 kV switching station between College Station and Grimes 138 kV substations called Runny. Build a new 138 kV line from Bryan to Runny. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2030-06-01 | 138 | 99400001
South | 50360 | War Eagle 138 kV: Construct New Substation and Lines | Construct a new War Eagle 138 kV substation approximately 0.3 miles north of the Oak Ridge 138 kV substation that cuts into the Oak Ridge – Metro 138 kV. Construct a new 138 kV line from Porter to the new War Eagle substation. Energize the abandoned 138 kV L-403 by terminating into the War Eagle and Forest 138 kV substations and rebuild. | TX | ENTERGY SERVICES, LLC. | BRP |  | 2029-06-01 | 138 | 110000002
South | 50361 | Willow Glen Protection Improvement SPOF Project | Install a new battery bank at Willow Glen 138 kV station. The primary 1 relay needs to be on a separate DC panel than primary 2/backup relay. The breakers for the AT must have trip coil #1 and trip coil #2 fed from separate DC panels and the DC panels must be fed from separate battery sets. The DC panels cannot be wired in series or in parallel to one another. Ensure redundant protection on all 138kV and 230kV buses, 138kV and 230kV lines, and 500/138kV and 230/138kV Autotransformers. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2026-06-01 | 138 | 4000000
South | 50362 | Richard 500/138 kV Bus SPOF | All 138kV line panels need to have primary 1 relays on a separate DC panel than primary 2/backup relays. The DC panels must be fed from separate battery sets. The existing auto relays need to be investigated to ensure sufficient contacts for the trip coils to be redundant. Existing auto relays will need to be replaced if there are no sufficient contacts. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2028-06-01 | 500 | 8700000
South | 50363 | Little Prairie – Mud Lake Low Voltage Project | Install 223.90 MVAR reactive support (2-SVCs) at Little Prairie 230 kV station | LA | ENTERGY SERVICES, LLC. | BRP |  | 2031-10-31 | 230 | 54300000
South | 50364 | Waterford 500/230 kV AT Upgrade | Upgrade Waterford 230 kV jumper (~0.26 miles, located inside 230 kV station) to 1200 MVA min. | LA | ENTERGY SERVICES, LLC. | BRP |  | 2030-06-01 | 230 | 310000
West | 50365 | Shannon Capacitor Bank Replacement | Replacing the two 230 kV and one 115 kV capacitor banks at the Shannon Substation. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2026-12-31 | 230 | 1750000
East | 50366 | Upgrade Mud Lake - Verona #1 138 kV line | Upgrade ~0.67 mile of 954 ACSR to 1431 ACSR on the Mud Lake – Verona 138 kV line No. 1. Also, upgrade the 2-4/0 Cu stranded bus at position “588” and switch 585 to at least 450 MVA for summer emergency rating. | MI | METC | BRP |  | 2030-06-01 | 138 | 1590000
South | 50367 | 2026 EML Asset Renewal Program | This project is for the EML Asset Renewal Program that will be executed in 2026 | MS | ENTERGY MISSISSIPPI, LLC. | Other | Age and Condition | 2026-12-31 | 500 | 68400000
South | 50368 | McAdams 500 kV Bus SPOF | All 500kV line panels at McAdams need to have primary 1 relays on a separate DC panel than primary 2/backup relays. • The breakers for these lines must have trip coil #1 and trip coil #2 fed from separate DC panels. • The DC panels must be fed from separate battery sets and the DC panels cannot be wired in series or in parallel to one another. | MS | ENTERGY MISSISSIPPI, LLC. | BRP |  | 2026-06-01 | 500 | 4100000
Central | 50369 | Rebuild Huntington Goblesville Jct to United Jct 69kV Line | Huntington Goblesville Jct to United Jct 69kV rebuild: 6.45 miles of line 6923 ckt. | IN | DUKE ENERGY INDIANA, LLC | Other | Age and Condition | 2026-12-11 | 69 | 9238000
Central | 50370 | Replace New London to Kokomo Highland Park 230kV Line | New London to Kokomo Highland Park 230kV - 23009 ckt. - Replace/Upgrade structures (7.5 miles) to get 100C operation of existing 900ACSR54X7@80C conductor | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2025-11-21 | 230 | 1976000
Central | 50371 | Lee Hanna 69/12kV Rebuild | Rebuild the existing Lee Hanna 69/12kV Substation to increase the capacity of the station to two 33.6MVA transformers for load growth, back-feeding, and construction power. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | Other | Load Growth | 2027-11-01 | 69 | 10000000
East | 50372 | Upgrade Dupont-White Lake 138 kV line | Upgrade line from Dupont to White Lake (~5.094 miles) from 336 ACSR to 954 ACSR. Also, upgrade buses at Dupont positions “199” and “177” to at least 332 MVA for summer emergency rating. | MI | METC | BRP |  | 2030-06-01 | 138 | 8298000
Central | 50374 | Upgrade Dresser 345kV Line | Dresser 345kV Line Upgrades: 34520 (to Fairbanks) and 34538 (to Sugar Crk) ckts. - replace structures to achieve line ratings of 100°C | IN | DUKE ENERGY INDIANA, LLC | GIP |  | 2027-07-01 | 345 | 11600000
Central | 50376 | Rebuild HE Bethany to Charlestown Jct 69kV Line | 6955 ckt. Rebuild HE Bethany to Charlestown Jct - 954 ACSR at 120C | IN | DUKE ENERGY INDIANA, LLC | Other | Load Growth | 2025-11-15 | 69 | 3305000
East | 50377 | Rebuild Blackstone 138 kV Station | Construct a new 138 kV station (tentatively called Lansing Ave) as 6-breaker ring bus configuration. All new 138 kV breakers should be standard 3000 A 50 kA breakers. All new equipment at the new station must be rated 450 MVA for summer emergency. Cut the Blackstone – Stable and Tompkins - Blackstone #2 138 kV lines into the new station. Tie existing Blackman - Blackstone #1 and Blackstone - Leoni #1 138 kV lines to form Blackman - Leoni 138 kV Line. Completely remove all the sag on this new Blackman – Leoni 138 kV line (on the formerly Blackman – Blackstone section). Construct new 138 kV lines (~0.37 miles each) from the new substation to CONS Blackstone 46 kV TRF #1 and TRF#2 using 954 ACSR conductor. Also, decommission all 138 kV equipment's from Blackstone 138 kV Sub. | MI | METC | Other | Age and Condition | 2030-06-01 | 138 | 17000000
West | 50378 | ITC Midwest SCADA Controlled Motor Operated Switch Addition blanket | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be used to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | IA; IL; MN | ITC MIDWEST | Other | Local Reliability | 2026-12-31 | 345 | 3125000
West | 50379 | ITC Midwest Load interconnection blanket | Projects of significant size (greater than $1 Million) will be reported individually. Since these projects are being done at the request of interconnection customers and do not address any specific ITCM reliability concerns, only one alternative was identified for each project. Unless any reliability concerns on the ITCM system are identified, the identified alternative typically matches the one requested by the customer to accommodate the customer’s site location or desired level of service/reliability. Only those projects as determined by ITC as having no significant impact on the transmission system are included. | IA; IL; MN | ITC MIDWEST | Other | Load Growth | 2027-12-31 | 345 | 3750000
West | 50380 | ITC Midwest Asset Management blanket | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA; IL; MN | ITC MIDWEST | Other | Age and Condition | 2027-12-31 | 345 | 53875000
Central | 50381 | Rebuild Riverside-Hardin Tap 69 kV line | Rebuild Riverside-Hardin Tap 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2026-12-01 | 69 | 5940000
South | 50383 | 2026 EAL Asset Renewal Program | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2026 asset renewal plans have not yet been finalized. | AR | ENTERGY ARKANSAS, LLC | Other | Age and Condition | 2026-12-30 | 161 | 16475000
South | 50384 | Hot Springs 500kV SPOF | All 500kV line panels and autotransformer panels at Hot Springs EHV, as well as Etta - Hot Springs 500kV line panel, will have primary 1 relays on a separate DC panel than primary 2/backup relays. The breakers for these lines and auto transformers will have trip coil #1 and trip coil #2 fed from separate DC panels. The DC panels will be fed from separate battery sets and cannot be wired in series or in parallel to one another. The autotransformer’s relays have been identified as not having redundant zones of protection and will need to be reviewed and rewired. The line panels should have redundant communication on both the local and remote ends. After completion of this SPOF project, all scenarios leading to delayed clearing and/or the loss of the entire Hot Springs 500 kV and/or 115 kV bus due to a non-redundant protection system component failure after a fault should have been fully mitigated. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2026-12-01 | 500 | 2757000
South | 50385 | El Dorado Donan - El Dorado Monsanto 115 kV: Rebuild Line | Rebuild the ~3.1 mile line segment along with any other station equipment to achieve a 1300 A flow-through rating. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2027-06-30 | 115 | 7900000
South | 50386 | Hilltop - Saint Joe 161kV: Rebuild Line | Rebuild Hilltop – St Joe along with any other station equipment to achieve a 1300 A through path rating. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2027-12-07 | 161 | 12384021
South | 50387 | Saint Joe - Everton Road 161kV: Rebuild Line | Rebuild St Joe – Everton Rd along with any other station equipment to achieve a 1300 A through path rating. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2028-07-20 | 161 | 29720000
South | 50388 | Everton Road - Harrison East 161kV: Rebuild Line | Rebuild Everton Rd – Harrison East along with any other station equipment to achieve a 1300 A through path rating. | AR | ENTERGY ARKANSAS, LLC | BRP |  | 2029-04-13 | 161 | 20140000
Central | 50389 | New Leesburg 345/138kV Transformer addition | Add a 2nd Leesburg 345/138kV Transformer | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2027-12-31 | 345 | 8000000
Central | 50390 | New Dune Acres 138 kV Breaker additions | Add Breakers to existing lines where feasible to complete double breaker double bus design. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | BRP |  | 2029-05-31 | 138 | 3000000
South | 50391 | Line 74B Rebuild | A complete rebuild of Line 74B (Colonial Collins – Colonial Kola 69kV) is recommended at 161kV insulation with more reliable structural designs and OPGW. This project will increase reliability of the transmission system and provide an OPGW communication link between Colonial Collins and Colonial Kola. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2027-01-01 | 69 | 900000
West | 50392 | Elk River Muni West | Remove and upgrade 600-amp switches EWSM11 and EWS10 with live parts to 1200 amp. The span of 266 ACSR transmission conductor between the two switch poles should be removed and upgraded to 477 ACSS. Switch EWS14 is 1200-amp and owned by Elk River Municipal and nothing needs to be done to this switch. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2026-10-30 | 69 | 68811
West | 50393 | Iron Range 500kV Reactor Addition | Adding a third 500kV line reactor to help mitigate overheating concerns with one unit out for maintenance. | MN | MINNESOTA POWER INC. | Other | Local Reliability | 2030-12-31 | 500 | 4000000
West | 50394 | Riverton Asset Renewal | GRE plans to upgrade equipment and relocated assets ahead of MP Riverton rebuild scheduled for in-service by 2030. The project includes pull all GRE assets out of MP control house that is planned for demo by 2030 into new GRE control house. GRE will also be upgrading physical assets in our yard including the 25WB1 oil breaker, relaying, the Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, GE PT’s, and bus modifications. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2028-06-30 | 115 | 2610398
West | 50395 | Transmission Line Pole Replacement 2025 | Replacing red-tag transmission line poles. | MN | MINNESOTA POWER INC. | Other | Age and Condition | 2025-12-31 | 230 | 8250000
Central | 50396 | New BREC Bon Harbor-OMU Sub ‘M’ 69 kV Interconnection | To be included in MTEP24, the creation of a 69 kV interconnection between BREC and OMU. | KY | BIG RIVERS ELECTRIC CORPORATION | Other | Local Reliability | 2026-12-01 | 69 | 7500000
West | 50398 | Install Inver Hills TRs and Feeders | Expand the Inver Hills substation and install two new distribution transformers and feeders to take over the existing Rich Valley loads | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2028-12-15 | 115 | 35100000
South | 50399 | Line 35A Rebuild | A complete rebuild of Line 35A (Benndale – Benndale GT 69kV) is recommended at 161kV insulation with more reliable structural designs and OPGW. This project will increase reliability of the transmission system and provide an additional OPGW communication link between Benndale and Benndale GT. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Local Reliability | 2028-06-01 | 69 | 900000
South | 50400 | Ovett 69kV Delivery Point | Tap Line 114A (Ellisville - NW Perry 69kV) with a 69kV GOAB and build a new transmission line to the delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2026-10-01 | 69 | 2100000
East | 50401 | Rebuild East Jordan Junction - Barnard 69 kV line to 138 kV capability | Rebuild and upgrade 24 miles of 69 kV line to 138 kV standard with steel poles, 795ACSS conductor, and OPGW. | MI | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Other | Age and Condition | 2029-12-31 | 69 | 26000000
West | 50402 | Boswell 115/23kV Transformer Addition | Expansion of the 115kV bus with an additional breaker to accommodate a new 115/23kV transformer for load serving. | MN | MINNESOTA POWER INC. | Other | Local Needs | 2026-12-31 | 115 | 1550000
Central | 50403 | Relocate Dardenne 161/138 kV Substation | The existing Dardenne Substation has the majority of its equipment that needs to be replaced due to reliability and condition based issues rendering it costly and unreliable. In addition, the existing configuration does not meet the needs for Operations or Planning. Therefore, all equipment will be re installed at Belleau substation and retired from Dardenne Substation. | MO | AMEREN MISSOURI | Other | Age and Condition | 2027-12-01 | 161 | 3600000
South | 50404 | Lake Walthall 115kV Delivery Point | Tap the Entergy owned 115kV line (Tylertown - Dexter) with a 115kV switching station and build a new transmission line to the delivery point. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Load Growth | 2026-12-01 | 115 | 2830000
Central | 50405 | Relocate Berlin-Amos 69 kV Line | Reroute Berlin-Amos 69 kV Line out of creek bottom | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2029-12-01 | 69 | 11175000
Central | 50406 | Rebuild Breiner-Kington 69 kV line | Rebuild Breiner-Kington 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2027-12-01 | 69 | 5665000
Central | 50407 | Rebuild Macomb-Spring Lake Junction 69 kV line | 1) Rebuild Macomb Bkr-Woodland 69 kV Line 2) Rebuild Woodland-Spring Lake Jct 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2027-12-01 | 69 | 2010000
Central | 50408 | Rebuild El Dara Junction-Hadley 69 kV line | Rebuild El Dara Jct-Hadley 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Age and Condition | 2029-12-01 | 69 | 2820000
Central | 50409 | New Andrew-Salisbury 69 kV Line | Add 2nd circuit to existing Andrew-Salisbury Tap 69 kV Line for dedicated feed to Salisbury | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2028-12-01 | 69 | 1500000
Central | 50412 | New Paragon-Grove City 69 kV line | 1) New Paragon-Dunkel 69 kV Line 2) New Dunkel-Owaneco 69kV Line 3) New Owaneco-Velma 69 kV Line 4) New Velma-Grove City 69 kV Line | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2030-12-01 | 69 | 19890000
Central | 50413 | New Edinburg 69 kV Breaker Station | New 3 terminal Breaker Station near Taylorville Sub | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2030-12-01 | 69 | 3400000
Central | 50414 | New Henton 69 kV Breaker Station | 1) New 3 terminal Breaker Station 2) New 4.8 MVAR Capacitor Bank | IL | PRAIRIE POWER, INC. | Other | Local Reliability | 2029-12-01 | 69 | 3400000
West | 50415 | Grand Lake Area Projects | Relocate and reterminate 69 kV transmission line into the new Grand Lake high side. | MN | GREAT RIVER ENERGY | Other | Local Needs | 2025-10-31 | 69 | 1200259
West | 50416 | Pine City Breaker Replacement | • Replace breaker 4NB2 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace breaker 4NB3 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace 69kV bus PTs, Grasston line PT and Rush City/Rock Lake line CCVT o Remove 69kV PT Fuses • Replace line arresters with new 48kV MCOV Surge Arresters on Grasston and Bear Creek/Hinckley Lines • Replace 69kV bus relaying with SEL-487E pri/sec panel • Replace the #3 311B panel with 2 line 311C panel • Remove NS3 bypass switch • Update Station Service System o Install new 50kVA SSVT (Pri.) o Install new 200A ATS o Install new 200A Safety Switch (Pri.) o Install new 200A Safety Switch (Emer.) o ECE to replace existing 10kVA Aux Xfmr with 50kVA Aux Xfmr • Update line naming/3 letter mnemonics • Review grounding | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2027-12-31 | 69 | 1364747
West | 50417 | Rebuild 0735 St Bonifacius to Mound | Rebuild line 0735 from St. Bonifacious to Mound and add OPGW | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2026-12-31 | 69 | 13157400
West | 50418 | Denham - Kettle River Rebuild | Rebuild the existing Kettle River to Denham (DK line) 69 kV. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2026-12-31 | 69 | 11442911
West | 50419 | Bena Area Projects | Rebuild BE line from SS2505 to Bena Substation. Line length is approx. 15 miles. Enbridge plans to remove Line 3 which is located roughly 15ft north of GRE’s BE line between Bena Sub and Str 158 near the Mississippi River crossing (approx 12mi). The corridor where the pipeline and transmission line are located is very crowded, swampy and includes a LCP distribution line which is located about 12ft north of the BE line between the Enbridge Pipeline and BE line. The GRE line and LCP line are tied together with crossarms on many structures and there are side guys which extend under the pipeline in many locations. LCP plans to remove their distribution and relocate. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2029-11-29 | 69 | 17450679
West | 50420 | Lakefield Area Projects | Expansion of the 345kV Gen tie bus at the Lakefield substation to accommodate the Three Waters Wind (340MW) Wind Farm. Installation of new 345kV breakers on the existing generator and installation of the GRE controlled EEE, 1500’ of 345kV Transmission to the interconnect 161kV/345kV step up substation | MN | GREAT RIVER ENERGY | GIP |  | 2027-08-24 | 345 | 5217392
West | 50421 | Rebuild 0737 Gleason Lake to Mound | Rebuild line 0737 from Gleason Lake to Mound and add OPGW | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2028-03-15 | 69 | 12996320
West | 50422 | Coon Creek Breaker ELR | Replace 3 345kV and 2 115kV breakers at Coon Creek that are at end of life | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2025-12-01 | 345 | 2250000
West | 50423 | Essig Substation Rebuild | Rebuild end of life Essig substation at neighboring site, converting old 2.4 kV system to standard 12.47kV | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2027-08-31 | 69 | 681832
West | 50424 | Maple Street Substation | Install new distribution substation to meet load growth in area | SD | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2027-06-01 | 115 | 13000000
West | 50425 | Fischer Substation Rebuild | DEA plans to update their 115-kV Fisher in/out distribution substation (both east and west) on the same property to replace the aged substation equipment. GRE will need to move the meter and telecom equipment as part of this work. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2026-03-31 | 115 | 1476377
West | 50426 | Thunder Substation | Install new distribution substation to meet load growth in area | ND | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2027-10-15 | 115 | 7300000
West | 50427 | Winthrop to Bell rebuild projects | Rebuild Winthrop to Bell line, about 12 miles. | MN | GREAT RIVER ENERGY | Other | Age and Condition | 2028-08-31 | 69 | 9868407
West | 50428 | Replace Cass County TR1 | Upgrade transformer to support load growth | ND | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2028-06-01 | 115 | 12200000
West | 50429 | West Byron TR 2 | Install new distribution transformer to meet load growth in area | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2026-10-15 | 69 | 7535000
West | 50430 | Souris Upgrades | Install new bus tie breaker and upgrade limiting equipment at Souris substation | ND | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2028-05-31 | 115 | 2000000
West | 50431 | Line 0846 Relocation | Relocate structures on line 0846 High Bridge - Daytons Bluff 115kV | MN | NORTHERN STATES POWER COMPANY | Other | Local Needs | 2024-12-01 | 115 | 200000
West | 50433 | Install Pine Island Island Area Substation | Install new distribution substation to meet load growth in area | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2026-12-30 | 69 | 8900000
West | 50434 | Replace Meire Grove TR1 | Upgrade transformer 1 at Meire Grove to support load growth | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2027-05-03 | 69 | 6200000
West | 50435 | Install East Mankato Area Substation | Install new distribution substation in East Mankato to meet load growth in area | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2027-12-31 | 115 | 6700000
West | 50436 | rebuild W3449 Marshland to Mississippi River | rebuild W3449 Marshland to Mississippi River | WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2027-12-15 | 69 | 7800000
West | 50437 | Horseshoe Lake Substation | Build new Horseshoe Lake Substation to transfer load from Richmond Substation | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2027-01-01 | 69 | 8500000
West | 50438 | Line 0955 Relocation | Relocate 2 structures on line 0955 Alexandria to Bison 345kV | ND | NORTHERN STATES POWER COMPANY | Other | Local Needs | 2025-04-30 | 345 | 1897429
West | 50440 | West Maple Grove Substation | Build new Substation in Northwest Maple Grove to accommodate load growth | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2028-09-01 | 115 | 25000000
South | 50441 | Wrightsville 115kV: Build two 115kV lines | Build two 3.5 mile new radial 115kV transmission lines from Wrightsville 115kV substation to a new customer station to serve new load. | AR | ENTERGY ARKANSAS, LLC | Other | Load Growth | 2027-04-28 | 115 | 17800000
West | 50442 | Rebuild 5400 Richmond to Rich Springs Tap | rebuild 2.6 miles of 69kV Line 5400 from Richmond to Rich Springs Tap | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2028-12-29 | 69 | 2404191
West | 50443 | Monroe County Breaker and Transformer EOL Replacement | Replace 4 breakers and TR01 and TR02 at Monroe county | MN; WI | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2028-12-01 | 161 | 8000000
West | 50445 | Sioux Falls 115kV Conversion | Rebuild lines 0730 and 0729 Lawrence - South Sioux Falls, West Sioux Falls - South Sioux Falls, South Sioux Falls - Lincoln to 115kV. Convert remaining 69kV substations to 115kV. | SD | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2029-06-01 | 115 | 60000000
East | 50447 | New [CONS] Baker Interconnection | METC to install two 138 kV, 63kA breakers at Weeds Lake to terminate Consumers Energy's new Baker connection at position “BM8” and construct approximately 36.5 miles of new 138 kV line on double-circuit structures (leave vacant side for future use) using 954 ACSR conductor. | MI | METC | Other | Local Needs | 2030-06-01 | 138 | 108810000
West | 50449 | Roughrider Substation | Install new distribution substation to meet load growth in area | ND | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2029-10-15 | 115 | 7500000
West | 50450 | Upgrade end of life Wilmarth TR7 and TR8 | Upgrade end of life Wilmarth TR7 and TR8 | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2028-12-31 | 115 | 5000000
West | 50451 | Magic City Reactor | Install new reactor at Magic City | ND | NORTHERN STATES POWER COMPANY | BRP |  | 2028-09-01 | 230 | 500000
West | 50452 | Peace Garden Reactor | Install new reactor at Peace Garden | ND | NORTHERN STATES POWER COMPANY | BRP |  | 2027-12-01 | 230 | 1500000
West | 50453 | Prairie Island Breaker Addition | Replace motor operated disconnects 8H10 and 8H12 with breakers | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2028-12-01 | 345 | 3000000
West | 50454 | Line 0730 Souris - West Sioux Falls Rebuild | Replace steel poles on line 0730 Souris - West Sioux Falls | ND; SD | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-09-01 | 69 | 1000000
West | 50455 | Prairie Reactor | Install new reactor and substation upgrades to accommodate new reactor at Prairie. Three (3) 115kV, 40MVA, capacitor banks will be removed | MN; ND | NORTHERN STATES POWER COMPANY | BRP |  | 2029-01-01 | 230 | 16000000
West | 50456 | Fort Ridgely 69kV Rebuild | Upgrade 69 kV lines Fort Ridgley-GRE Schilling Tap, Lafayette-GRE Lafayette, GRE Schilling Tap-GRE Lafayette Tap, and Winthrop-Lafayette | MN | NORTHERN STATES POWER COMPANY | Other | Local Reliability | 2029-01-01 | 69 | 14000000
West | 50457 | Install Montrose TR2 | Install new distribution transformer to meet load growth in area | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2026-12-31 | 69 | 7450000
West | 50458 | Install Avon Area Substation | Install new distribution substation to meet load growth in area | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2027-12-31 | 69 | 10000000
West | 50459 | Install Stewart TR2 | Install new distribution transformer to meet load growth in area | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2027-12-31 | 69 | 15000000
West | 50460 | Prairie Island TR10 Replacement | Replace end of life Prairie Island TR10 | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2031-12-01 | 345 | 7990300
West | 50461 | Line 0868 Le Sauk - Fischer Hills - St Stephens Rebuild | Rebuild 0868 from Le Sauk to Fisher Hills to St. Stephens | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2029-01-01 | 115 | 12231418
East | 50463 | Rebuild [CONS] Blackstone 46 kV Station | Consumers Energy notified METC, LLC of a planned project to rebuild the HVD portion of the Blackstone Street 138/46 kV bulk power substation. CONS will replace the two existing 60/80/100 MVA, 138/46 kV three-winding transformers with two new 60/80/100 MVA autotransformers. The new transformers will have an impedance of approximately 7.2% on a 60 MVA base. METC to install a new 138 kV, 40 kA breaker with disconnects at “188” position and re-name existing CONS “199” breaker as “288” after conveyed to METC. Also, METC to build two new radial 138 kV single-circuit lines using 954 ACSR conductor with OPGW from Blackstone to CONS TRF #1 terminating at "188" position and Blackstone to CONS TRF #2 terminating at "288" position. | MI | METC | Other | Local Needs | 2028-10-01 | 138 | 3295000
West | 50464 | Erie Road Substation Rebuild | Rebuild the Erie Road substation in Marshall with new 115 kV breakers and other equipment. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Age and Condition | 2029-01-01 | 115 | 6418700
West | 50465 | Pella Underground Conversion | Rebuild a section of overhead line (~1,135 linear feet of transmission line) to underground line (~800 feet of underground cable). | IA | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Local Needs | 2026-01-01 | 69 | 500000
East | 50466 | METC Customer Interconnections - 2028 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. | MI | METC | Other | Load Growth | 2028-12-31 | 345 | 2500000
West | 50467 | OTP Maple River Reactor Retirements | Retire 2 x 25 MVAR reactors off transformer tertiaries at Maple River 345 kV substation. | ND | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2025-12-31 | 35 | 1
East | 50468 | ITCT Customer Interconnections - 2028 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. | MI | ITC | Other | Load Growth | 2028-12-31 | 345 | 2500000
West | 50469 | OTP Big Stone South Reactor Retirement | Retire 25 MVAR reactor off tertiary winding of Big Stone South transformer #1. | SD | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2025-12-31 | 35 | 1
West | 50470 | OTP Cyrus - Farwell 41.6 kV Rebuild | Rebuild 41.6 kV line between Cyrus 41.6 kV and Farwell 41.6 kV. | MN | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2025-12-31 | 42 | 1130000
West | 50471 | OTP Ivanhoe 41.6kV Line Recloser | Install line recloser near Ivanhoe 41.6 kV. | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2025-12-31 | 42 | 350000
West | 50472 | Hawick Breaker Station | Convert the Hawick switching station to a breaker station by installing three breakers at the existing site. | MN | GREAT RIVER ENERGY | BRP |  | 2026-09-30 | 69 | 2000000
West | 50473 | Pennock Area Projects | Construct a new 69 kV line from the Pennock distribution substation to a new breaker station at the point of interconnection of the GRE owned WS 69 kV line and the WMUC 69 kV line (St. Johns breaker station). Retire BR line west of AG-RK to Granite Falls. | MN | GREAT RIVER ENERGY | Other | Local Reliability | 2029-12-31 | 69 | 11000000
East | 50474 | METC Line Relocation - 2026 | Relocate portion(s) of METC's transmission lines located in public right of way at the government entities’ mandate. | MI | METC | Other | Local Needs | 2026-12-31 | 345 | 2500000
East | 50475 | METC Line Relocation - 2027 | Relocate portion(s) of METC transmission lines located in public right of way at the government entities’ mandate. | MI | METC | Other | Local Needs | 2027-12-31 | 345 | 2500000
East | 50476 | ITCT Line Relocation - 2026 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. | MI | ITC | Other | Local Needs | 2026-12-31 | 345 | 2500000
East | 50477 | ITCT Line Relocation - 2027 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. | MI | ITC | Other | Local Needs | 2027-12-31 | 345 | 2500000
East | 50478 | METC Asset Replacement Program - 2027 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | MI | METC | Other | Age and Condition | 2027-12-31 | 345 | 53875000
East | 50479 | ITCT Asset Replacement Program - 2027 | Equipment that is past its expected design life, utilizes outdated functionality or whose failure rates and maintenance requirements have increased the potential for misoperations and higher maintenance costs associated with their ongoing use. | MI | ITC | Other | Age and Condition | 2027-12-31 | 345 | 59750000
West | 50481 | LG - 2 | Install new facilities to meet load growth in the area. | MN | GREAT RIVER ENERGY | Other | Load Growth | 2030-12-31 | 345 | 120000000
West | 50482 | LG - 3 | Install new facilities to meet load growth in the area. | MN | GREAT RIVER ENERGY | Other | Load Growth | 2026-12-31 | 115 | 25000000
West | 50483 | St. John's Lake Breaker Station | Construct a new 69 kV breaker station near Willmar and rebuild the 69 kV line from the WMU tap to this breaker station to a double circuit line. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Local Reliability | 2029-12-30 | 69 | 9000000
West | 50484 | Priam Second Transformer | This project adds a second 115/69 kV transformer at the Priam substation near Willmar and expands the substation buses. | MN | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Other | Local Reliability | 2029-12-30 | 115 | 9000000
West | 50485 | OTP Eden - Grenville 41.6 kV Rebuild | Rebuild 41.6 kV line between Eden 41.6 kV and Grenville 41.6 kV. | SD | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2029-12-31 | 42 | 1400000
West | 50486 | OTP Casselton Town New 115 kV Delivery | New 115 kV delivery to uprate Casselton town from 41.6 kV to 115 kV. | ND | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2026-12-31 | 115 | 1000000
West | 50487 | OTP Bemidji Nymore Circuit Breaker | New 69 kV breaker at Bemidji Nymore substation. | MN | OTTER TAIL POWER COMPANY | Other | Local Reliability | 2026-12-31 | 69 | 350000
Central | 50488 | Upgrade Dumont to Stillwell 138 kV line (PJM Project B3775.11) | NIPSCO will replace conductor drops at its Stillwell station on the Dumont-Stillwell 345 kV line with (2) 1590 ASCR conductor. NIPSCO will also replace the existing A phase wave trap with a 4000A wave trap. These upgrades are necessary to increase station terminal ratings above line conductor rating. | IN | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Other | Local Reliability | 2026-12-01 | 345 | 601914
West | 50489 | Split Rock - Chanarambie 345kV line JTIQ | Tap JTIQ line Lyon Co-Lakefield, route into Chanarambie. Add (2) 345/115kV transformers at Chanarambie. Add (1) 345kV/115kV transformer at Renner. New 345kV line Split Rock -Renner-Chanarambie. Upgrade 115kV line Split Rock-Pipestone-Chanarambie. | MN; SD | NORTHERN STATES POWER COMPANY | Other | Local Needs | 2033-06-30 | 345 | 165000000
Central | 50490 | Merom Station 345kV Expansion and New 345kV line | Expand Merom 345kV station with additional 345kV position for new line. Extend a new 1.5-mile 345KV line to new customer substation. | IN | HOOSIER ENERGY | Other | Load Growth | 2030-12-01 | 345 | 14000000
Central | 50491 | New Ellettsville 345kV Station | Construct new 345kV transmission station ring-bus along existing Worthington-Bloomington 345kV transmission line. | IN | HOOSIER ENERGY | Other | Load Growth | 2035-01-01 | 345 | 20000000
Central | 50492 | Expand Wheeler Creek 138 kV Station | Expand Wheeler Creek Transmission Station to accept the 138 feeds from SIPC Hamilton and Ameren Kays. One 138 kV Breaker will be required as well as conversion to a ring bus. This is being planned in conjunction with other projects from Ameren and SIPC as part of coordinated portfolio of projects called "South Central Illinois Transmission Expansion". | IN | HOOSIER ENERGY | Other | Local Reliability | 2029-12-01 | 138 | 4700000
Central | 50493 | Rebuild Ashland Tap - Cisne Junction 69 kV Line | The 5.7 mile 69 kV line from Ashland Tap - Cisne Junction will be rebuilt with poles replaced, an upgraded conductor, and a new switch at Ashland Junction. | IL | HOOSIER ENERGY | Other | Local Reliability | 2028-12-01 | 69 | 9500000
West | 50494 | Knight Substation | Install new 115/34.5kV substation in the Dayton area to meet area load growth. | MN | NORTHERN STATES POWER COMPANY | Other | Load Growth | 2026-12-01 | 115 | 29600
West | 50495 | J1745 Fitzgerald SS Network Upgrades and Interconnection Facilities | J1745 is a 100 MW solar farm in Winnebago County, Wisconsin. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2029-06-11 | 138 | 2021000
South | 50496 | MPFCA Replace Sherwood 115kV Breakers | The 1200 A, 17.5 kA oil circuit breakers B0350 and B0397 will be replaced with new 3000 A gas circuit breakers. Disconnect switch B0392 will be replaced and two new replay panels for power transformers #1 and #2. | AR | ENTERGY ARKANSAS, LLC | GIP |  | 2026-10-31 | 115 | 2132000
Central | 50728 | Add 3rd 345/138kV Bank at Edwards Sub | This is part of LEAP Phase 2 EPR mitigations. This will add a third 606MVA bank to Edwards substation, as well as updating normal and emergency line ratings for the LEAP 138kV lines | IN | WABASH VALLEY POWER ASSOCIATION, INC. | BRP |  | 2029-06-30 | 345 | 15000000
Central | 23046 | Upgrade Montgomery 345/161 kV Substation | Address aging infrastructure items and expand 161 kV bus | MO | AMEREN MISSOURI | Other | Local Reliability | 2026-06-01 | 345 | 17000000
Central | 25497 | Reconfigure Overton 161kV Substation | Rebuild the existing Overton 161kV straight bus as a breaker-and-a-half (BAAH) station. | MO | AMEREN MISSOURI | Other | Local Reliability | 2027-12-01 | 161 | 46000000
West | 25240 | Line Clearance Mitigation Program 2026 | Line Clearance Mitigation projects have shorter project life cycles. Projects are driven by the ongoing assessment and analysis of field line clearances using Light Detection and Ranging (LiDAR) technology. Clearance mitigation work immediately follows data assessments and issue identification to maintain safety and system reliability. Initial capital spend for this program expected in 2026. | MI; WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2026-12-31 | 345 | 9000000
West | 21922 | Sigel - Vesper 69 kV (Y-108/Y-107), Partial Rebuild | This project is to partially rebuild portions of Y-107 and Y-108 near Sigel and Vesper substations. Each circuit has ~1.5 miles of rebuild work that is needed. This work is intended to cover remaining scope of work that is not on potential LRTP Tranche 1 scope of work in this area. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2030-12-31 | 69 | 5500000
West | 24474 | Winnebago County, New DIC | WPS is proposing to construct a new T-D substation with two new 69/12.47 kV transformers with circuit breakers. ATC will construct a 69 kV loop-through straight bus with two line switches with load breaks. ATC will also install two manual bus-tie switches and make provisions for a future bus-tie breaker. ATC will loop through the new substation from the Sunset Point – Oshkosh 69 kV (E-5) line on the line section between Sunset Point and Bowen St. | WI | AMERICAN TRANSMISSION COMPANY | Other | Load Growth | 2027-07-15 | 69 | 2900000
West | 25371 | Lake Yankton SVC Retirement | Retire Lake Yankton SVC. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2025-12-01 | 115 | 700000
Central | 25496 | New Blanchette 138 kV Ring Bus | Install a 4 position ring bus at Blanchette 138kV Substation. In addition, fiber will be installed to Kisker with some line re-routing. | MO | AMEREN MISSOURI | Other | Local Reliability | 2029-06-01 | 138 | 7000000
East | 18192 | Rebuild Hines - Levan 120 kV Line | Rebuild the 954 ACSR sections (~0.5 mile) from structure #5680A to Levan and from structure #5686 to Hines with 1431 ACSR using 120 kV, double-circuit construction. Install OPGW on the rebuilt sections. Also, upgrade the 954 ACSR bus (line drop) at Levan “HD” to at least 375 MVA for summer emergency rating. Terminate fiber at both ends. | MI | ITC | BRP |  | 2028-03-15 | 120 | 1935000
West | 25203 | Highland – Hill Valley 138 kV, Construct New Line | Create a new Highland - Hill Valley 138 kV line by: - Converting 6.25 miles of the existing Highland - Eden 69 kV line Y-207 to 138 kV. Along the 69 kV corridor, new easements will be required. - Construct 0.2 miles of new 138 kV into Highland SS. - Construct 1 mile of new 138 kV into Hill Valley SS. - Add one new ring bus position at Highland SS. - Add one new ring bus position at Hill Valley SS. - Retire and remove 0.2 miles of Y-207 into Eden SS and Highland SS. - Retire and remove two breakers, one at Eden SS and one at Highland SS. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2026-09-03 | 138 | 9500000
West | 25267 | 180 Line Rebuild | Rebuild 115kV 180 Line (Hibbing -Maturi) with 636 ACSR. | MN | MINNESOTA POWER INC. | BRP |  | 2028-12-31 | 115 | 9750000
South | 25502 | Line 4B Rebuild | A complete rebuild of Line 4B and line extension to the existing Decatur Substation (Lake – Decatur 69kV) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Lake and Decatur. | MS | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Other | Age and Condition | 2027-03-01 | 69 | 10430000
Central | 50118 | Upgrade Powerton-Tazewell 345 kV line (AE1-163) | This transmission project will consist of all network upgrades required to relieve the overloaded Powerton-Tazewell 345 kV transmission line caused by PJM project AE1-163. | IL | AMEREN ILLINOIS | GIP |  | 2025-12-01 | 345 | 1500000
Central | 50119 | New Moro-Cottage Hills 138 kV Line (C1908 MPFCA) | These Common Use Upgrades consist of equipment for all the substation and transmission line upgrades to support New Moro-Cottage Hills MPFCA. Add 138 kV position at Moro, expand Cottage Hills to a 4 pos., 6 ult. ring bus. Add second circuit between Moro and Cottage Hills on existing ROW utilizing DC structures. Rebuild Moro to Laclede N Tap, Cottage Hills to Laclede S tap and Laclede S tap to Mississippi tap. | IL | AMEREN ILLINOIS | GIP |  | 2028-06-30 | 138 | 38550000
Central | 50631 | Missouri Multi-Entity New Transmission (MoMENT) Project (Primary) | New 40 mile 345 kV line from Loose Creek to Barnett. New 345/161 kV substation at Barnett. New 38 mile 345 and 161 kV double circuit line from Overton to Barnett. New 65 mile double circuit 345 kV line from Barnett to Clinton. New Clinton substation. New 50 mile double circuit 345 kV line from Clinton to LaCygne. | MO | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Other | Local Reliability | 2030-12-01 | 345 | 604000001
Central | 50636 | New Diamond Core Load Addition (RECC Territory) at Mogul 345 kV substation | This new load will connect to MOGL-DBDS-4566 345 kV line that feeds (J1464) Double Black Diamond Solar and will be separately metered. RECC will install, own, and operate the metering at the data center. | IL; MO | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Other | Load Growth | 2027-12-01 | 138 | 0
Central | 50637 | Big Muddy Solar - J1303 Generator Interconnection | Installation of a new 161 kV switchyard on the SIPC Jackson to Campbell Hill line. | IL | Southern Illinois Power Cooperative | GIP |  | 2026-10-01 | 161 | 9389000
West | 50642 | Substation Technology Package #3 - 2026 | Installation of Edge computing hardware at multiple substation locations. Scope includes edge compute interoperability with physical security cameras, rogue detection sensors and asset monitor devices. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Needs | 2026-12-31 | 0 | 3000000
West | 50655 | R1049/R5061 Edgewater SS, Network Upgrades and Interconnection Facilities | Supporting R1049/R5061 interconnection via 345 kV CT contributions, bus 3 differential relay panel, wiring updates in the bus 3 differential relay panels, and System Protection Setting Modifications and Supporting Activities. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2026-09-30 | 345 | 260000
West | 50670 | Werner SS Relay and Remote Asset Renewal | Asset renewal of Werner control house and 138kV relay asset renewal at Werner, Werner West and White Lake SS. Install an additional breaker and eliminate two S&C Mark VI circuit switchers when replacing cap bank relaying at Werner. | WI | AMERICAN TRANSMISSION COMPANY | Other | Age and Condition | 2027-04-15 | 138 | 5300000
South | 50671 | RiverPlex 500-230 kV Station | Entergy is proposing to construct a new 500-230 kV station named RiverPlex to serve a new customer cut into the new Commodore to Churchill 500 kV line and the Commodore to Blue Point, Blue Point to Waterford, and Donaldsonville to Evergreen 230 kV lines near Donaldsonville, LA. Two new 230 kV lines will be constructed between RiverPlex 230 kV and the new Mulberry Road 230 kV station which will serve the new load. One new 230 kV line will be constructed between Blue Point and Mulberry Road 230 kV stations. The RiverPlex 500 kV station will be configured as a ring bus, while the RiverPlex 230 kV station will be configured as a breaker and a half bus. Two 500-230 kV 1200 MVA autotransformers will also be installed at the station. The new station has a target ISD in August 2028. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2028-08-30 | 500 | 284000000
West | 50673 | Portage - Columbia 138 kV (X-13/X-20), Reconductor | This project resolves thermal overloads under single contingency conditions on either the X-13 or X-20 lines between Portage and Columbia. | WI | AMERICAN TRANSMISSION COMPANY | BRP |  | 2027-06-30 | 138 | 17296600
South | 50675 | Cove Ridge 138 kV Station | Entergy is proposing to construct a new 138 kV station named Cove Ridge to serve a new customer cut into the existing Hollywood-Orange 138 kV line near Vinton, LA. The Cove Ridge 138 kV station will be equipped with two breakers and a Capacitor Bank. | LA | ENTERGY SERVICES, LLC. | Other | Load Growth | 2027-12-01 | 138 | 24100000
Central | 50691 | LEAP Phase 2 EPR Mitigations | Reactive and thermal project mitigations for LEAP Phase 2 (MTEP 50208) area large load. | IN | WABASH VALLEY POWER ASSOCIATION, INC. | BRP |  | 2029-06-29 | 345 | 45000000
West | 50497 | MidAmerican Upgrades for MTEP 50157 Big Cedar Load Expansion | Network upgrades on MidAmerican Energy's transmission system identified during the MISO Expedited Project Review study for MTEP 50157 Big Cedar Load Expansion | IA | MIDAMERICAN ENERGY CO. | BRP |  | 2028-12-31 | 345 | 16700000
West | 50498 | Byron - Cascade Creek Line Relocation | Relocation of 1.2miles of 161kV transmission lines due to MnDOT developing a new interchange on intersection of Hwy 14 & Hwy 44. MnDOT requests the project be completed by Spring 2025. | MN | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Other | Local Needs | 2026-12-31 | 161 | 3627000
West | 50500 | Byron - Pleasant Valley 161kV Line Upgrade | Upgrade Byron - Pleasant Valley 161kV line | MN | NORTHERN STATES POWER COMPANY | Other | Local Needs | 2029-06-01 | 161 | 20000000
West | 50501 | Byron - Pleasant Valley 161kV Terminal Upgrade | Upgrade of terminal equipment of Byron - Pleasant Valley 161kV line to match joint facility owners. Upgrading outdated breakers and relays. | MN | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | BRP |  | 2027-12-01 | 345 | 3800000
Central | 50502 | New Brownsburg East 138 kV Substation | In conjunction with MTEP 24274's phase 1. New 138 kV WVPA Brownsburg East substation with 2 138 kV feeds from Maloney Road. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Load Growth | 2025-12-31 | 138 | 8600000
Central | 50503 | New Pleasant Acres Substation Feed 2 138 kV line | Second 138 kV feed and 1 22.4 MVA transformer for Pleasant Acres substation. In conjunction with MTEP 24293. Project required to match MOD submission. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | Other | Load Growth | 2025-12-31 | 138 | 2000000
Central | 50504 | Upgrade Dupo Ferry 138 kV breakers | Dupo Ferry 138kV Breakers Upgrade - Replace 4 overstressed 138kV circuit breakers, existing interrupting capability 40kA, with 50kA new breakers 3000A minimum continuous | IL | AMEREN ILLINOIS | GIP |  | 2026-12-01 | 138 | 2500000
West | 50505 | J1793 Holland SS Network Upgrades | J1793 is a 75 MW solar facility in Sheboygan County, WI. There are no TOIF upgrades required as a part of the J1793 interconnection request as the J1793 generator lead line will utilize the J1153 Generator Lead Line to the same TOIF equipment covered under the J1153 GIA. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2025-12-09 | 138 | 142000
West | 50506 | J1706 North Monroe SS Network Upgrades and Interconnection Facilities | J1706 is a 100 MW solar facility in Green County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2029-06-11 | 138 | 18266000
West | 50507 | J1508 Galvin Ave SS Network Upgrades and Interconnection Facilities | J1508 is a 98.9 MW wind facility in Marathon County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2029-03-13 | 115 | 14094000
West | 50508 | J1629 Welsh Prairie SS Network Upgrades and Interconnection Facilities | J1629 is a 200 MW solar facility in Columbia County, WI. | WI | AMERICAN TRANSMISSION COMPANY | GIP |  | 2030-09-10 | 345 | 21461000
West | 50510 | OTP Bellingham 115 kV Delivery | New 115 kV delivery for town of Bellingham by tapping the Big Stone to Marietta 115 kV line. | MN | OTTER TAIL POWER COMPANY | Other | Age and Condition | 2030-12-31 | 115 | 650000
Central | 50718 | Rebuild Cayuga to Nucor 345 kV line | Line rebuild (~32.3mi) to bundled 954ACSS conductor or 4000A equivalent. | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2029-06-01 | 345 | 95529061
Central | 50719 | Rebuild Nucor to Wolf Creek 345 kV line | Line rebuild (~14mi) to bundled 954ACSS conductor or 4000A equivalent. | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2029-06-01 | 345 | 49000000
West | 50720 | Fargo-St. Cloud-Monticello 345kV Davit Arm Replacement | Replace select steel davit arms on the Fargo-St. Cloud-Monticello 345 kV Transmission line. | MN | NORTHERN STATES POWER COMPANY | Other | Age and Condition | 2030-09-30 | 345 | 12500000
Central | 50722 | New Pond Creek 345 : 138 kV Substation | New 345 : 138 kV substation in Pike County, Indiana to address thermal overloads at Petersburg substation | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2029-06-01 | 345 | 40000000
Central | 50723 | Uprate IPL Petersburg to Cato 138 kV Equipment | Replace IPL leads and wave trap | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2028-12-31 | 138 | 4000000
West | 50724 | North Appleton - Werner West (NAPL31) 345 kV, Rerate | Rerate NAPL31 to resolve 10 spans with ground issues to the existing SELD rating. | WI | AMERICAN TRANSMISSION COMPANY | Other | Local Reliability | 2026-12-26 | 345 | 5300000
Central | 50725 | Rebuild Kokomo HP to Tipton West to Cammack Rd Jct 230kV | Rebuild two separate 230kV lines to mitigate overloads due to EPR study. ~11.8mi of 23008 line from Tipton to Cammack Rd Jct to bundled 954ACSS conductor or 4000A equivalent and ~14.4mi of 23032 line from Kokomo Highland Park to Tipton West to bundled 954ACSS conductor or 4000A equivalent. | IN | DUKE ENERGY INDIANA, LLC | BRP |  | 2029-06-01 | 230 | 65500000
Central | 50727 | Replace Thompson 345/138/13.75 MVA Autotransformer at Thompson Substation | Replace 275 MVA, 345 : 138 kV Autotransformer with 500 MVA, 345 : 138 kV Autotransformer. | IN | INDIANAPOLIS POWER & LIGHT COMPANY | BRP |  | 2029-12-31 | 345 | 15000000

## MTEP25 Facilities
Target Appendix | App AB | Planning Region | Geographic Location by TO Member System | PrjID | Facility ID | Facility Type | Expected ISD | From Sub | To Sub | Ckt | Max kV | Min kV | Description | State | Miles Upgrade | Miles New | Plan Status | Estimated Cost | Submitting Comp. | Cost Shared
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14 | Column15 | Column16 | Column17 | Column18 | Column19 | Column20 | Column21
A |  | West | IA | 50624 | 51329 | Voltage Device | 2026-06-01 | Substation 74 |  |  | 161 |  | Relocate the existing 161 kV, 50.4 MVAR capacitor bank from Substation A to Substation 74. | IA |  |  | M1 - Proposed | 1600000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | WI | 50622 | 51331 | Misc. | 2027-11-30 | South Beaver Dam |  |  | 0 |  | The objective of ATC’s Substation (HVP) Equipment Removal project is to enhance safety within and outside the control house by decommissioning the remaining High Voltage Protection (HVP) telecommunications equipment from (~269) ATC substations. The legacy HVP (copper cable) equipment is no longer in use due to the migration to fiber optic technology upgrades within ATC’s substation environment. | WI |  |  | M1 - Proposed | 3000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | IN | 50628 | 51339 | Transformer | 2029-06-30 | Fayette/Wolf Creek | Edwards |  | 345 | 138 | a new 345kV ring bus and approx. 12 miles of 345kV line to the west side of Lebanon where WVPA will construct a 345/138kV substation. Approx. 15 miles of 345kV line will be built to network this 345/138kV station to a planned 345/138kV station on the north side of the LEAP district. WVPA will also connect into the Nucor-Whitestown 345kV line and construct a new 345kV ring and approx. 6 miles of new 345kV line to the new step down substation. | IN |  | 33 | M2 - Appendix A Approved | 345000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | West | WI | 50514 | 50812 | Substation | 2028-06-30 | Emerson Rd |  |  | 345 |  | The TO’s new 345kV Interconnection Switching Station is arranged as follows: • in an initial three (3) position, • ultimate four (4) position, • three (3) 345kV circuit breaker ring bus with: o a single (1) Generator Lead Line position and o two (2) transmission line positions. | WI |  |  | M1 - Proposed | 16094000 | AMERICAN TRANSMISSION COMPANY | Shared
A |  | West | WI | 50514 | 50813 | Line New | 2028-06-30 | Briggs Road | North Madison | W-13 | 345 |  | The existing W-13 345kV line between Briggs Road and North Madison Substations will be tapped and looped into the new 345kV Interconnection Switching Station to provide transmission access. | WI |  |  | M1 - Proposed | 2426000 | AMERICAN TRANSMISSION COMPANY | Shared
A |  | West | WI | 50514 | 50814 | Misc. | 2028-06-30 | North Madison |  |  | 345 |  | The existing Transmission Owner’s 345kV W-13 Line will be rerouted into the Interconnection Station. The existing line relaying at North Madison substation will be upgraded per Transmission Owner system relay protection standards to align with the new Interconnection Station to ensure the line is properly protected. On the Briggs Road line at North Madison substation, there is a phasing designation change between Xcel Energy and ATC. During detailed design it will be determined where location of phase change will occur. | WI |  |  | M1 - Proposed | 441000 | AMERICAN TRANSMISSION COMPANY | Shared
A |  | West | WI | 50514 | 50815 | Substation | 2028-06-30 | Emerson Rd |  |  | 345 |  | The J1502 Transmission Owner Interconnected Facilities consists of substation work associated with the Generator Lead Line entrance at the new Interconnection Switching Station. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. | WI |  |  | M1 - Proposed | 886000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50515 | 50816 | Misc. | 2027-10-31 | Rockdale |  |  | 345 |  | The J1214/J1326 Interconnect Station and TOIF facilities are constructed and placed in-service as set forth in the J1214/J1326 GIA. System Protection and supporting activities are required. | WI |  |  | M1 - Proposed | 25000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50516 | 50817 | Substation | 2025-04-30 | Tennyson |  |  | 138 |  | The S1017 project consists of the installation of 100MW of battery storage at the J947 collector station. The J947 lead line and TOIF facilities at Tennyson Substation will be utilized. Analysis and remediation of the Tennyson Substation ground grid may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. ATC Substation Design Guide and/or Criteria, GDE-1030/CRT-0060, will be used. If no ATC standards apply, then applicable local distribution company (LDC) standards or industry standards will be used. | WI |  |  | M4 - Project in Service | 200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50516 | 50818 | Misc. | 2025-04-30 | Tennyson |  |  | 138 |  | ATC Protection and supporting activities | WI |  |  | M4 - Project in Service | 25000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50517 | 50819 | Substation | 2026-08-03 | 7 Mile Creek |  |  | 138 |  | Analysis and remediation of the 7 Mile Creek, Port Edwards, Sand Lake and Wautoma substation ground grids may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. | WI |  |  | M1 - Proposed | 775000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50517 | 50820 | Substation | 2026-08-03 | Port Edwards |  |  | 138 |  | Analysis and remediation of the 7 Mile Creek, Port Edwards, Sand Lake and Wautoma substation ground grids may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. | WI |  |  | M1 - Proposed | 200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50517 | 50821 | Substation | 2026-08-03 | Sand Lake |  |  | 138 |  | Analysis and remediation of the 7 Mile Creek, Port Edwards, Sand Lake and Wautoma substation ground grids may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. | WI |  |  | M1 - Proposed | 200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50517 | 50822 | Substation | 2026-08-03 | Wautoma |  |  | 138 |  | Analysis and remediation of the 7 Mile Creek, Port Edwards, Sand Lake and Wautoma substation ground grids may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. | WI |  |  | M1 - Proposed | 200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50517 | 50823 | Misc. | 2026-08-03 | 7 Mile Creek |  |  | 138 |  | ATC Protection and supporting activities | WI |  |  | M1 - Proposed | 100000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50518 | 50824 | Line Upgrade | 2027-10-10 | Hill Valley | Eden | X-127 | 138 |  | The Hill Valley – Eden 138kV (X-127) reconductor project will replace approximately 1.0 mile of conductor with a bundled TP 477 kcmil ACSR 26/7 Hawk conductor. | WI | 1 |  | M1 - Proposed | 1625089 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50518 | 50825 | Line Upgrade | 2027-10-10 | Eden | Highland | X-147 | 138 |  | The Eden – Highland 138 kV (X-147) rebuild project will reconductor approximately 4.5 miles with TP 556.5 kcmil ACSR 26/7 Dove conductor with 26 structures being rebuilt or remediated to support the new conductor. | WI | 4.5 |  | M1 - Proposed | 5998000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50519 | 50826 | Voltage Device | 2028-06-30 | North Madison | J1502 POI |  | 345 |  | Relocate the 80 Mvar reactor from North Madison SS to J1502 POI SS to regulate voltage when J1502 is unavailable. | WI |  |  | M1 - Proposed | 5165000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MN | 50520 | 50827 | Line Upgrade | 2028-12-31 | Donaldson 115 kV | Donaldson South 115 kV | 1 | 115 |  | Structure replacements to uprate the line from Donaldson to Donaldson South, the POI for J1575, 115 kV transmission line. | MN |  |  | M1 - Proposed | 83341 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50520 | 50828 | Substation | 2028-12-31 | Donaldson 115 kV |  |  | 115 |  | Substation upgrades at Donaldson 115 kV. | MN |  |  | M1 - Proposed | 692951 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50521 | 50829 | Substation | 2028-08-03 | Donaldson South 115 kV |  |  | 115 |  | New substation designated Donaldson South for the POI of J1575. | MN |  |  | M1 - Proposed | 4739048 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50521 | 50830 | Line New | 2028-08-03 | Donaldson South 115 kV |  |  | 115 |  | In and out line connections from Donaldson - Warsaw 115 kV line to new Donaldson South J1575 POI 115 kV substation. | MN |  |  | M1 - Proposed | 449718 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50521 | 50831 | Misc. | 2028-08-03 | Donaldson 115 kV |  |  | 115 |  | Relaying at Donaldson 115 kV. | MN |  |  | M1 - Proposed | 60000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | ND | 50521 | 50832 | Misc. | 2028-08-03 | Oslo 115 kV |  |  | 115 |  | Relaying at Oslo 115 kV. | ND |  |  | M1 - Proposed | 11000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50521 | 50833 | Line Upgrade | 2028-08-03 | J1575 |  |  | 115 |  | Deadend at J1575. | MN |  |  | M1 - Proposed | 709287 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50521 | 50834 | Line New | 2028-08-03 | Donaldson South 115 kV | J1575 115 kV | 1 | 115 |  | 115 kV tie line from Donaldson South to J1575. Includes commissioning. | MN |  | 2 | M1 - Proposed | 2091244 | OTTER TAIL POWER COMPANY | Not Shared
A | A | South | LA | 50528 | 50852 | Substation | 2027-07-01 | Mud Lake | Big Lake |  | 230 |  | Construct a 230 kV Benoit Station on the Mud Lake to Big Lake line. | LA |  |  | M2 - Appendix A Approved | 51800000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50528 | 50853 | Voltage Device | 2027-07-01 | Benoit |  |  | 230 |  | Two 64.8 MVAR Capacitor Banks | LA |  |  | M2 - Appendix A Approved | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | MN | 50498 | 50854 | Misc. | 2026-12-31 | Byron | Cascade Creek |  | 161 |  | Relocation of 1.2miles of 161kV transmission lines due to MnDOT developing a new interchange on intersection of Hwy 14 & Hwy 44. MnDOT requests the project be completed by Spring 2025. | MN |  |  | M1 - Proposed | 3627000 | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
A |  | West | WI | 50529 | 50855 | Line New | 2029-05-01 | City Limits | Northside |  | 138 |  | 1) Construct new 138kV line between City Limits – Northside 2) Rebuild a 138kV line section of 50632 (From STR132131 - City Limits), 3) Rebuild a 138kV line section of 43025 (From STR132131 - Northside), 4) Rebuild two 138kV line sections of 971K11 (Melissa - Meadows Tap and Meadows Tap - Kaukauna Central Tap). | WI |  |  | M1 - Proposed | 35700000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MI | 50530 | 50856 | Substation | 2029-03-13 | Grace Lake |  |  | 138 |  | ATC shall construct a 138 kV line interconnection substation to accommodate the generating facility’s collector station to the power system. The new J1750 Substation will be arranged in a three breaker ring bus configuration with one generation position and two line positions, capable of future expansion to an ultimate 4 position ring bus. The new J1750 Substation will segment the Transmission Owner’s overhead X-119 transmission line between existing Empire and Huron Substations into two segments, X-TBD and X-119. All new substation equipment (bus, jumpers, switches, breakers etc) carrying transmission system network current should target a minimum continuous SN rating of 2,000 Amps. New equipment designations will be requested and provided by ATC System Operations. Relay protection and control will consist of two line relay panels with primary and secondary schemes and power line carrier communication (X-TBD and X-119), one line relay panel with dual redundant fiber communications (J1750 Generator lead line), and two panels consisting of breaker failure and auto reclose relay protection for the three J1750 substation breakers. The Transmission Owner will maintain ownership of all X-119 and X-TBD related work and J1750 Substation up to the Point of Change of Ownership (PCO). | MI |  |  | M1 - Proposed | 10068000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MI | 50530 | 50857 | Line New | 2029-03-13 | Grace Lake | Empire | X-119 | 138 |  | The X-119 138 kV Transmission Line Loop-In project will consist of installing two single-circuit 90deg dead-end steel poles in place of existing tangent H-Frame structure 111 that will segment the line into X-119 towards Huron and X-TBD towards Empire, routing the line through the Transmission Owner’s new switchyard. Insulators on the line dead-end poles and switchyard dead-ends will route the conductors to the bus connections and surge arresters. Shield wire for X-119/X-TBD will terminate at the new two-pole structure and new wires will be strung between the two-pole structure and the switchyard dead-end structures. All equipment and hardware on the switchyard side of the line and shield wire terminations is addressed in the Transmission Owner’s new Interconnection switching station. The Transmission Owner will retain ownership of the line segments, support poles and interconnection facility. | MI |  |  | M1 - Proposed | 1581000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MI | 50530 | 50858 | Substation | 2029-03-13 | Grace Lake |  |  | 138 |  | The J1750 TOIF will consist of jumpers and equipment to connect the Interconnection Customer’s generator lead line equipment with the Transmission Owner rigid bus. The Transmission Owner will furnish, install, own, operate, and maintain the relays and associated communication equipment that are located in the Transmission Owner’s facility for the generator lead line. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. | MI |  |  | M1 - Proposed | 461000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | MO | 50531 | 50859 | Substation | 2027-12-01 | Fredericktown |  |  | 161 | 138 | Line position at Fredericktown 138 kV for AECI | MO |  |  | M2 - Appendix A Approved | 1200000 | AMEREN MISSOURI | Not Shared
A |  | West | WI | 50532 | 50860 | Line Upgrade | 2028-05-01 | Stiles | Sherwood | L-142 | 138 |  | ~50 structures to replace, initial assumption is to transfer existing wires. | WI |  |  | M1 - Proposed | 7000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50533 | 50861 | Substation | 2026-09-05 | Lone Rock |  |  | 69 |  | The S1016 project consists of the installation of 25MW of battery storage and an 8.4 MVAR capacitor bank at the J864 collector station. The J864 lead line and TOIF facilities at Lone Rock Substation will be utilized. Analysis and remediation of the Lone Rock Substation ground grid may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. | WI |  |  | M1 - Proposed | 775000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50533 | 50862 | Misc. | 2026-09-05 | Lone Rock |  |  | 69 |  | ATC Protection and supporting activities | WI |  |  | M1 - Proposed | 25000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50534 | 50863 | Misc. | 2027-12-31 | Academy |  |  | 138 |  | The J1824 network upgrades at Academy Substation consist of adding one (1) new line protection panel to the existing control house. New control and fiber will be run from the new line GCB to the control house. | WI |  |  | M1 - Proposed | 790000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50534 | 50864 | Substation | 2027-12-31 | Academy |  |  | 138 |  | The J1824 TOIF at Academy Substation will consist of adding one (1) 138kV Gas Circuit Breaker, and two (2) disconnect switches, to connect the Customer’s Generator Lead Line to the Transmission Owner’s strain bus 1. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. | WI |  |  | M1 - Proposed | 631000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50534 | 50865 | Transformer | 2027-12-31 | Academy |  |  | 138 | 69 | The Academy Substation project will consist of replacing the existing 138/69 kV T31 autotransformer with a new 138/69 kV autotransformer per Transmission Owner standards. A concrete oil containment will be installed around the new transformer and rigid bus will be used to connect from the transformer to the 69 kV box structure. | WI |  |  | M1 - Proposed | 8823000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50535 | 50866 | Substation | 2027-12-31 | Wolfram Rd |  |  | 138 |  | TO shall construct a 138 kV interconnection substation to accommodate a generation collection facility addition to the power system. The new J1732 interconnection substation will be located adjacent to the Interconnection Customer yard with a shared fence. | WI |  |  | M1 - Proposed | 7988000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50535 | 50867 | Line New | 2027-12-31 | Lewiston | Trienda | X-68 | 138 |  | The X-68 138 kV Transmission Line Loop-In consists of two (2) horizontal monopole dead-end structures routing the line through the Transmission Owner’s new substation, segmenting X-68 between the Lewiston and Trienda substations. Also: • Line renaming will be required and determined in detailed design. • Line disconnect switches will isolate the line from the ring bus interconnection substation facility. • Insulators on the line dead-end poles and substation dead-ends will route the conductors to the bus connections and surge arresters. Existing wire for transmission lines will terminate at the new poles and new wire will be strung between the poles and their associated substation dead-end structure. | WI |  |  | M1 - Proposed | 902000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50535 | 50868 | Substation | 2027-12-31 | Trienda |  |  | 138 |  | The Trienda Substation project will consist of modifications to the protection and communications equipment on the X-68 line terminal to J1732 Substation in support of the J1732 interconnection project. | WI |  |  | M1 - Proposed | 357000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50535 | 50869 | Substation | 2027-12-31 | Kilbourn |  |  | 138 |  | The Kilbourn Substation project will consist of modifications to the protection and communications equipment on the X-68 line terminal to J1732 Substation in support of the J1732 interconnection project. | WI |  |  | M1 - Proposed | 301000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50535 | 50870 | Substation | 2027-12-31 | Wolfram Rd |  |  | 138 |  | The J1732 interconnection will consist of bus and equipment to connect the Interconnection Customer’s Generator Lead Line to the Transmission Owner’s rigid bus. A motor operated line disconnect switch will isolate the Generator Lead Line from the three position ring bus interconnection substation. All aspects of the customer owned yard to be designed and installed by others. Any shielding wire for Interconnection Customer facilities will terminate at the Interconnection substation dead end shield wire vangs. All new substation equipment will target a minimum continuous summer normal rating of 2,000 amps. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. | WI |  |  | M1 - Proposed | 346000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | IN | 50538 | 50877 | Line New | 2028-05-31 | Green Acres |  |  | 138 |  | Construct Transmission Owner’s Interconnection Facilities at Transmission Owner’s Green Acres Substation consisting of one monopole, H frame pull off structure, metering equipment, conductor, and fiber optics. | IN |  |  | M1 - Proposed | 1726367 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50538 | 50878 | Substation | 2028-05-31 | Green Acres |  |  | 138 |  | Create new position on double breaker double bus Green Acres 138kV bus for generating lead line. | IN |  |  | M1 - Proposed | 6397253 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | A | South | AR | 50541 | 50879 | Transformer | 2028-12-01 | El Dorado |  |  | 500 | 345 | Upgrade the existing 500/345kV autotransformers and associated equipment to 1200MVA. | AR |  |  | M2 - Appendix A Approved | 35725000 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | West | WI | 50511 | 50807 | Line Upgrade | 2029-06-11 | Columbia |  |  | 138 |  | The J1746 network upgrades at Columbia Substation consist of adding: • one (1) 138kV Circuit Breaker, strain span, • three (3) 138kV Bus PTs, • two (2) fiber vaults, • one (1) new line protection panel, and • one (1) new breaker protection & control panel. • New control cable will be run from the new 138kV Circuit Breaker, 138kV PT’s, and • fiber will be run from the existing Northeast A-Frame dead-end to the control house via new buried conduit and existing cable trench. | WI |  |  | M1 - Proposed | 1464000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50511 | 50808 | Substation | 2029-06-11 | Columbia |  |  | 138 |  | The J1746 TOIF at Columbia Substation will consist of adding three (3) surge arresters, two (2) OPGW splice enclosures, one (1) line disconnect switch to support the new Generator Lead Line. Any shielding wire for Interconnection Customer facilities will terminate at the Interconnection substation dead end shield wire vangs. All new substation equipment will target a minimum continuous summer normal rating of 2,000 amps. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. | WI |  |  | M1 - Proposed | 381000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50512 | 50809 | Misc. | 2027-11-09 | Paris |  |  | 138 |  | The scope of work at Paris Substation includes upgrading the protection on Line PARG51 to convert the existing SEL-311C to a DCU scheme over a power line carrier communication channel. A UPLC-II and 85 Cut-Off switch will be installed in the existing PARG51 line relay panel. A wave trap and tuner will be installed on the existing line CCVT on the PARG51 line position to Berryville Substation. Disconnect switches and jumpers will be upgraded for breaker position BS5-6. | WI |  |  | M1 - Proposed | 287000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50512 | 50810 | Misc. | 2027-11-09 | Berryville |  |  | 138 |  | The scope of work at Berryville Substation includes upgrading the protection on Line PARG51 to convert the existing SEL-311C to DCU scheme over a power line carrier communication channel. A UPLC-II and 85 Cut-Off switch will be installed in the existing PARG51 line relay panel. A 138 kV CCVT, wave trap, and tuner will be installed on the PARG51 line position to Paris Substation. The scope of work at Berryville Substation also includes upgrading the protection on Line 3124 to convert the existing SEL-311C to POTT scheme over a fiber communication channel. An 85 Cut-Off Switch to block fiber communication will be installed on the relay panel controlling Line 3124 to Albers Substation. | WI |  |  | M1 - Proposed | 315000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50512 | 50811 | Misc. | 2027-11-09 | Albers |  |  | 138 |  | The scope of work at Albers Substation includes replacing the line relaying panel protecting Line 3124 with a 421/311C POTT protection scheme. | WI |  |  | M1 - Proposed | 209000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50124 | 50201 | Substation | 2028-12-01 | Portage |  |  | 138 | 69 | Asset Renewal of the Portage SS control house, all assets within the control house, and 5 oil circuit breakers. | WI |  |  | M1 - Proposed | 7100000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50125 | 50202 | Misc. | 2028-12-01 | Rock River |  |  | 138 | 69 | Asset Renewal of several relay panels, disconnect switches, and two battery banks at Rock River SS. | WI |  |  | M1 - Proposed | 3986000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50125 | 50203 | Misc. | 2028-12-01 | Town Line Road |  |  | 138 | 69 | Asset renewals of several relay panels, RTU panel, disconnect switches, and battery bank at Town Line Road SS. | WI |  |  | M1 - Proposed | 1628000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50126 | 50204 | Substation | 2028-12-01 | Coyne St |  |  | 115 |  | At Coyne Street SS, asset renewal of four 115 kV oil circuit breakers, six 115 kV disconnect switches, and 1 control house with all panels and components. | WI |  |  | M1 - Proposed | 7950000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50127 | 50205 | Misc. | 2028-12-01 | Finger Road |  |  | 69 |  | Asset Renewal of the Finger Road SS control house and all assets within the control house. | WI |  |  | M1 - Proposed | 5205000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50127 | 50206 | Misc. | 2028-12-01 | Danz Ave |  |  | 69 |  | Project also includes the remote end asset renewal of 3 relay panels and the RTU panel at Danz Avenue. | WI |  |  | M1 - Proposed | 596000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50128 | 50207 | Misc. | 2028-12-01 | Eden |  |  | 138 | 69 | Asset Renewal of the Eden SS control house and all assets within the control house. | WI |  |  | M1 - Proposed | 5081000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50134 | 50213 | Line Upgrade | 2028-11-30 | Huiskamp | Division Street Tap | Y-132 | 69 |  | Rebuild and install OPGW on approximately 2.7 miles of Y-132 from Huiskamp SS to Division Street Tap switch structure, in addition rebuild 0.2 miles of the Division Street Tap to Division Street SS and install OPGW from Waunakee to Huiskamp SS. | WI |  |  | M1 - Proposed | 8500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50542 | 50880 | Substation | 2027-06-15 | Sheepskin |  |  | 69 |  | Analysis and remediation of the Sheepskin Substation ground grid may be required. A comprehensive analysis will be performed during detailed design and new ground grid will be designed per the most recent version of the Owners ground grid design criteria. | WI |  |  | M1 - Proposed | 200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50542 | 50881 | Misc. | 2027-06-15 | Sheepskin |  |  | 69 |  | ATC Protection and supporting activities | WI |  |  | M1 - Proposed | 25000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50543 | 50882 | Substation | 2028-04-01 | Cosmos |  |  | 345 |  | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, 138 kV capacitor banks, and 4 – 345 kV line terminals, and 1 – 138 kV line terminals with a series reactor. | WI |  |  | M1 - Proposed | 195000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50544 | 50883 | Substation | 2027-10-10 | Rockdale |  |  | 138 |  | The Rockdale 138 kV Substation project will consist of replacing 8 station post insulators and adding sixteen (16) CCVTs to address overdutied breakers 631-S, 636-S, 646-S, 628-S, 2327-S, and 622-S. 3,000 pF of capacitance is required within 300 feet of the line- or transformer-side bushings on each overdutied breaker. Sixteen (16) pier foundations and sixteen (16) standard low 1Ø CCVT stands will be added to the line terminals and transformer buses. No conduit or control cable will be needed. Jumpers will connect the CCVTs to the bus via compression fittings. Ground tails will be connected to the existing grid via exothermic welds and tees. Eight (8) station post insulators will be replaced with extra-high strength insulators to withstand the 47.6 kA fault current on the 138 kV bus. No conduit, junction boxes, or control cable will be connected to the new CCVTs. Each CCVT will self-power its anti-condensation heater. | WI |  |  | M1 - Proposed | 1120000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50884 | Substation | 2028-05-15 | Shady Dr |  |  | 138 |  | The proposed 138kV Interconnection Switching Station is arranged in an initial three (3) position, future four (4) position ultimate ring bus configuration with a single (1) Generator Lead Line position and two (2) transmission line positions. The proposed fenced area is approximately 241 feet x 241 feet. The proposed Interconnection Switching Station also includes a ‘hardened’ control building that will house control and protection panels, IT Comm / RTU panels, main termination cabinets (MTC), and AC and DC station service equipment. | WI |  |  | M1 - Proposed | 11576000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50885 | Line New | 2028-05-15 | Arnott | Hartman Creek | O-119 | 138 |  | The existing 138 kV line O-119 between Arnott substation and Hartman Creek substation will be looped into the new 138 kV Interconnection Switching Station to provided transmission access. | WI |  |  | M1 - Proposed | 2370000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50886 | Substation | 2028-05-15 | Arnott |  |  | 138 |  | At Arnott Substation, an independent, redundant comm-assisted relay scheme will be required. An additional line CCVT, line tuner, and wave trap will be installed on line O-119 to the new Interconnection Switching Station and the existing line O-119 relay panel 20-02 will be replaced with a new dual UPLC relay panel. | WI |  |  | M1 - Proposed | 755000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50887 | Substation | 2028-05-15 | Golden Sands |  |  | 138 |  | At Golden Sands Substation, the scope of work includes installing an underground fiber to the new J1752 Interconnection Switching Station. | WI |  |  | M1 - Proposed | 247000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50888 | Substation | 2028-05-15 | Hartman Creek |  |  | 138 |  | At Hartman Creek Substation an independent, redundant comm-assisted relay scheme will be required. (1) One additional line CCVT, line tuner, and wave trap will be installed on the existing line O-119. New jumpers will be installed to connect the new line trap. The existing line O-119 relay panel N3 will be replaced with new dual UPLC relay panel. | WI |  |  | M1 - Proposed | 845000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50889 | Misc. | 2028-05-15 | Harrison North |  |  | 138 |  | At Harrison Substation, line relaying for A-105 line to Hartman Creek will require settings changes. | WI |  |  | M1 - Proposed | 46000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50545 | 50890 | Substation | 2028-05-15 | Shady Dr |  |  | 138 |  | The J1752 Transmission Owner Interconnected Facilities consists of substation work associated with the generator lead line entrance at the new interconnection switching station. The generator lead line will terminate on the attachment vangs of the H-frame dead-end serving as the Point of Change of Ownership (PCO). The TOIF portion will then include all bus and equipment from there down through the motor-operated disconnect (MOD) switch, surge arresters, rigid bus, and all foundations and steel support structures to the POI where it connects to the main bus within the 3-position ring. | WI |  |  | M1 - Proposed | 616000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | South | LA | 50546 | 50892 | Substation | 2027-08-01 | Commodore | Waterford | 1 | 230 |  | Entergy is proposing to construct a new 230 kV four breaker ring bus station named Bluepoint to serve a new customer cut into the new Commodore to Waterford 230 kV line (~10.4 miles in and out) near Donaldsonville, LA. | LA |  | 10.4 | M2 - Appendix A Approved | 59600000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | WI | 50547 | 50893 | Substation | 2028-12-30 | East Beloit |  |  | 138 | 12 | In support of a distribution substation relocation/rebuild, ATC will extend COR-BEG 138kV (X-41) line approximately 0.15 mile (double circuit transmission) to the new East Beloit substation and install 2 sets of bus-tie disconnect switches. ATC will retire COR-ESB 69kV (Y-140) line (Approx. 0.5 miles) and the existing East Beloit SS location and install 2 line circuit breakers and 2 line disconnects at Dickinson SS. | WI |  |  | M1 - Proposed | 7200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50548 | 50894 | Substation | 2027-06-01 | Juneau Industrial |  |  | 69 | 12 | In support of a distribution transformer addition, ATC will rebuild Juneau Industrial and will install 1 bus-side load break disconnect switch, 1 bus side air break 2 bus-tie disconnect switches. | WI |  |  | M1 - Proposed | 4800000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50549 | 50895 | Substation | 2028-12-31 | Wilson St |  |  | 69 | 12 | To support a new distribution substation and associated station retirements, ATC will loop through the existing WAN-WANT 69kV (Y-306) line for new Wilson St SS. ATC will install 2 line disconnect switches and 2 bus-tie disconnect switches. ATC to retire portion of WAN-WANT 69kV (Y-306) line to Waupun Westside (WAW), Waupun Southside (WSS) and Comtech (COMH). | WI |  |  | M1 - Proposed | 3200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | IA | 50213 | 50896 | Misc. | 2028-12-31 | Rock Creek | Rock Creek | 1 | 345 | 345 | Relocate TOIF for J1084 to new Rock Creek substation location | IA |  |  | M1 - Proposed | 1139666 | ITC MIDWEST | Not Shared
A |  | West | WI | 50550 | 50897 | Substation | 2028-12-01 | North Monroe |  |  | 138 | 69 | Asset Renewal of existing substation equipment due to age and condition. Existing and anticipated future poor performance and reliability issues. Replace 138kV Capacitor cans and update bank specifications and equipment as appropriate. ATC Planning to confirm the required MVAR capacity and switching device required. Replace relay panels and Station Manager RTU. Install to current ATC standards including Dual bus differential relays on the 69kV and 138kV busses. Replace 69kV Siemens model SP breaker in Position 719-S. Replace three Turner Electric disconnects and one ITE model HPL disconnect. Replace S&C circuit switcher in Position 207-S. Replace station power transformer connected to 69kV bus. | WI |  |  | M1 - Proposed | 3105000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | IN | 50551 | 51220 | Line New | 2028-12-31 | Elderberry | Stillwell |  | 345 |  | Approximately 15 miles of 345kV transmission line | IN |  |  | M2 - Appendix A Approved | 75000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | KY | 50577 | 51223 | Voltage Device | 2027-12-01 | Henderson County |  |  | 69 |  | Henderson County Capacitor Bank Addition | KY |  |  | M1 - Proposed | 1500000 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A | A | South | AR | 50581 | 51230 | Substation | 2026-03-31 | Fort Mountain |  |  | 161 |  | Entergy is proposing to build the high-side portion of the substation. This will consist of (3) MOS switches, site, foundation, metering transformers, metering equipment and RTU. Metering, RTU and telecom equipment will be housed in Entergy owned control house. Entergy will cut into the Berryville-Green Forest 161 kV line and build 1 mile of two 161kV lines to the POD at the Customer owned substation. | AR |  | 1 | M3 - Under Construction | 5727876 | ENTERGY ARKANSAS, LLC | Shared
A |  | South | MS | 50368 | 51238 | Misc. | 2026-06-01 | McAdams 500kV |  |  | 500 |  | Ensure the McAdams 500 kV station has redundant DC protection. | MS |  |  | M1 - Proposed | 4100000 | ENTERGY MISSISSIPPI, LLC. | Not Shared
A |  | South | MS | 50367 | 51239 | Substation | 2026-12-31 | Multiple |  |  | 500 |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements | MS |  |  | M1 - Proposed | 68400000 | ENTERGY MISSISSIPPI, LLC. | Not Shared
A |  | South | TX | 50352 | 51240 | Line Upgrade | 2029-12-31 | Amelia | Poly |  | 69 | 69 | Amelia - Poly 69 kV line upgrade. Upgrade bus and line bay bus at Poly. Upgrade jumpers and line bay riser at Amelia and Poly. Upgrade a couple spans on each end, all to a minimum of 1600A. | TX |  |  | M1 - Proposed | 3700000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50354 | 51241 | Line Upgrade | 2027-12-17 | Mid County | Stonegate |  | 138 | 138 | Mid County - Stonegate 138 kV line | TX |  |  | M1 - Proposed | 6540000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50539 | 51242 | Substation | 2026-12-01 | Cargas |  |  | 500 |  | Cargas 500 kV station will be cut into the Perryville to Sterlington 500 kV lines 1 and 2 and Perryville to Baxter Wilson 500 kV line. | LA |  |  | M2 - Appendix A Approved | 1210000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50356 | 51243 | Line Upgrade | 2028-06-01 | Port Acres | Legend | 1 | 230 | 230 | Cut Port Acres Bulk to Sandling 230 kV line in and out of Legend. Rebuild both Port Acres Bulk to Legend 230 kV lines. | TX |  |  | M1 - Proposed | 21900000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50539 | 51244 | Substation | 2026-12-01 | Cargas | Smalling |  | 500 | 230 | Smalling 500/230 kV station will be cut into the Cargas to Baxter Wilson 500 kV line. Two additional 27 mile 500 kV lines from Smalling to Cargas. The Smalling 230 kV station will be a breaker and a half substation, including four 1,500 MVA 500/230 kV autotransformers and eight 230 kV lines going to six 230 kV stations which will feed the new load. | LA |  | 54 | M2 - Appendix A Approved | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50356 | 51245 | Line Upgrade | 2028-06-01 | Port Acres | Legend | 2 | 230 | 230 | Port Acres Bulk to Legend 230 kV Rebuild ckt 2 | TX |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50540 | 51246 | Line New | 2028-12-01 | Sarepta | Mt Olive |  | 500 |  | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer | LA |  | 60 | M2 - Appendix A Approved | 470100000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50540 | 51247 | Transformer | 2028-12-01 | Mt Olive |  |  | 500 | 230 | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer | LA |  |  | M2 - Appendix A Approved | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50540 | 51248 | Transformer | 2028-12-01 | Sarepta |  |  | 500 | 345 | Entergy is proposing to construct • Sarepta 500 kV station including a Sarepta 500-345 kV Autotransformer • New ~60 mile Mt Olive to Sarepta 500 kV line. • Upgrade existing Mt Olive 500-230 kV Autotransformer | LA |  |  | M2 - Appendix A Approved | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50350 | 51249 | Line New | 2030-06-01 | Babel | Webre |  | 500 |  | Construct a new ~145-mile 500 kV line from Babel to Webre 500 kV line. | LA |  | 145 | M1 - Proposed | 1066000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50357 | 51250 | Line Upgrade | 2027-06-01 | Harelson | Jones Creek |  | 69 |  | Upgrade Harelson to Jone Creek 69 kV line | LA |  |  | M1 - Proposed | 14700000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50361 | 51251 | Misc. | 2026-06-01 | Willow Glen |  |  | 138 |  | Install a new battery bank at Willow Glen 138 kV station. The primary 1 relay needs to be on a separate DC panel than primary 2/backup relay. The breakers for the AT must have trip coil #1 and trip coil #2 fed from separate DC panels and the DC panels must be fed from separate battery sets. The DC panels cannot be wired in series or in parallel to one another. | LA |  |  | M1 - Proposed | 4000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50362 | 51252 | Misc. | 2028-06-01 | Richard |  |  | 500 | 138 | Relay upgrades for the 138 kV bus, 500 kV bus, including lines | LA |  |  | M1 - Proposed | 8700000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50363 | 51253 | Voltage Device | 2031-10-31 | Little Prairie |  |  | 230 |  | Install 223.90 MVAR reactive support (2-SVCs) at Little Prairie 230 kV station | LA |  |  | M1 - Proposed | 54300000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50364 | 51254 | Substation | 2030-06-01 | Waterford |  |  | 230 |  | Upgrade Waterford 230 kV jumper (~0.26 miles, located inside 230 kV station) to 1200 MVA min. | LA |  |  | M1 - Proposed | 310000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50360 | 51255 | Substation | 2029-06-01 | War Eagle |  |  | 138 |  | Construct a new War Eagle 138 kV substation approximately 0.3 miles north of the Oak Ridge 138 kV substation that cuts into the Oak Ridge – Metro 138 kV. | TX |  |  | M1 - Proposed | 110000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50360 | 51256 | Line New | 2029-06-01 | Porter | War Eagle |  | 138 |  | Construct a new 138 kV line from Porter to the new War Eagle substation. | TX |  | 8 | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50360 | 51257 | Line New | 2029-06-01 | Forest | War Eagle |  | 138 |  | Energize the abandoned 138 kV L-403 by terminating into the War Eagle and Forest 138 kV substations and rebuild. | TX |  | 2.5 | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50359 | 51258 | Substation | 2030-06-01 | Runny |  |  | 138 |  | Build a new 138 kV switching station between College Station and Grimes 138 kV substations called Runny. | TX |  |  | M1 - Proposed | 99400000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50359 | 51259 | Line New | 2030-06-01 | Bryan | Runny |  | 138 |  | Construct new Bryan to Runny 138 kV line | TX |  | 13 | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50586 | 51260 | Substation | 2026-12-31 | Multiple |  |  | 500 | 69 | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | TX |  |  | M1 - Proposed | 34400000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50353 | 51261 | Substation | 2026-12-31 | Multiple |  |  | 230 | 69 | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | LA |  |  | M1 - Proposed | 3200000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | LA | 50355 | 51262 | Substation | 2026-12-31 | Multiple |  |  | 500 | 69 | Address aging and failing equipment such as structures, breakers, relay panels, RTU's, arresters, circuit switchers, etc | LA |  |  | M1 - Proposed | 83300000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 50358 | 51263 | Substation | 2029-12-01 | Supont Beaumont |  |  | 69 | 69 | Upgrade a switch at Dupont Beaumont 69 kV station | TX |  |  | M1 - Proposed | 250000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | MN | 50587 | 51264 | Substation | 2026-09-15 | Darnen |  |  | 115 | 115 | Tap the Great River Energy (GRE) owned 'AG-MB' 115 kV line between Morris and Walden to serve a new distribution substation with an 'in-and-out' configuration. | MN |  |  | M1 - Proposed | 2362888 | GREAT RIVER ENERGY | Not Shared
A |  | West | IA | 50329 | 51265 | Line New | 2028-12-31 | Sub 91 | Quad Cities | 1 | 345 |  | Relocate the existing Sub 91-Quad Cities 345 kV line to a new line terminal at Sub 91 | IA |  |  | M1 - Proposed | 3000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50329 | 51266 | Line New | 2028-12-31 | Sub 91 | Sub 56 | 1 | 345 |  | Relocate the existing Sub 91-Sub 56 345 kV line to a new line terminal at Sub 91 | IA |  |  | M1 - Proposed | 3500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | WI | 50588 | 51267 | Line Upgrade | 2029-01-01 | Forest Junction | Branch River |  | 345 |  | Uprate W-15 Forest Junction – Branch River 345 kV line per ATC T-Line design standards to achieve minimum 1918 Amps (1146 MVA) normal and 2490 Amps (1488 MVA) emergency ratings for all seasons. | WI |  |  | M1 - Proposed | 7754000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | East | MI | 50212 | 51268 | Misc. | 2027-09-30 | Avery | Midtown |  | 120 |  | Install underground Fiber from Avery to Midtown station. | MI |  |  | M2 - Appendix A Approved | 1721000 | ITC | Not Shared
A | A | East | MI | 50212 | 51269 | Misc. | 2027-09-30 | Avery | Stonepool |  | 120 |  | Install underground Fiber from Avery to Stone Pool station. | MI |  |  | M2 - Appendix A Approved | 2108000 | ITC | Not Shared
A |  | East | MI | 50590 | 51273 | Substation | 2030-06-01 | Sunset |  |  | 120 |  | Upgrade "HI" switch at Sunset 120 kV station | MI |  |  | M1 - Proposed | 168000 | ITC | Not Shared
A |  | East | MI | 50591 | 51274 | Voltage Device | 2030-06-01 | Phoenix |  |  | 120 |  | Install a 50 MVAr capacitor at Phoenix 120 kV bus 103 and a synchronous breaker with associated disconnects. | MI |  |  | M1 - Proposed | 1500000 | ITC | Not Shared
A | A | South | AR | 50594 | 51278 | Line New | 2028-12-01 | Helena Harbor 230kV | Ritchie 230kV |  | 230 |  | A member cooperative's new 230kV Helena Harbor station will be served on a new, approximately 6-mile 230kV radial line off Entergy's Ritchie 230kV station. | AR |  | 6 | M2 - Appendix A Approved | 13200000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | A | South | AR | 50594 | 51279 | Substation | 2028-12-01 | Entergy's 230kV Ritchie |  |  | 230 |  | Entergy will add a new 230kV position to their existing 230kV Ritchie station to accommodate a new radial line. | AR |  |  | M2 - Appendix A Approved | 5000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A |  | East | MI | 50597 | 51283 | Substation | 2028-03-31 | New Hudson |  |  | 120 |  | Construct New Hudson as a new 4-breaker ring bus configuration, 120 kV station and allow enough space for future breaker and a half station configuration once DTE’s future positions are needed. All new 120 kV breakers should be standard 3000 A 40 kA breakers. We want to reserve 4 additional rows for future connections. | MI |  |  | M1 - Proposed | 10000000 | ITC | Not Shared
A |  | East | MI | 50597 | 51284 | Misc. | 2028-03-31 | Proud |  |  | 120 |  | Add CVT and modify relaying at position HB. | MI |  |  | M1 - Proposed | 103000 | ITC | Not Shared
A |  | East | MI | 50597 | 51285 | Misc. | 2028-03-31 | Cody |  |  | 120 |  | Add CVTs to HC and Bus 101 and modify relaying. | MI |  |  | M1 - Proposed | 267500 | ITC | Not Shared
A |  | East | MI | 50597 | 51286 | Line New | 2028-03-31 | Cody | Proud |  | 120 |  | Cut in Cody – Proud 120 kV line about 0.15 mile from Tamarack 120 kV Tap into New Hudson 120 kV station. | MI |  |  | M1 - Proposed | 1793000 | ITC | Not Shared
A |  | West | WI | 50598 | 51287 | Substation | 2027-06-30 | Progress |  |  | 138 |  | ATC will install a 138 kV loop through substation on the Aviation - Ellinwood 138 kV (X-50) line with line switches to support a distribution substation rebuild. | WI |  |  | M1 - Proposed | 2500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | IN | 50599 | 51288 | Line New | 2026-07-01 | Merom |  |  | 345 |  | Extend a new 345kV line from Merom Transmission Station, approximately 1-mile, to a new data center. | IN |  | 1 | M2 - Appendix A Approved | 7520000 | HOOSIER ENERGY | Not Shared
A | A | Central | IN | 50599 | 51289 | Substation | 2026-07-01 | Merom |  |  | 345 |  | Install 345 kV breaker and make station upgrades at Merom station to accommodate the new 345kV line. | IN |  |  | M2 - Appendix A Approved | 1626381 | HOOSIER ENERGY | Not Shared
A | A | Central | IN | 50599 | 51290 | Substation | 2026-07-01 | Merom |  |  | 345 |  | Construct new 345kV straight bus station for customer | IN |  |  | M2 - Appendix A Approved | 3644303 | HOOSIER ENERGY | Not Shared
A |  | South | MS | 50600 | 51291 | Substation | 2029-12-01 | Oak Bend |  |  | 230 |  | New Oak Bend 230 kV station fed from Baxter Wilson 230 kV substation | MS |  |  | M1 - Proposed | 150000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | MS | 50600 | 51292 | Transformer | 2029-12-01 | Baxter Wilson |  |  | 500 | 230 | 2x 500/230 autotransformers at Baxter Wilson 500/230 station | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | MS | 50600 | 51293 | Substation | 2029-12-01 | Baxter Wilson |  |  | 230 |  | new Baxter Wilson 230 kV station fed from existing Baxter Wilson 500 kV through 2-500/230 kV auto transformers. | MS |  |  | M1 - Proposed | 1 | ENTERGY MISSISSIPPI, LLC. | Not Shared
A |  | South | MS | 50601 | 51294 | Substation | 2028-04-01 | Andes |  |  | 230 |  | Expand existing 230 kV Andes Substation with three breaker bays with (3) 150 MVA 230/34.5 kV transformers. | MS |  |  | M1 - Proposed | 40000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | MS | 50602 | 51295 | Substation | 2028-12-01 | Green Acres |  |  | 500 | 230 | New Green Acres 500/230 kV station will cut in on Lakeover – Ray Braswell 500 kV and Lakeover - McAdams 500 kV lines. | MS |  |  | M1 - Proposed | 240000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | MS | 50602 | 51296 | Substation | 2029-12-01 | County Line | Green Acres |  | 230 |  | New 230 kV substation fed from 3-230 lines from the Green Acres 500/230 substation | MS |  |  | M1 - Proposed | 72000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | MS | 50602 | 51297 | Transformer | 2028-12-01 | Green Acres |  |  | 500 | 230 | 2-500/230 Autotransformers install at new Green Acres 500/230 station. | MS |  |  | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | MS | 50602 | 51298 | Line New | 2029-12-01 | Green Acres | County Line |  | 230 |  | 3-230 kV lines connecting Green Acres - County line | MS |  | 3 | M1 - Proposed | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | A | West | SD | 50603 | 51299 | Substation | 2025-09-19 | Big Stone South Crown Ridge Wind Load 230 kV |  |  | 230 | 35 | New 230/34.5 kV distribution substation connecting to the Big Stone South to Crowned Ridge 230 kV line right near the Big Stone South substation to serve new 155 MW load addition and move an existing load of about 10.5 MW to be served from. | SD |  |  | M2 - Appendix A Approved | 0 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50501 | 51311 | Substation | 2026-12-31 | Byron |  |  | 345 | 161 | Replacing outdated breakers and relays. | MN |  |  | M1 - Proposed | 2300000 | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
A | A | South | LA | 50608 | 51312 | Substation | 2026-12-30 | Alliance | Happy Jack |  | 115 |  | Entergy is proposing to construct a new 115 kV station named Riparian to serve a new customer cut into the existing Alliance to Happy Jack 115 kV line in Point Celeste, LA. | LA |  |  | M2 - Appendix A Approved | 38200000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | WI | 50612 | 51315 | Misc. | 2027-12-01 | Terrace Ave Riser |  |  | 69 |  | Modernize the technology for the HPFF (high-pressure fluid-filled) pressurizing system, install physical security, install expanded metal fence, and make modifications to existing building to address corrosion issues at Terrace Ave Riser SS. | WI |  |  | M1 - Proposed | 3200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50613 | 51316 | Substation | 2026-04-01 | Central |  |  | 69 |  | Construct a new substation with one new 69/12.47 kV, 3.75/5.25 MVA transformer with high-side switch. Install 3-way MOD with supervisory control near Y-71 structure 99. Route approx. 0.5 miles of new 69kV line to new SS location. | WI |  | 0.5 | M1 - Proposed | 3200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | IN | 50614 | 51317 | Substation | 2027-10-01 | Trimble County | Ghent |  | 345 |  | 345 kV Ring-Bus Station with 4 positions | IN |  |  | M2 - Appendix A Approved | 16000000 | HOOSIER ENERGY | Not Shared
A | A | Central | IN | 50614 | 51318 | Line New | 2027-10-01 | Marble Hill Station | Marble Hill Customer |  | 345 |  | Construct two 345kV lines (approximately 0.5 miles each) from Marble Hill 345kV Station to the new customer substation. | IN |  | 1 | M2 - Appendix A Approved | 4500000 | HOOSIER ENERGY | Not Shared
A | A | Central | MO | 50615 | 51319 | Substation | 2028-06-01 | Central |  |  | 138 |  | New 138 kV position at Central substation | MO |  |  | M2 - Appendix A Approved | 1000000 | AMEREN MISSOURI | Not Shared
A | A | Central | MO | 50617 | 51320 | Substation | 2027-12-01 | Lumberjack |  |  | 345 |  | New 345 kV Lumberjack substation | MO |  |  | M2 - Appendix A Approved | 20000000 | AMEREN MISSOURI | Not Shared
A | A | Central | MO | 50617 | 51321 | Substation | 2027-12-01 | Montgomery |  |  | 345 |  | Add 345 kV position for line to new Lumberjack substation | MO |  |  | M2 - Appendix A Approved | 4500000 | AMEREN MISSOURI | Not Shared
A | A | Central | MO | 50617 | 51322 | Line Upgrade | 2027-12-01 | Montgomery | Lumberjack |  | 345 |  | New 345 kV Line from Montgomery to Lumberjack substation. Double circuit with existing Montgomery-Labadie 345 kV | MO |  |  | M2 - Appendix A Approved | 14000000 | AMEREN MISSOURI | Not Shared
A |  | Central | IN | 50104 | 50154 | Substation | 2026-06-01 | St. John | Crete | 1 | 345 |  | Replace existing switch and associated cabling to 4000A. | IN |  |  | M1 - Proposed | 1150000 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50105 | 50155 | Substation | 2026-06-01 | Green Acres |  |  | 345 |  | At Green Acres, Upgrade the existing 34517 line drop to 4000A (2-1590 AL). Project will also reconfigure the existing St. John and Green Acres 345kV connections, creating a Green Acres to University Park 345kV line and St. Johns to Olive 345kV line. Project includes all associated protection and communication needed to create new tie lines. | IN |  |  | M1 - Proposed | 2150000 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | A | Central | IL | 22788 | 26898 | Line Upgrade | 2025-12-01 | Prest | Tibbs |  | 138 |  | Repair issues found during inspections | IL |  |  | M3 - Under Construction | 23000000 | AMEREN ILLINOIS | Not Shared
A |  | Central | MO | 22874 | 26907 | Substation | 2027-12-01 | Ashley |  |  | 138 |  | Install high side interrupting devices on XFMRs 1, 2, & 3 Install line breakers on Cahokia and Hall Street | MO |  |  | M1 - Proposed | 4100000 | AMEREN MISSOURI | Not Shared
A |  | Central | IL | 22907 | 26916 | Substation | 2026-12-01 | Tuscola West |  |  | 138 |  | Rebuild to ring bus | IL |  |  | M1 - Proposed | 5800000 | AMEREN ILLINOIS | Not Shared
A | B | Central | MO | 22881 | 26920 | Substation | 2026-12-01 | Belleau |  |  | 138 |  | Expand Belleau by adding 2 positions for O'Fallon so they don't tap the lines. (i.e. (2)new 138kV Line positions for 138kV Feeds to O'Fallon) | MO |  |  | M1 - Proposed | 3000000 | AMEREN MISSOURI | Not Shared
A |  | Central | IL | 22908 | 26922 | Line Upgrade | 2030-12-01 | Joppa | Marion South |  | 161 |  | Rebuild the Joppa-Marion South-1 161 kV line on direct-embed steel H-Frame structures with conductor capable of carry 2000 amps at Summer Emergency conditions. | IL |  |  | M1 - Proposed | 46500000 | AMEREN ILLINOIS | Not Shared
A |  | Central | MO | 23046 | 26948 | Substation | 2026-06-01 | Montgomery |  |  | 345 | 161 | Line Breaker at MTGY on WARR-MTGL-3 | MO |  |  | M1 - Proposed | 17000000 | AMEREN MISSOURI | Not Shared
A |  | South | TX | 25436 | 28683 | Voltage Device | 2027-06-01 | Dobbin |  |  | 138 | 138 | 25.1 MVAR Capacitor Bank | TX |  |  | M1 - Proposed | 9000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 25436 | 28684 | Misc. | 2026-09-30 | Grimes |  |  | 345 | 138 | Ensure Grimes 138 kV bus and 345/138 kV AT1 have redundant high-speed protection including redundant DC supply such that loss of any component of the auto protection scheme would not result in delayed fault clearing. | TX |  |  | M1 - Proposed | 3000000 | ENTERGY SERVICES, LLC. | Not Shared
A | B | Central | MO | 23530 | 27300 | Substation | 2024-05-03 | Spencer Creek |  |  | 345 |  | Expand 345 kV bus to allow J956 and J1026 connections | MO |  |  | M4 - Project in Service | 4600000 | AMEREN MISSOURI | Shared
A | A | West | WI | 50166 | 51417 | Transformer | 2025-12-01 | Mount Pleasant |  |  | 138 |  | Mount Pleasant +/- 350 Mvar STATCOM. WO 605957 | WI |  |  | M3 - Under Construction | 83000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | West | WI | 50166 | 51418 | Transformer | 2027-01-01 | Mount Pleasant |  |  | 345 | 138 | Mount Pleasant Expansion for Western Feed & 138 kV capacitor banks. WO 606270 | WI |  |  | M3 - Under Construction | 20000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 50149 | 50243 | Misc. | 2028-12-31 | Arrowhead 230kV |  |  | 230 |  | Add redundancy or monitoring to the single point of failures to mitigate P5 contingencies associated with the Arrowhead 230kV buses. | MN |  |  | M1 - Proposed | 100000 | MINNESOTA POWER INC. | Not Shared
A |  | Central | MO | 50154 | 50256 | Substation | 2027-12-01 | Overton |  |  | 345 |  | Overton 345kV switchyard will be converted to four (4) position ring bus and a second 345 / 161 kV transformer rated for 560 MVA will be installed. | MO |  |  | M1 - Proposed | 31000000 | AMEREN MISSOURI | Shared
A |  | Central | MO | 50154 | 50257 | Line Upgrade | 2027-12-01 | California | Overton |  | 161 |  | Rebuild ~0.04 miles of the California - Overton 161 kV transmission line to be rated for a minimum of 1600 Amps. This is the span of line from the California 161 kV Arbor to first structure (205) outside of the same substation. | MO |  |  | M1 - Proposed | 1000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50154 | 50258 | Line Upgrade | 2027-12-01 | Montgomery | Burns |  | 345 |  | Rebuild Montgomery-Burns-5481 345kV line to be 3000 Amps summer emergency rated. This is approximately 30 miles of line from the Montgomery 345 kV substation to the new Burns 345 kV substation | MO |  |  | M1 - Proposed | 31000000 | AMEREN MISSOURI | Shared
A |  | Central | MO | 50154 | 50259 | Substation | 2027-12-01 | Montgomery |  |  | 345 |  | To relieve base case and contingency overload on McCredie to Montgomery 345kV line Ameren will upgrade limiting bus conductor at Montgomery substation to 3000 Amps summer emergency rating. | MO |  |  | M1 - Proposed | 350000 | AMEREN MISSOURI | Shared
A |  | Central | MO | 50154 | 50260 | Substation | 2027-12-01 | Loy Martin |  |  | 161 |  | Bus conductor at Loy Martin 161 kV will be upgraded for 1600 Amps minimum. Upgrade Loy Martin H3 Line jumper conductor and H2 bus tie jumper conductor. | MO |  |  | M1 - Proposed | 110000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50154 | 50261 | Line Upgrade | 2027-12-01 | Loy Martin | Katy |  | 161 |  | Rebuild approximately 8.94 miles of the Loy Martin-Katy-7429 161 kV transmission line for 1600 Amps minimum. This is the length of line from the Loy Martin 161 kV substation to structure 676 outside of the newly constructed Katy 161 kV substation | MO |  |  | M1 - Proposed | 5500000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50154 | 50262 | Substation | 2027-12-01 | Cooper |  |  | 161 |  | The former Overton-Sedalia East-1 line will be relocated to the new Cooper 161 kV Substation. | MO |  |  | M1 - Proposed | 1500000 | AMEREN MISSOURI | Not Shared
A | A | West | IA | 50157 | 50269 | Substation | 2027-09-30 | Big Cedar | Big Cedar |  | 345 | 345 | Expand Big Cedar 345 kV Switching Station to accommodate two new 345 kV lines to serve a new customer owned substation and a new 2nd 345 kV line between Big Cedar and Morgan Valley. | IA |  |  | M2 - Appendix A Approved | 14615214 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50270 | Voltage Device | 2027-09-30 | Big Cedar | Big Cedar |  | 345 | 345 | Add reactive compensation at Big Cedar to support Phase 1 load addition | IA |  |  | M2 - Appendix A Approved | 11996367 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50271 | Line Upgrade | 2027-09-30 | Big Cedar | Morgan Valley |  | 345 | 345 | Add 2nd Big Cedar - Morgan Valley 345 kV line on existing structures | IA | 6 |  | M2 - Appendix A Approved | 6997500 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50272 | Substation | 2027-09-30 | Morgan Valley | Morgan Valley |  | 345 | 345 | Expand Morgan Valley to add new line terminal for new Big Cedar - Morgan Valley #2 345 kV line | IA | 6 |  | M2 - Appendix A Approved | 1847560 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50273 | Line Upgrade | 2027-09-30 | Beverly | Hills |  | 345 | 345 | Construct new Beverly - Hills 345 kV line to support Phase 1 load addition at Big Cedar, a portion of the line to be located on new ROW and a portion of the line to overbuild existing 161 kV line between Bertram - Rose Hollow - Johnson | IA | 35 | 5 | M2 - Appendix A Approved | 159575000 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50274 | Line Upgrade | 2027-09-30 | Bertram | Rose Hollow |  | 161 | 161 | Rebuild portion of Bertram - Rose Hollow 161 kV that is overbuilt by new Beverly - Johnson 345 kV line | IA | 16 |  | M2 - Appendix A Approved | 6017500 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50275 | Line Upgrade | 2027-09-30 | Johnson | Rose Hollow |  | 161 | 161 | Rebuild portion of Johnson - Rose Hollow 161 kV that is overbuilt by new Beverly - Johnson 345 kV line | IA | 12 |  | M2 - Appendix A Approved | 4427500 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50277 | Substation | 2027-09-30 | Beverly | Beverly |  | 345 | 345 | Expand Beverly substation to accommodate the new Beverly - Johnson 345 kV line terminal | IA |  |  | M2 - Appendix A Approved | 4342675 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50278 | Line New | 2027-09-30 | Big Cedar | Customer Owned Substation |  | 345 | 345 | Construct new 345 kV line from Big Cedar to customer owned substation | IA |  | 0.25 | M2 - Appendix A Approved | 1767500 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50279 | Line New | 2027-09-30 | Big Cedar | Customer Owned Substation |  | 345 | 345 | Construct new 345 kV line from Big Cedar to customer owned substation | IA |  | 0.25 | M2 - Appendix A Approved | 1767500 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50280 | Substation | 2028-09-30 | Big Cedar | Big Cedar |  | 345 | 345 | Expand Big Cedar 345 kV Switching Station to accommodate two new 345 kV lines to serve a new customer owned substation and a new terminal for phase 2 reactive compensation. | IA |  |  | M2 - Appendix A Approved | 7552222 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50281 | Voltage Device | 2028-09-30 | Big Cedar | Big Cedar |  | 345 | 345 | Install additional reactive compensation (a new +500 MVAR SCU is being initially proposed) to support the additional load at Big Cedar. | IA |  |  | M2 - Appendix A Approved | 150000000 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50282 | Line New | 2028-09-30 | Big Cedar | Customer Owned Substation |  | 345 | 345 | Construct new 345 kV line from Big Cedar to customer owned substation | IA |  | 0.5 | M2 - Appendix A Approved | 3433750 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50283 | Line New | 2028-09-30 | Big Cedar | Customer Owned Substation |  | 345 | 345 | Construct new 345 kV line from Big Cedar to customer owned substation | IA |  | 0.5 | M2 - Appendix A Approved | 3433750 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50284 | Substation | 2027-09-30 | Rose Hollow | Rose Hollow |  | 161 | 161 | Upgrade relays at Rose Hollow due to addition of Beverly - Johnson 345 kV line | IA |  |  | M2 - Appendix A Approved | 424412 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50285 | Line Upgrade | 2027-09-30 | Johnson | Hills |  | 345 | 345 | Relocate existing Hills - Johnson line to new 345 kV ring bus at Johnson | IA | 0.25 |  | M2 - Appendix A Approved | 2161250 | ITC MIDWEST | Not Shared
A | A | West | IA | 50157 | 50287 | Substation | 2027-09-30 | PCI | PCI |  | 161 | 161 | Upgrade relays at PCI due to addition of Beverly - Johnson 345 kV line | IA |  |  | M2 - Appendix A Approved | 189925 | ITC MIDWEST | Not Shared
A |  | West | MI | 50161 | 50289 | Misc. | 2027-12-31 | Empire Mine | Huron | X-119 | 138 |  | ~10.4 Miles of OPGW Installation - This project will align with the 446 T-Line Reinsulate Project between the National and Presque Isle substations as well as the ~7.5 Miles of OPGW Installation on X-118 (MTEP24) will provide an alternate fiber path establishing two diverse OPGW fiber routes providing high-speed fiber communications connecting into ATC larger OPGW Network Infrastructure. | MI |  |  | M1 - Proposed | 13000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50162 | 50290 | Misc. | 2026-12-31 | Various |  |  | 0 |  | High level scope is to install Wi-Fi AP’s & Rogue Detection at various substations and remove Inverter equipment at various substations to complete the Wireless connectivity and Cyber Security fortifications. | WI |  |  | M1 - Proposed | 11700000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | IN | 50163 | 50291 | Substation | 2028-05-31 | Luchtman Rd | Shoreline | 1 | 138 |  | A greenfield 138kV breaker and a half substation that will be cut into the Luchtman Road – Shoreline 138kV line | IN |  |  | M1 - Proposed | 19346657 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50163 | 50292 | Line New | 2028-05-31 | Luchtman Rd | Shoreline | 1 | 138 |  | Tap in / tap out facilities from Luchtman Road – Shoreline 138kV line to new greenfield 138kV station plus fiber runs from greenfield station to Luchtman Road station. | IN |  |  | M1 - Proposed | 2385428 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50163 | 50293 | Line New | 2028-05-31 | Luchtman Rd | Shoreline | 1 | 138 |  | 2 monopoles for lead line to Generating Facility plus metering infrastructure. | IN |  |  | M1 - Proposed | 1664900 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A | A | West | WI | 50165 | 50294 | Substation | 2026-07-31 | Stratus |  |  | 138 |  | A new 138/24.9 kV breaker-and-a-half substation named Stratus, 138 kV capacitor banks, and construct short transmission lines to cut into the Mount Pleasant-Nimbus 138 kV lines (X-171, X-172) and loop in and out of the Stratus Substation. | WI |  |  | M3 - Under Construction | 68500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | West | WI | 50166 | 50295 | Transformer | 2025-06-01 | Mount Pleasant |  |  | 345 | 138 | Mount Pleasant SS - Install a new 500 MVA, 345/138 kV transformer. WO 605767 | WI |  |  | M4 - Project in Service | 14000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | West | WI | 50167 | 50296 | Substation | 2027-01-01 | Jupiter |  |  | 345 | 138 | Install a new 345/138 kV breaker-and-a half substation with 4 –500 MVA 345/138 kV transformers, +/- 350 Mvar STATCOM, 138 kV capacitor banks, 4 – 345 kV line terminal. | WI |  |  | M3 - Under Construction | 295000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | West | WI | 50168 | 50297 | Line New | 2027-01-01 | Jupiter | Mount Pleasant |  | 345 | 138 | Construct two new 345 kV double circuit lines from the existing Arcadian – Pleasant Prairie (PLPL81)/Arcadian – Paris (W-30) 345 kV double circuit line to loop in and out of the Jupiter and Mount Pleasant. Construct a new Jupiter – Mount Pleasant 345 kV line. | WI |  |  | M2 - Appendix A Approved | 124000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | East | MI | 18192 | 25026 | Line Upgrade | 2028-03-15 | Hines | Levan | 1 | 120 |  | Rebuild the 954 ACSR sections (~0.5 mile) from structure #5680A to Levan and from structure #5686 to Hines with 1431 ACSR using 120kV, double-circuit construction. Install OPGW on the rebuilt sections. | MI | 0.5 |  | M1 - Proposed | 1645000 | ITC | Not Shared
A | B | East | MI | 18192 | 25028 | Line Upgrade | 2028-03-15 | Hines |  |  | 120 |  | Replace substation fiber runs and patch panels at Hines and install comm cabinet for patch panels at this station. | MI |  |  | M1 - Proposed | 141000 | ITC | Not Shared
A | B | East | MI | 18192 | 25029 | Line Upgrade | 2028-03-15 | Levan |  |  | 120 |  | Upgrade the 954 ACSR bus (line drop) at Levan 120kV position "HD" to at least 375 MVA for summer emergency rating. Replace substation fiber runs and patch panels at Levan and install comm cabinet for patch panels at this station. | MI |  |  | M1 - Proposed | 149000 | ITC | Not Shared
A |  | Central | IL | 25328 | 28483 | Line Upgrade | 2027-06-01 | Charleston NE |  |  | 138 |  | Add line breakers and address aging infrastructure | IL |  |  | M1 - Proposed | 4019794 | AMEREN ILLINOIS | Not Shared
A | B | West | MN | 25371 | 28520 | Misc. | 2025-12-01 | Lake Yankton |  |  | 115 |  | Retire Lake Yankton SVC. | MN |  |  | M1 - Proposed | 700000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | Central | IN | 50731 | 51506 | Line Upgrade | 2026-12-31 | Whitestown | J993 |  | 345 |  | Seasonal Rating Adoption | IN |  |  | M1 - Proposed | 0 |  | Not Shared
A |  | Central | IN | 50731 | 51507 | Line Upgrade | 2029-12-31 | Whitestown | Wolf Creek |  | 345 |  | Seasonal Rating Adoption | IN |  |  | M1 - Proposed | 0 |  | Not Shared
A | B | West | MN | 50149 | 51550 | Misc. | 2027-12-31 | Arrowhead 230 kV |  |  | 230 |  | A new EEE will be required to address the redundancy needed to mitigate single points of failure within the Projection System | MN |  |  | M1 - Proposed | 2900000 | MINNESOTA POWER INC. | Not Shared
A | B | West | WI | 25203 | 28255 | Line New | 2026-09-03 | Highland | Hill Valley |  | 138 |  | Create a new Highland - Hill Valley 138 kV line by: - Converting 6.25 miles of the existing Highland - Eden 69 kV line Y-207 to 138 kV. Along the 69 kV corridor, new easements will be required. - Construct 0.2 miles of new 138 kV into Highland SS. - Construct 1 mile of new 138 kV into Hill Valley SS. - Add one new ring bus position at Highland SS. - Add one new ring bus position at Hill Valley SS. - Retire and remove 0.2 miles of Y-207 into Eden SS and Highland SS. - Retire and remove two breakers, one at Eden SS and one at Highland SS. | WI | 6.4 | 1 | M1 - Proposed | 9500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25185 | 28264 | Substation | 2031-03-31 | Various Subs |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 45000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25186 | 28265 | Misc. | 2028-06-30 | Various Subs |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 2100000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25240 | 28266 | Line Upgrade | 2026-12-31 | Various Lines |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 9000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 25187 | 28267 | Substation | 2027-12-31 | Various Subs |  |  | 345 | 69 | See project description. | WI |  |  | M1 - Proposed | 19000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | MO | 50696 | 51440 | Line New | 2027-06-01 | Huster | McClay |  | 138 |  | Huster-McClay 138 kV line tap | MO |  |  | M2 - Appendix A Approved | 500000 | AMEREN MISSOURI | Not Shared
A | A | Central | IN | 50698 | 51443 | Substation | 2029-12-01 | 16PETE | 16W_BLOOMINGTON |  | 345 |  | 345/69kV Ring-Bus Station | IN |  |  | M2 - Appendix A Approved | 16000000 | HOOSIER ENERGY | Not Shared
A | A | Central | IN | 50698 | 51444 | Transformer | 2029-12-01 | Scotland 345kV |  |  | 345 |  | Two 345/69kV Transformers, 168 MVA each | IN |  |  | M2 - Appendix A Approved | 14000000 | HOOSIER ENERGY | Not Shared
A | A | Central | IN | 50698 | 51445 | Substation | 2029-12-01 | Scotland 69kV |  |  | 69 |  | 69kV Ring-Bus Station | IN |  |  | M2 - Appendix A Approved | 8000000 | HOOSIER ENERGY | Not Shared
A |  | West | WI | 50702 | 51449 | Substation | 2029-12-01 | Elm Road |  |  | 345 |  | Asset Renewal | WI |  |  | M1 - Proposed | 8400000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MN | 50711 | 51458 | Line Upgrade | 2030-09-30 | Lyon County | Brookings County | 1 | 345 |  | Condition replacement of cracked Davit Arms on Brookings County- Hawks Nest Lake - Lyon County and Brookings County - Steep Bank Lake - Lyon County and Hampton Helena 345kV line structures. | MN | 58 |  | M1 - Proposed | 18100000 | NORTHERN STATES POWER COMPANY | Shared
A |  | West | SD | 50489 | 51460 | Transformer | 2033-06-30 | Renner |  |  | 345 | 115 | Add (1) 345/115kV transformers at Renner | SD |  |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50711 | 51461 | Line Upgrade | 2030-09-30 | Lyon County | Helena | 1 | 345 |  | Age and Condition rebuild of davit arms for Lyon County to Helena (inclusive of line segments extending from Lyon County to MN Valley, and Cedar Mountain to Franklin). | MN | 177 |  | M1 - Proposed | 57100000 | NORTHERN STATES POWER COMPANY | Shared
A |  | West | MN | 50711 | 51462 | Line Upgrade | 2030-09-30 | Hampton | Helena | 1 | 345 |  | Like-for-like age and condition replacement of select davit arms on Hampton - Helena 345kV line | MN | 52 |  | M1 - Proposed | 16700000 | NORTHERN STATES POWER COMPANY | Shared
A | A | Central | IN | 50691 | 51437 | Voltage Device | 2029-06-29 | Edwards |  |  | 345 | 138 | Reactive and thermal project mitigations for LEAP Phase 2 (MTEP 50208) area large load. | IN |  |  | M2 - Appendix A Approved | 45000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IL | 50077 | 50117 | Substation | 2026-06-01 | Aster |  |  | 138 |  | The Great Plains Solar (J1777) Generating Facility will interconnect with the Transmission System via a 138 kV leadline running from the Interconnection Customer's collector substation to the Transmission Owner's Aster Substation in Perry County, IL. | IL |  |  | M1 - Proposed | 800000 | AMEREN ILLINOIS | Not Shared
A |  | Central | IL | 50084 | 50124 | Substation | 2026-12-01 | Ramsey East |  |  | 138 |  | Install a new 138 kV line position to serve as the Point of Interconnection for Saluki Solar, LLC within the Ramsey East Substation. | IL |  |  | M1 - Proposed | 800000 | AMEREN ILLINOIS | Not Shared
A |  | Central | MO | 50100 | 50149 | Substation | 2028-06-01 | Baumgartner |  |  | 138 |  | Baumgartner 138 Aging Infrastructure | MO |  |  | M1 - Proposed | 6300000 | AMEREN MISSOURI | Not Shared
A |  | Central | IL | 50185 | 50323 | Transformer | 2026-12-01 | Marion South |  |  | 161 |  | Replace XFMR 1 at Marion South with a new 161/138kV 300 MVA unit. | IL |  |  | M1 - Proposed | 3600000 | AMEREN ILLINOIS | Not Shared
A |  | Central | MO | 50186 | 50324 | Substation | 2030-12-01 | Montgomery |  |  | 345 | 161 | Montgomery 345kV Substation BAAH Leg | MO |  |  | M1 - Proposed | 3000000 | AMEREN MISSOURI | Shared
A |  | Central | MO | 50186 | 50325 | Line New | 2030-12-01 | Montgomery | Burns |  | 345 |  | New 345 kV line | MO |  |  | M1 - Proposed | 84000000 | AMEREN MISSOURI | Shared
A |  | Central | IL | 50189 | 50329 | Line Upgrade | 2027-12-01 | Latham | Docket |  | 138 |  | Rebuild 5 miles of the existing 138 kV Latham-Docket-1409 with OPGW and 1600 A conductor. | IL |  |  | M1 - Proposed | 4000000 | AMEREN ILLINOIS | Not Shared
A | A | Central | IL | 50190 | 50330 | Line New | 2029-06-01 | Princeton | Peru (Future) |  | 138 |  | Rebuild the existing Princeton substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. Construct a new 23-mile 138 kV Transmission line from Ameren's Princeton substation to the new substation near the City of Peru. | IL |  |  | M2 - Appendix A Approved | 74000000 | AMEREN ILLINOIS | Not Shared
A |  | West | IA | 50192 | 50331 | Substation | 2027-09-01 | J1529 Sub |  |  | 69 |  | Network Upgrades for J1529 Generator (69 kV Interconnection Sub) | IA |  |  | M1 - Proposed | 12800000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50192 | 50332 | Line New | 2027-09-01 | Carroll County | Auburn |  | 69 |  | Network Upgrades for J1529 Generator (69 kV line taps) | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50193 | 50333 | Substation | 2026-09-30 | J1530 Sub |  |  | 69 |  | Network Upgrades for J1530 Generator (69 kV Interconnection Sub) | IA |  |  | M1 - Proposed | 12800000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50193 | 50334 | Line New | 2026-09-30 | Hastings | Macedonia |  | 69 |  | Network Upgrades for J1530 Generator (69 kV line taps) | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50194 | 50335 | Substation | 2027-09-01 | J1532 Sub |  |  | 69 |  | Network Upgrades for J1532 Generator (69 kV Interconnection Sub) | IA |  |  | M1 - Proposed | 12900000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50194 | 50336 | Line New | 2027-09-01 | Clarinda | Coburg Tap |  | 69 |  | Network Upgrades for J1532 Generator (69 kV line taps) | IA |  |  | M1 - Proposed | 1000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50195 | 50337 | Line Upgrade | 2027-12-01 | Carroll County | Carroll South | 1 | 69 |  | Network Upgrades for J1529 Generator (69 kV line rebuild) | IA |  |  | M1 - Proposed | 7500000 | MIDAMERICAN ENERGY CO. | Shared
A |  | South | AR | 50191 | 50338 | Substation | 2028-09-01 | Beebe North SS |  |  | 115 |  | Switching Station that will tap EAI's Beebe to Garner line. | AR |  |  | M1 - Proposed | 7000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A |  | South | AR | 50191 | 50339 | Substation | 2028-09-01 | Sylvania 115kV Substation |  |  | 115 |  | Substation that will serve existing Member Coop load. This substation will tap a new 14-mile line from the new Beebe North SS to the new Nelson SS. | AR |  |  | M1 - Proposed | 8000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A |  | South | AR | 50191 | 50340 | Substation | 2028-09-01 | Nelson 115kV SS |  |  | 115 |  | Switching Station that will tie into Member Coop's existing 115kV system. | AR |  |  | M1 - Proposed | 7000000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A |  | South | AR | 50191 | 50341 | Line New | 2028-09-01 | Beebe North SS | Sylvania |  | 115 |  | New 115kV transmission line from the new Beebe North SS to the new Sylvania 115kV substation. | AR |  | 7 | M1 - Proposed | 7500000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A |  | South | AR | 50191 | 50342 | Line New | 2028-09-01 | Nelson 115kV SS | Sylvania |  | 115 |  | New 115kV transmission line from the new Nelson SS to the new Sylvania substation. | AR |  | 7 | M1 - Proposed | 7500000 | ARKANSAS ELECTRIC COOPERATIVE CORPORATION | Not Shared
A | A | South | LA | 50196 | 50343 | Substation | 2025-09-01 | Kirk | Moril |  | 138 |  | The Admiral 138 kV station will be designed as a 138kV six breaker ring bus. The substation will include six (6) breakers, one (1) Cap Bank, two (2) 67MVA power transformers, and two (2) main/feeder breakers. | LA |  |  | M4 - Project in Service | 54400000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50196 | 50344 | Line New | 2025-09-01 | Moril | Admiral | 1 | 138 |  | Construction and installation of a new line from Moril substation to Admiral will also be part of the permanent scope of work, along with the installation of a new 138kV breaker at Moril. | LA |  | 2.15 | M4 - Project in Service | 1 | ENTERGY SERVICES, LLC. | Not Shared
A | A | Central | IL | 50198 | 50346 | Substation | 2026-12-01 | Falls |  |  | 138 |  | Construct a new 138 kV substation, four position ultimate in a ring bus arrangement, 3000 Amps minimum continuous capability. The substation will be located approximately 1 mile east from the existing Wood River 138 kV substation. Split the existing Granite City 23rd Street-Wood River-1452 138 kV line and route into the new substation. Provide two positions at the new ring bus for the connection of Wieland Metals. | IL |  |  | M2 - Appendix A Approved | 10700000 | AMEREN ILLINOIS | Not Shared
A | A | South | TX | 50199 | 50347 | Substation | 2025-08-26 | Garden | Rhodair |  | 230 |  | Entergy is proposing to construct new 230 kV transmission lines sourced from the existing Garden 230 kV station to serve new load at the new Rhodair 230 kV station near Port Arthur, TX. | TX |  |  | M4 - Project in Service | 64400000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | TX | 50199 | 50348 | Substation | 2025-08-26 | Garden | Rhodair |  | 230 |  | Upgrades needed at Garden 230 kV station to accommodate the two new lines. | TX |  |  | M4 - Project in Service | 6300000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | TX | 50199 | 50349 | Line New | 2025-08-26 | Garden | Rhodair |  | 230 |  | The Garden to Rhodair 230 kV circuits 1 and 2 are a combined ~4.5 miles long | TX |  | 4.5 | M4 - Project in Service | 14300000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | WI | 50200 | 50350 | Line Upgrade | 2027-01-31 | Arcadian | Pleasant Prairie, Paris | PLPL81, W-30 | 345 |  | Uprate low rated segments of the Arcadian to Pleasant Prairie 345 kV line (PLPL81) and the Arcadian to Paris 345 kV line (W-30). | WI |  |  | M1 - Proposed | 9500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | IN | 50201 | 50354 | Line Upgrade | 2031-06-01 | Slugger | LGE Trimble Co Jct | 1 | 345 |  | 34530 Rebuild - Slugger to LGE Trimble to (2)954ACSS@200C (DEI-owned portion only) | IN | 19 |  | M1 - Proposed | 42964000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | East | MI | 50203 | 50355 | Substation | 2029-12-31 | New Station |  |  | 138 |  | Rebuild the 138 kV Alma station to three rows of breaker and a half station capable of three additional rows of BAH expansion. Install eight (8) 138 kV, 3000 A breakers with at least 40 kA interrupting capability. Install new control house and 25 MVAR capacitor. | MI |  |  | M1 - Proposed | 13350000 | METC | Not Shared
A |  | East | MI | 50203 | 50356 | Line New | 2029-12-31 | New Station | Regal |  | 138 |  | Redirect lines #1 and #2 from Regal into the new station utilizing 954 ACSR Conductor. | MI |  |  | M1 - Proposed | 975000 | METC | Not Shared
A |  | East | MI | 50203 | 50357 | Line New | 2029-12-31 | New Station | Vestaburg |  | 138 |  | Redirect line from Vestaburg into the new station utilizing 954 ACSS Conductor. | MI |  |  | M1 - Proposed | 325000 | METC | Not Shared
A |  | East | MI | 50203 | 50358 | Substation | 2029-12-31 | Alma |  |  | 138 |  | Remove transmission equipment at Alma. | MI |  |  | M1 - Proposed | 540000 | METC | Not Shared
A |  | Central | MO | 50186 | 50361 | Line Upgrade | 2030-12-01 | Big Creek | Warrenton |  | 161 |  | Big Creek-Warrenton 161 kV reconductor | MO |  |  | M1 - Proposed | 4000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50186 | 50362 | Line Upgrade | 2030-12-01 | Miller | Meta |  | 138 |  | Rebuild 11 miles of the Bland-Miller 138 kV transmission line between Miller and Meta. | MO |  |  | M1 - Proposed | 28200000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50186 | 50363 | Line Upgrade | 2030-12-01 | Belle | Meta |  | 138 |  | Rebuild 20.7 miles of the Bland-Miller 138 kV transmission line between Belle and Meta | MO |  |  | M1 - Proposed | 39700000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50186 | 50364 | Line Upgrade | 2030-12-01 | Warrenton | Montgomery |  | 161 |  | Reconductor 17.6 miles of the existing 161 kV Warrenton-Montgomery-3 transmission line | MO |  |  | M1 - Proposed | 4000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50186 | 50365 | Line Upgrade | 2030-12-01 | Bland | Gasco |  | 138 |  | Rebuild 8.3 miles of the Bland-Miller 138 kV transmission line between Bland and Gasco. | MO |  |  | M1 - Proposed | 8100000 | AMEREN MISSOURI | Not Shared
A |  | West | IA | 50204 | 50366 | Substation | 2026-06-01 | Clinton Rail Air Park Substation |  |  | 161 |  | ITCM will build the 161 kV 2 row 4 position breaker and a half substation with 2 line positions and 2 transformer positions. | IA |  |  | M1 - Proposed | 6659139 | ITC MIDWEST | Not Shared
A |  | West | IA | 50204 | 50367 | Line New | 2026-06-01 | Clinton Rail Air Park Substation |  |  | 161 |  | ITCMW will install the line taps to the new 161 kV Clinton Rail and Air Park substation | IA |  |  | M1 - Proposed | 2101250 | ITC MIDWEST | Not Shared
A |  | West | IA | 50205 | 50368 | Misc. | 2028-12-31 | Belmond Diesel | Hancock |  | 69 |  | ITCMW will re-route the Belmond Diesel to Hancock line to a different river crossing | IA |  |  | M1 - Proposed | 4097500 | ITC MIDWEST | Not Shared
A |  | West | IA | 50206 | 50369 | Transformer | 2027-12-31 | Rock Creek |  |  | 69 |  | T2 will be replaced with a new 150 MVA 161/69 kV transformer with LTC and the current motor operated switch will be removed and replaced with a new high side breaker and disconnect. | IA |  |  | M1 - Proposed | 4044728 | ITC MIDWEST | Not Shared
A |  | West | IA | 50207 | 50370 | Substation | 2028-12-31 | Spirit Lake Anchor |  |  | 69 |  | ITCMW will build the 69 kV portion of the Spirit Lake Anchor substation | IA |  |  | M1 - Proposed | 4451411 | ITC MIDWEST | Not Shared
A |  | West | IA | 50207 | 50371 | Line New | 2028-12-31 | Spirit Lake Anchor |  |  | 69 |  | ITCMW will build the tap to connect the Spirit Lake Anchor substation to its 69 kV transmission system. | IA |  |  | M1 - Proposed | 947500 | ITC MIDWEST | Not Shared
A | A | Central | IN | 50208 | 50372 | Line New | 2026-12-31 | Whitestown/Hortonville |  |  | 345 |  | 345kV double circuit to new substation | IN |  | 10 | M2 - Appendix A Approved | 99000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A | A | Central | IN | 50208 | 50373 | Transformer | 2026-12-31 | WItt |  |  | 345 | 138 | New 345/138kV substation with breaker and half at both voltage levels | IN |  |  | M2 - Appendix A Approved | 49500000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A | A | Central | IN | 50208 | 50374 | Substation | 2026-12-31 | LEAP North |  |  | 138 |  | New 138kV switching station, breaker and a half | IN |  |  | M2 - Appendix A Approved | 27500000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A | A | Central | IN | 50208 | 50375 | Line New | 2026-12-31 | LEAP North |  |  | 138 |  | 138kV transmission network to serve customer sites | IN |  |  | M2 - Appendix A Approved | 46200000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A | A | South | TX | 50209 | 50376 | Substation | 2025-05-12 | Cheek | Petry Woods |  | 138 |  | Cut new station into the Cheek to Petry Woods 138 kV line. | TX |  |  | M4 - Project in Service | 5800000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | IA | 50210 | 50377 | Misc. | 2027-12-31 | Keokuk West |  |  | 69 |  | ITC will build a new, separate control enclosure and replace all of its existing relays, and install a new bus tie breaker at the Keokuk West substation. | IA |  |  | M1 - Proposed | 2958416 | ITC MIDWEST | Not Shared
A |  | West | IA | 50211 | 50378 | Line Upgrade | 2028-12-30 | Hayward | County Line |  | 69 |  | Rebuild 13.34 miles of 69kV line to T2-477 ACSR with 69 kV standard between Hayward and County Line | IA | 13.34 |  | M1 - Proposed | 10671250 | ITC MIDWEST | Not Shared
A |  | West | IA | 50211 | 50379 | Line Upgrade | 2028-12-30 | County Line | Ellendale |  | 69 |  | Rebuild 5.71 miles of 69kV line to T2-477 ACSR with 69kV standards | IA | 5.71 |  | M1 - Proposed | 5232500 | ITC MIDWEST | Not Shared
A |  | West | IA | 50211 | 50380 | Line Upgrade | 2028-12-30 | Hayward |  |  | 69 |  | ITC will replace the jumpers on breaker terminal 617 with a conductor that is capable of 1200 Amps or greater. | IA |  |  | M1 - Proposed | 112005 | ITC MIDWEST | Not Shared
A | A | East | MI | 50212 | 50381 | Substation | 2027-09-30 | Avery |  |  | 120 |  | Construct a new 120 kV station as 5-breaker ring bus configuration. All new 120 kV breakers should be 3000 A 50 kA breakers. | MI |  |  | M2 - Appendix A Approved | 6700000 | ITC | Not Shared
A | A | East | MI | 50212 | 50382 | Line New | 2027-09-30 | Avery |  |  | 120 |  | Cut the Frisbie – Waterman 120 kV line at approximately 2 miles to Frisbie to provide transmission service to the new Avery 120 kV station. | MI |  |  | M2 - Appendix A Approved | 6184000 | ITC | Not Shared
A |  | West | IA | 50213 | 50383 | Substation | 2028-12-31 | Rock Creek |  |  | 345 |  | ITC will be expanding the Rock Creek 345 kV substation to accommodate two additional 345 kV lines. The substation will be expanded to a Breaker and a Half configuration. All new substation equipment will be capable of 3000 Amps or greater. | IA |  |  | M1 - Proposed | 23740163 | ITC MIDWEST | Not Shared
A |  | West | IA | 50213 | 50384 | Misc. | 2028-12-31 | Rock Creek |  |  | 345 |  | Move Rock Creek - Bryant 345kV line to terminate from rebuilt Rock Creek | IA |  |  | M1 - Proposed | 5138750 | ITC MIDWEST | Not Shared
A |  | West | IA | 50213 | 50385 | Substation | 2028-12-31 | Rock Creek |  |  | 345 |  | Relocate Rock Creek transformer terminal upon rebuild of the substation | IA |  |  | M1 - Proposed | 1571250 | ITC MIDWEST | Not Shared
A |  | West | MN | 50218 | 50393 | Voltage Device | 2028-03-31 | Riverton 230 kV |  |  | 230 |  | Installing a +/- 300 MVAR STATCOM at the Riverton 230 kV Substation | MN |  |  | M1 - Proposed | 70000000 | MINNESOTA POWER INC. | Not Shared
A |  | Central | MO | 50220 | 50396 | Line Upgrade | 2031-06-01 | McCredie | Overton |  | 345 |  | Rebuild 35.5 miles of the 345 kV McCredie-Overton | MO |  |  | M1 - Proposed | 63115000 | AMEREN MISSOURI | Shared
A |  | Central | MO | 50221 | 50397 | Line Upgrade | 2030-12-01 | McBaine | Overton |  | 161 |  | McBaine Tap -Overton 161 kV Line Upgrade | MO |  |  | M1 - Proposed | 9552000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50222 | 50398 | Line Upgrade | 2030-12-01 | Overton | Sedalia East |  | 161 |  | Rebuild 10 miles of existing Overton – Sedalia East 161 kV | MO |  |  | M1 - Proposed | 9710000 | AMEREN MISSOURI | Not Shared
A | A | West | WI | 50223 | 50399 | Voltage Device | 2027-01-01 | Whitewaterq | Sugar Creek |  | 138 |  | The Whitewater – Sugar Creek (WHIG53) 138 kV, flow control device is needed to control power flow on WHIG52 and 6541 supporting load additions in south-east Wisconsin. The project will install three single-phase 20-ohm series reactors at the Sugar Creek terminal of WHIG53. | WI |  |  | M2 - Appendix A Approved | 3358000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | West | WI | 50225 | 50401 | Line Upgrade | 2026-08-15 | North Lake Geneva | Elkhorn | X-55 | 138 |  | Rebuild X-55 North Lake Geneva - Elkhorn 138 kV line per ATC T-Line design standards to achieve minimum 1342 Amps (321 MVA) normal and 1822 Amps (436 MVA) emergency ratings for all seasons. Missing easements will be acquired. Safety and maintenance improvement expected with distribution removal from double-circuit area. | WI |  |  | M2 - Appendix A Approved | 23900000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | MO | 50226 | 50402 | Substation | 2030-12-01 | Vulcan |  |  | 138 |  | Build a new 138-34.5 kV bulk substation on property adjacent to the MSD Lemay Pump | MO |  |  | M1 - Proposed | 12000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50227 | 50403 | Substation | 2028-06-01 | California |  |  | 161 |  | California 161 kV Terminal Upgrades | MO |  |  | M1 - Proposed | 17800000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50227 | 50404 | Line Upgrade | 2028-06-01 | California | Apache Flat Tap |  | 161 |  | Double Circuit Rebuild California to Apache Flat Tap 161kV | MO |  |  | M1 - Proposed | 4800000 | AMEREN MISSOURI | Not Shared
A |  | East | MI | 50229 | 50405 | Substation | 2029-12-31 | Oneida |  |  | 138 |  | Install new 138 kV breaker capable of 40 kA interrupting and complete an existing row at Oneida 138 kV station. | MI |  |  | M1 - Proposed | 1080000 | METC | Not Shared
A |  | East | MI | 50229 | 50406 | Line New | 2029-12-31 | Oneida | Tallman |  | 138 |  | Build new Oneida – Tallman 138 kV circuit utilizing 1431 ACSR and double circuit structures capable of OPGW. Use 9.5 miles METC existing easement and obtaining new 0.5 miles ROW to connect this corridor to CE's Tallman. | MI |  | 10 | M1 - Proposed | 20890000 | METC | Not Shared
A |  | East | MI | 50229 | 50407 | Substation | 2029-12-31 | Looking Glass |  |  | 138 |  | Install new 138 kV three breaker ring bus station at Looking Glass. Install three 138 kV breakers capable of 40 kA interrupting. | MI |  |  | M1 - Proposed | 5920000 | METC | Not Shared
A |  | East | MI | 50229 | 50408 | Line Upgrade | 2029-12-31 | Looking Glass | Bingham |  | 138 |  | METC to reterminate Looking Glass - Bingham and perform any other line work needed due to Looking Glass station rebuild. | MI |  |  | M1 - Proposed | 1470000 | METC | Not Shared
A |  | East | MI | 50229 | 50409 | Substation | 2029-12-31 | Bingham |  |  | 138 |  | Work for fiber jumpers to establish network communications between Bingham and Looking Glass. | MI |  |  | M1 - Proposed | 70000 | METC | Not Shared
A |  | East | MI | 50229 | 50410 | Substation | 2029-12-31 | Oneida |  |  | 138 |  | Work to reterminate LBWL line at Oneida to accommodate new line entrance. | MI |  |  | M1 - Proposed | 200000 | METC | Not Shared
A |  | Central | IL | 50230 | 50411 | Line New | 2029-12-31 | Harco South | Carrier Mills |  | 161 |  | Harco South-Carrier Mills 161 kV line | IL |  |  | M1 - Proposed | 15000000 | AMEREN ILLINOIS | Not Shared
A |  | Central | IL | 50230 | 50412 | Substation | 2029-12-31 | Harco South |  |  | 161 | 138 | Harco South 138 kV Ring Bus and 138/161 kV Transformer | IL |  |  | M1 - Proposed | 15000000 | AMEREN ILLINOIS | Not Shared
A |  | Central | MO | 50140 | 50222 | Substation | 2029-12-01 | Fargo |  |  | 345 |  | New 138kV breaker required on Fargo 138kV Bus breaker and a half scheme, and new circuit switcher on the high side of the substation. AIC to construct a new 138kV/13.2kV distribution substation near the Fargo bulk supply substation | MO |  |  | M1 - Proposed | 2000000 | AMEREN ILLINOIS | Not Shared
A |  | West | WI | 50145 | 50236 | Substation | 2027-06-30 | TBD |  |  | 138 | 12 | - WPL will construct a new substation with two new 138/12.47 kV, 20/33 MVA transformers. - WPL will install a high side circuit breaker for transformer protection and low side bus. - ATC will install two 138kV feeds from the line section between BOC Gas Tap and Tripp Road (X-111) to the new Beloit LNG substation to support the new loop through configuration. - ATC will remove a section of the conductor from X-111. - ATC will install a new loop through configuration at the New Beloit LNG substation with space provision for a future bus tie breaker. - ATC will construct a 138 kV loop through bus at the new Beloit LNG substation and install two 138 kV line circuit breakers with associated line and bus side disconnect switches. - ATC will install two bus-tie disconnect switches and allow space provision for a future bus-tie breaker. | WI |  |  | M1 - Proposed | 9000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50146 | 50237 | Line Upgrade | 2027-01-01 | BOC Gasses Tap | Town Line Road | X-111 | 138 |  | Rebuild BOC Gasses Tap – Town Line Rd (X-111) 138-kV line to achieve target rating. | WI |  |  | M1 - Proposed | 2427000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | IN | 50170 | 50299 | Substation | 2028-06-01 | Stillwell |  |  | 138 |  | Expand existing 138kV bus at Transmission Owner’s Stillwell substation by adding two breakers to accommodate Generating Facility lead line. | IN |  |  | M2 - Appendix A Approved | 2330778 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50170 | 50300 | Substation | 2028-06-01 | Stillwell |  |  | 138 |  | Construct Transmission Owner’s Interconnection Facilities at Transmission Owner’s Stillwell Substation consisting of two monopoles, H frame pull off structure, metering equipment, conductor, shield wire, and fiber optics. | IN |  |  | M1 - Proposed | 1904848 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50171 | 50301 | Misc. | 2026-07-30 | Schahfer |  |  | 345 |  | RM Schahfer station’s relay protection requires full redundancy. Both the northwest and northeast 345kV buses at RM Schahfer currently have only one system of protection. To meet the requirements triggered by this interconnection, both buses will require additional bus protection relays. The protection and control schemes require new relaying that will include two bus differential relay panels and the addition of battery monitoring. Major Items  Two (2) bus differential relay panels  Battery monitoring system | IN |  |  | M1 - Proposed | 512947 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Shared
A |  | West | WI | 50172 | 50302 | Transformer | 2028-12-01 | Arpin |  |  | 345 |  | Arpin SS T21 Power Transformer Asset Renewal | WI |  |  | M1 - Proposed | 9800000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50173 | 50303 | Transformer | 2028-12-01 | Ellinwood |  |  | 138 | 69 | Ellinwood SS T1 Power Transformer Asset Renewal | WI |  |  | M1 - Proposed | 9900000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | IL | 50175 | 50305 | Substation | 2026-12-01 | Taylorville South |  |  | 138 |  | This project will reconfigure Taylorville South 138 kV substation in a 4 position ring bus configuration. Replace circuit breakers 1511, 1512 and 1514. Replace associated switches 1511B, 1511L, 1512B, 1512L, 1514B, and 1514L. Install one new 138 kV circuit breaker and two associated breaker disconnect switches. Remove shield wire over substation and install lightning masts and finials. | IL |  |  | M1 - Proposed | 5200000 | AMEREN ILLINOIS | Not Shared
A | A | South | LA | 50176 | 50306 | Line New | 2026-01-01 | Audubon | Customer Sub |  | 230 |  | There will be two ~2.8 mile new 230 kV lines from Audubon to the customer station. | LA |  | 5.6 | M2 - Appendix A Approved | 5700000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50176 | 50307 | Line Upgrade | 2026-01-01 | Willow Glen | Point Pleaasant |  | 230 |  | Upgrade Willow Glen to Point Pleasant 230 kV line | LA |  |  | M2 - Appendix A Approved | 100000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50176 | 50308 | Line Upgrade | 2026-01-01 | Willow Glen | Wise |  | 230 |  | Willow Glen to Wise 230 kV upgrade | LA |  |  | M2 - Appendix A Approved | 100000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | IA | 50231 | 50413 | Substation | 2026-02-27 | Prairie Creek Industrial |  |  | 69 |  | Equipment dedicated to connecting the J1359 generating facility to a new 69 kV breaker position in the PCI substation. TOIF cost to include the new breaker, switches, relay panel and any new associated equipment. | IA |  |  | M1 - Proposed | 790014 | ITC MIDWEST | Not Shared
A |  | West | IA | 50231 | 50414 | Line New | 2026-02-27 | Prairie Creek Industrial |  |  | 69 |  | A new approximately 0.75 mile 69 kV line from the PCI substation to the J1359 generating facility will need to be constructed. | IA |  | 0.75 | M1 - Proposed | 1055000 | ITC MIDWEST | Not Shared
A |  | West | WI | 50233 | 50415 | Substation | 2028-12-31 | Whitcomb | Deer Trail | Y-86 | 69 |  | Build a greenfield 69 kV switching station near the location of the Birnamwood tap. The station will be a 6-position straight bus with three breakered line terminals, one for the line segment to Deer Trail, one for the segment to Whitcomb, and one for the radial line to Birnamwood. One position for an 8 MVAR cap bank, provisions for a bus tie breaker and two future positions. | WI |  |  | M1 - Proposed | 17500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | IA | 50232 | 50416 | Substation | 2026-03-01 | Prairie Creek Industrial |  |  | 69 |  | The PCI 69 kV bus will be extended to accommodate an additional position for the J1359 TOIF line terminal. | IA |  |  | M1 - Proposed | 401708 | ITC MIDWEST | Not Shared
A |  | West | MN | 50234 | 50417 | Substation | 2027-02-15 | MN River |  |  | 115 |  | Penn. Breaker Installation | MN |  |  | M1 - Proposed | 625800 | MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
A |  | West | IA | 50235 | 50418 | Substation | 2025-09-01 | DAEC |  |  | 345 |  | Equipment dedicated to the J1444 generating facility. TOIF cost to include: dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. | IA |  |  | M1 - Proposed | 760648 | ITC MIDWEST | Not Shared
A |  | West | IA | 50236 | 50419 | Substation | 2025-09-01 | DAEC |  |  | 345 |  | the addition of 3 breaker positions, switches and associated equipment to upgrade to a breaker and half configuration. | IA |  |  | M1 - Proposed | 3777724 | ITC MIDWEST | Shared
A |  | West | MN | 50237 | 50420 | Line Upgrade | 2029-12-21 | Butternut | Butternut Tap | 1 | 69 | 69 | Rebuild BE-BUT line. SS145 to the Butternut Substation. Line length is approx. 4.5 miles | MN | 4.5 |  | M1 - Proposed | 4947000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50238 | 50421 | Substation | 2027-10-31 | Huntley |  |  | 345 |  | TOIF to include dead-end, PTs, relay panel for gen-tie line, line disconnect switch and other facilities at the switching station dedicated to the gen-tie line at the Huntley substation. | MN |  |  | M1 - Proposed | 1083794 | ITC MIDWEST | Not Shared
A |  | West | MN | 50239 | 50422 | Substation | 2027-10-31 | Huntley |  |  | 345 |  | Completing the 2nd row of 345kV breakers by adding two 345kV breakers and adding two 345kV breakers of a 3rd row, and other facilities required to convert the Huntley 345kV ring-bus to breaker and 1/2 station with approx. 3,000A capacity. 90% FSA, 10% Attachment GG. | MN |  |  | M1 - Proposed | 5489562 | ITC MIDWEST | Shared
A |  | Central | IN | 50241 | 50423 | Transformer | 2027-12-31 | Boonville |  |  | 69 |  | Replace transformer #1 with new 20MVA. | IN |  |  | M1 - Proposed | 2360000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | West | MN | 50242 | 50424 | Line Upgrade | 2030-02-28 | New Sweden | New Sweden Tap | 1 | 69 | 69 | Rebuild BE-NST line from SS2831 to New Sweden Substation. Line length is approx. 7.4 miles. | MN | 7.4 |  | M1 - Proposed | 6996498 | GREAT RIVER ENERGY | Not Shared
A |  | West | IA | 50240 | 50425 | Substation | 2027-10-31 | Bluebill |  |  | 345 |  | Equipment dedicated to the J1520 generating facility. TOIF cost to include: dead end, line disconnect switch, arresters, PT’s, relay panel, and other associated equipment. | IA |  |  | M1 - Proposed | 1101322 | ITC MIDWEST | Not Shared
A |  | Central | IN | 50245 | 50426 | Substation | 2027-12-31 | Culley 138kV |  |  | 138 |  | Replace existing line, breaker, and bus relaying panels. Replace existing CCVT junction boxes with new stainless-steel boxes. | IN |  |  | M1 - Proposed | 1600000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | West | IA | 50244 | 50427 | Substation | 2027-10-31 | Bluebill |  |  | 345 |  | Add 3rd row and one line position at Bluebill | IA |  |  | M1 - Proposed | 4048730 | ITC MIDWEST | Shared
A |  | Central | IN | 50247 | 50428 | Transformer | 2027-12-31 | Elliott |  |  | 138 |  | Replace existing ‘Transformer #1’ & ‘Transformer #2’ with new 100MVA transformers. Add new transformer protective relaying. Replace existing 138kV circuit breakers ‘1000’ & ‘3000’ and 69kV circuit breakers ‘100’, ‘200’, ‘300’ & ‘600’. Replace breaker foundations, breaker/line switches, and protective relaying. Replace two (2) existing 69kV capacitor banks. | IN |  |  | M1 - Proposed | 15700000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | Central | IN | 50248 | 50429 | Substation | 2027-12-31 | Newburgh |  |  | 69 |  | Remove existing 69kV high-side fuses and associated switch ‘199’ and replace with new 69kV circuit switcher. Install an auto-sectionalizing and RTU panels. Replace existing 7200V voltage regulators. | IN |  |  | M1 - Proposed | 1550000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | Central | IN | 50249 | 50430 | Transformer | 2027-12-31 | Dubois |  |  | 138 |  | Replace existing 100MVA, 138/69kV ‘Transformer #1’. Replace existing 69kV breakers ‘100’, ‘200’, ‘300’, ‘400’ and ‘500’. Replace existing 138kV and 69kV CCVTs. Install new transformer, 138kV and 69kV breaker and line relaying panels. | IN |  |  | M1 - Proposed | 7870000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | East | MI | 50251 | 50433 | Line Upgrade | 2029-12-31 | Batavia | Byers | 1 | 138 |  | Rebuild sections of the Batavia – Dorrance #1 & #2 circuits between Structure 124D100 to Batavia (~4.1mi) with 954 ACSR conductor and OPGW.. | MI | 4.1 |  | M1 - Proposed | 10305000 | METC | Not Shared
A |  | East | MI | 50251 | 50434 | Substation | 2029-12-31 | Batavia |  |  | 138 |  | Terminate OPGW in Batavia substation | MI |  |  | M1 - Proposed | 125000 | METC | Not Shared
A |  | East | MI | 50251 | 50436 | Substation | 2029-12-31 | Dorrance |  |  | 138 |  | Install fiber jumpers for Batavia. | MI |  |  | M1 - Proposed | 125000 | METC | Not Shared
A |  | South | TX | 25436 | 50438 | Voltage Device | 2029-06-01 | Dobbin |  |  | 138 | 138 | 25.1 MVAR Capacitor Bank | TX |  |  | M1 - Proposed | 10000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 25436 | 50439 | Line Upgrade | 2031-06-01 | Fish Creek | Deer Lake | 1 | 138 | 138 | Rebuild Fish Creek - Deer Lake 138 kV line | TX | 4.83 |  | M1 - Proposed | 17000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 25436 | 50440 | Line Upgrade | 2031-06-01 | Dobbin | Tubular | 1 | 138 | 138 | Rebuild Dobbin - Tubular 138 kV line | TX | 18.6 |  | M1 - Proposed | 65000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 25436 | 50441 | Line Upgrade | 2034-06-01 | Deer Lake | Spring Branch | 1 | 138 | 138 | Rebuild Deer Lake - Spring Branch 138 kV line | TX | 4.76 |  | M1 - Proposed | 17000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | South | TX | 25436 | 50442 | Line Upgrade | 2034-12-31 | Dobbin | Spring Branch | 1 | 138 | 138 | Rebuild Dobbin - Spring Branch 138 kV line | TX | 5.2 |  | M1 - Proposed | 17000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | East | MI | 50253 | 50444 | Substation | 2027-12-01 | Oliver |  |  | 120 |  | Construct Oliver 120kV station as a straight bus station with two new 40kA line breakers and allow enough space for future expansion. DTE to install reverse power relay at Oliver. | MI |  |  | M1 - Proposed | 3740000 | ITC | Not Shared
A |  | East | MI | 50253 | 50445 | Line New | 2027-12-01 | Bad Axe | Wyatt | 1 | 120 |  | Remove the Cosmo tap from the Bad Axe – Wyatt #1 120kV line near structure 6267A and bring the Cosmo Tap into a terminate position HN at Bad Axe 120kV through new construction of 0.5 mile using 954 ACSR. Loop in the Bad Axe – Wyatt 1 120kV line near Structures #52027 to provide transmission service to Oliver 120kV. Also Remove 2001 and 2065 PT switches at CosmoTP. | MI |  |  | M1 - Proposed | 685000 | ITC | Not Shared
A |  | East | MI | 50253 | 50446 | Misc. | 2027-12-01 | Bad Axe | Oliver | 1 | 120 |  | Install OPGW from Bad Axe – Oliver for relay communication. | MI |  |  | M1 - Proposed | 167500 | ITC | Not Shared
A |  | East | MI | 50253 | 50447 | Substation | 2027-12-01 | Bad Axe | Oliver | 1 | 120 |  | Install a 120kV, 3000 A, 40kA breaker at position HN. Terminate the Bad Axe – Oliver 120kV line at position HN. | MI |  |  | M1 - Proposed | 1013000 | ITC | Not Shared
A |  | West | IA | 50254 | 50448 | Substation | 2027-09-15 | Remsen Township |  |  | 345 |  | Network Upgrades for J1590 Plymouth Wind Energy | IA |  |  | M1 - Proposed | 4000000 | MIDAMERICAN ENERGY CO. | Shared
A |  | West | WI | 50255 | 50449 | Misc. | 2026-12-31 | Huiskamp | Ruskin | 6937 | 69 |  | Install ~1.75 miles of ATC standard (DNO-10455) 48 strand OPGW fiber optic cable from structure #232 on T-Line (6937) into the Ruskin substation to complete the connection from Huiskamp. | WI |  |  | M1 - Proposed | 4000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | MO | 50256 | 50450 | Substation | 2029-12-01 | Tibbe |  |  | 138 |  | Tibbe 138-34.5 kV Substation | MO |  |  | M1 - Proposed | 11000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50256 | 50451 | Line Upgrade | 2029-12-01 | Gray Summit | Tibbe |  | 138 |  | Gray Summit-Tibbe 138 kV line | MO |  |  | M1 - Proposed | 11000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 50256 | 50452 | Line New | 2029-12-01 | Franklin | Tibbe |  | 138 |  | Franklin-Tibbe 138 kV line | MO |  |  | M1 - Proposed | 11000000 | AMEREN MISSOURI | Not Shared
A |  | Central | IL | 50257 | 50453 | Substation | 2026-12-01 | Steeleville |  |  | 138 |  | Rebuild Steeleville 138 kV as a five-position switching station, in a ring bus arrangement, with one additional position for future expansion with continuous capability of 3000 A. Install a new 40 Mvar 138 kV capacitor bank in one of the initial ring bus positions | IL |  |  | M1 - Proposed | 6001746 | AMEREN ILLINOIS | Not Shared
A |  | West | ND | 50260 | 50455 | Substation | 2029-12-31 | Hettinger |  |  | 230 | 42 | Add a 115 kV bay to the Hettinger substation. | ND |  |  | M1 - Proposed | 600000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A |  | West | ND | 50260 | 50456 | Line Upgrade | 2029-12-31 | Hettinger | Elgin | 1 | 115 |  | Build a new 115/69/41.6 kV substation with the rebuild of the Hettinger-Elgin line to 115 kV. | ND |  | 42.2 | M1 - Proposed | 23000000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A |  | Central | MO | 50259 | 50457 | Misc. | 2025-04-01 | Fletcher | Pilot Knob | 2 | 161 |  | Replace wood structures 68-75 due to wood-pecker damage and replace guy at structure 84. | MO |  |  | M4 - Project in Service | 1400000 | AMEREN MISSOURI | Not Shared
A |  | West | ND | 50260 | 50458 | Substation | 2029-12-31 | Elgin |  |  | 115 | 42 | Build new substation at Elgin 115/69/41.6 kV. | ND |  |  | M1 - Proposed | 7000000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A |  | West | ND | 50260 | 50459 | Transformer | 2029-12-31 | Elgin |  |  | 115 |  | New transformers | ND |  |  | M1 - Proposed | 1500000 | MONTANA-DAKOTA UTILITIES CO. | Not Shared
A |  | West | MN | 50243 | 50460 | Line Upgrade | 2030-09-30 | Merton | SS2755 | 1 | 69 | 69 | Rebuild SW-OM line. SS2755 to Merton Substation. Line length is approx. 6.5 miles. Planning has requested line be rebuilt to 161kV. | MN |  |  | M1 - Proposed | 9273000 | GREAT RIVER ENERGY | Not Shared
A |  | West | WI | 50262 | 50461 | Substation | 2028-12-01 | Chaffee Creek |  |  | 69 |  | Asset renewal replacement of oil circuit breakers at Chaffee Creek SS. In addition, replace the aging capacitor bank and internal components of the control house. | WI |  |  | M1 - Proposed | 5155000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MN | 50263 | 50462 | Line Upgrade | 2029-08-31 | Pine City | Rush City | 1 | 69 | 69 | Rebuild CP line. CPX Line to the CPT Line. Line length is approx. 11 miles. Rebuild RLT Line. Line length is approx. 0.1 miles Rebuild CPT Line. SS2984 to SS2555. Line length is approx. 1.5 miles | MN | 12.6 |  | M1 - Proposed | 11751000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50264 | 50463 | Line Upgrade | 2031-03-31 | Blaine | Soderville | 1 | 69 | 69 | Rebuild SP line. Soderville Substation to #152. Line length is approx. 10 miles | MN | 10 |  | M1 - Proposed | 21269000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50265 | 50464 | Line Upgrade | 2029-12-12 | Lake Jennie Tap | Victor | 1 | 69 | 69 | Rebuild DS line. DSX Line to SS377. Line length is approx. 9.25 miles | MN | 9.25 |  | M1 - Proposed | 8093000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50266 | 50465 | Line Upgrade | 2030-04-30 | Hawick | Spicer Tap | 1 | 69 | 69 | Rebuild SH line. SS306 to Green Lake Sub to Hawick Sub. Line length is approx. 13.7 miles | MN | 13.7 |  | M1 - Proposed | 12790000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50261 | 50466 | Transformer | 2026-12-31 | Blue Earth North |  |  | 161 |  | 2nd 161/69kV Transformer 45/60/75 MVA | MN |  |  | M1 - Proposed | 11200000 | Central Minnesota Municipal Power Agency | Not Shared
A |  | West | MN | 50267 | 50467 | Substation | 2029-12-31 | Johnsville |  |  | 69 | 69 | GRE to convert the existing Johnsville substation to an in-and-out substation. GRE will need to build a short 69 kV transmission line tap and add/alter metering/telecom for the 2nd transformer. 2000-amp motor operated FLB switches should be used. | MN |  |  | M1 - Proposed | 2362908 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50268 | 50468 | Transformer | 2026-05-31 | Blue Earth Rice Street |  |  | 69 |  | Rice Street 12/20 MVA Transformer | MN |  |  | M1 - Proposed | 2400000 | Central Minnesota Municipal Power Agency | Not Shared
A |  | West | WI | 50270 | 50469 | Substation | 2027-07-02 | Barron |  |  | 161 |  | Barron 161 kV ring bus expansion and POI facilities. | WI |  |  | M1 - Proposed | 1438367 | DAIRYLAND POWER COOPERATIVE | Not Shared
A |  | West | MN | 50271 | 50470 | Line Upgrade | 2028-03-01 | Rock Dell | Pleasant Valley |  | 69 |  | Rebuild of 2.0 miles of 69 kV transmission between Rock Dell and Pleasant Valley. | MN | 2 |  | M1 - Proposed | 1227000 | DAIRYLAND POWER COOPERATIVE | Not Shared
A |  | West | MN | 50272 | 50471 | Line Upgrade | 2026-06-02 | Genoa Dist | Ringe |  | 69 |  | Rebuild 7.88 miles of 69 kV transmission between Genoa Dist. Tap and Ringe Tap on DPC's N470 line. | MN |  |  | M1 - Proposed | 2959357 | DAIRYLAND POWER COOPERATIVE | Not Shared
A |  | West | MN | 50274 | 50472 | Substation | 2027-12-31 | Iona | Iona Tap | 1 | 115 | 115 | The Iona 115 kV Conversion Project involves building a 0.5-mile 115 kV tap line to interconnect the existing Todd-Wadena Electric Cooperative (TWEC) Iona substation to the 47 Line via a 3-way, 2000-amp, full load break 115 kV switch. Utilize 477 ACSR conductor. | MN |  | 3.5 | M1 - Proposed | 266271 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50274 | 50473 | Line New | 2027-12-31 | Iona | Iona Tap | 1 | 115 | 115 | The Iona 115 kV Conversion Project involves building a 0.5-mile 115 kV tap line to interconnect the existing Todd-Wadena Electric Cooperative (TWEC) Iona substation to the 47 Line via a 3-way, 2000-amp, full load break 115 kV switch. Utilize 477 ACSR conductor. | MN |  | 3.5 | M1 - Proposed | 2049476 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50273 | 50474 | Substation | 2029-10-01 | Heartland |  |  | 115 | 115 | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. | MN |  |  | M1 - Proposed | 203802 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50273 | 50475 | Substation | 2029-10-01 | Hubbard |  |  | 115 | 115 | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. | MN |  |  | M1 - Proposed | 1361504 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50273 | 50476 | Line New | 2029-10-01 | Heartland | Hubbard | 1 | 115 | 115 | 1. Build a new, ~5.0-mile 115 kV tap line from IM-HSX line to the new Heartland Lakes distribution substation. 2. Add High side structure, breaker, switch, and relaying at the Hubbard substation 3. Utilize 477 ACSR conductor. | MN |  | 5 | M1 - Proposed | 6920195 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50269 | 50477 | Transformer | 2026-05-31 | Blue Earth Northeast |  |  | 69 |  | 2nd 20-37.3 MVA Transformer | MN |  |  | M1 - Proposed | 4800000 | Central Minnesota Municipal Power Agency | Not Shared
A |  | West | MN | 50275 | 50478 | Transformer | 2029-05-31 | Blue Earth West Sub |  |  | 69 |  | Add 2nd 10/14 MVA Transformer | MN |  |  | M1 - Proposed | 2900000 | Central Minnesota Municipal Power Agency | Not Shared
A |  | Central | IN | 50279 | 50482 | Transformer | 2028-05-26 | Staunton |  |  | 230 | 138 | replace / upgrade the two existing banks 1 and 2 with 250MVA nameplate | IN |  |  | M1 - Proposed | 18800000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50280 | 50483 | Substation | 2029-12-31 | Project Mars |  |  | 138 |  | Project Neuron (fka Mars) - Lafayette new load @ 27MWs; to be served from the 13806 line very near Tipmont Co Farm - reconfiguration required to loop in existing radial to Tipmont Co Farm and new customer. | IN | 0.5 | 1.5 | M1 - Proposed | 24970000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IL | 50282 | 50489 | Voltage Device | 2026-12-01 | Leghorn and Radbourn |  |  | 345 |  | Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Radbourn 345 kV substation. Install (1) 50 Mvar shunt reactor, (1) 345 kV circuit breaker, and (1) motor-operated disconnect switch at Leghorn 345 kV substation. | IL |  |  | M1 - Proposed | 4800000 | AMEREN ILLINOIS | Not Shared
A |  | West | MN | 50284 | 50490 | Line Upgrade | 2030-11-29 | Cormorant | Tamarac | 1 | 115 | 115 | Rebuild all sections of the LR-PC line. | MN | 9 |  | M1 - Proposed | 8501468 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50284 | 50491 | Line Upgrade | 2030-05-31 | Pelican Rapids | Tamarac | 1 | 115 | 115 | Rebuild all sections of the LR-PC line. | MN | 7 |  | M1 - Proposed | 6620453 | GREAT RIVER ENERGY | Not Shared
A |  | Central | IN | 50285 | 50492 | Substation | 2026-06-01 | HE Shadow Lake 138/12kV Sub |  |  | 138 | 12 | New HE Shadow Lake 138/12kV distribution substation for Clark Co REMC to be inserted in the 13898 Speed – Jeffersonville 138kV line between River Ridge Central and Stoney Point Jct.; looped through with ATO; loop in/out with 954ACSS/TW20x7@200C conductor | IN |  |  | M1 - Proposed | 2974000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50286 | 50493 | Line New | 2027-10-01 | Rosston | Lebanon Industrial |  | 69 |  | Construct 13 miles of new 69kV | IN |  | 13 | M1 - Proposed | 30311869 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50287 | 50494 | Line Upgrade | 2026-07-06 | Gessie |  |  | 69 |  | 3.5 miles from tap point to Gessie Substation | IN | 3.5 |  | M1 - Proposed | 7194654 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IL | 50288 | 50496 | Transformer | 2027-12-01 | Marblehead North |  |  | 161 |  | Replace existing transformer at Marblehead North with the onsite spare 161/138kV 300 MVA unit. | IL |  |  | M1 - Proposed | 1500000 | AMEREN ILLINOIS | Not Shared
A |  | Central | IN | 50289 | 50497 | Substation | 2026-10-16 | Wabash Industrial 69/12kV Sub |  |  | 69 | 12 | Wabash Industrial 69/12kV new sub to serve new 20+MW customer in the 69132 ckt - near Chippewa; includes 14.4MVAR capacitor | IN |  |  | M1 - Proposed | 2968000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50292 | 50502 | Transformer | 2028-12-31 | Fishback Creek |  |  | 69 | 12 | 69/12kV Substation | IN |  |  | M1 - Proposed | 6000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50293 | 50503 | Substation | 2029-12-31 | North Manchester |  |  | 69 |  | 3 terminal 69kV ring | IN |  |  | M1 - Proposed | 6800000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50294 | 50504 | Substation | 2028-12-31 | Flexel Jct |  |  | 69 |  | 3 terminal 69kV ring | IN |  |  | M1 - Proposed | 6800000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50295 | 50505 | Substation | 2030-12-31 | Cherry Grove |  |  | 69 |  | 3 terminal 69kV ring bus | IN |  |  | M1 - Proposed | 6800000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50296 | 50506 | Transformer | 2027-12-31 | Dover |  |  | 69 | 12 | New 69/12kV 22.4MVA substation | IN |  |  | M1 - Proposed | 5500000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50297 | 50507 | Transformer | 2027-11-24 | Milnon |  |  | 69 | 12 | 14MVA 69/12kV Substation | IN |  |  | M1 - Proposed | 6649226 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50298 | 50508 | Transformer | 2027-12-01 | Four Corners |  |  | 69 | 12 | 14MVA 69/12kV Substation | IN |  |  | M1 - Proposed | 5764132 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50298 | 50509 | Line New | 2026-12-31 | Four Corners |  |  | 69 |  | 2.5 miles of 69kV | IN |  |  | M1 - Proposed | 8287998 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50300 | 50510 | Transformer | 2027-12-01 | Beaver Creek |  |  | 69 | 12 | 14MVA 69/12kV Station | IN |  |  | M1 - Proposed | 5205938 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50300 | 50511 | Line New | 2027-12-01 | Beaver Creek |  |  | 69 |  | 2 miles of new 69kV | IN |  |  | M1 - Proposed | 5043488 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50301 | 50512 | Line New | 2027-12-31 | Maple Leaf |  |  | 69 |  | 6 miles of 69kV line | IN |  |  | M1 - Proposed | 15000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50302 | 50513 | Transformer | 2029-12-31 | Lacrosse |  |  | 69 |  | New 14MVA 69/12kV Substatoin | IN |  |  | M1 - Proposed | 5500000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50302 | 50514 | Line New | 2029-12-31 | Lacrosse |  |  | 69 |  | 2-3 miles of new 69kV | IN |  |  | M1 - Proposed | 7000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50303 | 50515 | Transformer | 2027-12-31 | Jacob Mack |  |  | 69 | 12 | Add a 2nd bank and expand the 69kV bus for a looped feed | IN |  |  | M1 - Proposed | 8594249 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IL | 50299 | 50516 | Substation | 2027-12-01 | Wakefield |  |  | 138 |  | Construct a three (3) position 138 kV substation in a ring bus configuration, with one (1) additional position available for future expansion, all with a 3000 A minimum continuous capability. Route the existing South Bloomington-Tabor-1445 138 kV line in and out of the new Wakefield substation. | IL |  |  | M1 - Proposed | 10700000 | AMEREN ILLINOIS | Not Shared
A |  | West | MN | 50304 | 50517 | Substation | 2025-12-31 | Slayton | Slayton Tap | 1 | 69 | 69 | Nobles is planning on relocating Slayton/Nobles substation out of town. Currently, Nobles is planning an energization date of fall of 2025. This will require GRE to tap into the new substation, retap in Xcel’s line from the new Slayton substation and retire the tap line (etc) from the old Slayton substation. | MN |  | 0.25 | M1 - Proposed | 873200 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50305 | 50518 | Substation | 2027-10-29 | Blue Earth |  |  | 69 | 69 | BENCO plans to rebuild their 69kV Blue Earth distribution substation on an adjacent property to replace the aged substation as well as increase transformer size to 7.5 MVA bottom 10.5 MVA top end rating . GRE will need to relocate line and install a new building, meter, and telecom equipment. GRE planning has requested the high side be an in-and-out. | MN |  |  | M1 - Proposed | 1443735 | GREAT RIVER ENERGY | Not Shared
A |  | Central | IN | 50316 | 50523 | Line Upgrade | 2028-12-31 | Duff |  |  | 138 |  | Complete rebuild of Z84 from Duff to IPL Petersburgh plant. Total rebuild distance is 19.9 miles and involves replacing wood h-frame structures with galvanized steel monopole structures. The existing 765 Drake ACSR conductor to be replaced with new 2-bundled 954 Rail conductor. | IN | 19.9 |  | M1 - Proposed | 38040000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | West | IA | 50318 | 50524 | Line Upgrade | 2027-09-01 | Adans County | Creston | 1 | 161 |  | Network Upgrades for J1530 and J1532 Generators (161 kV structure replacement) | IA |  |  | M1 - Proposed | 700000 | MIDAMERICAN ENERGY CO. | Shared
A |  | East | MI | 50317 | 50525 | Substation | 2028-12-31 | Hincka |  |  | 138 |  | Install Row 6 and 5 138 kV, 40kA breakers to accommodate Wolverine's interconnection. | MI |  |  | M1 - Proposed | 5010000 | METC | Not Shared
A |  | West | IA | 50319 | 50526 | Line Upgrade | 2026-12-01 | West Des Moines | 73rd & Buffalo |  | 69 |  | Rebuild and reconfigure West Des Moines 69 kV line to 73rd & Buffalo substations. | IA | 0.75 |  | M1 - Proposed | 1700000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50319 | 50527 | Line Upgrade | 2026-12-01 | West Des Moines | 37th & Rock Island |  | 69 |  | Rebuild and reconfigure West Des Moines 69 kV line to 37th & Rock Island substations. | IA | 0.1 |  | M1 - Proposed | 400000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50319 | 50528 | Substation | 2026-12-01 | West Des Moines |  |  | 69 |  | Replace 69 kV breaker DAE601 at West Des Moines Substation. | IA |  |  | M1 - Proposed | 450000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50320 | 50529 | Substation | 2028-06-01 | E. 17th & Washington |  |  | 69 |  | Expand E. 17th & Washington Substation steel to accommodate two 69 kV line breakers. | IA |  |  | M1 - Proposed | 0 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50321 | 50530 | Substation | 2028-10-01 | E. 17th & Broadway |  |  | 69 |  | Install three 69 kV line breakers at E. 17th & Broadway Substation | IA |  |  | M1 - Proposed | 0 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50324 | 50537 | Substation | 2027-12-31 | 88th Street |  |  | 161 |  | Expand 88th St Substation steel to ring bus and add a third 161-13 kV transformer | IA |  |  | M1 - Proposed | 9000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50325 | 50538 | Misc. | 2026-03-01 | NE Ankeny | New ITC Sub |  | 161 |  | NE Ankeny - new ITC substation line relaying | IA |  |  | M1 - Proposed | 400000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | Central | IN | 50326 | 50539 | Line Upgrade | 2027-12-31 | Northwest |  |  | 138 |  | Rebuild aging portions of the Z95 Northwest to AB Brown 138kV transmission line. The first section is approximately 1.57 miles long and the second section is approximately 3.47 miles long. Both sections have 795 Drake conductor, which will be replaced with 954 Rail conductor. Aging wood poles will be replaced with tubular steel structures. | IN |  |  | M1 - Proposed | 8700000 | Southern Indiana Gas & Electric Company d/b/a Centerpoint Energy Indiana South | Not Shared
A |  | West | IA | 50327 | 50540 | Misc. | 2028-09-01 | Raun |  |  | 161 |  | Network Upgrades for SPP Generator 105 at Raun Substation | IA |  |  | M1 - Proposed | 750000 | MIDAMERICAN ENERGY CO. | Shared
A |  | West | IA | 50328 | 50541 | Misc. | 2029-12-01 | Neal North |  |  | 161 | 69 | Replace 161-69 kV transformer relaying and 69 kV breaker at Neal North Substation | IA |  |  | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50329 | 50542 | Transformer | 2028-12-31 | Substation 91 |  |  | 345 | 161 | Expand Substation 91 by converting the 345 kV yard to a ring bus configuration and by installing a second 345-161 kV transformer. | IA |  |  | M1 - Proposed | 58000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50330 | 50543 | Line Upgrade | 2026-06-01 | Plymouth | Merrill |  | 69 |  | Replace structures on the Plymouth-Merrill 69 kV line | IA |  |  | M1 - Proposed | 325000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IL | 50331 | 50544 | Transformer | 2029-06-01 | Substation 39 |  |  | 345 | 161 | At Substation 39, replace the existing 345-161 kV, 500 MVA Transformer 9T1 with a new 560 MVA transformer. | IL |  |  | M1 - Proposed | 10500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50332 | 50545 | Line Upgrade | 2027-06-01 | Division | Eastside |  | 69 |  | Rebuild and reconductor Division-Eastside 69 kV line | IA |  |  | M1 - Proposed | 2200000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50333 | 50546 | Misc. | 2025-06-19 | Franklin |  |  | 161 |  | Replace primary and secondary line and breaker failure relaying on Franklin 161 kV Breaker 9920 to ITC Midwest’s Nuthatch Substation | IA |  |  | M4 - Project in Service | 300000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50334 | 50547 | Line New | 2028-06-01 | Eagle Grove | Goldfield | 1 | 69 |  | Install two line switches on a steel pole | IA |  |  | M1 - Proposed | 500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50334 | 50548 | Line Upgrade | 2028-06-01 | Clarion | Latimer | 1 | 69 |  | Rebuild the Clarion-Latimer 69 kV line sections. | IA | 19.5 |  | M1 - Proposed | 11500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50335 | 50549 | Substation | 2027-08-01 | Johnson Creek |  |  | 161 |  | Install 161 kV breakers and associated equipment. | IA |  |  | M1 - Proposed | 2000000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50336 | 50550 | Substation | 2026-12-01 | Kellogg |  |  | 161 |  | Replace three 161 kV oil circuit breakers at Kellogg Substation | IA |  |  | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50336 | 50551 | Substation | 2027-12-01 | Missouri Valley |  |  | 69 |  | Replace two 69 kV breakers and associated disconnect switches at Missouri Valley Substation | IA |  |  | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50336 | 50552 | Substation | 2026-12-01 | Sub T Fort Dodge |  |  | 161 |  | Replace four 161 kV oil circuit breakers and two switches at Sub T in Fort Dodge | IA |  |  | M1 - Proposed | 3500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | IA | 50336 | 50553 | Substation | 2028-12-31 | Various |  |  | 345 | 69 | Replace substation equipment because of condition and/or to improve reliability at various substations | IA |  |  | M1 - Proposed | 14500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | East | MI | 50337 | 50554 | Line Upgrade | 2029-12-31 | Tower | Black Lake |  | 69 | 69 | Tower to Black Lake transmission line. | MI |  | 4.5 | M1 - Proposed | 4500000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A |  | East | MI | 50338 | 50555 | Line Upgrade | 2029-12-31 | Linoln Junction | Lincoln |  | 69 | 69 | 5 Miles of transmission line between Lincoln and Lincoln Junction | MI | 5 |  | M1 - Proposed | 5000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A |  | East | MI | 50339 | 50556 | Line Upgrade | 2029-12-31 | Bass Lake | Wolfe Lake |  | 69 | 69 | 11 Miles of transmission line between the Bass Lake and Wolfe Lake substations. | MI | 11 |  | M1 - Proposed | 11000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A |  | Central | IN | 50341 | 50558 | Line Upgrade | 2027-05-21 | Gibson | Petersburg |  | 345 |  | 34507 Gibson-Petersburg Line Improvements - replace 16 aluminum Kaiser A, B, or C towers with 3 pole dead end structures at 2.5 mile intervals | IN | 33.53 |  | M1 - Proposed | 15207000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50342 | 50559 | Line Upgrade | 2026-06-01 | Greencastle Industrial Jct. | WVPA Vandalia (new sub) |  | 69 |  | 6996 Greencastle Industrial Jct. to WVPA Vandalia Rebuild - 0.74 miles with 477ACSR/VR2@120C; Greencastle Industrial Jct. upgrade to ATO / SCADA control | IN | 0.74 |  | M1 - Proposed | 1984000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50343 | 50560 | Substation | 2028-12-11 | Terre Haure Water St. |  |  | 138 |  | Terre Haure Water St. 138kV sub - construct 3-breaker 138kV ring bus | IN |  |  | M1 - Proposed | 16520000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50345 | 50562 | Substation | 2030-10-18 | WVPA Richland |  |  | 69 |  | WVPA Richland 69kV ring bus: install 3 - CB ring at existing sub; rebuild 0.9 mile WVPA Richland to Rochester Tap 6968 with 954ACSR | IN | 0.9 |  | M1 - Proposed | 11736000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50347 | 50564 | Transformer | 2026-07-31 | Frankfort 230/69 Bk1 |  |  | 230 | 69 | Frankfort 230/69 Bk1: Replace 84MVA 230/69kV Transformer with new 150MVA transformer; replace 23069-1 ckt. switcher; replace substation RTU | IN |  |  | M1 - Proposed | 6329000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50349 | 50566 | Transformer | 2027-12-07 | Crane South |  |  | 138 | 69 | Crane South Substation: expand 138kV bus into (4) CB Ring; Install 100MVA 138/69kV Transformer Bank 2; Add (2) 69kV breakers to the existing ring; construct new 69kV line to Crane Naval Base NW; reconductor 69193 line from Crane South to Crane Naval Base | IN |  |  | M1 - Proposed | 28966000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50351 | 50567 | Line Upgrade | 2027-11-23 | Arcadia | Arcadia North |  | 69 |  | Arcadia N to Arcadia 69kV Rebuild - 2.5 miles of 69kV line 69180 from Arcadia north sub to Arcadia sub | IN | 2.5 |  | M1 - Proposed | 5500000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | West | MN | 50365 | 50568 | Voltage Device | 2026-12-31 | Shannon |  |  | 230 |  | Replace the two existing 230 kV capacitor banks with two 54.3 MVAR capacitor banks | MN |  |  | M1 - Proposed | 1200000 | MINNESOTA POWER INC. | Not Shared
A |  | West | MN | 50365 | 50569 | Voltage Device | 2026-12-31 | Shannon |  |  | 115 |  | Replace the existing 115 kV capacitor bank with a 19.5 MVAR capacitor bank | MN |  |  | M1 - Proposed | 550000 | MINNESOTA POWER INC. | Not Shared
A |  | East | MI | 50366 | 50570 | Line Upgrade | 2030-06-01 | Mud Lake | Verona | 1 | 138 |  | Upgrade ~0.67 mile of 954 ACSR to 1431 ACSR on the Mud Lake – Verona #1 138 kV line. | MI | 0.67 |  | M1 - Proposed | 1410000 | METC | Not Shared
A |  | East | MI | 50366 | 50571 | Substation | 2030-06-01 | Verona |  |  | 138 |  | Upgrade the 2-4/0 Cu stranded bus at position “588” and switch 585 to at least 450 MVA for summer emergency rating. | MI |  |  | M1 - Proposed | 180000 | METC | Not Shared
A |  | Central | IN | 50369 | 50572 | Line Upgrade | 2026-12-11 | Huntington Goblesville Jct | United (Bippus) Jct |  | 69 |  | Huntington Goblesville Jct to United Jct 69kV rebuild: 6.45 miles of line 6923 ckt. | IN | 6.45 |  | M1 - Proposed | 9238000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50370 | 50573 | Line Upgrade | 2025-11-21 | New London | Kokomo Highland Park |  | 230 |  | New London to Kokomo Highland Park 230kV - 23009 ckt. - Replace/Upgrade structures (7.5 miles) to get 100C operation of existing 900ACSR54X7@80C conductor | IN | 7.5 |  | M3 - Under Construction | 1976000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | Central | IN | 50371 | 50574 | Transformer | 2027-11-01 | Lee Hanna |  |  | 69 |  | New 33.6MVA substation 69/12kV | IN |  |  | M1 - Proposed | 10000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A |  | Central | IN | 50374 | 50576 | Line Upgrade | 2027-07-01 | Dresser | 345 lines |  | 345 |  | Dresser 345kV Line Upgrades: 34520 (to Fairbanks) and 34538 (to Sugar Crk) ckts. - replace structures to achieve line ratings of 100°C | IN | 16.52 |  | M1 - Proposed | 11600000 | DUKE ENERGY INDIANA, LLC | Shared
A |  | Central | IN | 50376 | 50578 | Line Upgrade | 2025-11-15 | HE Bethany | Charlestown Jct |  | 69 |  | 6955 ckt. Rebuild HE Bethany to Charlestown Jct - 954 ACSR at 120C | IN | 2.5 |  | M1 - Proposed | 3305000 | DUKE ENERGY INDIANA, LLC | Not Shared
A |  | East | MI | 50377 | 50579 | Substation | 2030-06-01 | New Station |  |  | 138 |  | Rebuild Blackstone 138kV station at a new site approximately 0.20 miles to the north, utilizing new equipment in a six (6) breaker ring bus configuration. All new 138kV breakers should be standard 3000A 50kA breakers. All new equipment at the new station must be rated 450MVA for summer emergency. The tentative name of the new 138kV station is Lansing Ave. | MI |  |  | M1 - Proposed | 9450000 | METC | Not Shared
A |  | East | MI | 50377 | 50580 | Line New | 2030-06-01 | New Station | Broughwell |  | 138 |  | Cut Blackstone-Broughwell 138kV line into the new station utilizing 1431 ACSR Conductor. | MI |  |  | M1 - Proposed | 1240000 | METC | Not Shared
A |  | East | MI | 50377 | 50581 | Line New | 2030-06-01 | New Station | Maines Road |  | 138 |  | Cut the Blackstone-Stable 138kV line (Main-Blackstone section) to new station utilizing 1431 ACSR Conductor. | MI |  |  | M1 - Proposed | 1170000 | METC | Not Shared
A |  | Central | IL | 50381 | 50582 | Line Upgrade | 2026-12-01 | Riverside | Hardin Tap |  | 69 |  | Rebuild Riverside-Hardin Tap 69 kV Line | IL | 10.8 |  | M1 - Proposed | 5940000 | PRAIRIE POWER, INC. | Not Shared
A |  | East | MI | 50377 | 50583 | Line New | 2030-06-01 | Blackman | Leoni |  | 138 |  | Tie the existing Blackman-Blackstone #1 and Blackstone-Leoni #1 line utilizing 1431 ACSR Conductor to form the new Blackman-Leoni 138kV line. Also remove all sag limit on Blackman-Leoni 138kV line (on the original Blackman-Blackstone section). | MI |  |  | M1 - Proposed | 1440000 | METC | Not Shared
A |  | East | MI | 50377 | 50584 | Line New | 2030-06-01 | New Station | Blackstone 46kV |  | 138 |  | Construct 0.37 miles of 138kV line from Lansing Ave to CE 46kV TRF #1 utilizing 954 ACSR Conductor. | MI |  |  | M1 - Proposed | 1255000 | METC | Not Shared
A |  | East | MI | 50377 | 50585 | Substation | 2030-06-01 | Blackstone |  |  | 138 |  | Decommission 138kV Blackstone substation. | MI |  |  | M1 - Proposed | 1370000 | METC | Not Shared
A |  | South | AR | 50383 | 50587 | Substation | 2026-12-30 | Greenbrier |  |  | 161 |  | The asset renewal programs replace aged and/or degraded transmission line and transmission substation assets. Entergy continuously reviews asset health to prioritize those replacements and the specifics for the 2025 asset renewal plans have not yet been finalized. | AR |  |  | M1 - Proposed | 16475000 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | South | AR | 50384 | 50588 | Substation | 2026-12-01 | Hot Springs |  |  | 500 |  | All 500kV line panels at Hot Springs need to have primary 1 relays on a separate DC panel than primary 2/backup relays. The breakers for these lines must have trip coil #1 and trip coil #2 fed from separate DC panels. The DC panels must be fed from separate battery sets and the DC panels cannot be wired in series or in parallel to one another. | AR |  |  | M1 - Proposed | 2757000 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | South | AR | 50385 | 50589 | Line Upgrade | 2027-06-30 | El Dorado Donan | El Dorado Monsanto |  | 115 |  | Rebuild the ~3.1 mile line segment along with any other station equipment to achieve a 1300 A flow-through rating. | AR |  |  | M1 - Proposed | 7900000 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | South | AR | 50386 | 50590 | Line Upgrade | 2027-12-07 | Hilltop | Saint Joe |  | 161 |  | Rebuild Hilltop – St Joe along with any other station equipment to achieve a 1300 A through path rating. | AR |  |  | M1 - Proposed | 12384021 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | South | AR | 50387 | 50591 | Line Upgrade | 2028-07-20 | Saint Joe | Everton Road |  | 161 |  | Rebuild St Joe – Everton Rd along with any other station equipment to achieve a 1300 A through path rating. | AR |  |  | M1 - Proposed | 29720000 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | South | AR | 50388 | 50592 | Line Upgrade | 2029-04-13 | Everton Road | Harrison East |  | 161 |  | Compliance with NERC Reliability Standard TPL-001, R2.7. Increased reliability by updating aging infrastructure and increased line capacity for improved transmission system performance. | AR |  |  | M1 - Proposed | 20140000 | ENTERGY ARKANSAS, LLC | Not Shared
A |  | East | MI | 50377 | 50593 | Line New | 2030-06-01 | New Station | Blackstone 46kV |  | 138 |  | Construct 0.37 miles of 138kV line from Lansing Ave to CE 46kV TRF #2 utilizing 954 ACSR Conductor. | MI |  |  | M1 - Proposed | 1075000 | METC | Not Shared
A |  | East | MI | 50246 | 50594 | Transformer | 2028-12-31 | Caniff |  |  | 345 |  | Replace the Caniff 303(AB) PST Transformer with at least 736 MVA (3543 Amps) summer emergency rated transformer. | MI |  |  | M1 - Proposed | 30000000 | ITC | Not Shared
A |  | Central | IN | 50389 | 50601 | Transformer | 2027-12-31 | Leesburg |  |  | 345 | 138 | Addition of 2nd Leesburg 345/138kV Transformer | IN |  |  | M1 - Proposed | 8000000 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | Central | IN | 50390 | 50602 | Substation | 2029-05-31 | Dune Acres |  |  | 138 |  | Add Breakers to 138kV lines on existing single breaker. | IN |  |  | M1 - Proposed | 3000000 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | South | MS | 50391 | 50603 | Line Upgrade | 2027-01-01 | Colonial Collins | Colonial Kola |  | 69 |  | A complete rebuild of Line 74B (Colonial Collins – Colonial Kola 0.77 mi.) is recommended at 161kV insulation with more reliable structural designs and OPGW. | MS |  |  | M1 - Proposed | 900000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | West | MN | 50392 | 50604 | Line Upgrade | 2026-10-30 | Elk River Muni West |  |  | 69 | 69 | Remove and upgrade 600-amp switches EWSM11 and EWS10 with live parts to 1200 amp. The span of 266 ACSR transmission conductor between the two switch poles should be removed and upgraded to 477 ACSS. Switch EWS14 is 1200-amp and owned by Elk River Municipal and nothing needs to be done to this switch. | MN |  |  | M1 - Proposed | 68811 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50393 | 50605 | Voltage Device | 2030-12-31 | Iron Range |  |  | 500 |  | New 500kV reactor, 150 MVAR. | MN |  |  | M1 - Proposed | 4000000 | MINNESOTA POWER INC. | Not Shared
A |  | West | MN | 50394 | 50606 | Substation | 2028-06-30 | Riverton |  |  | 115 | 115 | GRE plans to upgrade equipment and relocated assets ahead of MP Riverton rebuild scheduled for in-service by 2030. The project includes pull all GRE assets out of MP control house that is planned for demo by 2030 into new GRE control house. GRE will also be upgrading physical assets in our yard including the 25WB1 oil breaker, relaying, the Westinghouse 3-phase 115kV PT with 3 single phase CCVTs on 115kV bus, GE PT’s, and bus modifications. | MN |  |  | M1 - Proposed | 2610398 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50395 | 50607 | Line New | 2025-12-31 | MP Asset Blanket for 2025 |  |  | 230 | 115 | Replace aging poles reaching end of life. | MN |  |  | M1 - Proposed | 8250000 | MINNESOTA POWER INC. | Not Shared
A | A | Central | KY | 50396 | 50608 | Line New | 2026-12-01 | Bon Harbor |  | 1 | 69 |  | This will be a 0.3 mile 69 kV line between BREC's 69 kV system by means of a tap to connect to OMU's Substation M. | KY |  | 0.3 | M2 - Appendix A Approved | 7500000 | BIG RIVERS ELECTRIC CORPORATION | Not Shared
A |  | South | MS | 50399 | 50609 | Line Upgrade | 2028-06-01 | Benndale | Benndale GT |  | 69 |  | A complete rebuild of Line 35A (Benndale – Benndale GT 69kV) is recommended at 161kV insulation with more reliable structural designs and OPGW. This project will increase reliability of the transmission system and provide an additional OPGW communication link between Benndale and Benndale GT. | MS |  |  | M1 - Proposed | 900000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | South | MS | 50400 | 50610 | Line New | 2026-10-01 | Ovett GOAB | Ovett DP |  | 69 |  | Tap Line 114A (Ellisville - NW Perry 69kV) with a 69kV GOAB and build a new transmission line to the delivery point. | MS |  |  | M1 - Proposed | 1975000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | East | MI | 50372 | 50611 | Line Upgrade | 2030-06-01 | Dupont | White Lake |  | 138 |  | Upgrade line from Dupont to White Lake (~5.094 miles) from 336 ACSR to 954 ACSR. | MI |  |  | M1 - Proposed | 8050000 | METC | Not Shared
A |  | South | MS | 50400 | 50612 | Line New | 2026-10-01 | Ovett GOAB |  |  | 69 |  | Tap Line 114A (Ellisville - NW Perry 69kV) with a 69kV GOAB. | MS |  |  | M1 - Proposed | 125000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | East | MI | 50372 | 50613 | Substation | 2030-06-01 | Dupont |  |  | 138 |  | Upgrade buses at Dupont positions “199” and “177” to at least 332 MVA for summer emergency rating. | MI |  |  | M1 - Proposed | 248000 | METC | Not Shared
A |  | East | MI | 50401 | 50614 | Line Upgrade | 2024-12-31 | East Jordon Junction | East Jordon |  | 69 |  | 2.25 miles of single circuit steel pole contruction with 795 ACSS. | MI | 2.25 |  | M1 - Proposed | 2500000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A |  | West | MN | 50402 | 50615 | Substation | 2026-12-31 | Boswell |  |  | 115 |  | Bus expansion and breaker addition. | MN |  |  | M1 - Proposed | 1550000 | MINNESOTA POWER INC. | Not Shared
A |  | East | MI | 50401 | 50616 | Line Upgrade | 2029-12-31 | East Jordon | Eastport |  | 69 |  | 11.5 miles of single-circuit steel poles with 795 ACSS. | MI | 11.5 |  | M1 - Proposed | 13000000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A |  | Central | MO | 50403 | 50617 | Transformer | 2027-12-01 | Dardenne |  |  | 161 | 138 | Dardenne Substation Retirement | MO |  |  | M1 - Proposed | 3600000 | AMEREN MISSOURI | Not Shared
A |  | South | MS | 50404 | 50618 | Line New | 2026-12-01 | Lake Walthall SS | Lake Walthall DP |  | 115 |  | Tap the Entergy owned 115kV line (Tylertown - Dexter) with a 115kV switching station and build a new transmission line to the delivery point. | MS |  |  | M1 - Proposed | 1900000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | East | MI | 50401 | 50619 | Line Upgrade | 2029-12-31 | Eastport | Barnard |  | 69 |  | 10 miles of single-circuit steel poles with 795 ACSS | MI | 10 |  | M1 - Proposed | 10500000 | WOLVERINE POWER SUPPLY COOPERATIVE, INC | Not Shared
A |  | South | MS | 50404 | 50620 | Substation | 2026-12-01 | Lake Walthall SS |  |  | 115 |  | Tap the Entergy owned 115kV line (Tylertown - Dexter) with a 115kV switching station. | MS |  |  | M1 - Proposed | 930000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | Central | IL | 50405 | 50621 | Line New | 2029-12-01 | Berlin | Amos |  | 69 |  | Reroute Berlin-Amos 69 kV Line out of creek bottom. | IL | 1 | 19 | M1 - Proposed | 11175000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50406 | 50622 | Line Upgrade | 2027-12-01 | Breiner | Kington |  | 69 |  | Rebuild Breiner-Kington 69 kV Line | IL | 10.3 |  | M1 - Proposed | 5665000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50407 | 50623 | Line Upgrade | 2027-12-01 | Macomb Bkr | Woodland |  | 69 |  | Rebuild Macomb Bkr-Woodland 69 kV Line | IL | 1.75 |  | M1 - Proposed | 1010000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50407 | 50624 | Line Upgrade | 2026-12-01 | Woodland | Spring Lake Jct |  | 69 |  | Rebuild Woodland-Spring Lake Jct 69 kV Line | IL | 1.7 |  | M1 - Proposed | 1000000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50408 | 50626 | Line Upgrade | 2029-12-01 | El Dara Jct | Hadley |  | 69 |  | Rebuild El Dara Jct-Hadley 69 kV Line with 336 ACSR | IL | 5.25 |  | M1 - Proposed | 2820000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50409 | 50628 | Line New | 2028-12-01 | Andrew | Salisbury |  | 69 |  | New Andrew-Salisbury DC 69 kV Line with 336 ACSR and New Andrew 69 kV Breaker for dedicated feed. No new ROW | IL |  | 0.5 | M1 - Proposed | 1500000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50412 | 50632 | Line New | 2030-12-01 | Paragon | Dunkel |  | 69 |  | New Paragon-Dunkel 69 kV Line | IL |  | 3.9 | M1 - Proposed | 4550000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50412 | 50633 | Line New | 2030-12-01 | Dunkel | Velma |  | 69 |  | New Dunkel-Owaneco-Velma 69 kV Line | IL |  | 13 | M1 - Proposed | 9750000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50412 | 50635 | Line New | 2030-12-01 | Velma | Grove City |  | 69 |  | New Velma-Grove City 69 kV Line | IL |  | 8.6 | M1 - Proposed | 5590000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50413 | 50636 | Substation | 2030-12-01 | Edinburg |  |  | 69 |  | New Edinburg 69 kV Breaker Station | IL |  |  | M1 - Proposed | 3400000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50414 | 50637 | Substation | 2029-12-01 | Henton |  |  | 69 |  | New Henton 69 kV Breaker Station | IL |  |  | M1 - Proposed | 3000000 | PRAIRIE POWER, INC. | Not Shared
A |  | Central | IL | 50414 | 50638 | Voltage Device | 2029-12-01 | Henton |  |  | 69 |  | New Henton 69 kV Capacitor Bank 4.8 MVAR | IL |  |  | M1 - Proposed | 400000 | PRAIRIE POWER, INC. | Not Shared
A |  | West | MN | 50415 | 50639 | Substation | 2025-10-31 | Grand Lake |  |  | 69 | 69 | Relocate and reterminate 69 kV transmission line into the new Grand Lake high side. | MN |  |  | M1 - Proposed | 1200259 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50416 | 50640 | Substation | 2027-12-31 | Pine City |  |  | 69 | 69 | • Replace breaker 4NB2 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace breaker 4NB3 o New breaker slab, unless determined usable o New 795 AAC Jumpers • Replace 69kV bus PTs, Grasston line PT and Rush City/Rock Lake line CCVT o Remove 69kV PT Fuses • Replace line arresters with new 48kV MCOV Surge Arresters on Grasston and Bear Creek/Hinckley Lines • Replace 69kV bus relaying with SEL-487E pri/sec panel • Replace the #3 311B panel with 2 line 311C panel • Remove NS3 bypass switch • Update Station Service System o Install new 50kVA SSVT (Pri.) o Install new 200A ATS o Install new 200A Safety Switch (Pri.) o Install new 200A Safety Switch (Emer.) o ECE to replace existing 10kVA Aux Xfmr with 50kVA Aux Xfmr • Update line naming/3 letter mnemonics • Review grounding | MN |  |  | M1 - Proposed | 1364747 | GREAT RIVER ENERGY | Not Shared
A |  | Central | IN | 50315 | 50641 | Substation | 2031-03-01 | Ralston |  |  | 138 |  | New 4-position ring bus 138 kV Ralston substation looped in on 132-23 Eagle Valley-Sanitation Southport line. | IN | 0 | 0 | M1 - Proposed | 10000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50315 | 50642 | Substation | 2031-03-01 | Camby |  |  | 138 |  | Add new 138 kV line terminal at Camby substation​ | IN |  |  | M1 - Proposed | 4000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50315 | 50643 | Line New | 2031-03-01 | Ralston | Camby |  | 138 |  | Rebuild (as needed) nearby 138 kV idle line and connect into Ralston substation (1.82 rebuild for double circuit; 2.8 refurbish existing line).​ | IN | 2.8 | 1.82 | M1 - Proposed | 10000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50216 | 50644 | Substation | 2031-12-01 | Petersburg |  |  | 138 |  | Replace Petersburg 138 kV breakers #6, #7, & #9 from 40 kA to 63 kA. | IN |  |  | M1 - Proposed | 739000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50217 | 50645 | Substation | 2031-12-01 | Stout South |  |  | 138 |  | 80 kA Breakers for #1A, #2A, #2C, #3A, #3B, #3C, #4A, #4C, #5A, #5B, #5C, #5D | IN |  |  | M1 - Proposed | 3050000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | West | MN | 50398 | 50646 | Substation | 2028-12-15 | Inver Hills |  |  | 115 | 14 | Add 2x50 MVA Transformers Add breakers Extend feeders | MN | 0 | 0 | M1 - Proposed | 35100000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | Central | IN | 50311 | 50647 | Line Upgrade | 2033-12-01 | Sanitation Belmont | Southwest | 74 | 138 |  | Rebuild existing 2.114 miles 138 kV 132-74 Sanitation Belmont-Southwest line to new Summer rating of 2000A (478 MVA). | IN |  |  | M1 - Proposed | 5290000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50312 | 50648 | Line Upgrade | 2033-12-01 | Southwest | Lilly South |  | 138 |  | Rebuild existing 2.893 miles 138 kV 132-10 Southwest-Lilly South line to new Summer rating of 2000A (478 MVA). | IN |  | 2.89 | M1 - Proposed | 7070000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50313 | 50649 | Line Upgrade | 2033-12-01 | Lilly South | Center | 61 | 138 |  | Rebuild existing 1.267 miles 138 kV 132-61 Lilly South-Center line to new Summer rating of 2000A (478 MVA). | IN |  |  | M1 - Proposed | 2900000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50314 | 50650 | Line Upgrade | 2029-12-31 | Georgetown | North | 86 | 138 |  | Rebuild existing 7 miles 138 kV 132-86 Georgetown-North line to new Summer rating of 1600A (382 MVA). | IN |  |  | M1 - Proposed | 12760000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | West | MN | 50418 | 50651 | Line Upgrade | 2026-12-31 | Denham | Kettle River | 1 | 69 | 69 | The transmission line has had conductor failures over the last few years. A recent failure caused a grass fire. The line was planned to be rebuilt due to age/condition starting in 2027 and due to the current maintenance issues the project should start as soon as possible. | MN | 15.1 |  | M1 - Proposed | 11442911 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50417 | 50652 | Line Upgrade | 2026-12-31 | St. Bonifacious | Mound | 1 | 69 |  | Rebuild 0735 St Bonifacius to Mound and add OPGW | MN | 8.3 |  | M1 - Proposed | 13157400 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50419 | 50653 | Line Upgrade | 2029-11-29 | Bena | Bena Tap | 1 | 69 | 69 | Rebuild BE line from SS2505 to Bena Substation. Line length is approx. 15 miles. Enbridge plans to remove Line 3 which is located roughly 15ft north of GRE’s BE line between Bena Sub and Str 158 near the Mississippi River crossing (approx 12mi). The corridor where the pipeline and transmission line are located is very crowded, swampy and includes a LCP distribution line which is located about 12ft north of the BE line between the Enbridge Pipeline and BE line. The GRE line and LCP line are tied together with crossarms on many structures and there are side guys which extend under the pipeline in many locations. LCP plans to remove their distribution and relocate. | MN | 15 |  | M1 - Proposed | 17450679 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50420 | 50654 | Substation | 2027-08-24 | Lakefield |  |  | 345 | 345 | Expansion of the 345kV Gen tie bus at the Lakefield substation to accommodate the Three Waters Wind (340MW) Wind Farm. Installation of new 345kV breakers on the existing generator and installation of the GRE controlled EEE, 1500’ of 345kV Transmission to the interconnect 161kV/345kV step up substation | MN |  |  | M1 - Proposed | 5217392 | GREAT RIVER ENERGY | Shared
A |  | West | MN | 50421 | 50655 | Line Upgrade | 2028-03-15 | Gleason Lake | Mound | 1 | 69 |  | Rebuild 0737 Gleason Lake to Mound and install OPGW. | MN | 8.7 |  | M1 - Proposed | 12996320 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50422 | 50656 | Substation | 2025-12-01 | Coon Creek |  |  | 345 | 115 | Replace 3 345kV and 2 115kV breakers at Coon Creek that are at end of life | MN |  |  | M1 - Proposed | 2250000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50423 | 50657 | Substation | 2027-08-31 | Essig |  |  | 69 | 13 | Rebuild end of life Essig substation at neighboring site, converting old 2.4 kV system to standard 12.47kV | MN |  |  | M1 - Proposed | 681832 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50424 | 50658 | Substation | 2027-06-01 | Maple Street |  |  | 115 | 13 | Install new distribution substation to meet load growth in area | SD |  |  | M1 - Proposed | 13000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50425 | 50659 | Substation | 2026-03-31 | Fischer |  |  | 115 | 115 | DEA plans to update their 115-kV Fisher in/out distribution substation (both east and west) on the same property to replace the aged substation equipment. GRE will need to move the meter and telecom equipment as part of this work. | MN |  |  | M1 - Proposed | 1476377 | GREAT RIVER ENERGY | Not Shared
A |  | West | ND | 50426 | 50660 | Substation | 2027-10-15 | Thunder |  |  | 115 |  | Install new distribution substation to meet load growth in area | ND |  |  | M1 - Proposed | 7300000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50427 | 50661 | Line Upgrade | 2028-08-31 | Bell | Winthrop | 1 | 69 | 69 | Rebuild Winthrop to Bell line, about 12 miles. | MN | 12 |  | M1 - Proposed | 9868407 | GREAT RIVER ENERGY | Not Shared
A |  | West | ND | 50428 | 50665 | Transformer | 2028-06-01 | Cass County |  |  | 115 |  | Upgrade Cas County TR1 to support load growth. Rebuild distribution banks and include distribution reactors. | ND |  |  | M1 - Proposed | 12200000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | South | AR | 50441 | 50668 | Line New | 2027-04-28 | Wrightsville |  |  | 115 |  | New 3.5 mile transmission line from Wrightsville 115kV | AR |  | 3.5 | M1 - Proposed | 8900000 | ENTERGY ARKANSAS, LLC | Shared
A |  | South | AR | 50441 | 50669 | Line New | 2027-04-28 | Wrightsville |  |  | 115 |  | A new 3.5 mile 115kV transmission line from Wrightsville 115kV | AR |  | 3.5 | M1 - Proposed | 8900000 | ENTERGY ARKANSAS, LLC | Shared
A |  | East | MI | 50447 | 50677 | Substation | 2030-06-01 | Weeds Lake |  |  | 138 |  | Install two 138 kV, 63kA breakers at Weeds Lake to terminate Baker connection at position “BM8”. | MI |  |  | M1 - Proposed | 1910000 | METC | Not Shared
A |  | East | MI | 50447 | 50678 | Line New | 2030-06-01 | Weeds Lake | Baker |  | 138 |  | Construct ~36.5 miles of new 138 kV line on double-circuit structures (leave vacant side for future use) using 954 ACSR conductor. | MI |  | 36.5 | M1 - Proposed | 106900000 | METC | Not Shared
A |  | Central | IN | 50311 | 50681 | Line Upgrade | 2032-12-01 | Stout North | Sanitation Belmont | 01 | 138 |  | Rebuild existing ~1 mile 138 kV 132-01 Stout North-Sanitation Belmont line to new Summer rating of 2000A (478 MVA). | IN | 1 |  | M1 - Proposed | 4000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50311 | 50682 | Substation | 2032-12-01 | Stout North |  |  | 138 |  | Optimize Stout North: Move 132-14 south one bay (H16 & New H15), improve bay to double breaker​; Move 132-01 south one bay (H6 & H5) | IN |  |  | M1 - Proposed | 5700000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50306 | 50683 | Line Upgrade | 2029-12-31 | Southwest | Stout CT | 02 | 138 |  | Rebuild existing 2.85 mile 138 kV 132-02 Southwest-Stout CT line to new Summer rating of 2000A (478 MVA). | IN | 2.85 |  | M1 - Proposed | 9300000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50307 | 50684 | Line Upgrade | 2029-12-31 | Southwest | Northwest | 04 | 138 |  | Rebuild existing 4.75 miles 138 kV 132-04 Southwest-Northwest line to new Summer rating of 2000A (478 MVA). | IN | 4.75 |  | M1 - Proposed | 15200000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | East | MI | 50463 | 50685 | Substation | 2028-10-01 | Blackstone |  |  | 138 |  | Install a new 138 kV, 40 kA breaker with disconnects at “188” position (connected to Blue Bus). Existing CE “199” breaker with disconnects will be conveyed to METC. Re-name this CE “199” breaker as METC “288” breaker. | MI |  |  | M1 - Proposed | 1465000 | METC | Not Shared
A |  | East | MI | 50463 | 50686 | Line New | 2028-10-01 | Blackstone |  |  | 138 |  | METC to build a new radial 138kV single circuit line using 954 ACSR conductor and OPGW from Blackstone to CE TRF #1 terminating at "188" position. | MI |  |  | M1 - Proposed | 950000 | METC | Not Shared
A |  | East | MI | 50463 | 50687 | Line New | 2028-10-01 | Blackstone |  |  | 138 |  | METC to build a new radial 138kV single circuit line using 954 ACSR conductor and OPGW from Blackstone to CE TRF #2 terminating at "288" position. | MI |  |  | M1 - Proposed | 880000 | METC | Not Shared
A |  | West | MN | 50464 | 50688 | Substation | 2029-01-01 | Erie Rd 115 kV |  |  | 115 |  | Rebuild the Erie Road substation in Marshall with new 115 kV breakers and other equipment. | MN |  |  | M1 - Proposed | 6418700 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | West | IA | 50465 | 50689 | Line Upgrade | 2026-01-01 | Pella North Plant 69 kV | Pella Clark Street 69 kV | 1 | 69 |  | Rebuild a section of overhead line (~1,135 linear feet of transmission line) to underground line (~800 feet of underground cable). | IA | 0.2 | 0 | M1 - Proposed | 500000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | East | MI | 50466 | 50690 | Substation | 2028-12-31 | METC System |  |  | 345 | 138 | METC will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. | MI |  |  | M1 - Proposed | 2500000 | METC | Not Shared
A |  | West | ND | 50467 | 50691 | Voltage Device | 2025-12-31 | Maple River 345 kV |  |  | 35 |  | Retire 2 x 25 MVAR reactors off transformer tertiaries at Maple River 345 kV substation. | ND |  |  | M1 - Proposed | 1 | OTTER TAIL POWER COMPANY | Not Shared
A |  | East | MI | 50468 | 50692 | Substation | 2028-12-31 | ITCT System |  |  | 345 | 120 | ITCT will individually evaluate each request to ensure it does not adversely impact reliability. Projects that result in a system solution where the cost estimate is less than $2.5 Million that have an in-service date within the year 2028 will be associated with this project. When Customer Interconnection projects are evaluated to amount in a cost greater than $2.5 Million, a separate project will be submitted for approval. | MI |  |  | M1 - Proposed | 2500000 | ITC | Not Shared
A |  | West | SD | 50469 | 50693 | Voltage Device | 2025-12-31 | Big Stone South 345 kV |  |  | 35 |  | Retire 25 MVAR reactor off tertiary winding of Big Stone South transformer #1. | SD |  |  | M1 - Proposed | 1 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50470 | 50694 | Line Upgrade | 2025-12-31 | Cyrus 41.6 kV | Farwell 41.6 kV | 1 | 42 |  | Rebuild 41.6 kV line between Cyrus 41.6 kV and Farwell 41.6 kV. | MN | 14 |  | M1 - Proposed | 1130000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50471 | 50695 | Line Upgrade | 2025-12-31 | Ivanhoe 41.6 kV | Farwell 41.6 kV | 1 | 42 |  | Install line recloser near Ivanhoe 41.6 kV. | MN | 14 |  | M1 - Proposed | 350000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50472 | 50696 | Substation | 2026-09-30 | Hawick |  |  | 69 | 69 | Convert the Hawick switching station to a breaker station by installing three breakers at the existing site. | MN |  |  | M1 - Proposed | 2000000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50429 | 50697 | Transformer | 2026-10-15 | West Byron |  |  | 69 |  | Install new distribution transformer at West Byron to meet load growth in area | MN |  |  | M1 - Proposed | 7535000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | East | MI | 50474 | 50698 | Misc. | 2026-12-31 | METC Facilities |  |  | 345 | 138 | Relocate portion(s) of METC transmission lines located in public right of way at the government entities’ mandate. | MI |  |  | M1 - Proposed | 2500000 | METC | Not Shared
A |  | West | MN | 50473 | 50699 | Line New | 2029-12-31 | Pennock | St. Johns | 1 | 69 | 69 | Construct a new 69 kV line from the Pennock distribution substation to a new breaker station at the point of interconnection of the GRE owned WS 69 kV line and the WMUC 69 kV line (St. Johns breaker station). Retire BR line west of AG-RK to Granite Falls. | MN |  | 7.2 | M1 - Proposed | 11000000 | GREAT RIVER ENERGY | Not Shared
A |  | East | MI | 50475 | 50700 | Misc. | 2027-12-31 | METC Facilities |  |  | 345 | 138 | Relocate portion(s) of METC transmission lines located in public right of way at the government entities’ mandate. | MI |  |  | M1 - Proposed | 2500000 | METC | Not Shared
A |  | East | MI | 50476 | 50701 | Misc. | 2026-12-31 | ITCT Facilities |  |  | 345 | 120 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. | MI |  |  | M1 - Proposed | 2500000 | ITC | Not Shared
A |  | East | MI | 50477 | 50702 | Misc. | 2027-12-31 | ITCT Facilities |  |  | 345 | 120 | Relocate portion(s) of ITCT transmission lines located in public right of way at the government entities’ mandate. | MI |  |  | M1 - Proposed | 2500000 | ITC | Not Shared
A |  | East | MI | 50478 | 50703 | Substation | 2027-12-31 | METC Facilities |  |  | 345 | 138 | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | M1 - Proposed | 53875000 | METC | Not Shared
A |  | East | MI | 50479 | 50704 | Substation | 2027-12-31 | ITCT Facilities |  |  | 345 | 120 | Replace aging and outdated equipment on a cycle that will ensure each piece of equipment is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and typically will allow for longer maintenance intervals. New equipment is also commonly equipped with better monitoring and alarming functionality giving improved remote supervision. All of this will help to reduce overall maintenance costs. | MI |  |  | M1 - Proposed | 59750000 | ITC | Not Shared
A |  | West | MN | 50481 | 50706 | Substation | 2030-12-31 | LG - 2 |  |  | 345 |  | Install new facilities to meet load growth in the area. | MN |  |  | M1 - Proposed | 120000000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50482 | 50707 | Substation | 2026-12-31 | LG - 3 |  |  | 115 |  | Install new facilities to meet load growth in the area. | MN |  |  | M1 - Proposed | 25000000 | GREAT RIVER ENERGY | Not Shared
A |  | West | MN | 50483 | 50708 | Substation | 2029-12-30 | WMU-St Johns Lake 69 kV |  |  | 69 |  | Construct a new 69 kV breaker station near Willmar. | MN |  |  | M1 - Proposed | 6000000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | West | MN | 50483 | 50709 | Line Upgrade | 2029-12-30 | WMU-St Johns Lake 69 kV | WMU-Willmar Tap | 1 / 2 | 69 |  | Rebuild the 69 kV line from the WMU tap to the new St. John's breaker station to a double circuit line. | MN | 4 | 4 | M1 - Proposed | 3000000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | West | ND | 50430 | 50710 | Substation | 2028-05-31 | Souris |  |  | 115 |  | Install new bus tie breaker and upgrade limiting equipment at substation | ND |  |  | M1 - Proposed | 2000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50484 | 50711 | Transformer | 2029-12-30 | WMU-Priam 115 kV | WMU-Priam 69 kV | 2 | 115 | 69 | This project adds a second 115/69 kV transformer at the Priam substation near Willmar. | MN |  |  | M1 - Proposed | 4000000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | West | MN | 50431 | 50712 | Misc. | 2024-12-01 | High Bridge | Daytons Bluff | 1 | 115 |  | Relocate structures on High Bridge - Daytons Bluff 115kV line | MN | 2 |  | M1 - Proposed | 200000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50484 | 50715 | Substation | 2029-12-30 | WMU-Priam 115 kV |  |  | 115 |  | Expand the 115 kV substation bus for adding a second 115/69 kV transformer at the Priam substation. | MN |  |  | M1 - Proposed | 3700000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | West | MN | 50433 | 50716 | Substation | 2026-12-30 | Pine Island |  |  | 69 |  | Install new distribution substation in Pine Island Area to meet load growth in area | MN |  |  | M1 - Proposed | 8900000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50484 | 50717 | Substation | 2029-12-30 | WMU-Priam 69 kV |  |  | 69 |  | Expand the 69 kV substation bus for adding a second 115/69 kV transformer at the Priam substation. | MN |  |  | M1 - Proposed | 1300000 | MISSOURI RIVER ENERGY SERVICES - TRANSMISSION | Not Shared
A |  | West | MN | 50434 | 50718 | Transformer | 2027-05-03 | Meire Grove |  |  | 69 |  | Upgrade Meire Grove transformer 1 to support load growth | MN |  |  | M1 - Proposed | 6200000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50435 | 50719 | Substation | 2027-12-31 | East Mankato |  |  | 115 |  | Install new distribution substation in East Mankato area to meet load growth in area | MN |  |  | M1 - Proposed | 6700000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | WI | 50436 | 50720 | Line Upgrade | 2027-12-15 | Marshland | Winona |  | 69 |  | rebuild W3449 Marshland to Mississippi River | WI | 3.9 |  | M1 - Proposed | 7800000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50437 | 50721 | Substation | 2027-01-01 | Horseshoe Lake |  |  | 69 |  | Build new Horseshoe Lake Substation to transfer load from Richmond Substation | MN |  |  | M1 - Proposed | 8500000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | ND | 50438 | 50722 | Misc. | 2025-04-30 | Alexandria | Bison |  | 345 |  | Relocate 2 structures on Alexandria to Bison 345kV line | ND |  |  | M3 - Under Construction | 1897429 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50440 | 50724 | Substation | 2028-09-01 | West Maple Grove |  |  | 115 |  | Build new Substation in Northwest Maple Grove to accommodate load growth | MN |  |  | M1 - Proposed | 25000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50485 | 50725 | Line Upgrade | 2029-12-31 | Eden 41.6 kV | Grenville 41.6 kV | 1 | 42 |  | Rebuild 41.6 kV line between Eden 41.6 kV and Grenville 41.6 kV. | SD | 7 |  | M1 - Proposed | 1400000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | ND | 50486 | 50726 | Substation | 2026-12-31 | Casselton Town 115 kV |  |  | 115 |  | New 115 kV delivery to uprate Casselton town from 41.6 kV to 115 kV. | ND |  |  | M1 - Proposed | 1000000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | MN | 50487 | 50727 | Substation | 2026-12-31 | Bemidji Nymore 69 kV |  |  | 69 |  | New 69 kV breaker at Bemidji Nymore substation. | MN |  |  | M1 - Proposed | 350000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | Central | IN | 50488 | 50728 | Substation | 2026-12-01 | Stillwell |  |  | 345 |  | Upgrade Wave Trap and substation conductor on circuit 34501 Dumont to Stillwell | IN |  |  | M1 - Proposed | 601914 | NORTHERN INDIANA PUBLIC SERVICE COMPANY LLC | Not Shared
A |  | West | MN | 50442 | 50729 | Line Upgrade | 2028-12-29 | Richmond | Rich Springs |  | 69 |  | rebuild 2.6 miles of 69kV Line 5400 from Richfield to Rich Springs Tap | MN | 2.6 |  | M1 - Proposed | 2404191 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | WI | 50443 | 50730 | Substation | 2028-12-01 | Monroe County |  |  | 161 | 69 | Replace 4 breakers at Monroe county | WI |  |  | M1 - Proposed | 400000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50443 | 50731 | Transformer | 2028-12-01 | Monroe County |  |  | 161 | 69 | Replace TR01 and TR02 at Monroe county | MN |  |  | M1 - Proposed | 7600000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50445 | 50733 | Line Upgrade | 2029-06-01 | Lawrence | South Sioux Falls |  | 115 |  | Rebuild lines 0730 and 0729 Lawrence - South Sioux Falls | SD | 10 |  | M1 - Proposed | 10000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50445 | 50734 | Line Upgrade | 2029-06-01 | West Sioux Falls | South Sioux Falls |  | 115 |  | Sioux Falls 115kV Conversion. Rebuild lines 0730 and 0729 West Sioux Falls - South Sioux Falls | SD | 3 |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50445 | 50735 | Line Upgrade | 2029-06-01 | South Sioux Falls | Lincoln |  | 115 |  | Rebuild lines 0730 and 0729 South Sioux Falls - Lincoln to 115kV | SD | 3 |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50445 | 50736 | Substation | 2029-06-01 | South Sioux Falls | Lincoln |  | 115 |  | Convert Cliff Avenue 69kV substation to 115kV. | SD | 3 |  | M1 - Proposed | 15000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50445 | 50737 | Substation | 2029-06-01 | West Sioux Falls | Lincoln |  | 115 |  | Convert West Sioux Falls 69kV substation to 115kV | SD | 3 |  | M1 - Proposed | 10000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50445 | 50738 | Substation | 2029-06-01 | West Sioux Falls | Lincoln |  | 115 |  | Convert Lincoln 69kV substation to 115kV | SD | 3 |  | M1 - Proposed | 15000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | ND | 50449 | 50739 | Substation | 2029-10-15 | Roughrider |  |  | 115 |  | Install new distribution substation to meet load growth in Minot area | ND |  |  | M1 - Proposed | 7500000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50450 | 50740 | Transformer | 2028-12-31 | Wilmarth |  |  | 115 | 69 | Upgrade end of life Wilmarth TR7 and TR8 | MN |  |  | M1 - Proposed | 5000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | ND | 50451 | 50741 | Voltage Device | 2028-09-01 | Magic City |  |  | 230 | 115 | Install new reactor at Magic City | ND |  |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | ND | 50452 | 50742 | Voltage Device | 2027-12-01 | Peace Garden |  |  | 230 |  | Install new reactor at Peace Garden | ND |  |  | M1 - Proposed | 1500000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50453 | 50743 | Substation | 2028-12-01 | Prairie Island |  |  | 345 |  | Replace motor operated disconnects 8H10 and 8H12 with breakers | MN |  |  | M1 - Proposed | 3000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | SD | 50454 | 50744 | Line Upgrade | 2025-09-01 | Souris | West Sioux Falls | 1 | 69 |  | Replace steel poles on line 0730 Souris - West Sioux Falls | SD |  |  | M1 - Proposed | 1000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | ND | 50455 | 50745 | Voltage Device | 2026-01-01 | Prairie |  |  | 230 | 115 | Install new reactor at Prairie | ND |  |  | M1 - Proposed | 500000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50455 | 50746 | Substation | 2029-01-01 | Prairie |  |  | 230 | 115 | Substation upgrades to accommodate new reactor at Prairie including retirement of 3 capacitor banks. | MN |  |  | M1 - Proposed | 15500000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50456 | 50747 | Line Upgrade | 2029-01-01 | Fort Ridgley | Winthrop | 1 | 69 |  | Upgrade 69 kV lines Fort Ridgley-GRE Schilling Tap, Lafayette-GRE Lafayette, GRE Schilling Tap-GRE Lafayette Tap, and Winthrop-Lafayette | MN | 18 |  | M1 - Proposed | 14000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50457 | 50748 | Transformer | 2026-12-31 | Montrose |  |  | 69 |  | Install new distribution transformer to meet load growth in area | MN |  |  | M1 - Proposed | 7450000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50458 | 50749 | Substation | 2027-12-31 | Avon |  |  | 69 |  | Install new distribution substation to meet load growth in the Avon area | MN |  |  | M1 - Proposed | 10000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50459 | 50750 | Transformer | 2027-12-31 | Stewart |  |  | 69 |  | Install new Stewart distribution transformer 2 to meet load growth in area | MN |  |  | M1 - Proposed | 15000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50460 | 50751 | Transformer | 2031-12-01 | Prairie Island |  |  | 345 | 161 | Replace end of life Prairie Island TR10 | MN |  |  | M1 - Proposed | 7990300 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50461 | 50752 | Line Upgrade | 2029-01-01 | Le Sauk | St. Stephens | 1 | 115 |  | Rebuild 0868 from Le Sauk to Fisher Hills to St. Stephens | MN | 11 |  | M1 - Proposed | 12231418 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50489 | 50754 | Transformer | 2033-06-30 | Chanarambie |  |  | 345 | 115 | Add (2) 345/115kV transformers at Chanarambie | MN |  |  | M1 - Proposed | 10000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50489 | 50755 | Line New | 2033-06-30 | Split Rock | Chanarambie | 1 | 345 |  | New 345kV line Split Rock-Chanarambie | MN |  | 57.5 | M1 - Proposed | 125000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50489 | 50756 | Line Upgrade | 2033-06-30 | Pipestone | Chanarambie | 1 | 115 |  | Upgrade 115kV line Split Rock-Pipestone-Chanarambie. | MN | 12.2 |  | M1 - Proposed | 25000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | Central | IN | 50490 | 50757 | Line New | 2030-12-01 | Merom | New Customer |  | 345 |  | Construct a new 1.5-mile 345KV line from Merom station to new customer substation. | IN |  | 1.5 | M1 - Proposed | 6000000 | HOOSIER ENERGY | Not Shared
A |  | Central | IN | 50490 | 50758 | Substation | 2030-12-01 | Merom |  |  | 345 |  | Expand Merom 345kV station with additional 345kV bay. Install 345kV breaker and switches in new bay position at Merom 345kV station. | IN |  |  | M1 - Proposed | 8000000 | HOOSIER ENERGY | Not Shared
A |  | Central | IN | 50491 | 50759 | Substation | 2035-01-01 | Worthington | Bloomington |  | 345 |  | Construct new 345kV transmission station ring-bus along existing Worthington-Bloomington 345kV transmission line. | IN |  |  | M1 - Proposed | 20000000 | HOOSIER ENERGY | Not Shared
A |  | Central | IN | 50492 | 50760 | Substation | 2029-12-01 | Wheeler Creek |  |  | 138 |  | Expand Wheeler Creek Transmission Station to a ring-bus station to accept the 138 feeds from SIPC Hamilton and Ameren Kays. | IN |  |  | M1 - Proposed | 4700000 | HOOSIER ENERGY | Not Shared
A |  | Central | IL | 50493 | 50761 | Line Upgrade | 2028-12-01 | Ashland Tap | Cisne Junction |  | 69 |  | Ashland Tap - Cisne Junction is a 5.74 mile 69 kV line. The current conductor is 1/0, it will be upgraded to 477 ACSR. A new 3 way switch will be installed at Ashland Junction. | IL | 5.74 | 0 | M1 - Proposed | 9500000 | HOOSIER ENERGY | Not Shared
A |  | West | MN | 50494 | 50762 | Substation | 2026-12-01 | Monticello | Oakwood |  | 115 | 35 | Install new 115/34.5kV substation in Dayton area to meet area load growth. | MN |  |  | M1 - Proposed | 29600 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | IA | 50380 | 50763 | Line Upgrade | 2027-12-31 | ITCM Asset Blanket for 2026 | Throughout system |  | 345 | 69 | Replace aging and outdated equipment on a cycle that will ensure each system is replaced near its expected end of life. Modern equipment can improve reliability, use state of the art technology, and will typically use longer maintenance intervals which reduces maintenance costs. Equipment is commonly equipped with better monitoring and alarming functionality giving improved remote supervision. | IA |  |  | M1 - Proposed | 53875000 | ITC MIDWEST | Not Shared
A |  | West | IA | 50379 | 50764 | Line New | 2027-12-31 | Blanket for Customer Interconnections | Throughout system |  | 345 | 69 | These projects are being done at the request of an interconnection customer to facilitate new load, to re-distribute existing load, to improve the performance of the sub-transmission and distribution systems, or to accommodate a new Transmission-to-Transmission connection request. | IA |  |  | M1 - Proposed | 3750000 | ITC MIDWEST | Not Shared
A |  | West | IA | 50378 | 50765 | Line Upgrade | 2026-12-31 | Blanket for SCADA M.O. Switches for 2026 | Throughout system |  | 345 | 69 | ITC Midwest will add SCADA controlled motor operated switches on 69 kV lines that do not have existing remote sectionalizing capability and do not have any planned rebuilds. These 69 kV lines will be utilized to add SCADA controlled motor operated switches as part of an existing planned project to increase sectionalizing capability on the 69 kV system. ITC Midwest plans to install SCADA controlled motor operators on 3-5 lines/year as part of this program until existing circuits are brought up to ITC Midwest sectionalizing guidelines requirements. | IA |  |  | M1 - Proposed | 3125000 | ITC MIDWEST | Not Shared
A |  | West | IA | 50213 | 50768 | Line Upgrade | 2028-12-31 | Quad Cities Station | Rock Creek | 2 | 345 | 345 | Add 2nd Quad Cities - Rock Creek 345 kV line on existing spare position on existing structures. New line to be rated 3000 amps nominal. | IA |  |  | M1 - Proposed | 6405000 | ITC MIDWEST | Not Shared
A |  | West | IA | 50213 | 50769 | Line Upgrade | 2028-12-31 | Quad Cities Station | Rock Creek | 1 | 345 | 345 | Reconductor existing Quad Cities - Rock Creek 345 kV line to 3000 amp nominal conductor. | IA |  |  | M1 - Proposed | 6417500 | ITC MIDWEST | Not Shared
A |  | West | WI | 50495 | 50770 | Line Upgrade | 2029-06-11 | Fitzgerald |  |  | 138 |  | J1745 138kV Fitzgerald Substation Terminal Addition | WI |  |  | M1 - Proposed | 1017000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50495 | 50771 | Substation | 2029-06-11 | Fitzgerald |  |  | 138 |  | J1745 138kV Fitzgerald Interconnection Substation Interconnection Facilities | WI |  |  | M1 - Proposed | 1004000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | South | AR | 50496 | 50772 | Substation | 2026-10-31 | Sherwood |  |  | 115 |  | Sherwood 115kV Substation: Replace breakers B0350 and B0397 with new 3000A gas circuit breakers. Replace disconnect switch B0392. | AR |  |  | M1 - Proposed | 2132000 | ENTERGY ARKANSAS, LLC | Shared
A | A | Central | IN | 50728 | 51496 | Transformer | 2029-06-30 | Edwards |  |  | 345 | 138 | Adding a third bank to Edwards substation. It will be a 606MVA 345/138kV bank. | IN |  |  | M2 - Appendix A Approved | 15000000 | WABASH VALLEY POWER ASSOCIATION, INC. | Not Shared
A | B | Central | IL | 9740 | 21127 | Line Upgrade | 2029-12-01 | Grand Tower | Campbell Hill | 1 | 138 | 138 | Reconductor to 1200 A summer emergency capability. | IL | 7.94 |  | M1 - Proposed | 34900000 | AMEREN ILLINOIS | Not Shared
A | A | West | WI | 24919 | 28140 | Line Upgrade | 2027-10-01 | Mill Road | Granville |  | 345 | 138 | - Construct new 345/138 kV Mill Road SS, with one 500 MVA 345/138 kV transformer, - Loop in Granville – Arcadian 345 kV line and Cypress – Arcadian 345 kV line to new Mill Road 345 SS, Rebuild Mill Road SS – Granville SS section as 345 kV double circuit, - Loop in Germantown – Bark River 138 kV line and west portion of the Tamarack – Sussex 138 kV line into new Mill Road 138 kV SS, install series reactor in line to Sussex. - Construct new Mill Road SS – Tamarack SS – Butler SS 138 kV line, - Butler SS 138 kV reconfiguration, and install series reactor between Butler bus 1 and bus 2, - Granville SS 345 kV ring bus expansion, Replace 345/138 kV transformer T3. | WI |  |  | M2 - Appendix A Approved | 423705000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | IL | 25018 | 28149 | Substation | 2025-12-01 | Bootleg |  |  | 138 |  | The J1382 150MW Solar Interconnection Switching Station will split the existing Hutsonville-Neoga South-1 138 kV. | IL |  |  | M1 - Proposed | 8000000 | AMEREN ILLINOIS | Not Shared
A | B | West | MI | 24924 | 28170 | Substation | 2027-12-01 | Straits |  |  | 138 | 69 | Straits SS Power Transformer Asset Renewal | MI |  |  | M1 - Proposed | 11200000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 24982 | 28172 | Line Upgrade | 2028-06-01 | Range Line Dist | Range Line Switchyard | 61441 | 138 |  | Replace underground cable between Range Line Distribution SS and Range Line Switchyard. | WI |  |  | M1 - Proposed | 4000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 24925 | 28173 | Line Upgrade | 2028-06-01 | Range Line Dist | Range Line Switchyard | 61452 | 138 |  | Replace underground cable from Range Line Dist (WE) to Range Line Switchyard. | WI |  |  | M1 - Proposed | 6000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | MO | 25040 | 28191 | Transformer | 2030-12-01 | Tyson |  |  | 345 | 138 | Replace Tyson XFMR 3 with a new 345/138kV 700 MVA unit. | MO |  |  | M1 - Proposed | 8500000 | AMEREN MISSOURI | Not Shared
A | B | West | WI | 25161 | 28224 | Substation | 2029-06-30 | Sun Prairie Area |  |  | 138 | 69 | The Sun Prairie Area Reliability Project provides additional sources in the Sun Prairie Area to prevent thermal overloads due to multiple contingencies. Sun Prairie Area Reliability Project scope is as it follows: • Loop through Sun Prairie – Kegonsa (Y-81) 69-kV line in Reiner Road SS, constructing a 2-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Reiner Road SS. Finally, install new equipment due to asset renewal needs. • Loop through DeForest – Sun Prairie (Y-137) 69-kV line in Yahara River SS, constructing a 1.1-mile double circuited 69-kV line. In addition, install a new 138/69-kV transformer at Yahara River SS. Finally, install new equipment due to asset renewal needs. • Jumper replacements in Sun Prairie SS and additional modifications due to asset renewal needs. | WI |  |  | M1 - Proposed | 61450000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 21922 | 26530 | Line Upgrade | 2030-12-31 | Sigel | Vesper | Y-108/Y-107 | 69 |  | Sigel - Vesper 69 kV (Y-108/Y-107), Partial Rebuild | WI |  |  | M1 - Proposed | 5500000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | WI | 24474 | 27901 | Substation | 2027-07-15 | Winnebago County DIC |  |  | 69 |  | WPS is proposing to construct a new T-D substation with two new 69/12.47 kV transformers with circuit breakers. ATC will construct a 69 kV loop-through straight bus with two line switches with load breaks. ATC will also install two manual bus-tie switches and make provisions for a future bus-tie breaker. ATC will loop through the new substation from the Sunset Point – Oshkosh 69 kV (E-5) line on the line section between Sunset Point and Bowen St. | WI |  |  | M1 - Proposed | 2900000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | B | West | MN | 25264 | 28388 | Substation | 2027-12-31 | Ridgeview |  |  | 115 |  | Add two 115kV circuit breakers to existing Ring Bus to allow for a new 115/34.5 kV Transformer addition. | MN |  |  | M1 - Proposed | 2000000 | MINNESOTA POWER INC. | Not Shared
A | B | West | MN | 25267 | 28391 | Line Upgrade | 2028-12-31 | Hibbing | Maturi |  | 115 |  | Rebuild 115kV 180 Line (Hibbing -Maturi) with 636 ACSR. | MN |  |  | M1 - Proposed | 9750000 | MINNESOTA POWER INC. | Not Shared
A |  | Central | IL | 25269 | 28399 | Transformer | 2026-12-01 | West Frankfort East |  |  | 345 | 138 | At West Frankfort East substation replace the existing 560 MVA 345/138 kV Transformer 1 with a new 345/138 kV 700 MVA transformer | IL |  |  | M1 - Proposed | 10600000 | AMEREN ILLINOIS | Not Shared
A | B | West | WI | 25314 | 28400 | Substation | 2028-12-31 | Pittsville Area |  | X-42 | 138 |  | • ATC will construct ~9.6 miles of single circuit 138 kV transmission line to interconnect the proposed distribution substation. • ATC will construct a 138 kV loop-through straight bus with three line breakers to accommodate tapping X-42 and terminating the new line. | WI |  |  | M1 - Proposed | 35900000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | Central | MO | 25496 | 28758 | Substation | 2029-06-01 | Blanchette |  |  | 138 |  | Install a 4 position ring bus at Blanchette 138kV Substation. In addition, fiber will be installed to Kisker with some line re-routing. | MO |  |  | M1 - Proposed | 7000000 | AMEREN MISSOURI | Not Shared
A |  | Central | MO | 25497 | 28763 | Substation | 2027-12-01 | Overton |  |  | 161 |  | Rebuild the existing Overton 161kV straight bus as a breaker-and-a-half (BAAH) station. | MO |  |  | M1 - Proposed | 46000000 | AMEREN MISSOURI | Not Shared
A | B | South | MS | 25502 | 28767 | Line Upgrade | 2027-03-01 | Lake | Decatur |  | 69 |  | A complete rebuild of Line 4B and line extension to the existing Decatur Substation (Lake – Decatur 69kV) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Lake and Decatur. | MS |  |  | M1 - Proposed | 10430000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | South | MS | 25541 | 28768 | Line Upgrade | 2026-04-01 | Newton | Decatur |  | 69 |  | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 9.7 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | MS |  |  | M1 - Proposed | 5975000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A | B | South | MS | 25541 | 28769 | Line New | 2026-04-01 | Decatur |  |  | 69 |  | A complete rebuild of Line 5 and line extension to the existing Decatur Substation (Newton – Decatur 9.7 mi.) is recommended. This project will increase reliability of the transmission system and provide an OPGW communication link between Newton and Decatur. | MS |  |  | M1 - Proposed | 125000 | SOUTH MISSISSIPPI ELECTRIC POWER ASSOCIATION | Not Shared
A |  | East | MI | 20020 | 25705 | Line Upgrade | 2029-12-31 | Gaylord | Mio Dam | 1 | 138 |  | Rebuild the Gaylord – Mio Dam 138kV line with 954 ACSR overhead conductor capable of double circuit 230kV. OPGW will be installed on the rebuild. | MI | 40.5 |  | M1 - Proposed | 86900000 | METC | Not Shared
A |  | East | MI | 20020 | 25706 | Line Upgrade | 2029-12-31 | Gaylord |  |  | 138 |  | Upgrade terminal station equipment | MI |  |  | M1 - Proposed | 189000 | METC | Not Shared
A |  | East | MI | 20020 | 25707 | Line Upgrade | 2029-12-31 | Mio Dam |  |  | 138 |  | Upgrade terminal station equipment | MI |  |  | M1 - Proposed | 165000 | METC | Not Shared
A |  | Central | IL | 50118 | 50188 | Substation | 2025-12-01 | Powerton |  |  | 345 |  | This transmission project will consist of all network upgrades required to relieve the overloaded Powerton-Tazewell 345 kV transmission line caused by PJM project AE1-163. | IL |  |  | M1 - Proposed | 1500000 | AMEREN ILLINOIS | Shared
A |  | Central | IL | 50119 | 50189 | Substation | 2028-06-30 | Moro | Cottage Hills |  | 138 |  | These Common Use Upgrades consist of equipment for all the substation and transmission line upgrades to support New Moro-Cottage Hills MPFCA. Add 138 kV position at Moro, expand Cottage Hills to a 4 pos., 6 ult. ring bus. Add second circuit between Moro and Cottage Hills on existing ROW utilizing DC structures. Rebuild Moro to Laclede N Tap, Cottage Hills to Laclede S tap and Laclede S tap to Mississippi tap. | IL |  |  | M1 - Proposed | 38550000 | AMEREN ILLINOIS | Not Shared
A |  | Central | MO | 50631 | 51342 | Line New | 2029-12-01 | Loose Creek | Barnett |  | 345 |  | 40 mile single circuit line from Loose Creek-Barnett | MO |  | 40 | M1 - Proposed | 1 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | Central | MO | 50631 | 51343 | Substation | 2029-12-01 | Barnett |  |  | 345 | 161 | New 345/161 kV substation at Barnett | MO |  |  | M1 - Proposed | 16000000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | Central | MO | 50631 | 51344 | Line Upgrade | 2030-12-01 | Overton | Barnett |  | 345 | 161 | Convert existing 38 mile 345 and 161 kV double circuit line from Overton to Barnett. | MO |  | 38 | M1 - Proposed | 107000000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | Central | MO | 50631 | 51345 | Substation | 2030-12-01 | Clinton |  |  | 345 |  | New Clinton 345 kV Substation | MO |  |  | M1 - Proposed | 16000000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | Central | MO | 50631 | 51346 | Line New | 2030-12-01 | Clinton | Lacygne |  | 345 | 345 | New 50 mile double circuit 345 kV line from Clinton to LaCygne. | MO |  | 50 | M1 - Proposed | 205000000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | Central | MO | 50631 | 51352 | Line New | 2030-12-01 | Barnett | Clinton |  | 345 |  | New 65 mile double circuit 345 kV line from Barnett to Clinton | MO |  | 65 | M1 - Proposed | 260000000 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | Central | IL | 50637 | 51356 | Substation | 2026-10-01 | SIPC Jackson Substation |  |  | 161 |  | 161 kV Switchyard | IL |  |  | M1 - Proposed | 9389000 | Southern Illinois Power Cooperative | Not Shared
A |  | West | WI | 50642 | 51362 | Misc. | 2026-12-31 | Various |  |  | 0 |  | Installation of Edge computing hardware at multiple substation locations. Scope includes edge compute interoperability with physical security cameras, rogue detection sensors and asset monitor devices. | WI |  |  | M1 - Proposed | 3000000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50655 | 51380 | Misc. | 2026-09-30 | Edgewater |  |  | 345 |  | 345 kV CT contributions, bus 3 differential relay panel, wiring updates in the bus 3 differential relay panel to support Edgewater Unit 5 GSU high side circuit breaker installation | WI |  |  | M1 - Proposed | 225000 | AMERICAN TRANSMISSION COMPANY | Shared
A |  | West | WI | 50655 | 51381 | Misc. | 2026-09-30 | Edgewater |  |  | 345 |  | 345 kV Transmission Owner System Protection Facilities - System Protection Setting Modifications and Supporting Activities | WI |  |  | M1 - Proposed | 35000 | AMERICAN TRANSMISSION COMPANY | Shared
A | A | Central | MO | 50616 | 51382 | Substation | 2026-12-01 | Rootbeer |  |  | 345 |  | Add 345 kV position at Rootbeer substation | MO |  |  | M2 - Appendix A Approved | 2000000 | AMEREN MISSOURI | Not Shared
A | A | Central | IL | 50636 | 51383 | Line Upgrade | 2027-12-01 | Towerline | San Jose Rail |  | 138 |  | Towerline-San Jose Rail-increase line capacity | IL |  |  | M2 - Appendix A Approved | 0 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A | A | Central | MO | 50636 | 51384 | Line Upgrade | 2027-12-01 | Austin | Yvonne |  | 138 |  | Austin-Yvonne 138 kV increase line capacity | MO |  |  | M2 - Appendix A Approved | 0 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A | A | Central | MO | 50636 | 51385 | Line Upgrade | 2027-12-01 | Yvonne | Taylorville S |  | 138 |  | Yvonne-Taylorville 138kV increase line capacity | MO |  |  | M2 - Appendix A Approved | 0 | AMEREN TRANSMISSION COMPANY OF ILLINOIS | Not Shared
A |  | West | WI | 50670 | 51402 | Misc. | 2027-04-15 | Werner |  |  | 138 |  | Asset renewal of Werner control house and 138kV relay asset renewal at Werner, Werner West and White Lake SS. Install an additional breaker and eliminate two S&C Mark VI circuit switchers when replacing cap bank relaying at Werner. | WI |  |  | M1 - Proposed | 5300000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50673 | 51411 | Line Upgrade | 2027-06-30 | Portage | Columbia |  | 138 |  | This project resolves thermal overloads under single contingency conditions on either the X-13 or X-20 lines between Portage and Columbia. | WI |  |  | M1 - Proposed | 17296600 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | South | LA | 50675 | 51413 | Substation | 2027-12-01 | Hollywood | Orange |  | 138 |  | Substation including breakers and Capacitor bank | LA |  |  | M2 - Appendix A Approved | 24100000 | ENTERGY SERVICES, LLC. | Not Shared
A | A | South | LA | 50671 | 51414 | Substation | 2028-08-30 | RiverPlex |  |  | 500 | 230 | 500 kV ring bus and 6 bay breaker and a half 230 kV station | LA |  |  | M2 - Appendix A Approved | 284000000 | ENTERGY SERVICES, LLC. | Not Shared
A |  | West | MN | 50153 | 50773 | Voltage Device | 2027-01-01 | West Owatonna |  |  | 161 |  | 47MVAr Cap Bank located on 161kV bus to mitigate low voltage scenarios from P6 contingencies in the area. | MN |  |  | M1 - Proposed | 3500000 | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
A | A | West | IA | 50497 | 50774 | Substation | 2027-09-30 | Hills |  |  | 345 |  | Add new 345 kV line terminal at Hills to accommodate the new ITCM Hills-Beverly 345 kV line | IA |  |  | M2 - Appendix A Approved | 12000000 | MIDAMERICAN ENERGY CO. | Not Shared
A | A | West | IA | 50497 | 50775 | Line Upgrade | 2027-09-30 | Morgan Valley | Tiffin | 1 | 345 |  | Replace transmission structures to increase the rating of the Morgan Valley-Tiffin 345 kV line | IA |  |  | M2 - Appendix A Approved | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | A | West | IA | 50497 | 50776 | Line Upgrade | 2027-09-30 | Hills | Tiffin | 1 | 345 |  | Replace transmission structures to increase the rating of the Hills-Tiffin 345 kV line | IA |  |  | M2 - Appendix A Approved | 2500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | A | West | IA | 50497 | 50777 | Line Upgrade | 2028-12-31 | Sub 91 | Utica Ridge | 1 | 161 |  | Replace transmission structures to increase the rating of the Sub 91-Utica Ridge 161 kV line | IA |  |  | M2 - Appendix A Approved | 200000 | MIDAMERICAN ENERGY CO. | Not Shared
A | A | West | IA | 50497 | 50778 | Line Upgrade | 2028-12-31 | Sub 91 |  |  | 161 |  | Replace limiting equipment on the Sub 91-Utica Ridge and Sub 91-QC Enron 161 kV line terminals to increase the rating of each line | IA |  |  | M2 - Appendix A Approved | 500000 | MIDAMERICAN ENERGY CO. | Not Shared
A |  | West | MN | 50500 | 50779 | Line Upgrade | 2029-06-01 | Byron | Pleasant Valley | 1 | 161 |  | Upgrade Byron - Pleasant Valley 161kV Line | MN | 16.6 |  | M1 - Proposed | 20000000 | NORTHERN STATES POWER COMPANY | Not Shared
A |  | West | MN | 50501 | 50780 | Substation | 2027-12-01 | Byron |  |  | 161 |  | Upgrading Terminal equipment of line to 3000A. | MN |  |  | M1 - Proposed | 1500000 | SOUTHERN MINNESOTA MUNICIPAL POWER AGENCY | Not Shared
A |  | Central | IN | 50502 | 50781 | Substation | 2025-12-31 | Brownsburg East |  |  | 138 |  | New WVPA 138kV, 4 position ring bus substation to serve load | IN |  |  | M1 - Proposed | 8600000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IN | 50503 | 50782 | Line New | 2025-12-31 | Winding Ridge | Pleasant Acres |  | 138 |  | Second 138 kV feed from Winding Ridge to Pleasant Acres. Cost accounted for in MTEP 24293. | IN |  | 0.1 | M1 - Proposed | 2000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | Central | IL | 50504 | 50783 | Substation | 2026-12-01 | Dupo Ferry Road |  |  | 138 |  | Dupo Ferry 138kV Breakers Upgrade - Replace 4 overstressed 138kV circuit breakers, existing interrupting capability 40kA, with 50kA new breakers 3000A minimum continuous | IL |  |  | M1 - Proposed | 2500000 | AMEREN ILLINOIS | Not Shared
A |  | West | WI | 50505 | 50784 | Substation | 2025-12-09 | Holland |  |  | 138 |  | Protective relays will require new programming to protect line GT104 as a three-terminal line. Minor fiber jumper connection changes within the Transmission Owner’s existing fiber patch panel may need to be made for Transmission Owner’s relays to communicate with both the Customer’s relays along with the relays located in the existing Onion River Collector Substation (J1153). | WI |  |  | M1 - Proposed | 142000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50506 | 50785 | Substation | 2029-06-11 | North Monroe |  |  | 138 |  | The 138 kV yard at North Monroe Substation will be expanded to accommodate a generation collection facility addition to the power system. A new 138 kV line terminal will be built to the south requiring the yard to be expanded to the south 25 feet. Relay protection and control will be added for the new breaker and line position. | WI |  |  | M1 - Proposed | 1523000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50506 | 50786 | Substation | 2029-06-11 | North Monrow |  |  | 138 |  | The J1706 interconnection will consist of jumpers and equipment to connect the Interconnection Customer’s Transmission Line equipment with the Transmission Owner’s rigid bus. A line disconnect switch, breaker, and bus side disconnect switch will isolate the line from the 138 kV bus. Any shielding wire for interconnection Customer facilities will terminate at the dead-end vangs. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility | WI |  |  | M1 - Proposed | 686000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50506 | 50787 | Substation | 2029-06-11 | Elkhorn |  |  | 138 |  | The existing Elkhorn substation work will consist of upgrading the 138 kV X-55 line and bus jumpers entering the substation. | WI |  |  | M1 - Proposed | 216000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50506 | 50788 | Substation | 2029-06-11 | North Lake Geneva |  |  | 138 |  | The existing North Lake Geneva substation work will consist of upgrading the 138 kV X-55 line and bus jumpers entering the substation and 138 kV Bus 8B1 strain span. | WI |  |  | M1 - Proposed | 381000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50506 | 50789 | Line Upgrade | 2029-06-11 | Elkhorn | North Lake Geneva | X-55 | 138 |  | The X-55 138 kV Transmission Line Partial Rebuild project will consist of installing approximately 8 miles of T2-477 26/7 ACSR Hawk conductor per ATC design standards to achieve a minimum 1229 Amps (294 MVA) normal and 1682 Amps (402 MVA) emergency ratings for all seasons. The Transmission Owner will retain ownership of the line segment, support poles and Interconnection Facility. | WI | 8 |  | M1 - Proposed | 15460000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50790 | Substation | 2029-03-13 | Galvin Ave |  |  | 115 |  | New 115 kV Interconnection Switching Station that is to be arranged with 3 positions, 3 138 kV circuit breakers ring bus, with 1 generator lead line position, and 2 transmission line positions. The new station will also include a control house. | WI |  |  | M1 - Proposed | 8976000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50791 | Line New | 2029-03-13 | McMillan | Stratford South | B-54 | 115 |  | The existing B-54 115kV line between McMillan and Stratford South Substations will be tapped and looped into the new 115kV Interconnection Switching Station to provide transmission access. Existing structure 118 will be removed, and two (2) 138kV single circuit vertical monopole dead-end steel structures will be installed on the existing alignment between existing structures 119 and 117. New conductor, shield wire, and OPGW will be utilized to tap and loop the B-54 line into the new switching station. The Transmission Owner will retain ownership of the line segments, support poles and Interconnection Facility. | WI |  |  | M1 - Proposed | 998000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50792 | Misc. | 2029-03-13 | Arpin |  | U-14 | 115 |  | At Arpin substation, the existing U-14 relay panel will be removed from service and saved as system spare for future use. A new line protection relay panel will be installed for line U-14. A new module will be installed in existing ATC communication cabinet. | WI |  |  | M1 - Proposed | 266000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50793 | Misc. | 2029-03-13 | Hume |  |  | 115 |  | At Hume substation, CCVT/ wave trap/ line tuner will be installed at line A-157 and P-120. Secondary line protection packages of existing A-157 will be modified to utilize power line carrier. Existing P-120 line panel N4 will be removed and new line relay panel will be installed for line P-120. | WI |  |  | M1 - Proposed | 754000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50794 | Misc. | 2029-03-13 | McMillan |  |  | 115 |  | At McMillan substation, CCVT/ wave trap/ line tuner will be installed at line B-54 and N-144. A module will be installed and secondary line protection packages of existing B-54 and N-114 on both relay panels and will be modified to utilize power line carrier. In addition, existing relay will be removed and replaced on B-54 line panel. | WI |  |  | M1 - Proposed | 684000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50795 | Misc. | 2029-03-13 | Mill Creek |  |  | 115 |  | At Mill Creek substation, one new CCVT/ wave trap/ line tuner will be installed at line P-120. Existing line P-120 relay panel W-6 and U-14 panel W-7 will be removed. A new line relay panel will be installed for line P-120. A new line relay panel will be installed for line U-14. The existing wall mount ATC communications cabinet will be removed, and a new ATC communication cabinet will be installed in open position with the existing router relocated. | WI |  |  | M1 - Proposed | 767000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50796 | Misc. | 2029-03-13 | Wien |  |  | 115 |  | At Wein substation, one new CCVT/ wave trap/ line tuner will be installed at line B-54. Existing line B-54 relay panel S3 will be removed. A new line relay panel will be installed for line B-54. New module will be installed in existing ATC communication cabinet to establish communication ring. SEL-ICON at Wein substation will establish connection to SEL-ICON at Interconnection substation using existing fiber being cut-in at Interconnection Switching Station. | WI |  |  | M1 - Proposed | 592000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50797 | Misc. | 2029-03-13 | Wildwood |  |  | 115 |  | Existing A-157 and N-144 line CCVT will be removed. New CCVT/ wave trap/ line tuner will be installed at line A-157 and N-144. Line protection packages at existing A-157 and N-144 line panel will be modified to utilize power line carrier communication. | WI |  |  | M1 - Proposed | 605000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50507 | 50798 | Substation | 2029-03-13 | Galvin Ave |  |  | 115 |  | The J1508 Transmission Owner Interconnected Facilities consists of substation work associated with the Generator Lead Line entrance at the new interconnection Switching Station. | WI |  |  | M1 - Proposed | 452000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | IL | 50190 | 50799 | Substation | 2027-10-01 | Lima |  |  | 138 |  | Construct the new Lima substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. near Peru, IL. | IL |  |  | M2 - Appendix A Approved | 8000000 | AMEREN ILLINOIS | Not Shared
A | A | Central | IL | 50190 | 50800 | Substation | 2029-06-01 | Backbone |  |  | 138 |  | Rebuild the existing Princeton substation as a 4-position 138 kV substation in a ring bus configuration with two additional positions available for future expansion. | IL |  |  | M2 - Appendix A Approved | 8000000 | AMEREN ILLINOIS | Not Shared
A |  | West | WI | 50508 | 50801 | Substation | 2030-09-10 | Welsh Prairie |  |  | 345 |  | The new J1629 Interconnection Switching Station will be arranged in a three-breaker ring bus configuration with one generation position and two-line positions. The station will be capable of future expansion to an ultimate 6 position ring bus if future generation positions are added. The new J1629 interconnection switching station will bisect the Transmission Owner’s overhead W-5 345 kV transmission line between existing Columbia and South Fond du Lac substations in two segments, W-TBD and W-5. | WI |  |  | M1 - Proposed | 16826000 | AMERICAN TRANSMISSION COMPANY | Shared
A |  | West | WI | 50508 | 50802 | Misc. | 2030-09-10 | Welsh Prairie |  | W-56 | 345 |  | The existing relay protection for the 345kV line W-5 is presently using fiber through a ICON network as a relay communication path. Sectionalizing the line requires the ICON fiber network to be brought into the new substation to maintain this configuration. The existing ICON fiber network does not run along W-5. The ICON fiber network is on the Y-64 line which is north of the proposed J1629 Switching Station. The fiber ICON ring segment between South Fond du Lac Substation and Columbia Substation includes OPGW over Y-64 from structure 100076 at Y-64 ACEC Cambria Tap to the Rio Pumping Station. The existing fiber network will be tapped at splice box on structure 100075. From there the fiber will be routed to J1629 Switching Station by underground fiber buried along road ROW. Total fiber route is approximately 3 miles. | WI |  |  | M1 - Proposed | 1661000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | WI | 50508 | 50803 | Line New | 2030-09-10 | South Fond Du Lac | Columbia | W-5 | 345 |  | The W-5 345 kV Transmission Line Loop-In project will consist of installing two new single-circuit 90deg dead-end poles between structures 111 and 112, that will allow existing line W-5 to run through the Transmission Owner’s new switchyard, segmenting the line into W-5 towards South Fond Du Lac (SFL) and W-TBD towards Columbia (COL). The Transmission Owner will retain ownership of the line segments, support poles and Interconnection Facility. | WI |  |  | M1 - Proposed | 1994000 | AMERICAN TRANSMISSION COMPANY | Shared
A |  | West | WI | 50508 | 50804 | Substation | 2030-09-10 | Welsh Prairie |  |  | 345 |  | The J1629 TOIF will consist of jumpers and equipment to connect the Interconnection Customer’s Generator Lead Line equipment with the Transmission Owner’s rigid bus. The Transmission Owner will retain ownership of the dead-end, jumpers, switch, arresters and Interconnection Facility. | WI |  |  | M1 - Proposed | 980000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A |  | West | MN | 50510 | 50806 | Substation | 2030-12-31 | Bellingham 115 kV |  |  | 115 |  | New 115 kV delivery for town of Bellingham by tapping the Big Stone to Marietta 115 kV line. | MN |  |  | M1 - Proposed | 650000 | OTTER TAIL POWER COMPANY | Not Shared
A |  | West | IA | 50329 | 51468 | Line New | 2028-12-31 | Substation 91 | Utica Ridge | 1 | 161 |  | Reterminate the Sub 91-Utica Ridge 161 kV line on a new 161 kV line terminal at Sub 91. | IA |  |  | M1 - Proposed | 1500000 | MIDAMERICAN ENERGY CO. | Not Shared
A | A | Central | IN | 50718 | 51469 | Line Upgrade | 2029-06-01 | Cayuga | Nucor |  | 345 |  | Line rebuild (~32.3mi) to bundled 954ACSS conductor or 4000A equivalent. | IN | 32.3 |  | M2 - Appendix A Approved | 95529061 | DUKE ENERGY INDIANA, LLC | Shared
A | A | Central | IN | 50719 | 51470 | Line Upgrade | 2029-06-01 | Nucor | Wolf Creek |  | 345 |  | Line rebuild (~14mi) to bundled 954ACSS conductor or 4000A equivalent. | IN | 14 |  | M2 - Appendix A Approved | 49000000 | DUKE ENERGY INDIANA, LLC | Shared
A |  | West | MN | 50720 | 51471 | Line Upgrade | 2030-09-30 | Quarry | Monticello | 1 | 345 |  | Like-for-like age and condition replacement of select steel davit arms on line 0973 - Quarry to Monticello. | MN | 28.8 | 0 | M1 - Proposed | 12500000 | NORTHERN STATES POWER COMPANY | Shared
A | A | Central | IN | 50722 | 51476 | Substation | 2029-06-01 | Pond Creek |  |  | 345 |  | 345 kV portion of Substation | IN |  |  | M2 - Appendix A Approved | 20000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | A | Central | IN | 50722 | 51477 | Substation | 2029-06-01 | Pond Creek |  |  | 138 |  | 138 kV Portion of Pond Creek Substation | IN |  |  | M2 - Appendix A Approved | 10000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | A | Central | IN | 50722 | 51478 | Transformer | 2029-06-01 | Pond Creek |  |  | 345 | 138 | Transformation at Pond Creek | IN |  |  | M2 - Appendix A Approved | 10000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A |  | West | WI | 50724 | 51479 | Line Upgrade | 2026-12-26 | North Appleton | Werner West | NAPL31 | 345 |  | Line Clearance | WI |  |  | M1 - Proposed | 5300000 | AMERICAN TRANSMISSION COMPANY | Not Shared
A | A | Central | IN | 50725 | 51482 | Line Upgrade | 2029-06-01 | Tipton West | Cammack Rd Jct |  | 230 |  | ~11.8mi of 23008 line from Tipton West to Cammack Rd Jct to bundled 954ACSS conductor or 4000A equivalent | IN | 11.8 |  | M2 - Appendix A Approved | 29500000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | A | Central | IN | 50725 | 51483 | Line Upgrade | 2029-06-01 | Kokomo Highland Park | Tipton West |  | 230 |  | ~14.4mi of 23032 line from Kokomo Highland Park to Tipton West to bundled 954ACSS conductor or 4000A equivalent | IN | 14.4 |  | M2 - Appendix A Approved | 36000000 | DUKE ENERGY INDIANA, LLC | Not Shared
A | A | Central | IN | 50723 | 51494 | Substation | 2028-12-31 | Petersburg |  |  | 138 |  | Replace wave trap and jumpers at Petersburg | IN |  |  | M2 - Appendix A Approved | 4000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared
A | A | Central | IN | 50727 | 51495 | Transformer | 2029-12-31 | Thompson | Thompson |  | 345 | 138 | 500 MVA, 345 : 138n kV Autotransformer | IN |  |  | M2 - Appendix A Approved | 15000000 | INDIANAPOLIS POWER & LIGHT COMPANY | Not Shared

## hiddenSheet (hidden)
miso_project:wc6o/qLmZUvQFWCAceGW9BjASCKdQmVcYtSHXMekRp5EjsdejIxexQNybZh5poj4wJYMJuiSmNnncEEnLgcXPQ==:miso_projectid=%28Do%20Not%20Modify%29%20Project&checksumLogicalName=%28Do%20Not%20Modify%29%20Row%20Checksum&modifiedon=%28Do%20Not%20Modify%29%20Modified%20On&miso_planningregioncode=Planning%20Region&miso_mtepprojectid=MTEP%20Project%20ID&miso_name=Project%20Name&miso_projectdescription=Project%20Description&miso_states=State%28s%29&miso_submittingtoid=Submitting%20TO&miso_projecttypeid=Project%20Type&miso_othertypeid=Other%20Type&miso_expectedisdrollupdate=Expected%20ISD&miso_maxkv=Max%20kV&miso_currentcost=Current%20Cost
Central | East | South | West